## Issues_without_manufacturer_FG_
issue_code | project_name | region | issue_status | priority | reported_by | reported_on | responsibility_name | cx_level | issue_type | issue_category | discipline | asset_type | asset_name | equipment_type_name | manufacturer | model_number | description | issue_url | system_url
GI-017 | AM04-P3 | N-EMEA | Ready for Verification | P2 Medium CX | bjorn.ketelaar@eu.equinix.com | 2026-07-02 04:00:00.000 +0400 | Vendor- Manufacturer |  | Installation Damage | Commissioning | [6 empty] | GSCP has sustained transport damage not clear if internal components are operational, Cummins to verify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627803&prj=620&rqi=rCQSgQNdd3bXb8xoV5XF99bc14
GI-011 | AM04-P3 | N-EMEA | Closed | Outstanding Paperwork/Documentation | Willem.Zwaagstra@eu.equinix.com | 2026-06-03 04:00:00.000 +0400 | Vendor- Manufacturer |  | General Design Issue | Design | [6 empty] | Following site observations, Equinix would like to clarify the specification and compliance, particularly for the flange connections used in the cooling water piping. It appears that some of the flanges may have been fabricated, rather than standard manufactured flanges. As this system is part of a pressurized installation, we need to confirm that all installed components comply with the relevant pressure equipment standards. Additionally, based on observations in a previous project phase (AM4.P2), similar flange connections in comparable positions also appeared relatively light compared to the mating equipment flanges. However, in the current AM4.P3 installation, this difference appears more pronounced, with visibly thinner flanges being applied. Could you please confirm: - Which standards these flanges are designed and manufactured to (e.g. EN / ASME, pressure class / PN rating, DN designation); - That the flanges are suitable for the operating pressure and conditions of the system; - Whether the required markings (including DN, pressure class, and material/specification) are applied or otherwise traceable. This information is required to ensure compliance and to verify that the installation is suitable for safe and reliable long-term operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623916&prj=620&rqi=E1kmH2iqSuTtCFjHuuk6nmubH3
GI-007 | AM04-P3 | N-EMEA | Work Completed | P2 Medium CX | christiaan.Gillot@se.com | 2026-04-30 04:00:00.000 +0400 | Vendor- Manufacturer |  | Commissioning Issue | Commissioning | [6 empty] | extra terminals for supply loop XM144 XM145 k205 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620034&prj=620&rqi=Dwg3tmBK0UpQrBtWSK0d9qJ8aA
GI-019 | AT10x-1 | AMER | Open | P3 Low CX | christopher_boyle@fsttechnical.com | 2026-06-30 04:00:00.000 +0400 | VER - Vertiv |  | Installation not complete | Commissioning | [6 empty] | Containment bonding missing throughout Ehouses sparaticly. Please see attached examples of missing bonding throughout multiple Ehouses. Once all bonding is complete please coordinate a walk with Vertiv and FST to verify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627617&prj=601&rqi=nKwx3BUZmPAOQl0YphkICahukT
GI-007 | AT10x-1 | AMER | Closed | P3 Low CX | christopher_boyle@fsttechnical.com | 2026-06-29 04:00:00.000 +0400 | Electrical Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | 1GEN Torque report document issues please see attached red lined report. Affected reports -1GEN_R3 -1GEN_P -1GEN_Q -1GEN_S -1GEN_U -1GEN_V -1GEN_R4 -1GEN_W -1GEN_AA -1GEN_BB -1GEN_CC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627257&prj=601&rqi=d4JeaGLZPuRDVY40S0oRBkpm1r
SOR-57-001 | AT10x-1 | AMER | Open | P3 Low CX | eric_reinhard@fsttechnical.com | 2026-06-11 04:00:00.000 +0400 | Fire Contractor |  | Installation not correct | Commissioning | [6 empty] | Fire Pump Fuel Tank. Fuel line is called out in drawing #FP401-FPH, Detail 10 to have a "1/2 CL BLK nipple and electronically supervised ball valve or potter rbvs tamper switch". Inspection of the tank found that there is not a tamper switch installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635681&prj=601&rqi=IALb6T5wbfkplV0SuuSqZt3HxK
GI-011 | AT10x-1 | AMER | Closed | P2 Medium CX | christopher_boyle@fsttechnical.com | 2026-06-10 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MPZ_L_2 | PP - Power Panel |  |  | loose strands and broken strand in terminal on main circuit breaker to transformer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624781&prj=601&rqi=cr7xqmJQQ35jmcAkVfa1Oxt83H
GI-016 | AT10x-1 | AMER | Closed | P3 Low CX | christopher_boyle@fsttechnical.com | 2026-06-10 04:00:00.000 +0400 | VER - Vertiv |  | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MPZ_R2_1 | PP - Power Panel |  |  | ground cables not labeled inside asset or at earth bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624795&prj=601&rqi=CCPQ0iF6SCf2Ci5ewc9AYfU8Tu
GI-012 | AT10x-1 | AMER | Closed | P3 Low CX | christopher_boyle@fsttechnical.com | 2026-06-10 04:00:00.000 +0400 | VER - Vertiv |  | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MPZ_L_2 | PP - Power Panel |  |  | Ground cables not labeled inside asset and not labeled at earth bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624782&prj=601&rqi=dUMg4LInvJLKFGpAAodIvFYhny
RT1ELEC-2341-003 | AT10x-1 | AMER | Closed | P2 Medium CX | joseph_donnelly@fsttechnical.com | 2026-06-09 04:00:00.000 +0400 | Electrical Contractor | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1MPZ_L_2 | PP - Power Panel |  |  | Extension toe for neutral connection to terminal block loose. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624614&prj=601&rqi=A5cnfA1HuPXePpWhip9O7OLyMx
RT1ELEC-2341-001 | AT10x-1 | AMER | Closed | P2 Medium CX | joseph_donnelly@fsttechnical.com | 2026-06-09 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MPZ_L_2 | PP - Power Panel |  |  | cable strands damaged/exposed on main breaker tx side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624593&prj=601&rqi=jhYI7nTut1OrxMkyVqiWTXT9k9
RT1ELEC-2341-002 | AT10x-1 | AMER | Closed | P3 Low CX | joseph_donnelly@fsttechnical.com | 2026-06-09 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MPZ_L_2 | PP - Power Panel |  |  | latch on door damaged/loose. Will not hold open. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624594&prj=601&rqi=fhr6ln5YCqX80mKUKTAMfhyZSl
GI-005 | AT10x-1 | AMER | Closed | P2 Medium CX | eric_reinhard@fsttechnical.com | 2026-06-02 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | [6 empty] | The underground electrical duct terminations with pulled cable should be provided with temporary closure per spec 26 0543.3.5.I. "Sealing: Provide temporary closure at terminations of duct with pulled cables. Seal spare duct at terminations. Use sealing compound and plugs to withstand at least 15-psig hydrostatic pressure" This should be corrected site wide. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623708&prj=601&rqi=CzMGYczNZQwzM4p4fFTsVpNPbL
GI-004 | AT10x-1 | AMER | Closed | P2 Medium CX | eric_reinhard@fsttechnical.com | 2026-05-26 04:00:00.000 +0400 | VER - Vertiv Electrical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Per Equinix, opening issue for tracking purposes given the following concerns brought up in E-house permitting & Fire Protection meeting on 5/26/26: â€¢ Vertiv to share the Industrial Building Permit documents, and confirm the status of approvals and inspections. o Stamped EoR drawings showing final installation to be confirmed o Once shared, Northstar will coordinate this with the fire marshall | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623166&prj=601&rqi=zP2K7krOG3rtYWlJo864vAaJDz
RT1ELEC-2374-001 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-22 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1MPZ_AA_2 | PP - Power Panel |  |  | One of the leads heading to the transformer (480v) is not landed correctly, one half of the wire strains were in the breaker and it pulled right out. The other two leads are done very poorly.. The leaving leads (120v) coming from the transformer also have a lot of stray strains. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622810&prj=601&rqi=kt6vbUcX2WNub6LHX9pkzcz6Ke
GI-002 | AT10x-1 | AMER | Closed | P3 Low CX | eric_reinhard@fsttechnical.com | 2026-05-20 04:00:00.000 +0400 | Commissioning Authority |  | CxA Miss | Commissioning | [6 empty] | Facility Grid Training Session - Test Issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622424&prj=601&rqi=dtbakhrPKro0RvJP8GRVFwMtPJ
RT1ELEC-2380-001 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-20 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MPZ_CC_2 | PP - Power Panel |  |  | This panel is missing 2 covers, the main dead front to protect the breaker area and the other smaller dead front that protects the 90amp breaker feeding the transformer above. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622478&prj=601&rqi=FlXNRlc32dhIBmeQZRlvcxQAVa
GI-001 | AT10x-1 | AMER | Closed | P2 Medium CX | eric_reinhard@fsttechnical.com | 2026-05-14 04:00:00.000 +0400 | General Contractor |  | CxA Miss | Commissioning | [6 empty] | marvair units sitting on pad are not wrapped and are exposed to dust. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621915&prj=601&rqi=F4NqpzX1kDthqIhbfBRc5fBIeI
RT1ELEC-2365-001 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-12 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MPZ_W_2 | PP - Power Panel |  |  | The transformer wires coming down into the breaker and frayed and wire strands are not secured in the block | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621431&prj=601&rqi=Uf3z20lwkNp38ZdedfBtGRq3i0
RT1ELEC-2365-002 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-12 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MPZ_W_2 | PP - Power Panel |  |  | Missing project required double torque marks on the neutral wire landed on the neutral bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621432&prj=601&rqi=PL1KuFYt1KwFyYX6R0IcrIV9no
RT1ELEC-2350-001 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MPZ_Q_2 | PP - Power Panel |  |  | Missing double torque marks on on the neutral line coming from the transformer landed on the neutral bus, see attached picture. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620590&prj=601&rqi=lyL30pEngbXLQfUYJmFnuzPZGk
RT1ELEC-2353-001 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MPZ_S_2 | PP - Power Panel |  |  | Missing the the double torque marks on the 3 transfer leads coming down to the breaker and on the 1 Neutral line heading to the neutral bus bar. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620592&prj=601&rqi=xliQed82BQ2Bd6DqdyMaKtncdW
RT1ELEC-2359-002 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MPZ_U_2 | PP - Power Panel |  |  | The small bare ground is not landed on the ground bus | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620596&prj=601&rqi=0WxYHQeJNrGVJPILF3pvLvWHEh
RT1ELEC-2383-001 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MPZ_R3_1 | PP - Power Panel |  |  | Missing double torque marks on the transformer line coming down into the lower panel. See attached picture | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620571&prj=601&rqi=V1bul6GqM8nSs7DPT2uKOrqFhQ
RT1ELEC-2359-001 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MPZ_U_2 | PP - Power Panel |  |  | This unit is missing the dead front in the panel section of the unit. It is not anywhere in the room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620595&prj=601&rqi=z6594kz4xp75WXR9zNvLbeBCsC
BKT1ELEC-9-006 | AT10x-1 | AMER | Closed | P3 Low CX | Rangsiya_Faihin@fsttechnical.com | 2026-04-16 04:00:00.000 +0400 | VER - Vertiv Electrical | L1 | Installation Damage | Commissioning |  | equipment type |  |  |  |  | MSB_AMCOP Panel has not been received. In the delivery inspection that was submitted by Cleveland repetitive identify that a panel has been missing, and Vertiv is aware that all units is missing a panel, they stated that it will be installed at a later date. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618412&prj=601&rqi=EEgRaBUaL8CJnUOorJkOkTZCmE
SOR-14-001 | AT10x-1 | AMER | Closed | P3 Low CX | eric_reinhard@fsttechnical.com | 2026-03-30 04:00:00.000 +0400 | Fire Suppression Contractor |  | Installation not correct | Commissioning | [6 empty] | FST inspected one of the Dry Pipe Sprinkler Valve assemblies in Area C and found that the downstream isolation valve w/ tamper switch was not installed. The double-interlock Dry Pipe Valve is identified in detail #2 and #5, located on drawing [FP500-AT10x]. See attached images of details. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616879&prj=601&rqi=Q1A8jbCcafJZYU6FhavxR3OMee
YT1MECH-150-002 | CH05-2 | AMER | Closed | P2 Medium CX | benjamin.mei@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Design not as specified | Design | HVAC | equipment | 1WSHP_D_1 | HP - Heat Pump |  |  | Common to all WSHPs, breaker size off panel are 20A breakers which is correct per equipment submittal and panel schedule. Nameplate on units call for 15A breakers. Submittal for Phase 2 also lists for carrier as manufacturer not trane. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629145&prj=638&rqi=emNOrYxfh6RBWp9uCLcxA1sEWn
GT1MECH-125-001 | CH05-2 | AMER | Closed | P2 Medium CX | marcello.scalise@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Missing Components | Commissioning | HVAC | equipment | 1WSHP_F_2 | HP - Heat Pump |  |  | (1WSHP_F2) On/off switch is missing lockout bracket that is present on D skid WSHPs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628597&prj=638&rqi=VIW44iRpL80IhavSKc8b04j47T
GT1MECH-122-001 | CH05-2 | AMER | Closed | P2 Medium CX | marcello.scalise@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Missing Components | Commissioning | HVAC | equipment | 1WSHP_E_1 | HP - Heat Pump |  |  | (1WSHP_E1) On/off switch is missing lockout bracket that is present on D skid WSHPs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628594&prj=638&rqi=iMBXV46bE4w8FTOJD4eHDwt7vP
GT1MECH-124-001 | CH05-2 | AMER | Closed | P2 Medium CX | marcello.scalise@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Missing Components | Commissioning | HVAC | equipment | 1WSHP_F_1 | HP - Heat Pump |  |  | (1WSHP_F1) On/off switch is missing lockout bracket that is present on D skid WSHPs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628596&prj=638&rqi=QZo8tzLO8s6LPgaWeZg3IqxRSB
GT1MECH-123-001 | CH05-2 | AMER | Closed | P2 Medium CX | marcello.scalise@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Missing Components | Commissioning | HVAC | equipment | 1WSHP_E_2 | HP - Heat Pump |  |  | (1WSHP_E2) On/off switch is missing lockout bracket that is present on D skid WSHPs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628595&prj=638&rqi=4An2LJbTrtBIqayTnWtvjdQwcp
YT1MECH-150-001 | CH05-2 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | HVAC | equipment | 1WSHP_D_1 | HP - Heat Pump |  |  | (1WSHP_D_1) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624758&prj=638&rqi=qdHVyauE7J0Z9HyFmNf9hsmoFQ
YT1MECH-151-001 | CH05-2 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | HVAC | equipment | 1WSHP_D_2 | HP - Heat Pump |  |  | (1WSHP_D_2) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624760&prj=638&rqi=3yeQkL01BTw79rvC2wKKNM0dmF
YT1MECH-152-001 | CH05-2 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | HVAC | equipment | 1WSHP_E_1 | HP - Heat Pump |  |  | (1WSHP_E_1) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624761&prj=638&rqi=01eegegL1V6mUGXyQ9m5hwbHYE
YT1MECH-153-001 | CH05-2 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | HVAC | equipment | 1WSHP_E_2 | HP - Heat Pump |  |  | (1WSHP_E_2) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624763&prj=638&rqi=EbqvKOQea2qV6tzXOYyMQBBe7a
YT1MECH-155-002 | CH05-2 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | HVAC | equipment | 1WSHP_F_2 | HP - Heat Pump |  |  | (1WSHP_F_2) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624767&prj=638&rqi=5i9iMMERosvTVNxHpYVXkGAswV
YT1MECH-154-001 | CH05-2 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | HVAC | equipment | 1WSHP_F_1 | HP - Heat Pump |  |  | (1WSHP_F_1) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624765&prj=638&rqi=HAZ9KoQEpvF90VkVb5kNij6nkP
YT1MECH-155-001 | CH05-2 | AMER | Closed | P2 Medium CX | benjamin.mei@veolia.com | 2026-06-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Torque Required | Commissioning | HVAC | equipment | 1WSHP_F_2 | HP - Heat Pump |  |  | Common to all WSHPs, there are no factory torque marks on any connections. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623962&prj=638&rqi=HxKAjSECkrZ2Lyc8pJ2yacTpEC
RT1MECH-148-001 | CH05-2 | AMER | Open | P3 Low CX | benjamin.mei@veolia.com | 2026-06-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/Required | Commissioning | Mechanical â€“Air | equipment | 1EF_D_1 | EF - Exhaust Fan |  |  | Common to all SKID EFs - Factory Quality Control document has not been received. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623977&prj=638&rqi=6xTi4X5zAlpPfAWsOoNEBL9iI5
CCD-L2B-2-001 | CH05-2 | AMER | Closed | P2 Medium CX | ian.tsurumoto@veolia.com | 2026-04-29 04:00:00.000 +0400 | Design Professional | DELIVERABLES | Documentation not issued/Required | Commissioning |  | equipment type |  |  |  |  | STANTEC has not issued a final (SCCS) short circuit coordination study | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619954&prj=638&rqi=kDhmHpYl6xIM4YJYs30kKVMFnZ
RT1ELEC-500-001 | CH05-2 | AMER | Closed | P3 Low CX | karina.leonard@veolia.com | 2026-04-16 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_D_2 | LIBATT - UPS Battery |  |  | (1BATT_D2_2) 1BATT_D2_2 door handle is not secured. The bolt that attaches the locking mechanism to the handle is missing. Door doesnâ€™t stay shut.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618386&prj=638&rqi=LKtUUbdWS90UL7vVExT0IXPm11
GI-016 | CH05-2 | AMER | Closed | P3 Low CX | zachary.riddle@veolia.com | 2026-03-18 04:00:00.000 +0400 | Owner |  | General Design Issue | Design | [6 empty] | PDU Similar for all equipment. Provided hardware for PDU input cable connections is insufficient to complete proper connections. Higher grade hardware was used with approval from Equinix. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616004&prj=638&rqi=55sbR16rb3GEDJo72796DUj3Nx
GI-012 | CH05-2 | AMER | Closed | P3 Low CX | mcoday@etechgroup.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Each Delta CRAH remote temperature sensor is not mounted, and cable not ran to the associated UPS in each skid â€“ (6) total. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199783&prj=638&rqi=yTgAAI4YKkkfeVWqxHAmMIrcfp
RT1MECH-153-001 | CH05-2 | AMER | Closed | P3 Low CX | mcoday@etechgroup.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | HVAC | equipment | 1WSHP_E_1 | HP - Heat Pump |  |  | There are not CAT6 cables between the Trane WSHPâ€™s and the E Skid DMARK in each skid â€“ (6) total. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199786&prj=638&rqi=Bde3fybWjDN37hUPJiTUCk79eo
GI-013 | CH05-2 | AMER | Closed | P3 Low CX | mcoday@etechgroup.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | There are not CAT6 cables between the Delta BATT3 and the E Skid DMARK in each skid â€“ (3) total. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199785&prj=638&rqi=zykjr9k5xRTQODwirNAHrsOfFf
GI-015 | CH08x-1 | AMER | Ready for Verification | P1 High CX | dayele@equinix.com | 2026-08-06 04:00:00.000 +0400 | Electrical Contractor |  | FWT Issue | Commissioning | [6 empty] | The E-House contains three UPS systems and their associated battery cabinets. During testing, activation of a battery alarm from any battery cabinet caused all three UPSs to generate battery alarms. The expected operation is for a battery alarm to be reported only by the UPS associated with the battery cabinet experiencing the alarm condition. CECCo's investigation determined that the battery cabinet alarm input signal to the UPS and the outgoing alarm signal to the Marvair PLC are connected at the same point, allowing the alarm signal to propagate across all UPS systems and generate unintended battery alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632640&prj=677&rqi=39591KsOZbewfodUGJfJpC3qlW
GI-016 | CH08x-1 | AMER | Ready for Verification | P3 Low CX | dayele@equinix.com | 2026-08-06 04:00:00.000 +0400 | Electrical Contractor |  | FWT Issue | Commissioning | [6 empty] | The outside air intake openings on the Marvair ACUs are fully exposed to the environment and do not include protective hoods or weather protection. This configuration may allow rainwater ingress into the units during adverse weather conditions, potentially impacting equipment reliability and operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632647&prj=677&rqi=A1bz6RGaukIKUKThv1U9CsnQ5L
GI-018 | CH08x-1 | AMER | Closed | P3 Low CX | dayele@equinix.com | 2026-08-06 04:00:00.000 +0400 | Electrical Contractor |  | FWT Issue | Commissioning | [6 empty] | The Marvair ACUs are currently configured to control cooling based on their individual return air temperature sensors rather than the E-House temperature sensors as specified in the design. This configuration does not align with the intended control strategy and may result in non-uniform cooling operation within the E-House. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632652&prj=677&rqi=uT3gRUAsVVgIzARF7bEdN41LPg
GI-017 | CH08x-1 | AMER | Closed | P3 Low CX | dayele@equinix.com | 2026-08-06 04:00:00.000 +0400 | Electrical Contractor |  | FWT Issue | Commissioning | [6 empty] | The local temperature control setpoints configured on the Marvair ACUs do not match the individual unit control setpoints specified by Equinix. This discrepancy may result in unintended or non-standard cooling unit operation during communications loss conditions, as the units may not stage and operate in accordance with the intended control sequence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632648&prj=677&rqi=2jjILLAWH16TeXDPIawFBwKG4c
GI-014 | CH08x-1 | AMER | Ready for Verification | P1 High CX | dayele@equinix.com | 2026-08-06 04:00:00.000 +0400 | Electrical Contractor |  | FWT Issue | Commissioning | [6 empty] | During functional testing, activation of the fire alarm signal resulted in a UPS battery alarm being generated at the UPS system. Investigation indicates that the VESDA fire alarm signal and the UPS battery alarm signal are both terminated on the same input terminal of the MPC10 PLC. As a result, activation of the fire alarm signal backfeeds the UPS battery alarm circuit, causing an unintended battery alarm condition at the UPSs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632632&prj=677&rqi=ywqNb0XLKMa7y12CxlKOfc0Nfj
GI-006 | CH08x-1 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-29 04:00:00.000 +0400 | DEL - Delta Elec |  | FWT Issue | Commissioning |  | equipment type |  |  |  |  | FWT an out of phase alarm triggered | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619906&prj=677&rqi=DXj5IbDHGyeiQ6POFszVYTN1DQ
GI-007 | CH08x-1 | AMER | Closed | P1 High CX | rtyler@equinix.com | 2026-04-29 04:00:00.000 +0400 | Equinix Design Engineer |  | FWT Issue | Commissioning |  | equipment type |  |  |  |  | Logic Controller was not initiating source seek, upon S2 (GEN) supply failure whilst Load was supported by S2 (GEN) and S1 (UTILITY) was already available. Issue found during FWT for logic controller. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619907&prj=677&rqi=Ty41xlzL5fwVJlnyQtNDuX8nNt
GI-004 | CH08x-1 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | FWT Issue | Commissioning |  | equipment type |  |  |  |  | Upon normal S2 > S1 re-transfer (UTILITY RESTORE), as that is manually initiated by the operator, existing delays were insufficient for operator to step away from being in front of the panel. Issue found during FWT Logic Controller Testing. Equinix added a 10s walkaway timer. Delay mitigates risk of arc flash event affecting the operator. The requirement for the operator to step away at a safe distance from the panel board needs to be covered in the SOP. It should be noted that this delay is not present if fail to open/close or trip alarm are being acknowledged. SOP for those activities should require for the operator to disable the ATC first (ATC MODE = DISABLED or MAN) prior acknowledging any latched-on alarms inhibiting transfer/re-transfer sequences. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619623&prj=677&rqi=fa6N9rsNzVuqRpqtYw7JHh5Sf8
GI-003 | CH08x-1 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | FWT Issue | Commissioning | [6 empty] | Upon normal S2 > S1 re-transfer (UTILITY RESTORE), as that is manually initiated by the operator, existing delays were insufficient for operator to step away from being in front of the panel. Issue found during FWT Logic Controller Testing. Equinix added a 10s walkaway timer. Delay mitigates risk of arc flash event affecting the operator. The requirement for the operator to step away at a safe distance from the panel board needs to be covered in the SOP. It should be noted that this delay is not present if fail to open/close or trip alarm are being acknowledged. SOP for those activities should require for the operator to disable the ATC first (ATC MODE = DISABLED or MAN) prior acknowledging any latched-on alarms inhibiting transfer/re-transfer sequences. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619597&prj=677&rqi=IdIkjN0NPTighpyijPSkwBHhKR
GI-005 | CH08x-1 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | FWT Issue | Commissioning |  | equipment type |  |  |  |  | Controller was opening UMB or GMB if trip was issued by either breaker as the Service Disconnect state was intended to isolate both S1 and S2. Issue found during FWT Logic Controller testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619624&prj=677&rqi=YHdBqYoQhEXeoTsRKySn7m9xDX
GI-002 | CH08x-1 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | FWT Issue | Commissioning |  | equipment type |  |  |  |  | Internal buss needs to have more phase stickers applied to more easily identify buss to prevent confusion when working on the buss. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619594&prj=677&rqi=fPsSW7MoqqA4Dg1NrEdgRJLVna
GI-001 | CH08x-1 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | FWT Issue | Commissioning |  | equipment type |  |  |  |  | Equinix advised Hanley to separate the RELT and source lamp on/off circuits. In addition, the naming convention for the DC# breakers need to be updated per new circuits. Hanley to verify sources are correct throughout the shop drawings especially for the source for the door mounts. (See attached marked drawings) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619571&prj=677&rqi=Pxcf3eVk4h642rOht1Q8xfHROL
GI-078 | CN01-2 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | Arc flash covers interrupt the Communication cable need to be prepare dressing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622627&prj=664&rqi=2Mn37Nqx3ed9cGRQiJBg7xhsV9
GI-062 | CN01-2 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | BMU Filter to be provided at Back door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622120&prj=664&rqi=c1VteZggthJEBJZNdIL2dYIpjE
GI-050 | CN01-2 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | In module V welded bottom sheet overlaps to foundation holes need to be corrected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622105&prj=664&rqi=XFGQtDnZm2tefV30HU8dttFsDT
GI-042 | CN01-2 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | Ronis key not available in the RMU during the FWT, So not able to check Ronis keys interlock ABB has to do perform demonstrate at the site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621945&prj=664&rqi=WIRXRfx3QSQECMMkoclTBJF2F8
GI-043 | CN01-2 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | Ronis key not available in the RMU during the FWT, So not able to check Ronis keys interlock ABB has to do perform demonstrate at the site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621946&prj=664&rqi=PgR0d1Wr9l63qVecHYgGHq0Y3a
GI-047 | CN01-2 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | The bolts provided at the cable clamp are too long. The bolt size should be reduced, as the clearance between the bolt and the earthing connection is very less | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621951&prj=664&rqi=RqmtysILufji8zXdh1aD7EOEZ7
GI-048 | CN01-2 | APAC | Closed | P3 Low CX | sivakumar@abluae.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning | [6 empty] | Aluminium gland plate dimensions to be added in the GA drawing. The gland plate thickness is specified as 3 mm in the drawings; however, the actual observed thickness is 2.5 mm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621954&prj=664&rqi=T8jIPnBCYhrDRMMfr1v7Xya5VJ
GI-041 | CN01-2 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | Ronis key not available in the RMU during the FWT, So not able to check Ronis keys interlock ABB has to do perform demonstrate at the site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621944&prj=664&rqi=LWxAdIujMs5f0eq1naJqHnCXIC
GI-200 | DA11-4 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-08-28 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [6 empty] | Door to Electrical Room N is not latching shut. Pulls open freely. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635929&prj=614&rqi=c8FdRkE6yaTIZyKhsNKpACprsY
GI-199 | DA11-4 | AMER | Open | P3 Low CX | bramsay@critical2u.com | 2026-08-26 04:00:00.000 +0400 | Electrical Contractor |  | Cleaning | Commissioning | [6 empty] | T-Block room needs to be cleaned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635416&prj=614&rqi=5p5JixDbb0FUrHUZoHjA5uToTm
GI-196 | DA11-4 | AMER | Ready for Verification | P3 Low DCOS | jonathan.wright@alphafacilities.com | 2026-08-26 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | [6 empty] | Ground bus EGB-T-4 contains Zinc and Stainless Steel fasteners. Dissimilar metals would likely cause electrolysis and have dissimilar torque values. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635310&prj=614&rqi=WtVKSYInsiEGmDFWFLOXerNctR
GI-195 | DA11-4 | AMER | Ready for Verification | P3 Low CX | jonathan.wright@alphafacilities.com | 2026-08-25 04:00:00.000 +0400 | Mechanical Contractor |  | Cleaning | Commissioning | [6 empty] | Listed ACUs contain Material (I.e. brackets, screws) & FOD (I.e. dust, debris, trash) and need to be cleaned: ACU-2-16 ACU-2-17 ACU-2-18 ACU-2-19 ACU-2-20 ACU-2-21 ACU-2-22 ACU-2-23 ACU-2-24 ACU-2-25 ACU-2-30 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635097&prj=614&rqi=gnohNXR8Jns0sjWIyIs7wYLQZ5
FPT-430-002 | DA11-4 | AMER | Closed | P2 Medium CX | pnavarro@critical2u.com | 2026-07-30 04:00:00.000 +0400 | Controls Contractor | L4 | DCIM BCM Issue | DCIM | Electrical â€“ MV | equipment | Existing GEN-4A | Existing Generators |  |  | Gen 4A is not communicating with BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631450&prj=614&rqi=K62O8ZdW16qq95wj1GdLjpAMFs
FPT-430-001 | DA11-4 | AMER | Ready for Verification | P2 Medium CX | pnavarro@critical2u.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Component/Equipment Failure | Commissioning | Electrical â€“ MV | equipment | Existing GEN-4A | Existing Generators |  |  | Frequency recovery time do not meet the iso 8528 standards. See attached screenshots of readings and standard. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631330&prj=614&rqi=uWBq1dJUBHXnTP2Jn3ZcbmCWG6
GI-172 | DA11-4 | AMER | Ready for Verification | P3 Low CX | shuyck@morleymoss.com | 2026-07-14 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | DP-GEN-3 | DP-Distribution Panel |  |  | DP-GEN-3 is to have (2) Kirk keyed main breakers that are 800AF/600AT per W-Block SLD sheet E-601.20W but the panel currently has 600AF/600AT main breakers installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629262&prj=614&rqi=eWW18tuET3NgVx0o6QIfmeXf9R
GI-142 | DA11-4 | AMER | Closed | P3 Low CX | cdavis@clunegc.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning | [6 empty] | In CH-14, the 12" condenser water connection to the heat exchanger has 1" difference. Please advise a solution. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623672&prj=614&rqi=QqTgKOzxqCrBIj7yfbMPtr47bV
GI-120 | DA11-4 | AMER | Open | P2 Medium CX | sadkins@critical2u.com | 2026-04-30 04:00:00.000 +0400 | Owner |  | General Design Issue | Design | [6 empty] | USP-A-1, B-1 and C-1 Settings need to be updated. : DA11-2 moved the building to the substation, SCCS was not done correctly to coordinate the move. With DA11-4 being the first to tie directly into the substation, after we got the settings from Oncor it was found that we were not coordinated. Then we worked with Oncor to establish the correct settings, which is what has been implemented into DA11-4. Oncor has since go back and adjusted their side of POD 1, the only remaining item is to have Schneider update our side of the POD 1 to match the functions and settings that were established for DA11-4. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620086&prj=614&rqi=wNkUwOotmYzy90t87pBFuxcMab
GI-073 | DA11-4 | AMER | Closed | P3 Low CX | mwarwick@morleymoss.com | 2026-03-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | Mechanical â€“Air | equipment | CRAH-1-47 | CRAH - Computer room air handler |  |  | Pre-installed VA cable is on the wrong terminal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618545&prj=614&rqi=ssOST2IllBx1QSOrp6ryTllClK
GI-048 | DA11-4 | AMER | Closed | P3 Low CX | mwarwick@morleymoss.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  | equipment | MV Coms Panel Primary |  |  |  | Unit arrived with shipping damage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617268&prj=614&rqi=XMAseBildzoHnUWCptwsp5oUGA
GI-049 | DA11-4 | AMER | Closed | P3 Low CX | mwarwick@morleymoss.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  | equipment | MV Coms Panel Secondary |  |  |  | Cabinet arrived with shipping damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617269&prj=614&rqi=0KGNIs4kG9NfALQW2gWutOLl7h
L2L3 Sun-184-001 | DA12-1 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-07-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_AR1_3 | CRAH - Computer room air handler |  |  | Fan section - Upper door furthest RH side is misaligned and colliding against frame | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631077&prj=695&rqi=pdouQtkwgeMxACAVCW6P01x7Ti
L2L3 Sun-151-001 | DA12-1 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-07-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_BR1_2 | CRAH - Computer room air handler |  |  | Fan section - Upper door furthest RH side is misaligned and colliding against frame | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631081&prj=695&rqi=aJPV6FeycZLjRsMZqFEwGZ40l8
L2L3 Sun-185-001 | DA12-1 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-07-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_AR1_4 | CRAH - Computer room air handler |  |  | Electrical Vestibule - Bottom most door latch cannot fully rotate to locked position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631079&prj=695&rqi=GwJsF71ZjtcaYnu2QBLVtCjf58
L2L3 Sun-155-001 | DA12-1 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-07-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_BR1_4 | CRAH - Computer room air handler |  |  | ICDM Section - Top latch not aligned and cannot rotate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631083&prj=695&rqi=NAWKh0owZO9eHP0WmLPvD6T3gg
L2L3 Sun-20-001 | DA12-1 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-07-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Labelling | Commissioning | Electrical â€“ MV | equipment | 1MVCB_Z | MVCB - Medium Voltage Circuit Breaker |  |  | Labels on both doors do not match wording from the submittal (page 73) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629267&prj=695&rqi=yeVQdb2a2byFdwKmLlBNlWMT49
GI-030 | DC17-1 | AMER | Open | P2 Medium CX | EMAHLER@ramboll.com | 2026-09-02 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [6 empty] | Communications EMT (Division 27) does not have insulating bushings (Per Division 26) to protect the conductors at terminations with EMT connectors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636535&prj=658&rqi=YEtgkUIQIykVod3PdPuwjq2NHX
GI-027 | DC17-1 | AMER | Open | P3 Low CX | SOGOTI@ramboll.com | 2026-08-28 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1RSSB_1 | RSSB - Reserve Spine Switchboard |  |  | Unit has damage to the metallic plate located on top of the unit, please refer to the attached photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635877&prj=658&rqi=8wqB5pgTgt3MKCbChm5Kw0cyVG
GI-029 | DC17-1 | AMER | Open | P2 Medium CX | Jshaffer@ramboll.com | 2026-08-28 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1RSSB_1 | RSSB - Reserve Spine Switchboard |  |  | K55 and K52 key are both broken off inside the cylinders | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635985&prj=658&rqi=zipMdkGJpu21WBGh8AzJmmzYO7
GI-028 | DC17-1 | AMER | Open | P3 Low CX | SOGOTI@ramboll.com | 2026-08-28 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1RSSB_2 | RSSB - Reserve Spine Switchboard |  |  | Arc flash label on the front panel of the unit is missing, please refer to the photo attached for referece | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635878&prj=658&rqi=UWPtxnLmvpOTBkCcDJzYJR5iax
GI-024 | DC17-1 | AMER | Open | P3 Low CX | jbeall@rosendin.com | 2026-07-31 04:00:00.000 +0400 | SYC â€“ Systecon |  | Component/ Equipment Failure | Commissioning | [6 empty] | SSB-Q Chiller Breaker failed NETA testing - Would not trip on long time | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631868&prj=658&rqi=iq0j5F0m6HSkdmoEu4cGL8Lfwu
GI-023 | DC17-1 | AMER | Open | P3 Low CX | jbeall@rosendin.com | 2026-07-31 04:00:00.000 +0400 | SYC â€“ Systecon |  | Component/ Equipment Failure | Commissioning | [6 empty] | SSB-R1 Chiller Breaker failed NETA testing - Long time would not trip | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631863&prj=658&rqi=psMdcEhEmxMCyH5YHN7UwcG73l
GI-020 | DC17-1 | AMER | Open | P2 Medium CX | gkuczler@rosendin.com | 2026-06-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | UMDSB Termination Points for UPS-3 RBB. Hanley confirmed UPS-3 RBB Points will be 5 & 7 at UMDSB for DC17. Terminal Block in UMDSB only has (5) poles. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627247&prj=658&rqi=Zn4Uarr8htfOGM7y00KlRtSazg
GI-016 | DC17-1 | AMER | Closed | P2 Medium CX | gkuczler@rosendin.com | 2026-05-20 04:00:00.000 +0400 | Owner |  | General Design Issue | Design |  | equipment type |  |  |  |  | Hanley PDU Transformer Testing Polarization Index testing of PDU's requested by EQX requires isolation of transformer in PDU. Isolation requires removal of factory connection from XO to GND. Hanley has advised factory connections cannot be removed without warranty impact. Need direction on if test is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622633&prj=658&rqi=ntuXeB2WPiLPqyqQMZlMKnsFiR
GI-013 | DC17-1 | AMER | Closed | P3 Low CX | emilyma@dpr.com | 2026-05-11 04:00:00.000 +0400 | SGB-SMIT |  | Design correction needed | Design | [6 empty] | SGB MLTXs relay cut out incorrect size. SGB did not align the SE relay cutout per the dimensions in the submittal. Current dimensions are 8.07x5.12. Required dimensions based off SE relay is 8.07x7.09. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621176&prj=658&rqi=fhEGvpRAit2aiBYx97xipD4drc
GI-012 | DC17-1 | AMER | Closed | P2 Medium CX | emilyma@dpr.com | 2026-04-29 04:00:00.000 +0400 | JCI - Johnson Control |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Chiller W has a good amount of visible rust inside piping from factory. Other chillers may have the same problem. - Field inspection of Chiller W shows heavy, visible rust scale and oxidation on the internal surfaces of factory-installed piping and nozzle connections. Photographs confirm uniform orange/brown corrosion inside multiple pipe sections, including flanged connections and inlet/outlet barrels. The condition appears pre-installation and is consistent with improper factory preservation, moisture ingress, or lack of nitrogen purge/desiccant protection. Based on identical construction, other chillers are at high risk of the same internal condition. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619949&prj=658&rqi=kDEpfWvfYK0xHloms4NC0azO1B
GI-009 | DC17-1 | AMER | Work Completed | P2 Medium CX | gkuczler@rosendin.com | 2026-04-21 04:00:00.000 +0400 | DEL - Delta Elec |  | Component/ Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (3) STS Molded Case Switches were damaged by 3rd tier subcontractor in warehouse. Replacements are needed, DPR has been notified. Need update on replacement order. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619043&prj=658&rqi=0fFlGzz61bKRokMeMV7UBvC5Ii
GI-008 | DC17-1 | AMER | Work Completed | P2 Medium CX | gkuczler@rosendin.com | 2026-04-21 04:00:00.000 +0400 | DEL - Delta Elec |  | Component/ Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (2) STS Molded Case Switches arrived with bent pins. Replacements were ordered and expected with March delivery of STS units. No switches were received. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619026&prj=658&rqi=s6z2vXBKQqVgQ1D9oGh8kbp73C
GI-007 | DC17-1 | AMER | Closed | P2 Medium CX | emilyma@dpr.com | 2026-04-13 04:00:00.000 +0400 | VER - Vertiv |  | Installation Damage | Commissioning | [6 empty] | Damaged battery cabinet for L3. Vertiv to come out and inspect unit. model PHR3462-001A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617974&prj=658&rqi=9TIXnCpzBQHD1esbQSXFUPLE5B
GI-001 | DC17-1 | AMER | Closed | P2 Medium CX | emilyma@dpr.com | 2026-02-09 04:00:00.000 +0400 | VER - Vertiv |  | Installation Damage | Commissioning | [6 empty] | DC17-2 asset - Vertiv Damaged 1200kva UPS at A&A. 1/20/26. SN D25M006518. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198806&prj=658&rqi=NP7wdIDXH9LLbVLxiWjeux6zja
GI-106 | DC21-P2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-09-14 04:00:00.000 +0400 | General Contractor |  | Component/ Equipment Failure | Commissioning |  | equipment type |  |  |  |  | All Electrical Skid CRAH's: G and H. Valve feedback stays at 0 or in "Error" while the valve is commanded open Delta HVAC issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638003&prj=678&rqi=M15DHy0v4mAZBCfU3LjNTNBDMX
GI-105 | DC21-P2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-09-14 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/ Fault | DCOS |  | equipment type |  |  |  |  | All Electrical Skid CRAH's: BMS displays the supply air temperature setpoint at 0 and the differential setpoint as 0. Points do not match between HMI and BMS. The differential temperature setpoint automatically reverts back to displaying 0 after changing this setpoint on the unit HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638002&prj=678&rqi=uuZ1CUXSxZLDXoGNX4CyUMdIxC
GI-107 | DC21-P2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-09-14 04:00:00.000 +0400 | General Contractor |  | Component/ Equipment Failure | Commissioning |  | equipment type |  |  |  |  | All Electrical Skid CRAH's: Fan feedback (rpm) values are reading 0, even when fans are running. Awaiting PLC upgrade from Delta HVAC for 9/15/26 in the morning. Delta HVAC issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638006&prj=678&rqi=PhRqZxWtGZilLdnw4qJH74qee9
GI-103 | DC21-P2 | AMER | Open | P3 Low CX | william.park@veolia.com | 2026-09-09 04:00:00.000 +0400 | Electrical Contractor |  | Missing Components | Commissioning | [6 empty] | Exhaust Fan: Electrical Room H - Ground wire is missing from the exhaust fan controller box. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637530&prj=678&rqi=wvfi2P3UPtFgzajILZyHIt94Q8
GI-104 | DC21-P2 | AMER | Open | P3 Low CX | william.park@veolia.com | 2026-09-09 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | Exhaust Fans: Electrical Rooms H and G - Both exhaust fans have UPS wires not terminated and hanging within the exhaust fan controller box. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637534&prj=678&rqi=rHuFNk3MhApWL436q91iKiYrXo
GI-100 | DC21-P2 | AMER | Open | P3 Low CX | Aaron.Cross@veolia.com | 2026-09-04 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning | [6 empty] | Water on floor of GEN-H source unknownÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636880&prj=678&rqi=icOzRZZR04hPnnKzvxLAGbIWiw
GI-092 | DC21-P2 | AMER | Open | P3 Low CX | samuel.bruce@veolia.com | 2026-08-20 04:00:00.000 +0400 | Electrical Contractor |  | Incomplete Connections | Commissioning | [6 empty] | HVL-G knockout must be removed to route interconnect wires between sections 1 and 2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634512&prj=678&rqi=7gNWqgHiXmxNO6nKh9kYIiVcQn
GI-091 | DC21-P2 | AMER | Ready for Verification | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | 1-UPS-G-2: Too much copper is showing between the wire insulation and the crimp at the battery termination. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634482&prj=678&rqi=OYkMJ2ahh8QQU5gTqeYPh9q1ee
GI-090 | DC21-P2 | AMER | Open | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-08-20 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | [6 empty] | Some washers appear to be installed on the incorrect side of the ground terminations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634475&prj=678&rqi=rFY6tOHqh1fzWlmkBi0sJ6XzI5
GI-075 | DC21-P2 | AMER | Ready for Verification | P1 High CX | ayorinde.akinrinlola@veolia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | Skid D - Battery Exhaust Fan Control Box: Â Openings and Cable Protection The fan control box has two unused openings that are not sealed and should be fitted with appropriate hole plugs/covers. Additionally, the conduit entry currently in use is missing a protective collar, leaving the wire exposed where it passes through the conduit opening. Install the appropriate collar to protect the wiring and ensure proper installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630387&prj=678&rqi=Wwk41FdgkaFV0aqkvmsnVUrk55
GI-078 | DC21-P2 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning | [6 empty] | Water appears to be present on the floor outside and around the boardÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630465&prj=678&rqi=SgKIjhu9B4UKzRj592ueFDfaCZ
GI-074 | DC21-P2 | AMER | Ready for Verification | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/ Equipment Failure | Commissioning | [6 empty] | Skid D: Â Exhaust Fan Not Operational Â The exhaust fan on Skid D is not operational. Initial inspection indicates that the fan motor appears to be faulty, preventing the exhaust fan from running. The fan and motor should be inspected, tested, and replaced if confirmed defective | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630366&prj=678&rqi=C32iIxZk80Qd5ATltU20bDtJgm
GI-073 | DC21-P2 | AMER | Closed | P2 Medium CX | taquonya.washington@veolia.com | 2026-07-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Design correction needed | Design | [6 empty] | ECB-R-G needs the K2 Kirk key cylinder replaced with the KLB cylinder that matches the site (KLB SN 63374) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630038&prj=678&rqi=YXR1MjXXaVQU6R6zCWwMvMjQwr
GI-072 | DC21-P2 | AMER | Closed | P1 High CX | william.park@veolia.com | 2026-07-15 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | New Data Hall CRAH's: Main power conduit to the CRAH's was left in place on top of the dampers within the top damper section of the unit. Conduit was found to fall in between the dampers, and dampers will force closed on this conduit resulting in electrical failure and CRAH failure. The conduit must be propped on the side wall or top wall of the inside of the CRAH's with clamps to avoid this conduit from being near the dampers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629456&prj=678&rqi=1cefOpnxSA27WWmjVqjCxMlKfu
GI-045 | DC21-P2 | AMER | Ready for Verification | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | SKID G- Two sprinklers heads are missing in Skid G as shown in design drawings. Two Sprinkler heads were missing and not installed as shown in drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627468&prj=678&rqi=jw4JJCPQG9pC5HdF375Zuw249D
GI-039 | DC21-P2 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | SKID G & H- F/A Box need to be changes: Top F/A box will be removed and changed to an 11B box to provide proper clearance | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627391&prj=678&rqi=RNysfWb8dv5qjGjhMyP3FZhXsr
GI-043 | DC21-P2 | AMER | Ready for Verification | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | Skid G -The fire protection main line is missing the required connection point and has not been properly secured. The fire protection main line is not connected in accordance with the project requirements and must be properly connected and supported. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627464&prj=678&rqi=ivsXurDpOTBbHPJKGCurpFZSSx
GI-038 | DC21-P2 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | SKID G & H- Ground bars not complete: Ground bars are not jumped together inside of skids- 4 Ground Plates do not have jumpers between them. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627383&prj=678&rqi=jyZbvlTKkQu5RIhR0iwpGssGuS
GI-044 | DC21-P2 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | Skid D&H- Card Reader are higher. The Card Reader is at 56'' to Center. Need to be at 46''. MPS started to rectify these before it shipped out. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627467&prj=678&rqi=n7cA2e5Vz3pCF0EeFRSzfyaWeF
GI-030 | DC21-P2 | AMER | Open | P2 Medium CX | michael.acciaioli@veolia.com | 2026-06-29 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Chilled Water Pump Wiring - The Chilled water pump wiring connection was removed from Chillers D-17 & D-18. The chillers at this site have their chilled water pump getting power from the chiller main circuit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627238&prj=678&rqi=RNjbIVHDjyFWhSD1Ngxp7UVFZN
GI-029 | DC21-P2 | AMER | Open | P3 Low CX | taquonya.washington@veolia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | Label and placard outside of skid D needs to be updated now that the skid will no longer be tethered. One is made by REI, the other is made by MPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625529&prj=678&rqi=hST5i1G38ZMaW7egQ1yIZJZMKw
GI-028 | DC21-P2 | AMER | Closed | P3 Low CX | ron.brackin@veolia.com | 2026-05-26 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | [6 empty] | Flat washer installed is not in accordance with PDU submittal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623158&prj=678&rqi=r02kfs5mpSrZSEE0e8UTg8wwP9
GI-026 | DC21-P2 | AMER | Open | P3 Low CX | ron.brackin@veolia.com | 2026-05-26 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Change bus labeling on all G and H RPP's incoming feeders (currently says CBA, change to ABC). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623155&prj=678&rqi=UJy6LbZFxxjCo8mYT9HBqpp1gj
GI-027 | DC21-P2 | AMER | Closed | P3 Low CX | ron.brackin@veolia.com | 2026-05-26 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Labelling | Commissioning | [6 empty] | Phase labeling on incoming feeders are labeled incorrectly. In field -CBA, should be changed to ABC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623157&prj=678&rqi=lM20JSXE69xI5GX49F7wzgNWwN
GI-025 | DC21-P2 | AMER | Open | P3 Low CX | ron.brackin@veolia.com | 2026-05-20 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | [6 empty] | Exhaust fan receptacle fed from ups-backed source, shoud be non-ups. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622536&prj=678&rqi=fSjqcWXmIx4XwcD4GumKR8azvX
GI-023 | DC21-P2 | AMER | Open | P2 Medium DCOS | michael.acciaioli@veolia.com | 2026-05-14 04:00:00.000 +0400 | Owner's Representative |  | DCOS Design Issue | DCOS | [6 empty] | BMS Standard - The DC21 site was originally commissioned in 2020 and used the EBCS3 version 2.6 standard. At the time of DC21-P2&P3 the version for EBCS3 has changed to 4.8. During the Software Factory Acceptance test it was noted that the controls for the new equipment will match the existing standard and not the latest EBCS3 version. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621878&prj=678&rqi=EVtOCLHkXno6uIk6jhLaQ89hbD
GI-024 | DC21-P2 | AMER | Open | P3 Low CX | ron.brackin@veolia.com | 2026-05-14 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | [6 empty] | MV Switch D currently has primary and alternate designation swapped in terms of labeling.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621907&prj=678&rqi=MlXA4zNPYqBNnnFwGluS8K8RVw
GI-022 | DC21-P2 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | [6 empty] | SKID-D Existing chilled water piping and new chilled water piping in new half skid appear to be at different elevations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617092&prj=678&rqi=46a8xUf16QVaH15Mzpd1NInyHb
GI-546 | DC22-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | Commissioning Authority |  | DCOS Installation not complete | DCOS | [6 empty] | . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623745&prj=475&rqi=Cy8YNghFS1tjdCVgWTP5y7wXZQ
GI-545 | DC22-1 | AMER | Open | P2 Medium DCOS | manuel.gomez@eu.equinix.com | 2026-05-29 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Post RFS --- The Vertiv CRAHs have been wrongly integrated, duplicating 3 Modbus registers : -Return Air Temperature Setpoint -Supply Fan Command -Supply Fan Speed Command | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623469&prj=475&rqi=3JG1UhZMwWulSn1xwJt04zafrz
GI-542 | DC22-1 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-04-16 04:00:00.000 +0400 | SCH - Schneider Electric |  | Installation not complete | Commissioning | [6 empty] | E-house 2 wiring for the one BARD is not complete - this is wiring that should be done by the skid manufacturer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618443&prj=475&rqi=Bg4NLW9CVhsbsJ8D4EonuAL0WI
GI-539 | DC22-1 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-03-12 04:00:00.000 +0400 | Equinix Ops |  | Installation not correct | Commissioning | [6 empty] | RPP BCM â€“ Unlcear of setup of Janitiza for RPP BCM. 1/27 â€“ Trevor is currently reconfiguring RPP setup for 415V and single row consecutive at DC22-1. 2/9 â€“ Approximately 10 RPPâ€™s were locked out and not yet complete. Once placed back in service, will complete at DC22-1. 2/23 â€“ Veolia will follow up with DPR/REI on status of RPPâ€™s at DC22-1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615476&prj=475&rqi=pFKdmIUKn7qDIL0dxJLhgPRoNF
GI-537 | DC22-1 | AMER | Open | P3 Low CX | jonas.wudkwych@veolia.com | 2026-03-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | General Design issue | Design | [6 empty] | Kirk Key system for DC22 MV Ring design appears incorrect. ECB_R1_Q1 Final Solution â€“ Replace the K2/K55 cylinder with new K2 cylinder. K2 cylinder is at IAD but need to confirm that you can reuse the housing of the existing cylinder. ECB_R1_Q2 Final Solution â€“ Will swap door with another onsite Will take door from 4th floor (ECB_R1_RS_Q1) and take to 3rd floor (ECB_R1_Q2) once new door arrives. ECB_R1_RS_Q1 Final Solution (not till Tower 2 during DC22-3) â€“ Replace kirk key cylinder and transfer blocks as per design to be determined during DC22-3. New door with transfer blocks shipped from Ireland. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615464&prj=475&rqi=e0hNY0ZdLeoDRWSWR2LYP7v2Yg
GI-538 | DC22-1 | AMER | Work Completed | P3 Low CX | jonas.wudkwych@veolia.com | 2026-03-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design correction needed | Design | [6 empty] | Design Change --- No external control power to the ECBâ€™s (If the R-spine is down there is no control power and no communications through the BMS) - Qty: 3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615465&prj=475&rqi=7zchLJmjvFOHLOSjvuQvYdYc7M
GI-505 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [6 empty] | A generator yard plan should be provided Equipment in the Generator Yard, such as FCU's and Generator Fuel are not visible on a floor plan. Unable to see on the BMS. Suggest providing a generator yard plan with all devices being communicated to, or a way for end user to see all required control devices. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198500&prj=475&rqi=CA2MpkKKT9yLryniPrPO5iQear
GI-484 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | At time of testing, Exhaust Fans were not shown on the BMS graphics. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198468&prj=475&rqi=mQrShtUrb1O3Rxmcc2Y438Uc7c
GI-501 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | All Electrical Rooms: At the time of commissioning, Remote temp sensors for ER CRAH's needed their scaling updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198496&prj=475&rqi=cxRtYMgQPBSxycCCrQOptOA0Dc
GI-490 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Multiple Flow Meters and temp sensors are not reading correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198479&prj=475&rqi=J4dlqWTu1Xfwat6BuGa2gNgYaf
GI-510 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | At the time of commissioning, the supply fan percentage did not match the unit HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198505&prj=475&rqi=OFoZWQSulR8JXQss5ZLSXBul5S
GI-509 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | At the time of commissioning, we were unable to click on the individual compressors on the Chiller Faceplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198504&prj=475&rqi=nfwYkcigZEkzu2r90TIwfLV2Y5
GI-515 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [6 empty] | BMS Chilled Water Layout: The Weather Station Temperature was not reading accurately. When the ambient air temperature was below 40 degrees, the weather station was reporting 57 degrees on all three sensors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198512&prj=475&rqi=dxnW2ahXalX7fwJeje9XEbMUXG
GI-497 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | Chilled water flow deviation was not responding to range changes C5 and C6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198492&prj=475&rqi=Ik28aSrwZlQBlkHEcMOgnzaVH7
GI-508 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | At the time of commissioning, the chilled water pump data was not showing on the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198503&prj=475&rqi=KvfOe666sufiJgpx9odPEilqos
GI-519 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | CRAH Faceplate - During commissioning, we needed to add the min and max speed command (%) in the setup menu for unitary mode. Minimum fan speed should be 30% per the Equinix Standard | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198517&prj=475&rqi=Ol7El74pCmqUvsEZ9Vb4IVTHFx
GI-486 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | At time of testing, BMS was not showing FCU's | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198473&prj=475&rqi=QMea655Ut3ccUJKAQ1iNM2JBse
GI-506 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | At the time of commissioning, multiple chillers had active faults when a fault at the chiller is not present. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198501&prj=475&rqi=UdaYLKLNoRZgA33iMgSAa5oBnE
GI-535 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | RTU's: At the time of commissioning, we were losing comms on and off for RTU's. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198545&prj=475&rqi=Pwsx0iWCWYmf9gH9CgspzZKZaw
GI-514 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | During commissioning, a CRAH Summary alarm on the BMS was not triggered when there was an alarm on the CRAH. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198511&prj=475&rqi=uqtsi7Ms1Eq8y3w5AYs9KBkups
GI-517 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | At the time of commissioning, an acceptable range of values for the supply air temperature (60-80F) needed to be set. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198514&prj=475&rqi=2wzL2UbaFGKsD7W6SBcRlnfLim
GI-503 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | At the time of commissioning, none of the first-floor mechanical was visible on the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198498&prj=475&rqi=9UXQ9tOYA4Vu5EXJGsUjpEvijh
GI-525 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | CRAH Alarm Program: During commissioning, the return air sensor probe failure did not appear on the BMS. It only appeared on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198523&prj=475&rqi=FVGvgec1wYvt1VMJJQUaSKQEB3
GI-534 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Battery Room WSHP's: At the time of testing, heat pumps had no values that were shown on the faceplate that correspond to the actual units themselves. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198544&prj=475&rqi=gDbwO6IqQ68E3HWZ9ezm3eAnas
GI-533 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | CRAH Alarm Faceplate: During commissioning, the chilled water valve mismatch created a mismatch alarm without an alarm rectangle as well as a unit alarm with an alarm rectangle. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198542&prj=475&rqi=U9IOpUVxKqDPxfMjHl1umTkqjS
GI-532 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [6 empty] | Chiller String: During commissioning, Multiple Valves end switches did noy make while valves are fully open. We've seen this issue with Bray Valves due to temperature changes. E-tech verified if valves were configured correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198541&prj=475&rqi=rjX3UynsYnenw1YNHg2YQuy9lL
GI-494 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Riser designation text did not match actual destination. i.e. "first floor" corresponded to the riser serving the 3rd and 4th floors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198487&prj=475&rqi=QcgKSSDBTaZas5k7dFKGmRg3BY
GI-496 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | At the time of commissioning, chiller data was not being displayed on the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198491&prj=475&rqi=zvqPP7ebG0QX8PwhU2QStRvg4O
GI-531 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Alarm Banner: PLC_IO_Network Alarms were not counted in the full site alarm banner during commissioning. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198536&prj=475&rqi=dm1O0GjKqhpW3QJ7b71sayolAs
GI-530 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | CRAH HMI Program: During commissioning, CRAH's did not break out of grouping mode when not enough sensors are present. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198535&prj=475&rqi=ZtfOuEvgNcBvG40irvd8zonrpn
GI-529 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | CRAH Program: During commissioning, CRAH's did not pick a new lead unit when the lead unit was not communicating | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198534&prj=475&rqi=JafujXLb85cPFIsUJvsFdGut8b
GI-528 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Chiller Cooling Strings: During commissioning, a Wrench was displayed by the chilled water pump on cooling string chiller pages. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198532&prj=475&rqi=XsKw6qgzhP3gbbLS59s8NVsLl6
GI-491 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | MAU valves need to be controlled via temperatures sent by the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198481&prj=475&rqi=U3jdM3Vn6l2OpHNauoaZvX7LM4
GI-489 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | Chilled Water Manager - BMS During commissioning, chilled water bypass valve control wasn't functioning as intended. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198477&prj=475&rqi=eIGKreS9mPml7K976mXAPMvE48
GI-527 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | CRAH Alarm Program: During commissioning, a timer needed to be added to supply fan mismatch. When shutting down, as fans ramp down and command is 0, we shouldn't be in fan mismatch, add 30+ second supply fan mismatch timer. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198531&prj=475&rqi=nEF9A8x4B0UHpTBDJp6bSdSRCY
GI-523 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | CRAH Program: At the time of commissioning, The Supply Air Setpoint could not be changed manually on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198521&prj=475&rqi=4k7xm4RR4rqmnnvil90oQnLa81
GI-488 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | During commissioning, BMS did not have a roof plan showing - All required devices | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198476&prj=475&rqi=lbes9R7TcyQv4RbuSA7dckYfio
GI-495 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Chilled Water System BMS graphics: The DP being used on the manager page (to control pump speed) did not match the DP on the system page of the graphics. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198488&prj=475&rqi=p5yMkuRhvelR1K47Qy0fsDF0SJ
GI-526 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | CRAH Alarm Program: During commissioning, a "High Air Flow" alarm did not appear on the BMS. Alarm only appeared on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198524&prj=475&rqi=8OCV6kJD7JOR4y7BdU1dTwk351
GI-511 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | During commissioning, whenever a CRAH unit lost power, the dirty filter alarm was generated on the BMS. The normally closed contact was changed to normally open | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198506&prj=475&rqi=xjgHCJdizbQQ7nYMZ9wvWpY7wM
GI-516 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | During commissioning, the Isolation Damper Command Mismatch Alarm triggered within 22 seconds of the unit being commanded OFF by the BMS. The alarm cleared after 105 seconds. The Isolation Damper fail time is supposed to be 90 seconds. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198513&prj=475&rqi=qm0ZeD4GI9nFFJ77FAcaALuQAq
GI-485 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | At time of testing, BMS was missing all VAV's | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198469&prj=475&rqi=78yaPb9IOQQL4dR3cFWy8DpPUs
GI-513 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | During commissioning, we were able to write a negative Supply Air Temperature Setpoint on the HMI. We needed to set the range to not allow a value less than 0. Allowable range: 0-100F | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198510&prj=475&rqi=s0YMwaSXzdGJrxrKAIJoUOu5Yx
GI-518 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | During commissioning, when we tried to set the minimum fan speed in the setup menu (445), the minimum fan speed changes but did not reflect it on the faceplate Fan Speed Command. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198515&prj=475&rqi=QwE4ZVB1KIZUzP7RF2pcI7h4G7
GI-507 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | General Aveva Graphics Issue: At the time of commissioning, there was a hidden box at the name of equipment or type that didn't allow you to navigate to the correct window. It appears to be hidden for every name and if clicked it didn't do anything. These needed to be removed or hidden. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198502&prj=475&rqi=KNaQ9TppvqVjLWuUUJ90Fl9Lt9
GI-520 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | CRAH Program: During commissioning, the PID ramped up/down too fast when changing remote or supply temperature. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198518&prj=475&rqi=YjfaayJSA3W17QHmwIUvUEUFBo
GI-487 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | FOH/BOH --- At time of testing, BMS was not showing DX equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198475&prj=475&rqi=8b2RxBGh95ioaxf7D7iJZNgGIs
GI-524 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | CRAH Alarm Faceplate: During commissioning, in the event of a remote sensor fault, it showed a purple box on the CRAH alarm faceplate when it should have been a blue box around the alarm for a remote sensor fault. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198522&prj=475&rqi=EjarhJgb0FchpigqJv3JIqSouw
GI-504 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Fuel Fill Station is not shown on the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198499&prj=475&rqi=HzBfjn4955vsyUxhQFBnuJfDgU
GI-522 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | CRAH Program: At the time of commissioning, a power loss event on the CRAH unit didn't trigger a loss of Power alarm. A "Loss of Power" or separate power loss alarm is needed for this event. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198520&prj=475&rqi=tTNqn3iAOoUtR77BIZxqbbf3QS
GI-512 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | During commissioning, the supply and return CFM differed at the unit. Also, the BMS was registering the return CFM and not the Supply CFM on the Faceplate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198508&prj=475&rqi=h9WsDtHgn5kDm8CqaLVuOxVPo2
GI-500 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Boilers and Make Up Water are not shown on graphics on both the FOH and MOF | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198495&prj=475&rqi=5u8nkNg8OmL3LrcqjjYEfQOCVo
GI-521 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | During commissioning, the System Bypass Valves were hunting and going to 100%, making the pump speed increase to 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198519&prj=475&rqi=xDekNBoz4Hc60JfLvfNdRB1zha
GI-103 | DC22-2 | AMER | Ready for Verification | P3 Low CX | jonas.wudkwych@veolia.com | 2026-09-14 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS the TO DH 3001 button on the H block onelines page is not linked. Please fix | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638009&prj=673&rqi=xJXClMP80CDIQBhRor5vHkfinf
GI-102 | DC22-2 | AMER | Ready for Verification | P3 Low CX | jonas.wudkwych@veolia.com | 2026-09-14 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS Both buttons 1UPS_H_1 and 1UPS_H_2 are linked back to the C block onelines not H block | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637987&prj=673&rqi=vwzXjChDu8078I2xWItyTpuh9W
GI-104 | DC22-2 | AMER | Ready for Verification | P3 Low CX | jonas.wudkwych@veolia.com | 2026-09-14 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS the faceplate for the MLTX does not open when the MLTX is clicked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638012&prj=673&rqi=oTC1cGdHE9MpUVsH9HnEeU5Bbp
GI-099 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-09-09 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [6 empty] | Onelines are displayed differently for phase 2 compared to phase 1. Please clarify if we are using a different standard throughout the same building. Specifically there is now a second page that the UDPs STSs and PDUs are being shown. See screen shots. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637514&prj=673&rqi=TZyZrrqqGTruoirbciIYRNStYk
GI-098 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-09-09 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | MSB-ALL When one of the LBB breakers is closed the line animation between both the LBBs does not show power going through. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637502&prj=673&rqi=5GZMUEwpISGrwu8ktTFxrv2kR5
GI-095 | DC22-2 | AMER | Open | P3 Low CX | michael.acciaioli@veolia.com | 2026-09-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | DH CRAHs- CRAH graphics indicate CRAHs are in alarm for "not in Group" when units are in group mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636870&prj=673&rqi=brHxOT1iYQfaEIlPAxQlRrabW2
GI-096 | DC22-2 | AMER | Open | P3 Low CX | michael.acciaioli@veolia.com | 2026-09-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | DH CRAHs - Active number of CRAHs in Group on Unit HMI does not update. When removing units from the group or powering off units the number of units in the group does not change. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636872&prj=673&rqi=cl0wGenuxK8xaTpDWA0ylmSYvB
GI-097 | DC22-2 | AMER | Open | P3 Low CX | michael.acciaioli@veolia.com | 2026-09-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS |  | equipment type |  |  |  |  | EF's - Exhaust Fans that have been started and energized are not shown on the BMS. i.e. EF-C | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636877&prj=673&rqi=xaAgXJViUHuJzeHfRdVaiNTMRO
GI-094 | DC22-2 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-09-01 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | Chiller Bypass Valve logic: [Common to all ACC's on previous phase] After stage up to a new chiller, the enabled chiller goes through its normal start-up and starts increasing from 0 GPM to a flow similar to all running chillers. However, the bypass valve immediately reads this start-up as a failing to meet minimum flow state and starts to open. The bypass valve does not need to open during every stage up of a chiller, and should let the new chiller go through its normal ramp-up before being called to open. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636302&prj=673&rqi=PXXGIElKKZooh9BHq67u4Yy7be
GI-093 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-08-26 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | [6 empty] | Battery Cabinets - ALL the control power for the battery cabinets has not been labeled showing where power comes from. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635311&prj=673&rqi=4IMDzV9ISbMc7iNlordAMC506g
GI-092 | DC22-2 | AMER | Open | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-08-25 04:00:00.000 +0400 | DEL - Delta Elec |  | Missing Components | Commissioning | [6 empty] | On STSs there is hardware missing from multiple locations on multiple units. See photos. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635100&prj=673&rqi=qMp6051uwTYvAlqn5D87CMfG09
GI-085 | DC22-2 | AMER | Open | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-08-12 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | [6 empty] | On UPS_A_1, A_2, B_1, B_2, C_1, C_2, D_1, D_2, H_1 and H_2 There is a typo on the control wires labeled 1UPS_A_1-AP30_TB1-1 / 1UPS_A_1-AP30_TB1-2. These labels should read 1UPS_A_1_TB1-1 / 1UPS_A_1_TB1-2. This typo is across the 1 and 2 UPSs in all rooms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633234&prj=673&rqi=cy5Xs0ghMgTgj9JqrbG3s2yHfd
GI-078 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 1GSB_6 IO/Control Cabinet - SE DP discovered a common issue to all GSBs during phase 2 testing and inspection. During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633108&prj=673&rqi=BHk6KyNR3G5abssIcdHvQRv9a7
GI-077 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 1GSB_5 IO/Control Cabinet - SE DP discovered a common issue to all GSBs during phase 2 testing and inspection. During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633107&prj=673&rqi=weinrGbrMnRufMiQI6rF24SdJE
GI-072 | DC22-2 | AMER | Closed | P2 Medium CX | francis.callan@veolia.com | 2026-08-11 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [6 empty] | [Common to all ACC's/ Harmonic Filters]: Fuses continue to fail when opening and closing disconnect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633083&prj=673&rqi=3n31DAnSmWG1Ptvf6DTY834kGZ
GI-075 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 1GSB_3 IO/Control Cabinet - During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633103&prj=673&rqi=t6NBtVOdLoOTIdAFdldlDkPoKd
GI-073 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 1GSB_2 IO/Control Cabinet - During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633094&prj=673&rqi=1A4hgj8o3rILY5eSpmJ5tSiIxD
GI-074 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 1GSB_1 IO/Control Cabinet - During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633101&prj=673&rqi=FtYwqaPkSnGHCUy4BBJZ3LFPLi
GI-076 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 1GSB_4 IO/Control Cabinet - During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633105&prj=673&rqi=KHowelQA5WvuMj4BJEdyORdg2z
GI-079 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 1GSB_7 IO/Control Cabinet - SE DP discovered a common issue to all GSBs during phase 2 testing and inspection. During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633109&prj=673&rqi=jmawsovQ9B1m6JLPjfuFu0slpA
GI-080 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 1GSB_8 IO/Control Cabinet - SE DP discovered a common issue to all GSBs during phase 2 testing and inspection. During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633110&prj=673&rqi=Ku1Vi0jGynHTVBkEHV9HqGVoLx
GI-071 | DC22-2 | AMER | Open | P1 High CX | francis.callan@veolia.com | 2026-08-06 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | [Common to All CRAH's] No torque marks present on all victaulic clamps. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632600&prj=673&rqi=ZkFIBoSV6k4DnXa4y5Z2b0ygU6
GI-070 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-07-29 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/ Fault | DCOS | [6 empty] | MSB-ALL The PQMs on the MSBs cause comms loss when added onto the switch in the controls section of the MSB. Hanley troubleshooting is ongoing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631211&prj=673&rqi=nfXrGDnBU96WntNL9QLMiucBCY
GI-069 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-07-28 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/ Fault | DCOS |  | equipment type |  |  |  |  | MSB-All The Communication Alarm Status is not properly displaying on the faceplate for the breakers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631104&prj=673&rqi=8D1Pb4I41AZIIMglfdZuGBuuaw
GI-067 | DC22-2 | AMER | Closed | P2 Medium CX | william.park@veolia.com | 2026-07-28 04:00:00.000 +0400 | Electrical Contractor |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | ALL NEW DH CRAHS: Metal Shavings have been found all around and on top of the ATS within each electrical section of the Data Hall Mega CRAHS after drilling into the metal frame. Metal shavings need to be vacuumed and wiped away from each ATS and within each electrical box of the new 40 Data Hall CRAHS. Energization cannot occur until this action is completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631069&prj=673&rqi=Dj4RSsv4iuhqJEBe2zj2Kfhprs
GI-068 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-07-28 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | MSB-All The breaker racked out status displays when the breaker is racked out to the test position but the status returns to racked in when racked all the way out. This appears to be an issue with the point being brought in through Modbus. The test position status works correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631103&prj=673&rqi=qPMbNlUbUyOKJbFRbXXEUlqefj
GI-062 | DC22-2 | AMER | Closed | P3 Low CX | eric.gremp@veolia.com | 2026-07-10 04:00:00.000 +0400 | Electrical Contractor |  | Torque required | Commissioning |  | equipment type |  |  |  |  | STSs in electrical room H have all had 2 ground lugs torques broken. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628727&prj=673&rqi=luOiJoPwOeLkdFpbD6kyObaNuq
GI-056 | DC22-2 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-07-08 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning | [6 empty] | Hanley Gear- MSBs and UDPs ALL are missing the top hat grounding wires | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628386&prj=673&rqi=Hntn0Iq2KKJvF17UvDV4xIHKif
GI-053 | DC22-2 | AMER | Closed | P3 Low CX | eric.gremp@veolia.com | 2026-06-30 04:00:00.000 +0400 | VER - Vertiv |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | UPSs: All of H-block UPSs are missing kickplates. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627447&prj=673&rqi=IxkD6n8JGKAtFc2CI53iTns69E
GI-052 | DC22-2 | AMER | Work Completed | P3 Low CX | eric.gremp@veolia.com | 2026-06-25 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | PDUs: This general issue is to track all of the damaged nut inserts in the back of the PDUs so far for this issue damaged inserts have been discovered in 1PDU_C2R1_3, and 1PDUC2R1_2. As mor damaged inserts are found they will be added to this issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627076&prj=673&rqi=mft7AJXn13PPBlXOmt8ECzbaAj
GI-050 | DC22-2 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-06-16 04:00:00.000 +0400 | SGB-SMIT |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | MLTX-All We are missing the fiberglass supports for the MV cables on the high side of the transformers. I believe SGB will be shipping these to site to be assembled by Rosendin. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625543&prj=673&rqi=JF3rf7jXuF81N6qnLXbCo4kkld
GI-049 | DC22-2 | AMER | Closed | P3 Low CX | jonas.wudkwych@veolia.com | 2026-06-08 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning | [6 empty] | Electrical room CRAH stands came tack welded and are different from the first phase please see photos. Are these stands acceptable and can we get updated submittals showing these stands? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624340&prj=673&rqi=lAueRqsg5MOMQuBp9OJyMqcfG8
GI-048 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-06-08 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Damage | Commissioning | [6 empty] | One of the stands for the Vertiv electrical room CRAHs is damaged and will need repaired/replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624339&prj=673&rqi=FXL9EuLxLWlWwNGR5H6MgfbI9q
GI-047 | DC22-2 | AMER | Open | P3 Low CX | eric.gremp@veolia.com | 2026-06-04 04:00:00.000 +0400 | DEL - Delta Elec |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | STSs(H-Block): 1STS_H1R1_1, 1STS_H1R1_2, 1STS_H1R1_3, 1STS_H2R1_1, 1STS_H2R1_2, and 1STS_H2R1_3 all have been scratched and damaged while pulling MC cabling . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623984&prj=673&rqi=LQyeViNJkF2uzCPydjjXOUGPTi
GI-045 | DC22-2 | AMER | Open | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-05-18 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | UMDSB-ALL The Spare Breakers in Q08 have a 250A breaker plug but the submittal shows a 150A plug set @ 70A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622211&prj=673&rqi=04JCS6Ehb5a6ifLfvQNuDM6vKC
GI-044 | DC22-2 | AMER | Closed | P3 Low CX | eric.gremp@veolia.com | 2026-05-14 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | MSB (ALL): The Hanley Submittal RS-485 communications wiring does not match field installation including location of EOL resistors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621883&prj=673&rqi=kWgL0NcL273aZShLchg6GjFfke
GI-042 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-05-05 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MSB-H B & C a plate on each phase on each shipping split was missed when the bolts were torqued. Everyone on site is aware, old hardware is being removed, new hardware is on the way and the re-torqueing will start tomorrow. Â This issue has been added for tracking purposes.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620449&prj=673&rqi=aJYrFdHzEZeROsTlKvZUj2wc1e
GI-041 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-05-05 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | UMDSB-ALL 2 breakers on each board Q06 and Q07 have the incorrect lug sizes that can only accept 3/0-350 kcmil. The electrical 1 lines call for #1 or 2/0 AWG depending on the length of the run.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620387&prj=673&rqi=oF1CPafW9bp2aPI0tvb0sooOf3
GI-043 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-05-05 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design correction needed | Design |  | equipment type |  |  |  |  | MSB-ALL the top hat access in the top back of section 09A for chiller power faces the wall and will need to be modified or changed out to face forward to allow the conduit and cables to be installed. On the last phase the top hat was modified. (See photos of both attached) The front top hat is for the MC going to the MDSB (breaker Q10) and the back top hat is for the power to the chillers (breaker Q11). Â Because of the top hats that were included for the MC cables on this phase there still might be issues with access on the install and it might be better to install the chiller cables before the MC on section 09A Talking with Hanley there are 2 options, either the modification of the existing top hats or ordering new ones. Both will need approval from Hanley and ordering new will have a lead time that could push schedules. Â This will need to be done on 1 top hat on all 5 MSB lineups and has potential to cause delays with install and startup. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620450&prj=673&rqi=ZIAaky8B6mXbIwYwuqjNxcG52U
GI-038 | DC22-2 | AMER | Closed | P3 Low CX | jonas.wudkwych@veolia.com | 2026-05-04 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MDSB-ALL Make sure that the equipment meets the minimum clearance of 4 inches from the wall. It appears that MDSB-H as well as other units are less than the required 4 inches. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620248&prj=673&rqi=XKHGLk6hvk8fiGMKjKPle8Gs9z
GI-035 | DC22-2 | AMER | Open | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-05-01 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | MLTX-ALL The control wiring is landed in the control box terminations and not on the transformers. REI has schematics to land the wires in the control box but not on the transformer. Please confirm that this is a task for REI and not SGB as well as obtaining proper documentation to install these wires on the transformer from SGB if this is an REI task. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620132&prj=673&rqi=iNLuSvGkzqfF2E6lAguHvalte0
GI-036 | DC22-2 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-05-01 04:00:00.000 +0400 | SGB-SMIT |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | MLTX-ALL Missing components to land cables run going from the MVTBs to the MLTXs, on the last phase the connections were made on bus bar inside a separate part of the enclosure (see picture) and there were factory cable connections to the actual transformer. I do not see these connections or cabling and support. Will we be connecting the MLTXs the same way as the last phase, if so are we missing parts from SGB? If the cables are being terminated differently can we make sure we have proper documentation and instructions on making the terminations from SGB? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620133&prj=673&rqi=iR97HCVZPRMlUVGogVtDCYrwmM
GI-033 | DC22-2 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-04-28 04:00:00.000 +0400 | Electrical Contractor |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | MLTX-ALL The bus bar inside the enclosure on MLTX A, B, C, D, and H has been improperly installed and will need corrected. There is a missing insulator that should connect the bus bar to a support bracket. Please see pictures and attached document. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619767&prj=673&rqi=WIqvqjHsiGQ2oHShsd4dCvnS0Y
GI-032 | DC22-2 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-04-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MSB-ALL The ground bus bar on the back of all MSB sections that was converted to MC bus connections is missing a 1/4" spacer. This was missed during the rework done at the warehouse. This is an issue already known by Hanley and is being added for tracking purposes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619371&prj=673&rqi=BFm4REibXVnqh4Nmzi7X7vsArQ
GI-031 | DC22-2 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-04-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MSB-ALL. During the torqueing of the shipping splits between sections 3 and 4 it was found that some of the factory torque connections will need to be broken and associated hardware replaced because of the MC bus bar conversions. This was missed during the warehouse work completed by Hanley and will now need to be done on site. This will This will affect all MSBs This issue was entered for tracking purposes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619370&prj=673&rqi=aTFyPXxVxQVMO3jCLl8e930QhL
GI-028 | DC22-2 | AMER | Open | P3 Low CX | jonas.wudkwych@veolia.com | 2026-04-22 04:00:00.000 +0400 | DEL - Delta Elec |  | Labelling | Commissioning |  | equipment type |  |  |  |  | STSs (common to all) - SOO placards to be replaced with accurate placards showing correct key #s. The SOO placard installed shows references to K1 K2 and K3 keys but the actual keys are A1 B1 and A3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619100&prj=673&rqi=crtwc63aRDnWsupcieNSLLFxWS
GI-027 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-04-22 04:00:00.000 +0400 | DEL - Delta Elec |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | STSs (common to all) - fuse kits for MSB control power were not installed on the units. The photo with the fuse kit is from an STS on the previous phase.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619092&prj=673&rqi=vpDWpAuZ0kK6CXTN9qeinq2ezJ
GI-029 | DC22-2 | AMER | Open | P3 Low CX | jonas.wudkwych@veolia.com | 2026-04-22 04:00:00.000 +0400 | DEL - Delta Elec |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | STSs (common to all) - Neutral kit placards are missing. Please confirm that the neutral kits were installed on the units and provide/ install missing placards. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619101&prj=673&rqi=cO8v5D1Lvi9A3fzW1zeOKoeFWT
GI-026 | DC22-2 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-04-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MSB-ALL The ground bus bar between sections 3 and 4 appear to be improperly installed. Leonard from Hanley is already checking with the engineer on proper installation and sourcing the correct hardware. This is an issue across all the MSBs on site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618925&prj=673&rqi=kQQrxmRQg9cqfx6QroWYEfpDY5
GI-018 | DC22-2 | AMER | Closed | P3 Low CX | jonas.wudkwych@veolia.com | 2026-03-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | General Design Issue | Design |  | equipment type |  |  |  |  | MSB - ALL on page 2 of the MSB as-built the Q03 Breaker is shown as having accessory 7 (the 120V Shunt open) but that should be shown on the Q10 Breaker. Also Accessory 8 is not included in the accessories legend. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616568&prj=673&rqi=npWrxDXUOpWMSsgDqDzt7SEIYw
GI-009 | DC22-2 | AMER | Open | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-03-20 04:00:00.000 +0400 | Electrical Contractor |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | MVTB: The bottom front covers when taken off the unit are easily knocked over in a way that damages the front handles. One of these was accidentally knocked over when inspecting the unit and was damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616151&prj=673&rqi=qHT63x3JEQUqwxzozMD12q3AOb
GI-006 | DC22-2 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-03-20 04:00:00.000 +0400 | SCH - Schneider MV |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MVTB: Multiple bolts on the bus bars located in the bottom sections are not long enough to go all the way through the nuts to properly secure the bus bar. These will need to be replaced with longer bolts so at least 2 threads are showing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616148&prj=673&rqi=GS1fkGG2wgzxljK9shifPqLiic
GI-007 | DC22-2 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-03-20 04:00:00.000 +0400 | SCH - Schneider MV |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MVTB: Edge guard throughout the unit is held in place with painters tape in some places and is not properly fitted/installed to protect wiring from rubbing against metal edges. This issue is in multiple sections of the unit and will need to be addressed and wiring thoroughly checked to make sure the outer insulation on this and other units was not damaged during transport | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616149&prj=673&rqi=rwcwE5OLVurnRkVwIsk0feLAOW
GI-005 | DC22-2 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-03-20 04:00:00.000 +0400 | SGB-SMIT |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MLTX: Upside down washers on a bunch of the connections | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616147&prj=673&rqi=8pdVYHmdKmvphCAqMWPQdPykMF
GI-002 | DC22-2 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-03-20 04:00:00.000 +0400 | SGB-SMIT |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MLTX: Washers on non-electrical connections are not uniform in size across multiple transformers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616143&prj=673&rqi=TqHFMraD36iOQpja0OWJ7yrFV8
GI-391 | DX03-2 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-07-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Access Control System (ACS) â€“ The "Door Not Used/Opened" event shall be configured and programmed in the ACS. During testing, when a valid card was presented and the door was not opened within the configured time period, no corresponding event or notification was generated or recorded in the event log | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629339&prj=603&rqi=pYOr50jl2chljw54YLMX6z4Ayw
GI-392 | DX03-2 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-07-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Access Control System (ACS) â€“ Battery monitoring is not available. The system does not provide battery status, battery fault, or low battery indications for monitoring and alarm purposes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629340&prj=603&rqi=PcZkpPvSjclqROblJm4dBggjtb
GI-388 | DX03-2 | S-EMEA | Closed | P2 Medium CX | v.baddegama@core-group.me | 2026-07-13 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/ Equipment failure | Commissioning |  | system | Fuel System |  |  |  | Fuel PLC-1 was not communicating with DCOS. Fuel system vendor confirmed PLC-1 is operating correctly on site. DCOS team was not able to ping the PLC from Equinix local server however, it was possible to ping the PLC from the global EQX server. DCOS team advised it could be a network IT issue. UPDATED: DCOS team have confirmed the PLC is communicating to the PLC when connecting directly with the DCOS laptop. Several workshops have been held between the DCOS team, Vendor and Equinix Gen2/Server teams to work through why the PLC is not able to communicate across the network. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628805&prj=603&rqi=RLYzPOe0BA1Yz4w9a7VMSUvotn | https://equinix.facilitygrid.co.uk/x/project/603/system/12118
GI-389 | DX03-2 | S-EMEA | Closed | P2 Medium CX | v.baddegama@core-group.me | 2026-07-13 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/ Equipment failure | Commissioning |  | system | Fuel System |  |  |  | For Fuel storage tanks (FST) No. 3 and No. 4 located in DX3.1 (part of DX3.2 phase), an interstitial leak alarm was active on DCOS system. The fuel system vendor (Green Adaptech / GATSS) stated that the tank leak sensor is connected to the numeracator panel installed in the fuel pump room and the signal originates from numeracator panel and goes to the fuel PLC. GATSS stated the manufacturer of the numeracator panel and leak sensor (in the US) will need to be contacted to troubleshoot and resolve this issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628806&prj=603&rqi=jNVdsn3tX74Nnq9eQ5yrbI36Tb | https://equinix.facilitygrid.co.uk/x/project/603/system/12118
GI-387 | DX03-2 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-07-02 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Component/ Equipment failure | Commissioning | Electrical â€“ LV | equipment | 1-RPP-F-4 | RPP - Remote Power Panel |  |  | During Thermal scanning of the RPP's it was observed that the temperature with 54kW load connected . During investigation it was found that connection at the incoming MCCB (Factory assembled) was loose. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627711&prj=603&rqi=jXhMMukz2R1ULv17FAa8ABcj43
FPT-277-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-06-29 04:00:00.000 +0400 | ABEC - DCOS | L4 | Component/ Equipment failure | Commissioning |  | equipment | CHWS L4 FPT & Mech IST |  |  |  | One of 3 flowmeters on one supply flow header going to data hall (RAS-13) was removed to send for calibration. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627287&prj=603&rqi=uTmmBrEOq0tYcPXSHTMnPBghzR
GI-386 | DX03-2 | S-EMEA | Closed | P2 Medium CX | v.baddegama@core-group.me | 2026-06-27 04:00:00.000 +0400 | VER - Vertiv |  | Component/ Equipment failure | Commissioning |  | equipment type |  |  |  |  | APPLICABLE FOR ALL CRAH's: Vertiv/MDS stated that the CRAH HMI is a new product and that all HMIs need to be replaced. The following issues were observed during various times of testing: 1). When fan speed reaches 100% the HMI goes blank/white and HMI makes a sound. To reset the HMI, the cable connected to the HMI will need to unplugged and plugged in again. MDS engineer was observed to carry out this action multiple times on random CRAHs during various tests (chiller load testing and GF Data Hall load testing). 2). On random data hallCRAH's the HMI freezes preventing any touch input on the display by the user. This was particularly observed in the data hall CRAHs. 3). On random data hall CRAHs it was observed the response to user touch inputs was very slow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627170&prj=603&rqi=oV429KIH6PHcIqqvPLV7b0VeIW
GI-385 | DX03-2 | S-EMEA | Closed | P2 Medium DCOS | v.baddegama@core-group.me | 2026-06-26 04:00:00.000 +0400 | ABEC - DCOS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It was observed on 26th June 2026, the DCOS auto/Manual switch for number of devices in cooling manager manager was not working. Could not be changed from Auto to Manual. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627163&prj=603&rqi=AjzsSpHUwgLKCLveJvGpqUq7e3
GI-383 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-19 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | DCIM BCM Issue | DCIM |  | equipment type |  |  |  |  | During RPP checks with operations for DCIM communications it was recorded there were communication issues. ABEC traced the communication issue with the Schneider Gateway. The polarity of the internal connection to the SCU100 was found to be reversed. ABEC connected a separate cable directly from the SCU100 controller to the Schneider Gateway and confirmed that communication with the gateway is working properly. The panel wiring needs to be reverified to ensure proper communication. The cable is currently marked as A(-) and B(+), which appears to be incorrect. It should be A(+) and B(-). The termination should also be checked and verified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626225&prj=603&rqi=QAEM4GlhOsgbyZRVAvgjHExsVR
GI-111 | DX03-2 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-06-17 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/ Equipment failure | Commissioning | [6 empty] | Luminaires CMP2-GF-L7-15, CMP2-GF-L7-17, CMP2-GF-L7-19, CMP1-GF-L2-02, and CMP1-GF-L2-04 failed the Battery Autonomy Test (Ground Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625637&prj=603&rqi=2kUNrEnWCrcWyAVxXhVlMIyaVg
GI-110 | DX03-2 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-06-16 04:00:00.000 +0400 | VER - Vertiv |  | Component/ Equipment failure | Commissioning |  | equipment type |  |  |  |  | During STS-F-2 Testing the following was Observed in the ground floor Data Hall CRAH: - low Humidity Summary Alarms present in several CRAH. - Above alarms not resetting on HMI - â several HMI unresponsive - Several HMI were observed to have their â time & date reset to defat (year 2000) - â GC had to switch the CRAH off and on to reset alarms - â Fans not ramping up with return temp reaching 36deg (advised the CRAH were set to 36Deg return air). These were not reamping up individually or as a group. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625525&prj=603&rqi=Vrg8Dl1yuYAb6mfq4qrcf3JSSB
GI-106 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-11 04:00:00.000 +0400 | TRN - Trane |  | Commissioning Issue | Commissioning | [6 empty] | Trane site technician placed the HMI into STOP mode without notifying anyone. This caused the Chiller to not operate correctly (Compressors failed to start when required). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624896&prj=603&rqi=iSzhxeEiPHwDuou7s3dC9RW4Ws
FPT-366-001 | DX03-2 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-06-09 04:00:00.000 +0400 | ABEC - DCOS | L4 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1-STS-E-1 | STS - Static Transfer Switch |  |  | Observed the Kw reading not matching actual output kW on STS graphic. output side of STS and STSSB not energised (white) line. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624634&prj=603&rqi=9kYkeUbmCAlR8FGvLfrsv6Hc5T
GI-105 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-06 04:00:00.000 +0400 | VER - Vertiv |  | Labelling | Commissioning |  | equipment type |  |  |  |  | UPS labels to be corrected. 415V not 400V | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624283&prj=603&rqi=AYpIVSz277yAkMwvJnGJ18ykkZ
GI-103 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-05 04:00:00.000 +0400 | CMM - Cummins |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | During UPS level 4 testing, while on Generator source it was observed at both the Generator controller and DCOS the Power factor and the KVAR were reporting 'out of range' at the DCOS. The Power factor was showing a negative power factor. The readings at the Generator ACB on the MSB were found tpo be reading correctly. it is noted that the load bank from DX3.1 is a resistive LB and there is also live loads on the MSB Output board (CRT SMDB). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624126&prj=603&rqi=m4lmWE3IdU7TwmQrlP4Mt4UOUh
GI-097 | DX03-2 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | ABEC - DCOS |  | DCOS Comms Issue/ Fault | DCOS |  | equipment type |  |  |  |  | CHWS no/low flow observed across the system during UPS Level 4 testing (DCOS Cx is ongoing for valves and sensors) after the Data Hall CRAH were started up. In the off positions the CRAG PICV are held in 100% open position. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623883&prj=603&rqi=sDyIi44b7cQIzMGo0jbGXTvRWg
GI-102 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Battery cabinets (D, E & F) Cores 1 & 2 Labels to be corrected after cable orientation swap. ALL UPS battery cable labels to be corrected also. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623896&prj=603&rqi=aQoEO2rM84OrDVHaUbTjr61myP
GI-100 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Graphics Issue | DCOS | [6 empty] | UPS High Alarm limit incorrectly calculated on the DCOS Template (80%). Value inputted on the template is 2250, this should be 1780. These were corrected for UPS-D & UPS-E level 4 testing, however it has been observed these have reset to the incorrect values. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623893&prj=603&rqi=kuonmZhBMLMZmvgeljP6Jlf8Zp
GI-101 | DX03-2 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | ABEC - DCOS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | DCOS footer/banner missing Values from DX3.1 weather station including the OAT, OAH, OAWB, DX3.2 PUE value and Fire alarm status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623894&prj=603&rqi=FcuHjwH7WooJ4A4NUpxYMAc3wi
GI-099 | DX03-2 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | ABEC - DCOS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | DCOS Generator Template 'Deviation from set point'Was shown as Voltage instead as Percentage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623892&prj=603&rqi=uDdupwBe1IpstiebdSIJ1FYmEN
GI-098 | DX03-2 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | ABEC - DCOS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | DCOS LCP Templates are BLANK. This is applicable to ALL DCOS LCP panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623891&prj=603&rqi=LGv3aiNK3zzc3sn5uGSNi4mQRI
GI-096 | DX03-2 | S-EMEA | Closed | P2 Medium DCOS | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | Chiller Valve (located at the return to the chiller) was closing when the Chiller compressors switched off. this was causing the chiller to shutdown on Evaporator no flow alarm'. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623878&prj=603&rqi=nxvL1wwaXyjTDuV3s9FcqEp0nl
GI-092 | DX03-2 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-05-22 04:00:00.000 +0400 | Consultant |  | General Design Issue | Design |  | equipment type |  |  |  |  | CHWP supply MCCB at the MSB is furnished with an ELR with trip function. Is this necessary? During the UPS-D level 4 testing we observed that CHWP-D tripped on earth leakage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622809&prj=603&rqi=sTN9BF6UfKGUg72DNcNI0UZ9Ok
GI-089 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/ Equipment failure | Commissioning |  | equipment type |  |  |  |  | When switching the fuel system from Auto to manual the system operates fine. When switching from Manual to Auto Vendor is advising us that the PLC requires a re-boot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622465&prj=603&rqi=zrAW5NKdGB33YuZpAIGXDpkL5J
GI-090 | DX03-2 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/ Equipment failure | Commissioning |  | equipment type |  |  |  |  | During the inspection of Generator D, it was observed that when a low fuel alarm is triggered, fuel is pumped not only to Generator D but also to Generator E&F. This is not compliant with the intended operation, as each unit should function independently. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622466&prj=603&rqi=AThysfVnwFYLhU334GF4ireYpR
GI-088 | DX03-2 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-05-18 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | The MSB Breaker settings to be secondary tested based on the latest revision LV Coordination study. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622195&prj=603&rqi=wHDMRVzBHcAFeOGjfzR3c0piHa
GI-087 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Mimic on the panels for the castell key operation to be corrected (this was observed during L2 testing and has been recorded on the Cx meeting from 5th Februrary. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621769&prj=603&rqi=iUd8qyLyUmq83ILsrAkCBuyll6
GI-086 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-05-12 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | LVBR Specification section #23 'Aux Power supplies'. The sequence upon losing PS1 & PS2 then rebooting to PS3 upon receipt of Generator is not working correctly as the HMI moves to Maintenance Manual mode and locks out (requires manual resetting and no aut transfer can occur. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621252&prj=603&rqi=MnX7InfzBDPuL9rgiEZKZUiw7k
GI-084 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-05-09 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Component/ Equipment failure | Commissioning |  | equipment type |  |  |  |  | MSB-LVBR PSU with an inverted signal providing a DC alarm at HMI and to DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621038&prj=603&rqi=r3pEsuBfj7izmFFYMAWrIp60OW
GI-081 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-05-05 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning | [6 empty] | FUTURE LIQUID COOLING CHW LINE IN 1st floor Data Hall (1 No.) near CRAH-48: A minor clash was observed between 1 isolation valve handle and the DRV handle. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620388&prj=603&rqi=YUwCIKINJTHUlETP4odaSrtvWh
GI-074 | DX03-2 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Battery cables from UPS to Battery found to have been terminated in the incorrect battery cubical which do not correspond with the correct UPS_Cores. although this does not impact the operation of the UPS, this does not align with the design arrangement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619061&prj=603&rqi=nH73XDsbbHhqnz06lGdmr091lw
GI-073 | DX03-2 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-04-21 04:00:00.000 +0400 | VER - Vertiv |  | Component/ Equipment failure | Commissioning |  | equipment type |  |  |  |  | Advised by the GC & Vertiv during UPS L3 commissioning the UPS PCB requires replacement (applies all 3 UPS).. Vertiv toi confirm to provide a report and advise what the cause of the issue was. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618820&prj=603&rqi=jnStdenRtJIasRGFochl8DoGmt
GI-072 | DX03-2 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-04-14 04:00:00.000 +0400 | General Contractor - Commissioning |  | Incomplete Connections | Commissioning |  | equipment type |  |  |  |  | Incoming earth cable is not connected to the outgoing side of the isolator. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618106&prj=603&rqi=VRhcrkkrcliDBDol0zlQJi9a30
RT1ELEC-586-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-26 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1-GSM-RACK-02 | CAB - ICT Cabinets |  |  | GSM Rack-02: At the top of the GSM rack where the fiber optic cables enter into the rack, there is no brush type cover. There is a risk of dust and debris falling into the rack through this cable penetration hole. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616506&prj=603&rqi=Qq8SXvljx96zMSKcOhhQlruCLR
GI-066 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-03-26 04:00:00.000 +0400 | Equinix Design Engineer |  | General Design Issue | Design |  | equipment type |  |  |  |  | During Level 3 STS Start up, during total maintenance bypass (Bypass is energised but the STS including the HMI is shut down) there is no indication on the STS breakers/isolators (other than S2 MCCB LED) that there is LIVE power passing through the busbar, or any interlocks (doors, panel covers etc..The busbar is exposed within the panel as there is no isolation between panel sections of the STS. This is seen as potential safety risk hazard during maintenance activities. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616535&prj=603&rqi=jn8J6Zgj1EJch7LiDl9yZceHms
GI-067 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-03-26 04:00:00.000 +0400 | CMM - Cummins |  | Labelling | Commissioning |  | equipment type |  |  |  |  | The labelling in the field for circuits fed from the Generator DB within the container are incorrect and do not provide the circuit reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616551&prj=603&rqi=vzUDa2Ize6tYN59luUomhiPA4d
GI-060 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning |  | system | CHW System |  |  |  | It was observed that there was no chilled water flowing through the CRAHs in 1st floor electrical rooms (switchrooms and STS Rooms string D & E). Contractor needs to investigate the issue on site and provide a reason for no chilled water flow based on their observations at site. Please see attached some photos from the CRAH HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616268&prj=603&rqi=Vx0rGUFACuaXM62glZlo029vM8 | https://equinix.facilitygrid.co.uk/x/project/603/system/12115
YT1SEC-1-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-03-18 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not complete | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-C | ACU - Access Control |  |  | The doors on Buffer Vessel Room (1331-B, 1331-C, 1331-D, 1331-E) and Future ETS Room (1351-B) are not aligned, preventing the completion of ACS device installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615932&prj=603&rqi=cTE1Cx3WqlQLRXR6roMwK0VfKp
YT1ELEC-557-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | B2-ODF 4 | CAB - ICT Cabinets |  |  | The cable tagging inside B2-ODF-04 rack in DX3.2 FER-C is incorrect. Refer to attached photo for details. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615714&prj=603&rqi=edAgyRUzOMyPg6qOhVOXLi4pHT
YT1ELEC-143-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-03-16 04:00:00.000 +0400 | Low Voltage Electrical Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1-RPP-F-8 | RPP - Remote Power Panel |  |  | Drawing pocketvmissing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615708&prj=603&rqi=b3voHET4qRN25vN3f3Pa6ZXv2T
YT1SEC-3-003 | DX03-2 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-03-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not complete | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-E | ACU - Access Control |  |  | The door between 3.1 and 3.2 has not been installed, resulting in the installation of acs device remain pending. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615408&prj=603&rqi=mdmPXvxb1VDcKSPmqpjFrvpVxC
YT1SEC-3-002 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-E | ACU - Access Control |  |  | ACP-01 NER-E: FF ELECT ROOM has no label on door Motorised lock. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615247&prj=603&rqi=JlCAmRoq8JhdBAEbmJgZM923Lq
GI-057 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-03-10 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | PQM used for monitoring the Transformer points not configured at the factory, impacting Transformer L3 testing, | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615252&prj=603&rqi=IYWLvw90uxLI6Cv855FTixQ86y
YT1SEC-4-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Documentation not issued/ Required | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-F | ACU - Access Control |  |  | FOR ALL Access Control Panels: The related shop drawings (Schematic, Layouts and panel wiring diagrams) need to be updated as per site condition then uploaded officially to ProCore for approval. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615200&prj=603&rqi=MqSPOL8Ldzz4Qe7rQTIGqiDAM8
YT1SEC-3-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not complete | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-E | ACU - Access Control |  |  | No continuity observed on cable from ACP-01 NER-E panel to STS Room E motorized lock (EM). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615246&prj=603&rqi=fohY36fw7eQ4DXhwGWwf2rG76s
GI-055 | DX03-2 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-03-10 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | DCOS Installation not complete | DCOS |  | equipment type |  |  |  |  | During DCOS P2G testing it was observed that when the ACB on the MSB were racked to the test position then retuned to Service, these remained in the 'test' status showing on the DCOS Graphics. SAS Site team confirm that Modules for the ACB are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615250&prj=603&rqi=y2XTbBk0IkvfJoWa3hyn51LZy0
YT1SEC-2-002 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not complete | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-D | ACU - Access Control |  |  | The junction box cover is missing for the door of STS Room G (1100A). Also ensure junction box cover has the correct tag label. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615117&prj=603&rqi=GYLauCWVT6AAZ0IWgBouFct1yo
YT1SEC-2-003 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-D | ACU - Access Control |  |  | No cable continuity observed for door contact of GF Data Hall door B (1500 B) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615118&prj=603&rqi=dwdZ04KGSzJWoF8osIpmN8jScj
YT1SEC-2-004 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-D | ACU - Access Control |  |  | One of the door contact devices for the door of MMR-D (1081A) is damaged and needs to be replaced. Cable continuity test to be carried out after new door contact. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615119&prj=603&rqi=N7J589NahgB1d4Qmz96jdKRrwh
GI-049 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-04 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-F | ACU - Access Control |  |  | ACP-01 NER-F: Labelling on junction box above FF Data Hall Door C is pending. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614689&prj=603&rqi=tJ0DGCq6QqEuNDpXgeRcphqoff
GI-048 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-03-03 04:00:00.000 +0400 | Equinix Design Engineer |  | General Design Issue | Design |  | equipment type |  |  |  |  | It has been observed there is no Humidity control via a Heater battery or other physical device within the AFU/MAU's. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614606&prj=603&rqi=baQrNAHv5tUNZR0IYMIAuymdoP
GI-047 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-02-26 04:00:00.000 +0400 | TRN - Trane |  | Incomplete Connections | Commissioning |  | equipment type |  |  |  |  | Although torque marked, manufacturers earth bar connections found to require tightening. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352229&prj=603&rqi=nNJNzgfSQqlBtEqujZo1nhn5oI
YT1SEC-2-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-02-25 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-D | ACU - Access Control |  |  | During L2B Cable Point to Point inspection on 25th Feb 2026, it was observed that the cable connecting to the door contact in Battery Room F was damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212851&prj=603&rqi=cd0HAfk7ITjn9Idbsim7psOY7E
YT1ELEC-540-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | m.louie@core-group.me | 2026-02-20 04:00:00.000 +0400 | Low Voltage Electrical Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1-PFC-E | PFC - Power Factor Correction |  |  | The isolator rotary handle is missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199672&prj=603&rqi=7yD8EvqA2EqlHeDAzjNK7L6heG
GI-042 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-02-19 04:00:00.000 +0400 | Consultant |  | General Design Issue | Design |  | equipment type |  |  |  |  | Exhaust fans (EF) are not interfaced with the fire alarm system and therefore do not shut down in fire. This has been confirmed by the desing team and general contractor. Concern that ducts and fans are not fire rated and the risk of transerring smoke through adjacent fire zones and cause fires in adjacent areas. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199546&prj=603&rqi=pfUBVlgSmE4qtYypi9iqIKuNsC
GI-041 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-02-18 04:00:00.000 +0400 | SOC - Socomec |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | LOTO provisions missing from Sts source 1 isolator. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199456&prj=603&rqi=RvP2Wp7pjRsQMHDldgDjdIkgcR
GI-040 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-02-17 04:00:00.000 +0400 | General Contractor - Commissioning |  | Cleaning | Commissioning |  | equipment type |  |  |  |  | Red rust was observed inside the CRAH on the CHW pipe supports. In addition, white rust was observed on the internal side walls of the CRAH. Ensure all rust is removed from all CRAH's in the project. Refer to attached photos for reference from CRAH-F-E-59 in Switchroom F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199350&prj=603&rqi=YwqLaX63SkP7uWIt34NQgXy938
YT1ELEC-559-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-02-13 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | B2-GF-SEC-RACK-02 | CAB - ICT Cabinets |  |  | B2-GF-SEC-RACK-02 door lock is damaged and unable to close. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199206&prj=603&rqi=jPCLAJXdCwYyEFMATs7eC2caTL
GI-035 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-02-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Incomplete Connections | Commissioning |  | equipment type |  |  |  |  | All RMU incoming VT's were left in the open position which was picked uop during DEWA energisation. As per Se email dated 10thy februray RMU are safe to energise with the VT in the out of service position. PMU currently not measuring Voltage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199221&prj=603&rqi=RLeVRwfESDE7mUfG5rJUF4nDYi
YT1ELEC-560-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-02-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | B2-FF-SEC-RACK-01 | CAB - ICT Cabinets |  |  | During white glove inspection for B2-FF-SEC-RACK-01, it is observed the body of the Rack has been sprayed with gray paint to cover scratches/defect. The finish is poor and to be addressed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199146&prj=603&rqi=Roxk4UGPPQGBOxdb3Fle6JvHKi
GI-031 | DX03-2 | S-EMEA | Closed | P2 Medium CX | v.baddegama@core-group.me | 2026-02-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1-RPP-F-4 | RPP - Remote Power Panel |  |  | The earth bar inside all RPP's are missing provision (holes) for terminating earth cables. Refer to attached photo as a reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198852&prj=603&rqi=Dqsa5NzzRyPysHka2uojDRr7iG
YT1ELEC-532-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-02-06 04:00:00.000 +0400 | SOC - Socomec | L2B | Component/ Equipment failure | Commissioning | Electrical â€“ LV | equipment | 1-STS-F-2 | STS - Static Transfer Switch |  |  | STS-F-2 top cover showing deflection/damage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198684&prj=603&rqi=1IdtcYSHknsfmBMQFKWpjE4Fm0
GI-029 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-01-30 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Component/ Equipment failure | Commissioning | Electrical â€“ LV | equipment | 1-PFC-F | PFC - Power Factor Correction |  |  | PFC-F Blue phase LED cover damaged/missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198054&prj=603&rqi=rar8d0oGFY2lAZxJGsf109iDnH
YT1ELEC-530-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-01-20 04:00:00.000 +0400 | SOC - Socomec | L2B | Component/ Equipment failure | Commissioning | Electrical â€“ LV | equipment | 1-STS-E-1 | STS - Static Transfer Switch |  |  | STS door lock is faulty (not locking) and requires repair/replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197135&prj=603&rqi=tVaIByA98YOSZ6sikgddGI7vI2
GI-017 | DX03-2 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-01-06 04:00:00.000 +0400 | SCH - Schneider MV |  | General Design Issue | Design |  | equipment type |  |  |  |  | All RMU's Earth switch are not furnished with Locking devices. This deviates from Equinix design standards for MV Switchgear/RMU. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196385&prj=603&rqi=cbMsrb6PBrLqBdn31WORhRqwO4
GI-018 | DX03-2 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-01-06 04:00:00.000 +0400 | SCH - Schneider MV |  | General Design Issue | Design |  | equipment type |  |  |  |  | RMU Cannot be fully isolated (for LOTO pruposes). A cover has been provided on the mechanical ''On'' button only and not for the 1 - Earth switch (separate issue) 2 - CB on/off, Disconnector on/off by local pushbuttons or 3 - The remote pendant. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196386&prj=603&rqi=4SlQeeY5653FxeOubGSPVcUHOY
GI-004 | DX03-P1 | S-EMEA | Open | P3 Low CX | n.forde@core-emirates.com | 2026-09-15 04:00:00.000 +0400 | SOC - Socomec |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | STS are missing LOTO provisions on Q41 isolator (Source 1 Primary supply). This issue applies to ALL 4No STS supplied to DX3.P1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638274&prj=699&rqi=9aMJl6XOsvH3xCbI5B7wwTkE8e
RT1ELEC-54-001 | DX03-P1 | S-EMEA | Open | P3 Low CX | c.castro@core-group.me | 2026-09-11 04:00:00.000 +0400 | Low Voltage Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1-MSB-G | MSB - Main Input Switchboard |  |  | Installation of equipment is complete in final location and as per Manufacturers Spec. EKIP power supply modules are missing for 11Q1 and 12Q1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637733&prj=699&rqi=iMAfpIymWargF03RJehC8tZnZa
RT1ELEC-76-001 | DX03-P1 | S-EMEA | Open | P3 Low CX | c.castro@core-group.me | 2026-09-09 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1-RPP-H-1 | RPP - Remote Power Panel |  |  | Delivered as specified SCU100 controller is missing / not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637474&prj=699&rqi=9xAsEvakbPDhosuxm6Z57Oha8l
RT1ELEC-35-001 | DX03-P1 | S-EMEA | Open | P3 Low CX | c.castro@core-group.me | 2026-09-09 04:00:00.000 +0400 | SCH - Schneider MV | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1-BTU-RMU-H | BTU - Battery Tripping unit |  |  | Door limit switch found damage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637473&prj=699&rqi=mB2ebSzFG3eR0h2GzYt6P1FuqV
RT1ELEC-55-002 | DX03-P1 | S-EMEA | Open | P3 Low CX | c.castro@core-group.me | 2026-08-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1-MSB-H | MSB - Main Input Switchboard |  |  | Carry out full visual inspection of panel and confirm no defects, scratches, dents, abnormalities The door of 6.3 Q1 in cubicle 6 is not properly fitted to the breaker. A gap is visible between the door and the breaker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634881&prj=699&rqi=67LiwQDd2I2o9pCd7Q6djnsNUU
GI-003 | DX03-P1 | S-EMEA | Open | P3 Low CX | l.drake@core-group.me | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Cleaning | Commissioning |  | equipment type |  |  |  |  | White rust was observed on the internal side walls of the CRAH. Ensure all rust is removed from all CRAH's in the project. Refer to attached photos for reference taken from CRAH's 1-CRAH-G-F-55 1-CRAH-G-F-56 1-CRAH-G-F-57 1-CRAH-G-F-58 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633590&prj=699&rqi=qcdGYWoVk7XcQmqz5TqczM0Tb7
GI-002 | DX03-P1 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-08-12 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1-MSB-H | MSB - Main Input Switchboard |  |  | MSB-H ACB serving STSSB-H-2 is missing its' ABB EKIP Module (Complete module including Comms and power modules). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633404&prj=699&rqi=DrfBCoWocIKkv8PhW6iZEPNorK
GI-001 | DX03-P1 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-08-12 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1-MSB-H | MSB - Main Input Switchboard |  |  | MSB-H section 6.3Q MCCB (including handle) is missing. It appears the panel has been delivered to site with this component missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633403&prj=699&rqi=0vEjXybfap36zyJlhhqE4iyUTe
RT1ELEC-55-001 | DX03-P1 | S-EMEA | Open | P3 Low CX | g.madulid@core-group.me | 2026-08-05 04:00:00.000 +0400 | Low Voltage Electrical Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1-MSB-H | MSB - Main Input Switchboard |  |  | MSB-H Cubicle 9 and and 10 plinth damage/deformed. The damage is preventing remove of the panel cover als0. . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632271&prj=699&rqi=j7dW72NSpEt6Mdo7os7HHnbsuC
GT1ELEC-147-001 | FR08-3 | N-EMEA | Closed | P1 High CX | jyusufi@global-cxm.com | 2026-08-31 04:00:00.000 +0400 | SOC - Socomec | L3 | Installation Not Correct | Commissioning | Electrical â€“ LV | equipment | 1_STS_N_2 | STS - Static Transfer Switch |  |  | During Energisation the bolt losed and had a direct contact with the busbar which caused an ARC Flash incident. The Unit needs to be replaced or all the Parts within mentioned Area needs to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636058&prj=630&rqi=HEBW1urbv5L2Vr11FOy0PVO9jY
GI-091 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-08-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1_STS_N_1 | STS - Static Transfer Switch |  |  | on STS N1 the Lock on the Door handle is defective Broken. needs to be replaced. The Door is bended | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634877&prj=630&rqi=rMpywAZsUIPGzTUw94GEk5td3D
GI-092 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-08-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1_STS_N_2 | STS - Static Transfer Switch |  |  | plates on Top of STS N2 has been bended / Damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634878&prj=630&rqi=uQMkHEIEkJPMpnV5r2j84xdGCH
GI-090 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-08-07 04:00:00.000 +0400 | VER - Vertiv |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_UPS_K | UPS - Uninterrupted Power Supply |  |  | Batteries UPS K showing constant charge mode. Core 1 Right | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632694&prj=630&rqi=CWvRa5APsE8gpB49rdy7NW2KCZ
GI-089 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-08-07 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_STS_J_1 | STS - Static Transfer Switch |  |  | power factor incorrect on STS J | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632693&prj=630&rqi=k0gO2U36wPlh84CGDZVSGyjfw5
GI-087 | FR08-3 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-07-30 04:00:00.000 +0400 | Design Professional |  | Design Correction Needed | Design | [6 empty] | When utilitly failure and generator supply takes over, it takes 20 seconds for generator supply to take over. This generates AFD unhandled fault, comm loss AFD, AFD bump complete alarms on the chiller and shuts it down and they have to be manually reset. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631420&prj=630&rqi=FfgjaEVYAqRP0Q6f21yGmzGnHQ
GI-085 | FR08-3 | N-EMEA | Closed | P2 Medium CX | drobertshaw@global-cxm.com | 2026-07-27 04:00:00.000 +0400 | VER - Vertiv |  | Installation Damage | Commissioning | [6 empty] | UPS K Battery K - 10 MCCB needs to be replaced. During a site walk, Mercury and Global Cx brought to my attention that there were black soot marks visible on the MCCB breaker in battery cabinet 10 of UPS K. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630880&prj=630&rqi=lajlzjnmibh1WGfNhHD0f95piL
GI-086 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-07-27 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1_CWST_10_CWP_J_2 | CWP - Chilled water pump |  |  | Leak on motor shaft going into the impeller on the primary pump in PPR10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630888&prj=630&rqi=jtm3qpc4lRWJBrmu6GXElrtXk9
GI-084 | FR08-3 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-07-27 04:00:00.000 +0400 | VER - Vertiv |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1_BATT_M3_01 | LIBATT - UPS Battery |  |  | UPS M3 Battery cabinet 1 needs to be replaced. During snag remediation works on battery cabinet 7 of the UPS M3, a short circuit occurred, which resulted in the need to replace the cabinet, the MCCB, the AC power supply module, internal communication cables and a cable for the fan exhaust | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630839&prj=630&rqi=CRkYo5DJAJzdNGc2xIOTqdGgau
RT1ELEC-148-001 | FR08-3 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-07-07 04:00:00.000 +0400 | SOC - Socomec | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1_STS_N_1 | STS - Static Transfer Switch |  |  | Damage to door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628147&prj=630&rqi=tTEvxBVeiRTwxbf3tDblekAbwm
GI-080 | FR08-3 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-07-03 04:00:00.000 +0400 | VER - Vertiv |  | Component/Equipment Failure | Commissioning | [6 empty] | UPS H core 2 does not allow to go on battery autonomy. when you isloate the other cores on the UPS to perfom battery autonomy on that one core as soon as load is applied to the core while on battery the core goes offline. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627798&prj=630&rqi=3d07894izIsyxqeNUk1h8RB9MZ
GI-081 | FR08-3 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-07-03 04:00:00.000 +0400 | VER - Vertiv |  | Component/Equipment Failure | Commissioning | [6 empty] | UPS M3 - The issue with M3 occurred during the transient tests on the generator. No hardware faults were detected on the UPS. This behaviour is likely related to the interaction between the UPS and the generator, as the transient tests on the mains supply and all other tests were completed without any abnormalities. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627799&prj=630&rqi=lJWtrvekjxNykz7znR1bcshiGH
GI-079 | FR08-3 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-06-19 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design | [6 empty] | MSB Y x 1 250A breaker with neutral protection to be investigated. Breaker Q13 in panel MSB Y is a 3-pole MCCB and does not include neutral functionality. According to the engineering design by Anord Mardix and approved by RHK and Equinix, Q13 is configured accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626208&prj=630&rqi=wq53tgyTQ4g00KtIM5E226HIqp
GI-075 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1_STSSB_L_4 | STSSB - Static Transfer Switchboard |  |  | Covers / Plates are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624728&prj=630&rqi=4a0hwcqEujlEem5wk9EQIsm7tI
GI-076 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1_STSSB_L_1 | STSSB - Static Transfer Switchboard |  |  | Covers / Plate is missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624755&prj=630&rqi=H40pC7gWpU24CIWXG8L78DNqvI
GI-070 | FR08-3 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | VER - Vertiv |  | Component/Equipment Failure | Commissioning | [6 empty] | UPS K core 2 Rectifier / Inverter module PH.V failed when load is applied. This needs to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624672&prj=630&rqi=epVAGZjbizFwWaNHZpxytreWa3
GI-072 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1_STSSB_L_1 | STSSB - Static Transfer Switchboard |  |  | Covers / Plates are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624724&prj=630&rqi=IdD6bA56LHhGM1GWFnMXBnJcN4
GI-074 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1_STSSB_L_3 | STSSB - Static Transfer Switchboard |  |  | Covers / Plates are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624727&prj=630&rqi=nnwj64DYelKbNsGQFuqQqIZV0x
GI-071 | FR08-3 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | SOC - Socomec |  | Component/Equipment Failure | Commissioning | [6 empty] | STS in PPR 12. Went into fault due to back feed alarm causeing the output to open. STS was on S1 bypass, S1 has been seen as an unhealthy source STS has then tried to switch to S2 while S1 bypass is still engaged. Socomec to investigate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624685&prj=630&rqi=iCdOxlWsE2qlzOdByVIg2hn4lV
GI-073 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1_STSSB_L_2 | STSSB - Static Transfer Switchboard |  |  | Covers / Plates are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624726&prj=630&rqi=D2qXhKhF6tRg7Y9KUImUhF37kT
GI-077 | FR08-3 | N-EMEA | Closed | P2 Medium CX | drobertshaw@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [6 empty] | Transformer for the chiller control panel has failed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624778&prj=630&rqi=IhLKiJgUJd9j4MPSkXCG9SDV3B
GI-069 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-09 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1_CWST_12_DC_K_1 | HDAC - Hybrid Dry Air Cooler |  | HTK 3.24/10.9-2S-P4-CU-SLNF | Water distribution over the coils on the HDAC. On PPR 12 if stood facing the HDAC the right side of the unit is performing far better than the opposing side. need confirmation from Jaeggi if balancing has been done and if not, does the water distribution affect the WET mode of the HDAC which also affects performance in WET mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624480&prj=630&rqi=3O1CY2fo1SL9aFtTze44YzWsQj
GI-068 | FR08-3 | N-EMEA | Closed | P2 Medium CX | drobertshaw@global-cxm.com | 2026-06-09 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Component/Equipment Failure | Commissioning | [6 empty] | MSB R3 Q2 breaker chasis needs to be replaced. The winding mechanism has been turned to far and put stress on the internal gears causing the failure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624449&prj=630&rqi=Ky79Uz9rP4r9vzD18ltTYtl67E
GI-060 | FR08-3 | N-EMEA | Closed | P2 Medium CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1_CWST_10_CWP_J_1 | CWP - Condensator Water Pump |  |  | Leak on Condenser pumps in PPR10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623820&prj=630&rqi=g6MgBULntMO9YhnjByGe6RRTAP
GI-059 | FR08-3 | N-EMEA | Closed | P2 Medium CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1_CWST_15_CWP_H_1 | CWP - Condensator Water Pump |  |  | Leak on condenser pump in PPR15 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623819&prj=630&rqi=M3WSLv3Q57GoLGrBnmmaqe14qH
GI-049 | FR08-3 | N-EMEA | Closed | P2 Medium CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | [6 empty] | UV lamp defect on Jaegii HDAC PPR 09 HDAC 09 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623805&prj=630&rqi=BakZwETIunBDNJtiItlpiVnW4x
GI-050 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | [6 empty] | UV lamp defect on Jaegii HDAC PPR 10 HDAC 10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623806&prj=630&rqi=a27j7KtXnuhUM0yWLwZqzQdkwH
GI-063 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | Leak on TT05 in PPR 15 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623824&prj=630&rqi=hAQm1TnarPRAJfzwEqZmgZFiWR
GI-055 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | PPR 08 Leak on PICV 01 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623814&prj=630&rqi=JmXLQbNJZ5Sz47WijyBzgsNKkn
GI-056 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | PPR 12 leak on PICV 01 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623816&prj=630&rqi=4Rpr3bYKBPZmcJbZiwDwgaieJL
GI-065 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | Leak on Temperature gauge in PPR08 near Primary pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623826&prj=630&rqi=koiEZtN3LQ1ezu4WA47uPUKORf
GI-062 | FR08-3 | N-EMEA | Closed | P2 Medium CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | Leak on PPR 08 condenser pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623823&prj=630&rqi=3jAuPVtK8FV5utw9OGED3AT0l7
GI-053 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | Leak on TT09 in PPR10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623812&prj=630&rqi=LhpvE00NL67XumlyaKcFBOTtNO
GI-054 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | PPR 09 Leak on Overpressure valve (near to TT05) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623813&prj=630&rqi=lhWZH3qf2d1Ksa2BRUI4jqzl3V
GI-051 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | [6 empty] | Glycol sensor on HDAC 10 needs to be replaced. Vortmann advised it will be done next week | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623807&prj=630&rqi=j5CNnprDwwhhPNUloGKvUYCLkK
GI-057 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | PPR 09 Power socket not live in the CGM | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623817&prj=630&rqi=dmyIzTkIeDNX2IeNA3BgbfJgKE
GI-066 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | Leak on TT08 in PPR08 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623827&prj=630&rqi=NhP3RAMr9D6OlQE6J0DE3lht44
GI-052 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | PPR 09 TT10 - shows incorrect value when chiller is running. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623809&prj=630&rqi=Jd712mL7tv5jlqlrBqCRh5zU5r
GI-064 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | Leak on Temperature Gauge in PPR15 near to TT07 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623825&prj=630&rqi=KsiRoLG1LKeZwHZZPSqoyZZbDV
GI-058 | FR08-3 | N-EMEA | Closed | P2 Medium CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1_CWST_12_CWP_K_2 | CWP - Chilled water pump |  |  | PPR 15 - Leak on the airvalve on the primary pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623818&prj=630&rqi=Zq0NRbZ20dUTLDie3YrBUEDtQo
GI-067 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | Leak on drain off valve below the bypass near the heat exchanger in PPR 09 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623828&prj=630&rqi=v2U1hkFaDQaydTL54tMPAwbMIi
GI-061 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1_CWST_10_CWP_J_2 | CWP - Chilled water pump |  |  | Leak on primary pump in PPR 10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623822&prj=630&rqi=xSwlNWY7stfju8cK8S41UQitvX
GI-048 | FR08-3 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-05-22 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Not Correct | Commissioning | [6 empty] | Data Hall CRAH communication cable had been squeezed too tightly to the tray. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622778&prj=630&rqi=61ck8QmPkXBsYsYeZoqdmJhnQu
GI-041 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Cabinet door earthing cables are either missing or damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622395&prj=630&rqi=FldrSx6NOR9s17E4pbdL7jrdwa
GI-043 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | Electrical â€“ LV | equipment | 1_GCP_Y | CP - Control Panel (Generator) |  |  | Bone tags are missing on several internal and external cables. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622397&prj=630&rqi=UlSxXitaJROM681cVj80sfsCdj
GI-044 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1_GCP_Y | CP - Control Panel (Generator) |  |  | End clamps are missing for the complete breaker series, resulting in breaker movement and insufficient securing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622398&prj=630&rqi=0nPYmC73xrmEeqahhlYmIlP3CM
GI-045 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Torque required | Commissioning | Electrical â€“ LV | equipment | 1_UPS_Y | UPS - Uninterrupted Power Supply |  |  | DC battery cables are not double torque-marked. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622399&prj=630&rqi=DQaiJgqGUod51ajStqACzLmFPs
GI-039 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | On all battery cabinets, the covers are either damaged or missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622393&prj=630&rqi=VhYb4NbjTKzt2mMdSMo7YAdlB9
GI-040 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Torque required | Commissioning |  | equipment type |  |  |  |  | Torque marks are not valid, as the cables have not been properly torqued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622394&prj=630&rqi=cxlr3kYekdSxQS5NtZ3Dxvv5X2
GI-047 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1_UPS_Y | UPS - Uninterrupted Power Supply |  |  | Covering plates are missing. The Plates under the MSB / UDP are opened and they needs to be closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622402&prj=630&rqi=dIstpbqs8Tv691HgCDNUX4Bc3q
GI-046 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Correct | Commissioning | Electrical â€“ LV | equipment | 1_UPS_Y | UPS - Uninterrupted Power Supply |  |  | Cables are under tension. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622400&prj=630&rqi=wkZA6T1s5fhVLkPtGFFUFStUul
GI-042 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | On Cabinets 1 and 6, the DC cables are under tension. Please refer to the attached pictures. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622396&prj=630&rqi=Y82k1eZWo6dG8ksxylCsftnuxC
GT1ELEC-185-001 | FR08-3 | N-EMEA | Closed | P3 Low CX | tgates@global-cxm.com | 2026-05-13 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1_STS_K_5 | STS - Static Transfer Switch |  |  | Asset reference to be changed on DCOS and evidence provided, DCOS states 1_STS_K_10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621728&prj=630&rqi=MTmmpG9xoWSAs7vp6SbIN8Kt8H
GT1ELEC-184-001 | FR08-3 | N-EMEA | Closed | P3 Low CX | tgates@global-cxm.com | 2026-05-13 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1_STS_J_5 | STS - Static Transfer Switch |  |  | Asset reference to be changed on DCOS and evidence provided, DCOS states 1_STS_J_10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621713&prj=630&rqi=IcI2eegqivC3EenS5eP8KhsXSB
GI-023 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1_CWST_08_CHWP_L_1 | CWP - Chilled water pump |  |  | Armstrong pump - to be checked by Armstrong engineer regarding noise issues potentially with bearings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618826&prj=630&rqi=2U23mifPKuMaV9kDorpbKJqzMY
GI-024 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1_CWST_08_CWP_L_2 | CWP - Chilled water pump |  |  | Armstrong pump - to be checked by Armstrong engineer regarding noise issues potentially with bearings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618830&prj=630&rqi=4hkw1rFC1vyrSmu7KqEmrG7FNT
YT1ELEC-222-001 | FR08-3 | N-EMEA | Closed | P3 Low CX | tgates@global-cxm.com | 2026-04-09 04:00:00.000 +0400 | Construction Manager | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_GCP_K | CP - Control Panel (Generator) |  |  | Earth bond on door needs to be re terminated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617648&prj=630&rqi=MyDJHNW2IBB03fncHYGyuwkuue
YT1ELEC-228-001 | FR08-3 | N-EMEA | Closed | P3 Low CX | tgates@global-cxm.com | 2026-04-09 04:00:00.000 +0400 | CMM - Cummins | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_GSB_R3 | GSB - Generator Switchboard |  |  | Shutters behind the ACB are faulty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617614&prj=630&rqi=SCdhaQn44RISFQgy6bxQqH2ZML
GI-013 | FR08-3 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-04-09 04:00:00.000 +0400 | VER - Vertiv |  | Installation Not Correct | Commissioning | Electrical â€“ LV | equipment | 1_BATT_H_01 | LIBATT - UPS Battery |  |  | DC cableing for UPS batteys needs to be cleated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617606&prj=630&rqi=rj3auDCKz0AuzBfsse1u7OmQQI
GI-014 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-09 04:00:00.000 +0400 | VER - Vertiv |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_BATT_H_09 | LIBATT - UPS Battery |  |  | Battery Cabinet DC Cable installation covers damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617664&prj=630&rqi=HLbGZNYs7dx0h5vFysuvLLdzBp
GI-011 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_GCP_M3 | CP - Control Panel (Generator) |  |  | Cable cover is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617555&prj=630&rqi=hpawOp4mr7TmGHUfLcjdzBvVk9
GI-009 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_GCP_R3 | CP - Control Panel (Generator) |  |  | no bone Tags on the cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617551&prj=630&rqi=d5Hm7sDLQq5v7x1W9aNHss4sE5
GI-008 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_GCP_R3 | CP - Control Panel (Generator) |  |  | Cables are shorts and in tension according to VDE needs to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617550&prj=630&rqi=Y0XvbYy93K3SKXkTybKNS3mQt4
GI-010 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_GCP_M3 | CP - Control Panel (Generator) |  |  | no bone tags on the Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617554&prj=630&rqi=IZcoymEaKUpWOQ75RuSdp5JYu4
GI-012 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_GCP_M3 | CP - Control Panel (Generator) |  |  | GCP Door Handel is broken not functional | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617556&prj=630&rqi=A2BTyHwc7w85OIYUzL8rpu5CED
GI-007 | FR08-3 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-03-26 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1_STSSB_L_2 | STSSB - Static Transfer Switchboard |  |  | 2 MCCB breeaeker handles damaged on site. Need to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616536&prj=630&rqi=Nv6bfMZjy0Q6IHGod7yWHwXiiD
GI-006 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-03-25 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Commissioning Issue | Commissioning | Controls | equipment | 1_HMI_J | HMI - HMI Panel |  |  | HMI J faulty software & not for the designed Board | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616354&prj=630&rqi=Yzw1WDPnHgU6JsWDoGhp13QoQq
GI-003 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-03-23 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | ARC Flash protection been broken / Damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616193&prj=630&rqi=dd99Yeym2d7KM0aENs6m0SyrqJ
GI-002 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-03-09 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_EB_PPR_09 | ERTH - Earthing |  |  | FR8.3 STS L2B Armstong appear to have missed installing the Modbus TCP module ST300 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615124&prj=630&rqi=NWCVwqG2CHGZ6SVTrk7Ds9cvfS
GI-001 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-03-05 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Commissioning Issue | Commissioning | Controls | equipment | 1_HMI_L | HMI - HMI Panel |  |  | Damaged HMI Display | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614804&prj=630&rqi=elk2ez4ntOhGMRieIeiUP5umIm
GI-214 | FR10x-1 | N-EMEA | Closed | P2 Medium CX | cjjones@global-cxm.com | 2026-02-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | SUDB_3_Q07 - 1_MVTB_R2 (Q01) Incorrect circuit ref on torque report Torque report not signed Sign off dates incorrect | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=139154&prj=378&rqi=U0tYNe4cD9yDxE2YpaHvOvAB10
GI-006 | FR12-1 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1MVTB_N | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633613&prj=692&rqi=axxOMDQBFPKBDktL2EpdyVJ2GN
GI-002 | FR12-1 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1MVTB_D | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633607&prj=692&rqi=DlTC4kv9WwZ4BES9OQHI3Brssu
GI-003 | FR12-1 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1MVTB_L | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633610&prj=692&rqi=nKP7PSzYXS85GKNG9y00klG5Ao
GI-005 | FR12-1 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1MVTB_M4 | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633612&prj=692&rqi=269XkbkDzFAj3Y1LjqIflCmDss
GI-001 | FR12-1 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1MVTB_C | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633605&prj=692&rqi=XRdrZRmLLzVy5veu2PBKQfUs4s
GI-004 | FR12-1 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1MVTB_M1 | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633611&prj=692&rqi=RujJJFgm0TL15LwyEYTSoPxF4s
GI-007 | FR12-1 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1MVTB_R1 | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633615&prj=692&rqi=jtCHsNyroEDUdWjZYn0KpJvVJE
GI-015 | FR13-2 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | General Design issue | Design | [6 empty] | RMU Tx breaker tripping on in rush B, D, A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352280&prj=563&rqi=fRKOXjK3xbsZQesaQzg8IbK59t
GI-012 | FR13-2 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning | [6 empty] | Fuel system using low level bulk tank instead of high level bulk tank - Sigma to come and investigate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352277&prj=563&rqi=AzoQVbm9hHpj3Tor11aekMOnXc
GI-010 | FR13-2 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Graphics Issue | DCOS | [6 empty] | RMU B not visible on DCOS during mains failure test. Port issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352273&prj=563&rqi=jg80CEvHCsNdFf2jXPr6ndBOsj
GI-011 | FR13-2 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Graphics Issue | DCOS | [6 empty] | 2 breakers on UDP B showing tripped when on | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352276&prj=563&rqi=jYwXsNLZrUBYLusC32bgQkqiM1
GI-013 | FR13-2 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | General Design issue | Design | [6 empty] | When lose of power to fuel pumps you have to restart manually. To be discussed with EQX design and RHK (recommend UPS backed supply) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352278&prj=563&rqi=2oOHh78WBFR5P8l5u8bQLLd2iw
GI-014 | FR13-2 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Graphics Issue | DCOS | [6 empty] | Generator breaker on MSB C not showing as closed on DCOS graphic | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352279&prj=563&rqi=K8iqJ1Rn4uFAF0mJtx4GvbwfU6
GI-009 | FR13-2 | N-EMEA | Closed | P2 Medium DCOS | Alen.Francis@eu.equinix.com | 2026-02-13 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCIM Sync Service Issue | DCIM | [6 empty] | We are unable to verify all expected objects upserted to DCIM. System Integrator/ GC needs to update the DCOS/DCIM delivery time on when this will be completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199201&prj=563&rqi=77hRFLEOJtZaUV9HySRWfg5Bft
GI-028 | FR6 - Liquid Cooling | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-08-10 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | TCS/SFN-01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | Opened from a previous IRL. On the SFN some bolts are Carbon Steel and not Stainless Steel. Bolts are to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632976&prj=685&rqi=bkV3HlDFGmwsvUNY8Za08NDUkA
GI-027 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-05-26 04:00:00.000 +0400 | Owner |  | General Design Issue | Design |  | equipment type |  |  |  |  | Temp sensors on the racks does not show accurate readings, as the sensors are surface mounted and facing the CRAH supply air flow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623135&prj=685&rqi=0rzhgBQFrtceQsIcb9fkdtg4TI
GI-026 | FR6 - Liquid Cooling | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-05-18 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Missing Torque marks on the SFN. Torquing has been done but missing the marks | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622173&prj=685&rqi=Os3IPSXfBhwMvUCUOl7BKUP6ft
GI-025 | FR6 - Liquid Cooling | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-05-18 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Missing Valve Tag Number on the SFN | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622163&prj=685&rqi=9LsS6y9Izqd3LlWejiOXgQLyiw
GI-023 | FR6 - Liquid Cooling | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-05-05 04:00:00.000 +0400 | Owner |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Leak detection schematics are to be updated to include the new SFN area. the alarm is working and has been checked. only schematics to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620487&prj=685&rqi=zyLCMciMjbGatRJqcs8NqWK9tl
GI-024 | FR6 - Liquid Cooling | N-EMEA | Closed | P2 Medium CX | sdreik@global-cxm.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/ Equipment Failure | Commissioning | [6 empty] | Control Valve on the CDUs suppose to hold last recorded position after power failure. However, when the controller is starting the control valve is driving back to the lowest % set | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620495&prj=685&rqi=CAp6OoVZh6k8lD83Up7NtuxMc3
GI-022 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | CDU Internal tanks to have a label specifying the PG25 manufacturer sticker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619684&prj=685&rqi=EfoBNwLAo5Pe5r8ZSXk4Z5ZxBI
GI-015 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | The below alarms are not visible on DCOS graphics: - Secondary DP Setpoint - Critical Alarm - Non-Critical Alarm - High Secondary Supply temp Alarm - Low Secondary supply temp Alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619527&prj=685&rqi=LT6xN7ABZm6UIZ1KlE4LaLS31b
GI-020 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | on the CDU HMI, Filters 2 and 3 shows reading together not as separate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619536&prj=685&rqi=4FAC9nDwp9rJa6KUmM3tUC0kSt
GI-016 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Template Issue | DCOS |  | equipment type |  |  |  |  | Text to be fixed on the Graphics | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619529&prj=685&rqi=NCAqwpAvXW489U2VLWt3frnRPy
GI-018 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | Units to be unified between CDU HMI and DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619533&prj=685&rqi=y89FiVjSQJvX8kFLro1RCls66V
GI-019 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | Leak Detection alarm not available on the CDU graphics | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619534&prj=685&rqi=4X0OqI9yXcSSd2PSPHrbUXewQG
GI-021 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | text to be unified when losing a power source on the graphics | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619537&prj=685&rqi=EfaXrzLwr4J9rRdmqclI7tswAM
GI-017 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Template Issue | DCOS |  | equipment type |  |  |  |  | Text to be fixed not to cover the Graph | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619532&prj=685&rqi=d6vAoZqM20BbTTnJvS87UQJ1Pi
GI-011 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Comms Issue/ Fault | DCOS |  | equipment type |  |  |  |  | When a comm alarm is generated on the CDU. alarm is showing in the alarm section and incication around the HL point. However, nothing shows on the CDU DH graphics, meaning ops will not be able to see that we lost comm until they go into the CDU graph | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618860&prj=685&rqi=DEgxOV64Vjy7HKOiUP7rjfEak9
GI-014 | FR6 - Liquid Cooling | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | General Contractor |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | 2 valves handles are damaged and cannot operate the valves. at the moment the valves are kept open, but cannot be closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618986&prj=685&rqi=g5UqJh74ZXWYbKBR3CmH8n8vC9
GI-013 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Bolts installed on the SFN are short and cannot be fully torqued as the bolts does not even reaching to be flushed with the nut while it should be 3 threads exceeding the nut | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618911&prj=685&rqi=3QMQqyONJdsFHgjPZ0n3LdW7km
GI-010 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | ATS status showing on the graphics as a text. this should be amended to change or identify when a source is lost with an alarm and which source is still available | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618857&prj=685&rqi=utj81JcGEwt9JlV5EIIPHvV63x
GI-012 | FR6 - Liquid Cooling | N-EMEA | Closed | P2 Medium CX | sdreik@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | Owner |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Missing Flushing Valves on the SFN pipe work installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618906&prj=685&rqi=M0smdSyysaGXobFPVwtk2R9YL2
GI-009 | FR6 - Liquid Cooling | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-04-20 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | Mechanical â€“ Water | equipment | TCS/SFN-01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | SFN missing Pipe identification labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618764&prj=685&rqi=U0ybdYcxuhn7khvQIJkJKzPrip
GI-005 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-20 04:00:00.000 +0400 | Owner |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Pressure test was achieved on the SFN without installation of the By-pass valve. as discussed with designer, the system will be functioning without it. Once installed a pressure test is to be conducted on that section and closed with a protocol | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618752&prj=685&rqi=MVusWRL8ttk52JMNNJv0sO8qZc
GI-007 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-20 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Template Issue | DCOS |  | equipment type |  |  |  |  | The DCOS template shows 10 racks while the latest DWG shows 12. this is to be amended | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618759&prj=685&rqi=4nuFZnFWPS4PbDwTzlLN7qIJc8
GI-002 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-26 04:00:00.000 +0400 | Equinix Ops |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | Leak Detection | LEAK - Leak Detection |  |  | Leak Detection System installation not complete or L2A/L2B/L3/L4 commissioned. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352230&prj=659&rqi=Z7Ga4ciSf4fLejC4WrAADCqUWd
GI-001 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-25 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | TCS/SFN hoses supplied by Refcon are designed for steam with pinpricked outer membrane. EQX COE requires the hoses to be changed for hoses specifically designed for PG25. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352227&prj=659&rqi=DkTCmFQgC6mMpleuCYmt4pa56t
GT1MECH-4-002 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-19 04:00:00.000 +0400 | Equinix Ops | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Temperature Sensor Low Alarm does not remain red when coming up from a Low Low alarm, but it if you simulate a Low alarm from normal temperature it changes red. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199568&prj=659&rqi=ZvQarBY7EPK6BfwQzolBGDvwv1
RT1MECH-4-005 | HE7: Liquid Cooling | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-19 04:00:00.000 +0400 | Mechanical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Return joint under CDU02 not installed as per manufacturers recommendations as there is not proper "pad to pad" contact on both sides of the joint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199530&prj=659&rqi=eX6De5i9ohXiQSre9qzJ8KMpf1
YT1MECH-5-002 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-19 04:00:00.000 +0400 | Equinix Ops | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | No earth bonding on TCS/SFN. EQX to confirm Finnish design requirements on TCS/SFN pipework bonding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199545&prj=659&rqi=IKURELu06ZGKvPvYSmOeV9PSG4
GT1MECH-4-001 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-19 04:00:00.000 +0400 | Equinix Ops | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Temperature Sensor High Alarm does not remain red when coming down from a High High alarm, but it if you simulate a High alarm from normal temperature it changes red. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199567&prj=659&rqi=wnb0nTi8PEoMMoCK4zaPnLfrUk
RT1MECH-4-002 | HE7: Liquid Cooling | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | Mechanical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Rack 101-105 connections supports are compromised by existing electrical containment. Rack 105 support in particular needs attention/additional supports. Pipework and Valve not level. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199352&prj=659&rqi=DLdLqW4jU8BaE1EC1GfkTPJzbu
RT1MECH-4-001 | HE7: Liquid Cooling | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | Mechanical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Some TCS/SFN joints are not installed as per manufacturers recommendations as there is not proper "pad to pad" contact on both sides of some joints. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199351&prj=659&rqi=jHCvpJ8XkyDZ500g3r24jvrO8h
RT1MECH-4-003 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | Equinix Ops | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | All TCS/SFN temperature sensors are labelled with temporary stickers. Permanent labels to be installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199353&prj=659&rqi=IeMNdK595yB3KO9YBOSZBn4YlB
RT1MECH-4-004 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | Equinix Ops | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | All TCS/SFN valves are not labelled with ID tag/label. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199354&prj=659&rqi=49grMlru2PnC4NiNflsbTAg4yH
YT1MECH-5-001 | HE7: Liquid Cooling | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | Mechanical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Rack 101 bypass hose and valve are weeping | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199363&prj=659&rqi=Z8Dzbm7Mq9YNO9qRCdyoAkyA5S
RT1MECH-4-006 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-05 04:00:00.000 +0400 | Mechanical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Thread tape used on the brass drain valves and gauges installed on the TCS/SFN. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221141&prj=659&rqi=trrcTjpE4NQpiXOwwTLX7vSxvW
RT1MECH-4-007 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-05 04:00:00.000 +0400 | Mechanical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Brass drain valves and reg valves installed on the stainless TCS/SFN. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221142&prj=659&rqi=PaL8LDM9HRISpKV9iK7KOZrtbZ
GI-297 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | 15/F LVSB Rm -emergency lighting installation to comply with FSD requirement and within 2m of any FSI installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617733&prj=501&rqi=wgNx4nEEpHlwh6dBP4IORxUaNo
GI-294 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | R/F -Failure of the Battery discharge test for 4 nos. of emergency lighting | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617729&prj=501&rqi=gx3zXgfLRnGnSZeBDI1p3cr1RV
GI-295 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | 12/F LVSB Rm - emergency lighting installation to comply with FSD requirement and within 2m of any FSI installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617730&prj=501&rqi=gT0gUgsbJumFXVHP0PeAC9sidm
GI-296 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | 13/F LVSB Rm - emergency lighting installation to comply with FSD requirement and within 2m of any FSI installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617731&prj=501&rqi=53kEvvIEDUuTR7aNr4ZRrvBL3W
GI-293 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-04-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Task Uniformity (Min./ Avg. = 0.014) of R/F the Luminaire Schedule by NV5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617128&prj=501&rqi=s9OSO9iv7dAskZQNXJGFWCHzUs
GI-289 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | CAM 00024 has not been tested because it has not been installed. The installation requires conduit to be run through a CLP-controlled room, and CLP has denied access permission. The matter is currently being discussed by NV5, GEM, and EQX. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616820&prj=501&rqi=BzGuUJJ92n0TMcQlVmFb2halu8
GI-288 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | CAM 00054 have not been tested as it has not been installed due to requiring conduit installation through CLP-controlled room. CLP did not give permission fpr access. Currently under NV5, GEM and EQX discussion. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616819&prj=501&rqi=zBij3bnsRlNpOXcwda4W1wacPG
GI-291 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Door 20 (D20) have not been installed due to damaged door frame. EM Lock, Keypad Reader, and Break Glass Unit have been tested without door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616822&prj=501&rqi=YT75mjH2VQjPBh3YVYxmrR02J1
GI-290 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Door 28 (D28) will be replaced from double-acting doors to in-swing door with EM Lock upon completion of BD inspection on Apr 7. EM Lock, Keypad Reader, and Break Glass Unit have been tested without door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616821&prj=501&rqi=IK54R31QuQIHyFmRJC3y5nv3ds
GI-292 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | R/F - Emergency lighting discharge lower than 2 lux. (measure from floor) at the beginning of battery discharge. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616860&prj=501&rqi=RmCC07R2dxRdutTnbjJXc8D8Xh
GI-287 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | Task Uniformity (Min./ Avg. = 0.30) of 17/F Lounge cannot meet the Luminaire Schedule by NV5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616648&prj=501&rqi=hWfJrMKAbNU67sK6ySsuyPkiNr | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-284 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | emergency lighting installation to comply with FSD requirement and within 2m of any FSI installation" & "Emergency Lighting cannot fulfil the FS COP Requirements | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616639&prj=501&rqi=f3gObtI21FpilMOIDBQXG7PGw5 | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-285 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | Avg. Lux Measurement cannot meet @of 17/F Customer Kiosks, Main conference room, at lounge | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616645&prj=501&rqi=cLtMSavZvHT7vKI7a0cZbKFEQe | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-286 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | Avg. Lux Measurement of 17/F Customer Kiosks cannot meet the Luminaire Schedule by NV5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616647&prj=501&rqi=a0p2dFt0yOcUZKURTaHjN4q64l | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GT1DCOS-13-002 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-20 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning | Controls | equipment | 1DCOS_LCP_17 | DCOS - Control Panels |  |  | Unable to check points for flow (items 5 to 12 on point list / test record) as flow meter installation is pending for Water Department approval. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616067&prj=501&rqi=NkyCMtvo9AA8I2d3dADVAw0sFJ
GT1DCOS-13-001 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-20 04:00:00.000 +0400 | General Contractor | L3 | Component/Equipment failure | Commissioning | Controls | equipment | 1DCOS_LCP_17 | DCOS - Control Panels |  |  | 1041 FER Room TT sensor showing inaccurate from calibrated device. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616065&prj=501&rqi=yPlFleTkxk1GXz4ynFdvw5BNKZ
FPT-478-009 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Installation not complete | Commissioning | Fire Detection | system | Fire System |  |  |  | "Evacuate" flashing light box inside genset room 12/F & 13/F were not properly fixed. The light boxes were embedded into the promat board wall, and the wall opening was not properly sealed or backfilled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615903&prj=501&rqi=UiROlnopLjNgTeqqQUxIQsdG5K | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-005 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | system | Fire System |  |  |  | Missing label for 13F gas suppression system module | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615897&prj=501&rqi=xwLleB4tizRNs745PyrJJ3i5HW | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | system | Fire System |  |  |  | (ACS)(Typical for 12/F, 13/F & 15/F) Mantrap near passenger lift lobby interlock function malfunctioning ; door release function (by fire signal) works properly in FIST | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615889&prj=501&rqi=s0Q2xPgOW4250ENZcv9ZgzBZ8n | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-007 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Labelling | Commissioning | Fire Detection | system | Fire System |  |  |  | Permanent label for damper bypass control panel to be provided (typical) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615901&prj=501&rqi=bvYuYqzLoR8nT7LCmSgaKSSdfW | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-003 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | system | Fire System |  |  |  | Time synchronization issue for FS main panel and repeater panel (Has 1hr and 5mins discrepancy) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615892&prj=501&rqi=XFM9TDVqEBfk8TZAuQXsk2jjmJ | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-010 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | system | Fire System |  |  |  | 24V power supply to gas suppression system module is not available. Corresponding test for 17F gas suppression system cannot be conducted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615904&prj=501&rqi=gUZ3WDD1xL96wu1dQlHjIbDBwH | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-008 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | system | Fire System |  |  |  | Pre-action panel manual operation function cannot be tested since the base building sprinkler pumps are malfunctioned. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615902&prj=501&rqi=rkFuTJ3GgwUc3D6zJCTrfBAi8G | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-002 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | system | Fire System |  |  |  | Gas suppression system signage at 15F to be checked. The flash light effect is different from other signage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615890&prj=501&rqi=CNCOpQZJaIMIVLXfvEuVTegmYe | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-004 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | system | Fire System |  |  |  | Gas suppression system at 13F module does not receive MFSD feedback status; MFSD is actually closed onsite. After jumping the MFSD feedback signal, the corresponding module was triggered and then NOVEC logical function worked properly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615895&prj=501&rqi=oXtfqoyFsYQbsE68CCIN2ccfvw | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-006 | HK06-1 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | system | Fire System |  |  |  | (Typical for 12/F, 13/F, 15/F and 17/F) Genset did not receive "Remote E-stop" after fire signal triggered and therefore genset did not stop and MSFD also did not closed. Fuel supply system PLC did not receive "Fire Signal" to close the valve logically. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615900&prj=501&rqi=xgPIgRrngwqpKXDRZ8cKwkh6Za | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
GI-283 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | Unitary mode for chiller keeps coming on during IST2 on 17 March 26 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615907&prj=501&rqi=TNLf0KytX5cdGTgKguWGTsfFHH
FPT-479-014 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 10:45AM After failing CHWP-01 at string 1, the DCOS programme still counting for reset after 5 mins | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615751&prj=501&rqi=If56XMUYY63luyt3VcpceQjdKT | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-012 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 07:29AM 13040 TER Room, 1TT_01 sensor showing 0C, with a low temperature alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615744&prj=501&rqi=YHYTy845p9vPtWLWo78mfqkW9T | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-013 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 09:10AM UPS_A2 Alarm triggered momentarily. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615748&prj=501&rqi=ih8iWVdeMFVvasZqiQM3oKMSJ8 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-005 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 03:49AM PCP-02 Module Present Status alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615641&prj=501&rqi=G2a1LpnjinwkxOJaP3nPrAnIbN | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-011 | HK06-1 | APAC | Closed | P2 Medium DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 04:27AM After failing CT-02 at string 2, the WCC, CHWP, CWP all remained running. String 2 was still receiving command on in D2SD. WCC_2 shown off on DCOS but WCC_2 was running normally on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615649&prj=501&rqi=cm3ZV2bIaHS00SYo306LG7L2jL | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-021 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT-1(HLT2) 3/14/2026 11:00:00 PM 1UPS_A1,A2,B1,B2 had high output current, kVA and kW alarm on DCOS. Alarm configuration to be clarified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615674&prj=501&rqi=2ZLzSsGTEeSQlfCCoZu1yNp9Ty | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
GI-279 | HK06-1 | APAC | Closed | P2 Medium DCOS | ychoong@ap.equinix.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | Fuel Control Panel has no alarm when the panel is down with no power | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615660&prj=501&rqi=GcxCpNJ5pSR1au86ZYaIQuFtVG
FPT-482-032 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | Vendor- Manufacturer | L4 | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | During IST 2 EIST-01, the PLC panel for the fuel system riser is found to have burnt fuse. This affect the riser from changeover when a fault is detected for the riser | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615681&prj=501&rqi=CfN6vVUAXUWix22OL58eUgUTLV | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-479-007 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 03:52AM When PCP_01 was failed, PCP_02 became the primary unit, but "Power Supply Common Alarm" alarm was triggered for PCP_02 instead of PCP_01. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615643&prj=501&rqi=WFvs91Et8G453c8lucTxX3KLfH | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-004 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | CHWSTR1 DPT-04 loss communication alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615640&prj=501&rqi=2KJ9Zzq67XaJYOZDcEA8n7Wyj6 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-482-004 | HK06-1 | APAC | Closed | P2 Medium DCOS | ychoong@ap.equinix.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS Graphics Issue | DCOS | Electrical | system | Electrical System |  |  |  | DCOS graphic for MV network. -11kV voltage is shown on SUDB even when the main switch is opened. - Amps is shown even when no load is applied - Energized line and non energized line are wrong | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615658&prj=501&rqi=2YOanuEOHMQ8CcCkWqEfpoc754 | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-479-008 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 04:07AM When PCP 02 was failed, "Hot Standby Status" and "PCP Status" did not show on DCOS graphics, all greyed out. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615644&prj=501&rqi=8M6ty9V1Nd50wSaf8YsAn5uByn | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-006 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 03:52AM When PCP_01 was failed, PCP_02 became the primary unit, but "PLC Stopped" alarm was triggered for PCP_02 instead of PCP_01. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615642&prj=501&rqi=27daO8bfIdMjtfxAK3witpEaQK | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-485-003 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider MV | L4 | DCOS Graphics Issue | DCOS | Electrical | system | Electrical System |  |  |  | During the IST 2, at 14:35 - During the UPS_M1 is on maintenace bypass mode, the UPS PQM on DCOS is showing -0kW in effect a warning has shown. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615679&prj=501&rqi=uEmlrGX0tlENLUge5deCrG7TM7 | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-479-009 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 04:07AM When PCP_02 was failed, "Power Supply Common Alarm" alarm did not trigger for PCP_02. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615645&prj=501&rqi=h0KgCGoWfHJao3Uiu2QX6r4WgN | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-024 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | 3/14/2026 HLT-1(HLT2) 11:00PM 17F Lv Switch Room had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615677&prj=501&rqi=ZMKAuSVRgZAvE6k1a6ATaUlnyT | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-485-004 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | Vendor- Manufacturer | L4 | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | During IST 2 EIST-01, when the generator is started because total power failure is applied from the SUDB side, the fuel system on riser B is found to have fuel leakage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615680&prj=501&rqi=l6OPlaQTm4qZI3VpnHI7gt0BCu | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-483-022 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS Graphics Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT-1(HLT2) 3/14/2026 11:00PM 13F Tx Room had high temperature alarm triggered. Alarm configuration to be clarified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615675&prj=501&rqi=oHuCv6FTM2nAjHfoMQPbPYcppB | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-023 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | 3/14/2026 HLT-1(HLT2) 11:00PM 15F Battery Room had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615676&prj=501&rqi=6gzx5JaTgQRfNW9GIOpmNmwkIf | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-010 | HK06-1 | APAC | Closed | P2 Medium DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 04:27AM After failing CWP-02 at string 2, WCC & CHWP staged down. String 2 still received command on in D2SD, the cooling tower remained on. 13/F Data Hall 2 CRAH_AR1_14's supply air temperature reached 27C. Data Hall SLA temperature was maintained within SLA range. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615646&prj=501&rqi=VUzqN7VhqQ1FS2v8XtLArvmrlD | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-001 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | equipment | 1EF_B_3 | EF - Exhaust Fan |  |  | 1EF_B_3, 1SF_B_2, 1EF_A_2 and 1SF_A_1 communication match alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615637&prj=501&rqi=0UxAsgfMIQfqYKayB2RrqRuUPY
FPT-483-016 | HK06-1 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 L12 & L13 02:18AM After ATS changeover of 13/F CRAH units, it was observed that CRAH_AR1_01, 03, 08 chilled water valve command went to 0% and fan command went to 50%. 02:19AM 13/F Data Hall SLA temperature sensors exceeded 27C. Pentagon to clarify why power source changeover will cause fan speed command and valve opening command to drop. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615627&prj=501&rqi=okQlBQbPT8Ml1P3SKVQ9TcbdE7 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-015 | HK06-1 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 L12 & L13 01:56AM After ATS changeover of 12/F CRAH units, data hall temperature sensors exceeded SLA upper limit. It was found that the chilled water valves of the CRAH units closed, causing the supply air temperature to rise. 01:58AM Data Hall temperature dropped back within SLA range | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615626&prj=501&rqi=N51lRdsacjmUDPVEYg4d1ZILpA | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-485-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS Graphics Issue | DCOS | Electrical | system | Electrical System |  |  |  | In EIST-01, during the total power failure scenario where SUDB_1 & SUDB_5 Q01 incoming breaker is opened, the power line logic is wrong. It displays wrong graphic and response. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615634&prj=501&rqi=yLqcDWgnubAGAyMFy4ivyHJbOL | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-479-003 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Electrical | equipment | 1ATSMI_M1R1_25 (1ATSMI_M1R1_32) | ATS - Automatic Transfer Switch |  |  | 01:41AM "Emergency Source Not Available" triggered for ATSMI_M1R1_23, 25, 27 Emergency Source. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615639&prj=501&rqi=nzKLWorRHy9Hy36oOXP5tEpGxz
FPT-483-019 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 04:45AM For 13/F Data Hall 1, after Chilled Water Riser C failure reinstate, "High Return Air Temperature" alarm was triggered for CRAH_AR1_04, 05, 08, 09, 10, and 18. Data Hall temperature was maintained within SLA. Pentagon to clarify the alarm dead band for "High Return Air Temperature" alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615630&prj=501&rqi=7Fjh9NDMqulYXL8JRZG2DluF75 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-018 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 04:16AM For 13/F Data Hall 1, after Chilled Water Riser C was failed, "High Return Air Temperature" alarm was triggered for CRAH_AR1_01, 02, 03, 06, 7, and 17. Data Hall temperature was maintained within SLA. Pentagon to clarify the alarm dead band for "High Return Air Temperature" alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615629&prj=501&rqi=ZuO6tBmQexH4q4Hyinoo95GQ2p | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-017 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 03:56AM After closing the return and supply valves of Chilled Water Riser B, DCOS was still showing ~4.5L/s of water for Riser B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615628&prj=501&rqi=9LJKr6sHlBFQ0c28vi4UYgx4HM | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-011 | HK06-1 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-17 (HLT1) 3/8/2026 WCC- Compressor had discharge superheat warning repeatedly triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615590&prj=501&rqi=BUR7oH3RTDEmF5lul0PXsHmkWV | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-012 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT-20 (HLT1) 3/8/2026 CHWBT_4 TCV-03 valve had mismatch alarm triggered. (Typical) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615591&prj=501&rqi=aBzsRQiqE48g2163fkmLOmglc1 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-009 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 - Test 05 L12 & L13 06:09AM When increasing the data hall load from 75% to 100% for 13/F Data Hall 1, "High Supply Air Temperature" alarm was triggered for CRAH_AR1_04, 05, 08, 09, 10, and 18. Data Hall temperature was maintained within SLA. 06:15AM The "High Supply Air Temperature" alarms auto cleared once the supply air temperature dropped back below the alarm setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615619&prj=501&rqi=FKhJvLjIE3GFQujEGTz7uRDJYC | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-010 | HK06-1 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT 3 - Test 22 11:40 Observed CRAH_AR1_13 stop operation during riser failure scenario. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615609&prj=501&rqi=SL9w5vI9zvQwOZ48pC0zOG8pCA | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-005 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT2 Test-04 L12 & L13 DPT-04 in CHWSTR_1 lost communication | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615615&prj=501&rqi=9cdYJhdrjmSj07wbuYogp0Bl4w | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-003 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 1: 0% Data Hall load: 12F Tx Room receives low temperature alarm(25.1degC) at 17:42 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615601&prj=501&rqi=EjglWrI8EVHJvIcgC17eHbXkck | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-013 | HK06-1 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-2 (12F & 13F) Test 11: CRAH Failure at Data Hall 1 at L12 and L13. 3/14/2026 12:46 MAU_M3R2_1,2,3 had communication alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615623&prj=501&rqi=hO4FRTbMxKSS1AL4FPJFH2arry | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-011 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 - Test10 L12 & L13 11:04AM For 13/F Data Hall 01, after failing both CRAH_AR1_08 & 18, SLA sensor 80_TT_04 reached 27C and triggered the SLA upper limit alarm, momentarily. It was floating between 26.9C and 27C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615621&prj=501&rqi=SoGzrbySAN4sMsIlAPCPTjvLEf | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-007 | HK06-1 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 Test-05 L12 & L13 05:55AM After the data hall load was increased from 75% to 100%, CHWSTR_2 chiller was called to start, but it was not able to stage in. DCOS chiller received an external fault, but no alarm was found at the chiller HMI. Fail to start alarm triggered on CHWSTR2. String 2 then staged in under free cooling mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615617&prj=501&rqi=LR6L2pUdLws1UNATnyeATVXmzY | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-002 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 Test-01 L12 & L13 00:17AM When increasing the data hall load from 0% to 25% for 12/F Data Hall 1, "High Supply Air Temperature" alarm was triggered for CRAH_BR1_01 to 10, and 17. Data Hall temperature was maintained within SLA, no pre-alarms triggered for SLA sensors. 00:20AM The "High Supply Air Temperature" alarms auto cleared once the supply air temperature dropped back below the alarm setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615612&prj=501&rqi=XvqHNNqBsOIuRc6ywFM3aFRTDv | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-006 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 - Test 5 05:39AM When increasing the data hall load from 75% to 100% for 13/F Data Hall 1, "High Return Air Temperature" alarm was triggered for CRAH_AR1_01 to 03, 06, 07, and 17. Data Hall temperature was maintained within SLA, no pre-alarms triggered for SLA sensors. 05:42AM The "High Return Air Temperature" alarms auto cleared once the supply air temperature dropped back below the alarm setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615616&prj=501&rqi=q7W9utqE33GnXD97m7weujy1PJ | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-009 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT3 Test 3 - 09:56 Observe bleed off pump common alarm on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615608&prj=501&rqi=7NfEwFOaBUvmiMmg5gz3qihJCJ | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-013 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT-10 (HLT1) 3/8/2026 MAU_2 and MAU_3 had incorrect fan speed reading on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615592&prj=501&rqi=Fmj5hOx2iWtNGM8PadV6wf4Wra | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-012 | HK06-1 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 Test-10 L12 & L13 11:40AM For both 12/F and 13/F, it was noticed that for CRAH units that triggered "High Supply Air Temperature" alarm, the alarm is held even when the group temperature has dropped below 25.7C. Pentagon had to power reset the units with the alarm to clear them. Pentagon to clarify why the alarm is unable to clear. Also whether there are any delays, and what is the alarm deadband. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615622&prj=501&rqi=5NNnI0qjfjYR28RDd9Pml9epYA | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 Test-01 L12 & L13 00:00AM When increasing the data hall load from 0% to 25% for 13/F Data Hall 1, "High Supply Air Temperature" alarm was triggered for CRAH_AR1_01 to 03, 06, 07, and 17. Data Hall temperature was maintained within SLA, no pre-alarms triggered for SLA sensors. 00:12AM The "High Supply Air Temperature" alarms auto cleared once the supply air temperature dropped back below the alarm setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615611&prj=501&rqi=vFIr9vzQmdyNEJSVF6nFqg38dM | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
GI-275 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | HLT-05 L12 & L13 10:45AM For 13/F Data Hall 1, after CRAH_AR1_18 was failed, "High Supply Air Temperature" alarm was triggered for CRAH_AR1_04, 05, 08, 09, 10, and 18. Data Hall temperature was maintained within SLA. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615550&prj=501&rqi=28w9h6F03fAKAOMpAiaJYoalqK
FPT-483-008 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Electrical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 Test - 05 L12 & L13 UPS A2 Alarm triggered. After checking by vendor, it was found phase A was overloaded. After adjusting the loading, the alarm was cleared. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615618&prj=501&rqi=fuZ7Fv2E6iw2vZqfPhs2w6PoE7 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-010 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 Test - 05 L12 & L13 10:45AM For 13/F Data Hall 1, after CRAH_AR1_18 was failed, "High Supply Air Temperature" alarm was triggered for CRAH_AR1_04, 05, 08, 09, 10, and 18. Data Hall temperature was maintained within SLA. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615620&prj=501&rqi=SdLbOwMqe8PdKHRmMu3sf9qCHz | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-004 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS Graphics Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT2 - Test 03 1RPP_B2R1_2_01 graphic mismatch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615614&prj=501&rqi=MFTtAKwPJ2DuxGM8EKjcGjVETN | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-003 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 Test-01 L12 & L13 00:30AM When increasing the data hall load from 0% to 25% for 12/F Data Hall 1, "High Supply Air Temperature" alarm was triggered for CRAH_BR1_04, 05, 08, 09, 10, and 18. Data Hall temperature was maintained within SLA, no pre-alarms triggered for SLA sensors. 00:33AM The "High Supply Air Temperature" alarms auto cleared once the supply air temperature dropped back below the alarm setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615613&prj=501&rqi=dnk3Q0KVuCRA5muUnEYT9i2wL4 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-004 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 1 13F battery room high temperature alarm. Sensor replaced. Observed around 2 degC difference between actual measurement and DCOS reading. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615602&prj=501&rqi=dHhhZTmm8htYxE8q8TDXSYlQOR | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-007 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | Mechanical Contractor | L4 | DCOS Graphics Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 13 Pentagon to clarify why after remote air temperature sensor failure, some units will show 0C, but some will hold last status. 12/F: CRAH_BR1_11 sensor 1 shows 0C, CRAH_BR1_14 holds last known. 13/F: CRAH_AR1_11 & 14 sensor 1 holds last known | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615606&prj=501&rqi=ZAkLeKjCbbGpnz1ifXT4Yvakgd | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-008 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 17 SE to clarify 1RAS_06 (Input 3) still having flowrate reading (~4L/s) after shutting off riser B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615607&prj=501&rqi=ETuW1hmMrEmI6k8XMxBLoOwqkp | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-006 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | Mechanical Contractor | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT3 - Test4 12/F and 13/F No feedback status for CRAH ATS status | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615605&prj=501&rqi=tT9Rx0gn2au8Xfv9ak3oujC3qE | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-011 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT 3 Test 22 - Mechanical failure scenario. CHWSTR1 changeover to CHWSTR 2. Observe CHWSTR1 fail to start alarm on D2SD. CHWSTR2 operates normally after changeover. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615610&prj=501&rqi=NhPFdF6QBHy2scfV3GOAtefF4F | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
GI-266 | HK06-1 | APAC | Closed | P2 Medium DCOS | ShirleyLeong@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning |  | system | DCOS |  |  |  | SE to recheck and troubleshoot the system settings and parameters because SE uploads new software/firmware for the chiller/DCOS when unauthorized software upload is allowed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615518&prj=501&rqi=9O1hjunWYITT5DzXjYx9sUmkmz | https://equinix.facilitygrid.co.uk/x/project/501/system/13006
GI-253 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | 1RPP_B2R1_2-01 graphic mismatch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615378&prj=501&rqi=jDNXSoJHn8YHlhvvA9l9Rrshsm
FPT-484-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 1: 0% Data Hall load: 17F Lv Switch Room receives low temperature alarm(24.8degC) at 17:39 17F Tx Room receives low temperature alarm(24.3degC) at 17:39 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615597&prj=501&rqi=eZEqQpkps4BjnMR26BNKZmFfwN | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-002 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 1: 0% Data Hall load: 15F 1EF_R1_6 receives command mismatch alarm at 17:40 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615598&prj=501&rqi=rbI0XjftpGwduLx4GuvzWG28DW | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-005 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 2 19:10 13/F DH2 exceed SLA during ramp up IT load. Unload to retest. 19:19 start again to ramp up load. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615603&prj=501&rqi=4gwR1LpZhus45RPzM3XdCntRnW | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
GI-242 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | During L3 of Water Leak Detection Point-to-graphic test, it is observed that point signals incredibly high value when not detecting any leak. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615323&prj=501&rqi=28KmZ8UYtsIZDGN0rkOfcWAyXE
FPT-482-030 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | 11:46 - During the power changeover for R1 block, some ATS that has R1 block as emergency source did not show emergency source not available. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615350&prj=501&rqi=FD8CbZcWhajpdjlqSIfi9pJQaC | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-482-029 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | SCH - Schneider MV | L4 | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | 11:40 - 1SUDB_5 was triggered with battery tripping unit alarm during block R1 was failed on DCOS. It resumed automatically after block R1 is supplied by generator. GEM team confirmed on site that no alarm were triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615348&prj=501&rqi=Kcd01KkNiSIwteOHRiJMJQtcjF | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-241 | HK06-1 | APAC | Closed | P2 Medium DCOS | PerryLee@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Pre-HLT L12 12/F Data Hall 1 CRAH_BR1_02 loss of communication alarm, unable to reflect status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615316&prj=501&rqi=SZYcKucRKVsAzBXUpzX5neQpO4
GI-243 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | During functional tests of water leak detection system, it is observed that for panels connected to leak detection cables AND point-type sensors, when simulating a specific leak test, the panel and DCOS read distances well above the accepted criteria. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615334&prj=501&rqi=DVkp1GvFSfXDoF6gqeURRhLWUw
FPT-482-031 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | SIE- Siemens MV | L4 | DCOS General Issue | DCOS | Electrical | system | Electrical System |  |  |  | 11:34 - During the power changeover for R1 block, MLTX_M1 was triggered with communication alarm. It is confirmed by GEM that the MLTX_M1 is online during the changeover and no M1 equipment undergo changeover. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615351&prj=501&rqi=0lO4868YLwCQrmgeLGZlaURdWd | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-482-028 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | Electrical | system | Electrical System |  |  |  | 11:17 - 1MSB_B Q06 is detected with communication alarm during EIST-12 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615346&prj=501&rqi=z4034xaUP4KFDMk1wDDOAwMKDd | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-239 | HK06-1 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Pre-HLT L12 and L13 13/F Data Hall 2 80_TH_04 exceeded SLA limit, it recorded 27.1C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615313&prj=501&rqi=VsDrAKaxZeZyZZKht4FWOgFkHN
GI-238 | HK06-1 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Pre-L12 HLT Failure CRAH_BR1_08 and 18 12/F Data Hall 1 76_TT_02 exceeded SLA limit, it recorded 29.1C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615312&prj=501&rqi=so2oqRQa6OYJJOHB3I02z8IZoZ
GI-240 | HK06-1 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Pre-HLT L12 Test 11 12/F Data Hall 1 80_TH_04 exceeded SLA limit, it recorded 27.7oC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615315&prj=501&rqi=K55ApwHPLTtLASawcWuSJA1rHS
GI-207 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | When one outdoor unit was failed (via E-Stop), the standby outdoor unit cannot stage in automatically. It has to be staged in manually. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615192&prj=501&rqi=5OSGl00BKJ7MMwbV2lHsd24RsF
GI-237 | HK06-1 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | L12 & L13 Pre-HLT Day 1 Hot spot identified near CRAH-AR1-05 and CRAH-AR1-10, which caused exceed SLA limit on L12 Data Hall 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615299&prj=501&rqi=9y5TYqUOoa9jCWW2wLk6y8FxNZ
FPT-482-021 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | 16:45 - CT occur with vibration fault causing the chiller to change string during the power resume for block M1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615287&prj=501&rqi=UazswLaA8SjgLf1I4Fqw3aZMRx
FPT-482-022 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | 17:15 - For SLA sensor 01-07 in the 15/F big data hall, it received communication alarm from 15:31 to 17:38. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615288&prj=501&rqi=QuXo9n1TdeNDlyr6372wPS5R2q | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-213 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | During power failure test for VRF indoor unit, it is observed that there is no alarm on DCOS and it keeps showing last status on the graphic. Gammon to confirm the point schedule with EOR and provide SICD for VRF system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615206&prj=501&rqi=bJu2Pha6vlkXZW0UUljUEH7CMi
GI-200 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | MIST-03 (Failure of CHWP) MAU2 Compressor 1 fault alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615167&prj=501&rqi=v8zqfMSka51V802ohaX5PHPIJT
FPT-482-005 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | 11:27 - Before the EIST start, DCOS received "ATS id no. ATSMI_M1R1_30, 04, 03" Emergency Source Not Available alarm. GEM confirmed that the essential power was healthy on site. GME shall clarify the mismatch between actual status and DCOS status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615271&prj=501&rqi=2O2DhvBhJ3bSTHbEvjLz3LJpWG
FPT-482-023 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | 17:38 - CRAH in the 13/F LVSB room did not show which source is it on before the power failure started on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615289&prj=501&rqi=GL50RWEGMFy70eCjmFEe3GFZXL
GI-211 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Point to graphic test is conducted on graphic template from SFAT. Gammon to confirm the point schedule with EOR and provide SICD for VRF system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615203&prj=501&rqi=aHWeEI3RU0k5TSAUyPMDIU08DL
GI-201 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | MIST-12 When PCP 02 was failed, "Hot Standby Status" and "PCP Status" did not show on DCOS graphics, all greyed out. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615169&prj=501&rqi=SbkB0WaMLtVBmppkoouPKkuBQ5
FPT-482-016 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Electrical Contractor | L4 | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | All "input breaker open" alarm is triggered when the battery is discharged. It is confirmed that the UPS input breaker is not opened on site and on the graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615282&prj=501&rqi=ALsObS7fUSO6dqW403LQ8eJdDU
GI-210 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | During unit sensor fail, operating unit will be switched off and other unit will run in 100% to cater the load. Please clarify logic for this scenario for the battery room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615196&prj=501&rqi=BQAnMK2WyX2Ke7JGW39sKhpvms
GI-204 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | After CWP was failed and when STR 2 WCC stages in, the run status of WCC 2 would flicker between On/Off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615172&prj=501&rqi=DLW9px4fGYBx5UA4xp7GSdaVur
FPT-482-019 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | 16:11 - When the STS is showing alarm from the event log, the STS icon beneath UDP did not show any alarm or surrounded with any color of border line. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615285&prj=501&rqi=IaVRB78AsxHEM7yM6Ql6XKwdGv
FPT-482-006 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | 11:52 - During the load is ramping up to 25%, DCOS received "summary alarm" with red border line, this indicated as a "high high alarm" were triggered for all the CRAH in 15/F DH1 & DH2. STULZ confirmed it is "high supply air temperature alarm". | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615272&prj=501&rqi=yMizFpOZEFprpD01C0S7MtbWSt
FPT-482-010 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | equipment | MSFD-13-14 | MSFD - Motorised SmokeFire Damper |  |  | 15:10 - MSFD-13-14 located at he generator set in 13/F generator room was found to be closed abnormally due to the flexible link is loose and resume at 15:20 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615276&prj=501&rqi=i5OPDJ33rfUtaLLTCBXmT1iLyW
FPT-482-020 | HK06-1 | APAC | Closed | P3 Low DCOS | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | Electrical | equipment | 1UDP_B2 | UDP - UPS Output Switchboard |  |  | 16:17 - 1UDP_B2 "communication alarm" is triggered when block B changeover from generator source to main utility source. It is confirmed that the MOXA has UPS power backup. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615286&prj=501&rqi=Rk6Vvj87IvSXJ14UkpyNTVAcZA
FPT-482-007 | HK06-1 | APAC | Closed | P3 Low DCOS | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | Electrical | equipment | 1UDP_B2 | UDP - UPS Output Switchboard |  |  | 12:08 - During the load is ramping up to 50%, DCOS recived "Communication alarm". FSL confirmed that the breaker did not triggered any lost communication alarm on site. SE DCOS should rectify this matter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615273&prj=501&rqi=jQT68HGa9U2mLbOA3EfOSwaxDe
GI-205 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | CRAH_LR1_01 to 14 triggered "High Supply Air Temperature" Alarm, Data Hall SLA sensors were all within SLA range. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615173&prj=501&rqi=7W1Ke1IPgWHNvhxiVuPAlVU1wk
FPT-482-012 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | 15:24 - During the changeover for M1 block, normal power light in 17/F command centre and LOCC room were found and it was not resumed when generator power has kicked in. The power resume after around 5 minutes. GEM EL team claim that there was light work ongoing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615278&prj=501&rqi=4KWqTRjfokev9cdrPFW6dSdppm | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-209 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | During non working hours, when the room temperature exceeds 30C, the FCUs would operate. This logic is not available. Please clarify this logic with vendor and NV5 and which room is applicable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615195&prj=501&rqi=NErcc94rJVq9yhTutUoBTKsRla
GI-202 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | MIST-12 When PCP 02 was failed, "Hot Standby Status" and "PCP Status" did not show on DCOS graphics, all greyed out. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615170&prj=501&rqi=pqQmq11aebaXNpsSeFszh0uGfA
GI-206 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | TCV-03 for CHWBT feedback and common mismatch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615174&prj=501&rqi=xUrUfE2AR31hmNmKkmCil7keA9
GI-199 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | L15 MIST MAU 2 Loss of Communication Alarm due to R-Block no power | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615161&prj=501&rqi=DsmuF9J3pe3tiFnBjImweFkuJE
GI-212 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | VRV Alarm priority to be clarified. Gammon to confirm the point schedule with EOR and provide SICD for VRF system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615205&prj=501&rqi=oj0qlfWk3LFajMkisecoDQD0tR
GI-208 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | When one FCU has power loss, the other FCUs connected to the same outdoor unit will also receive the fault code and trip. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615193&prj=501&rqi=7Kdd5yFy1ovUy4pLmEbjBPlIfH
GI-203 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | CHWBT_5 Bypass valve mismatch alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615171&prj=501&rqi=bz29VEL4J3Znyp7nYcKyOgeoK3
GI-169 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | During HLT-10 (CRAH failure at Data hall 1 and Data hall 2), GW88_TT05 and GW94_TT06 reach high temperature after reinstate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615054&prj=501&rqi=vCFiIXpoT9FjlKHCALutVF7zWp
GI-171 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | During HLT-13 (CRAH sensor for remote temperature, failure at data hall 1 and data hall 2), data hall 2 exceed SLA temperature high limit of 27 degree. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615056&prj=501&rqi=5K2JeoqOQSSDVKUQzRzfmONqhB
GI-170 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | During HLT-12 (CRAH sensor failure at data hall 1 and data hall 2), Data hall 2 reached 29.25 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615055&prj=501&rqi=Ew2cFjHnTTrbX03iTzmE7EvZue
GI-165 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | [6 empty] | During Pre-EIST day 2, when we are ramping up the load to 75% (16:14), 12/F electrical room room temperature is below low limit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615044&prj=501&rqi=OovcvQoRSCnn4v6poVBoCpDitG
GI-167 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | [6 empty] | During Pre-HLT (HLT-3), when the data hall is on 50% load and maintaining for an 1hr, the 13/F battery room has high temp alarm triggered | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615052&prj=501&rqi=R47P43941sK5wxZ3fyGpXEglFS
GI-152 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Block B receive an overvoltage issue during the Pre-HLT, causing the changeover happen between main utility and generator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615006&prj=501&rqi=vk6TCTSFETFIoQYlWMUSkIWgKw
GI-190 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | HVAC | equipment | 1FCU_M3_17 | DXID - FCU/DX Indoor Unit |  |  | FCU_M3_17 controller air speed button broken. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615081&prj=501&rqi=b5V3ylyxgNVeuSv33MIRB7445k
GI-196 | HK06-1 | APAC | Closed | P3 Low CX | ychoong@ap.equinix.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | During Pre MIST - ChWP changeover/failure, both halls 1&2 exceeded 27degC SLA but return normal within 1 min. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615111&prj=501&rqi=AjuSAIqRkkAhEOLq3Z1ksbCA9P
GI-198 | HK06-1 | APAC | Closed | P3 Low DCOS | ychoong@ap.equinix.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | During Pre-MIST, When PCP 02 was failed, PCP 01 took over but "PLC Stopped" alarm was triggered for PCP 02 Redundancy fault error alarm and PLC were also triggered for both PCP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615113&prj=501&rqi=vHJRE9Ro8a8iJLadbCyu6tPUyW
GI-195 | HK06-1 | APAC | Closed | P2 Medium CX | ychoong@ap.equinix.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | During Pre-MIST, MAU 01 found to be not runing. "SA Dewpoint High" was found on unit HMI | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615110&prj=501&rqi=fYHdvJCXERP8ibNjrVkCy2d5Jq
GI-164 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | surge protection device failure alarm is still receiving and active on DCOS for all MSB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615042&prj=501&rqi=dvGSclZlEuKISJ3zZKRWhxl2rV
GI-162 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS | [6 empty] | Before the Pre-EIST started, all MSB are receiving priority 2 alarm and priority 1 alarm on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615037&prj=501&rqi=YIlESb8D1UeHxkyP6CVRAXmV0J
GI-160 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | During the whole Pre-EIST for 15/F, all the CRAH in DH 1 and DH 2 on 15/F, the high supply air alarm is triggered on their control panel and summary alarm is triggered on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615031&prj=501&rqi=kA0KvVbw4g16rnQ1HROXkyakc9
GI-155 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | [6 empty] | MAU triggered a fault alarm on DCOS but on site the MAU does not have any alarm shown during Pre-EIST | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615018&prj=501&rqi=f5yb7u3kqCPFI6h5TFPOF4RV8A
GI-168 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS | [6 empty] | During the Pre-HLT, unit individual reading should be shown on DCOS graphic and group control temperature should be | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615053&prj=501&rqi=YGgyW1tkERVywIyR0ZXA0aj5MT
GI-153 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | Communication alarm for ATS is at MSB-M1 triggered during Pre-EIST when load was at 50% no switching was occuring at that point. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615015&prj=501&rqi=W3ZRYrzg98ZOcjKHcHJTkLym81
GI-158 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | UPS is triggered with high limit alarm on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615024&prj=501&rqi=33izNldu8dO9O0WvkUqrTTi4Ev
GI-197 | HK06-1 | APAC | Closed | P3 Low DCOS | ychoong@ap.equinix.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | During Pre-MIST, PCP 01 was failed, PCP 02 took over but "PLC Stopped" alarm was triggered for PCP 02. Redundancy Fault error alarm and PLC were also triggered for both PCP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615112&prj=501&rqi=Ja9I4vpPvf1BaIJ2Z62H2rwbhq
GI-188 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | HVAC | equipment | 1VRFOD_M3_5 | VRF - DX Unit Variable Flow System |  |  | 1VRFOD_M3_5 CHW flow speed and return temperature higher than design rating, Calibration cert out/dated for water temperature sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615079&prj=501&rqi=VJym81BVfJfZtLKwIYFrYVr4wu
GI-161 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | During Pre-EIST (EIST-15), for both of the UPS in 17/F LVSB room, external bypass breaker is closed but both of the UPS did not show it is on external bypass mode on the UPS HMI panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615033&prj=501&rqi=7nWfAa9K8xuXYb84wLU4aMOj6S
GI-157 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | RMU_R1 is showing red-dotting line on DCOS, however no alarm can be acknowledged on the RMU_R1 side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615021&prj=501&rqi=hK5DJ3FrAq23aiLGqGlYJtuQYi
GI-154 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | STSSB communication alarm is triggered during Pre-EIST | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615017&prj=501&rqi=PgUk64b237vraX0ztx1SyXHoDd
GI-159 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | During the EIST-12, when the changeover occur between mains utility and generator, both CRAH in the 17/F LVSB room is showing source 2 unavailable instead of source 1 unavailable (R1M3_1, R1M3_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615028&prj=501&rqi=4OcolqkpuPIfyzD0znD1uplicv
GI-179 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | DCOS panels cannot emit fault signal for room temperature sensor for testing ICUs function for temperature sensor fault. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615070&prj=501&rqi=LXTbgUnko8nT9bFKRAjaowKgmZ
GI-189 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | All indoor units supply air temperature lower than temperature set point at controller (set point: 16oC, measured: ~22oC). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615080&prj=501&rqi=UjEIOHaVWhMV4jPRmPE4sYcIgc
GI-193 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS | [6 empty] | STSSB_B2R1_1 and STSSB_A1R1_1 communication alarm is triggered | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615084&prj=501&rqi=h3fHshZIOQ8voJHDDVrrnpnUBN
GI-166 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | Before the Pre-EIST, for all the SUDB that is not under this phase, MCB common fault is active and triggered on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615045&prj=501&rqi=6GaMYMDvuXUY6zWzJZ2Oq0QQas
GI-191 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | [6 empty] | For all the FCU in 17/F office rooms, E-stop not yet tested. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615082&prj=501&rqi=snRBOeV5LcHQABcadMgmCqPVD8
GI-192 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | [6 empty] | The name specified in approved drawings is "FCU_M3_24" but the name of master panel shows "FCU_R2_24". Please clarify and rectify with correct name shown. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615083&prj=501&rqi=T960EiVUQnddRD6dAAosIQIE4e
FPT-481-014 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-10 (HLT1) 3/8/2026 GW94_TT06 high temp 27.1 and drop down to 26.9 within sec @05:25 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615593&prj=501&rqi=cpi671HZEJkDk77Gr069zRp7Wx | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-010 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT-1 (HLT1) 3/8/2026 1EF_R1_6 had common mismatch alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615589&prj=501&rqi=dmJPxadFnc7CH4KsLQLfYTlinv | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-015 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT-21 (HLT1) 3/8/2026 After Estop the WCC, CHWP can keep running for 2 mins. However after 2 mins, reset estop WCC and reset string 1, but string 1 cannot be reset to resume operation (string 2 was in maintenance mode). SE to clarify whether it fulfills the design intend. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615594&prj=501&rqi=YD8GUdAiX6rd6Vg4dfgFaNwAUh | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-009 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT-1 (HLT1) 3/8/2026 CRAH_LR1_15 &16 had lo/lo temp alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615588&prj=501&rqi=Ub83AEkaxgInOAtlluiDcEuQ6Q | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-002 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | Tuning the bypass valve min flow delay to 20s at 02:38 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615578&prj=501&rqi=mxnrCWJr6Vl5anFSGhZ5VPCUsp | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-008 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-5 (HLT1) 3/6/2026 12F Tx Rm, 13F Tx Rm, 15F Batt Rm, Tx Rm and 17/F Tx Rm, LVSB Rm had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615587&prj=501&rqi=EfcJIOY4lCcbnD4OdQhEUpoXBF | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-005 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-3 (HLT1) 3/6/2026 DH1 CRAH 04,05,08,09,10 had high supply air temp alarm triggered at 04:18 and resume at 04:19 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615584&prj=501&rqi=r1TdwR1iLnpScEauhIkwRUEN7T | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-007 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-4 (HLT1) 3/6/2026 12F Lv switch room had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615586&prj=501&rqi=OkWYq1VW8ldDEttmBhHMNQpkW3 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-006 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-3 (HLT1) 3/6/2026 12F Tx Rm LVSB Rm; 13F Tx Rm, LVSB Rm; 15F Tx Rm and Batt Rm; 17F LVSB Rm 2 had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615585&prj=501&rqi=mT5E9MeBsxPojdDPxxtLTLjHbn | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-003 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | High supply air temperature alarm for DH2 CRAH were triggered at 03:32 and resume at 03:32. Datahall keeps maintaining SLA range. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615582&prj=501&rqi=nqYNOpbK1B91aABf31AoH6qKtz | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-1 (HLT1) 3/6/2026 12F LVSB Rm, Tx Rm; 15F Tx Rm, Batt Rm;17 LVSB Rm had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615574&prj=501&rqi=zgy61UfHsybmTA6805rjqqeWzc | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-004 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-2 (HLT1) 3/6/2026 13F Batt Rm, Tx Rm, LVSB Rm; 15 Tx Rm; 17F Lv Switch Rm had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615583&prj=501&rqi=ivymKQs7Xbn94HNmQWYwwAvFji | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
GI-149 | HK06-1 | APAC | Closed | P3 Low CX | keymanchan@commtechasia.com | 2026-03-05 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | 16/F Chiller Plant - Emergency lighting discharge lower than 2 lux. (measure from floor) at the beginning of battery discharge The possible reason is chiller block the path of light. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614773&prj=501&rqi=5t14kq51YVWzMLQ6qkFds4qRg6
GI-151 | HK06-1 | APAC | Closed | P3 Low DCOS | JosephHalim@commtechasia.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | MAU overview page showing Static Pressure (Pa) - to change to Fan Flow (l/s). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614792&prj=501&rqi=TjN4g7Il0HYBEA3xFfurSU5XBc
GI-150 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-05 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | During heating mode, 1 outdoor unit will run. If it fails, it does not changeover to the remaining units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614790&prj=501&rqi=Wq5wr9dCt8xpUN7sfABejmc6AS
GI-146 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Compressor #3 icon not showing running / not running status on MAU 1 & MAU 2 DCOS Graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483402&prj=501&rqi=zfoBqiYg01Tn2tmk0ngk0Qj7YZ
GI-148 | HK06-1 | APAC | Closed | P3 Low DCOS | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | GEM and SE to coordinate and ensure all setpoints put on DCOS are according to approved settings as alarms were not activated during testing due to incorrect setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483404&prj=501&rqi=L9tI5GpHu8umPZ7xHy14Zyqcat
GI-142 | HK06-1 | APAC | Closed | P2 Medium CX | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Gammon to clarify with NV5 the design intent and control logic for CHW Valve under Free-cooling mode. Whether it operates as pre-treatment or not under free cooling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483398&prj=501&rqi=2Rox14R4HadGWS2AuKU9BWodHc
GI-147 | HK06-1 | APAC | Closed | P3 Low DCOS | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Fan flow not showing correct reading on DCOS for MAU 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483403&prj=501&rqi=8NLWYLB3XBy4Kfj7tZQDIvzRtb
GI-145 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | GEM to coordinate with Saiver and SE DCOS to rectify DCOS-autoON function for MAU unable to automatically restart upon power failure resuming. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483401&prj=501&rqi=M61GrgmicEr4hV52OIOMiDDeQe
GI-143 | HK06-1 | APAC | Closed | P2 Medium CX | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Gammon to clarify with NV5 the design intent and control logic of outdoor unit activation under different cooling mode temperature. If it is solely controlled by off-coil CHW temperature reading, or if airflow is also considered. To clarify and update SoO. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483399&prj=501&rqi=v3995SEPGOj0F2Omuk6Z7MbACh
GI-144 | HK06-1 | APAC | Closed | P2 Medium CX | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Gammon to clarify with NV5 the design intent and control logic for CHW Valve under heating mode. Whether it operates as pre-treatment or not under Heating. To clarify and update SoO. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483400&prj=501&rqi=JDcfUVSBg88Insu4VYJIKyoY9F
GI-140 | HK06-1 | APAC | Closed | P2 Medium CX | JosephHalim@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Control logic deviation from SoO: After 20 minutes (1200s) of exceeding the high SA temperature dewpoint, MAU should raise a high SA temperature alarm and shutdown. However - only alarm appears with no shutdown sequence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483389&prj=501&rqi=L6Dp44fAGruyGZGqir3gLXVo5M
GI-141 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | HVAC | equipment | 1CHWBT_5 | CHWBT - Chilled Water Buffer Tank |  |  | TCV_03 for CHWBT_4 and CHWBT_5 mal-function | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483390&prj=501&rqi=hA4jPojowqh1v0FhnaD2cgRWjI
GT1DCOS-24-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_29 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352267&prj=501&rqi=DIZbSaV1WKvecJL3p5sJGtfBiy
GT1DCOS-28-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_33 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352265&prj=501&rqi=sMV5k1lgygQbz9RCAd2FHcfVFB
GT1DCOS-25-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_30 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352268&prj=501&rqi=K6mAcVNblnvozDtkmUiep4Dm7Q
GT1DCOS-27-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_32 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352264&prj=501&rqi=WNxfXhEbhGTYViRA3zAvRw1vzU
GT1DCOS-26-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_31 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352263&prj=501&rqi=1xNFdtS03KVeM9alM96UdX9ol9
GT1DCOS-23-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_28 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352266&prj=501&rqi=zJaEFGDQHN6pGeqan4CaDGWgHy
GI-137 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | system | DCOS |  |  |  | It is found that Environment sensor alarm cannot be shown in the alarm log (Area Hierarchy) Issue found on room temperature sensor at floor 6,9 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221089&prj=501&rqi=nL1GOGTZmTTDRfCdbBcVnpBDUt | https://equinix.facilitygrid.co.uk/x/project/501/system/13006
GT1MECH-2-007 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Humidifier running status to be clarified. Individual running status should be provided on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204111&prj=501&rqi=ceoeyXlNPyUVz806FCh3LMsLiV
GT1DCOS-29-001 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_34 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221094&prj=501&rqi=MqxEAcXlv9yCyrker03IaSo6Sh
GI-123 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that CRAH ATS on alternative status is off when normal source is resumed and ATS is counting down to transfer back to the normal source. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204094&prj=501&rqi=9o5TEZK5FeyhJAm95XgVf4z4eM
GI-128 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | It is observed that no command point is available on DCOS. Please clarify deviation with point schedule Chilled water valve command Return air temp setpoint Supply Air temp setpoint Supply Fan speed command | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204101&prj=501&rqi=qpl3hEPU06JTVN9uEK6ZkTkPyg
GT1DCOS-31-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_36 | DCOS - Control Panels |  |  | Full point-graphic report outstanding. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221097&prj=501&rqi=BNiIRTwaTIEtBCV4nGFC08Nq8w
GI-131 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | system | DCOS |  |  |  | It is found that SLA range is incorrectly set. Please confirm the setting and rectify it. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204124&prj=501&rqi=DUTdkiSIxo7R1hCd3jIGiim3B5 | https://equinix.facilitygrid.co.uk/x/project/501/system/13006
GI-136 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | system | DCOS |  |  |  | It is found that SLA sensor reading have disconnection issue on DCOS. Please double check the configuration. Issue found on SLA sensors at 15/F DH1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221088&prj=501&rqi=eUQoB8YGCwA9Hxd5EVALrYQF13 | https://equinix.facilitygrid.co.uk/x/project/501/system/13006
GT1MECH-2-011 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Smoke detector alarm mapping mismatch. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204116&prj=501&rqi=GQY2jJzFMs4jZPrQxrxRp2nO33
GI-130 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | system | DCOS |  |  |  | Some SLA sensor faceplates are mal-functioning which is normal during the point-GUI test before. Issue found on SLA sensors at 15/F DH1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204123&prj=501&rqi=ktNWDtBaRTMhTkbOkEBDX6ir2x | https://equinix.facilitygrid.co.uk/x/project/501/system/13006
GI-124 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that there is no status update under column "Total" and "Active". Please clarify any status when unit is running or having alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204095&prj=501&rqi=UQhp0H7H54Hey5oFZoiAWl3ddP
GI-121 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | ATS alarm log description should be aligned with the graphic description. Normal source available (Rename as normal source not available) Alternative source available (Rename as alternative source not available) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204088&prj=501&rqi=N7ap2aOf0qcm33ekFxbioLzAHT
GI-122 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that CRAH ATS alarm normal source not available alarm stay active even though normal source is resumed. Alarm returns to normal status after ATS transfer back to normal source. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204089&prj=501&rqi=HYv1RDVbtPVvyNaSIyk607ccAk
GI-117 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS |  | system | eWall B |  |  |  | DCOS power line issue - Some power line is not shown with color when it is energised, some is showing with color when it is not energised. In general, the DCOS power line graphic for each equipment has variation to the real-time situation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204083&prj=501&rqi=fHZupau1c5DEfKXGYTuQ243W92 | https://equinix.facilitygrid.co.uk/x/project/501/system/13008
GI-126 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | It is observed site legend shows critical, high, medium, low alarm. In DCOS SICD document for CRAH, alarm severity is shown as urgent, high, low, inform. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204097&prj=501&rqi=q72l6RGzOg85QL3VO5GgxoZP16
GI-125 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that no reading under column kW. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204096&prj=501&rqi=720OJPcS0G57GXajGqeKgJ162F
GI-118 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS |  | system | meWall M1 |  |  |  | DCOS power line issue - Some power line is not shown with color when it is energised, some is showing with color when it is not energised. In general, the DCOS power line graphic for each equipment has variation to the real-time situation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204084&prj=501&rqi=V89yueZ2hTsRJ8DygsP08IKClR | https://equinix.facilitygrid.co.uk/x/project/501/system/13009
GT1MECH-2-013 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment type | AHU - Air Handling Unit | AHU - Air Handling Unit |  |  | All MAU unit / EC fan Auto status not able to be shown as operating on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204118&prj=501&rqi=HadsBPCgJTqZmzMBwjpbYzC8Ja
GT1MECH-2-008 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Humidity setpoint is not available on DCOS. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204112&prj=501&rqi=Xw77gYhURtjxpMuWuNQ5rgQuEC
GT1MECH-2-006 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Humidifier control signal to be clarified. It functions as "Read" point which deviates with point schedule | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204110&prj=501&rqi=GKa3mOKZmSj0HvV8pXf7Nz4ZN1
GT1MECH-2-014 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | EC fan DC bus voltage is not available on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204119&prj=501&rqi=3UmVZN76hANXZbyQQ4vjCZBjfR
GT1MECH-2-003 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Low temperature detector alarm is not available. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204107&prj=501&rqi=iQhh4DZDmpGP7cmRStI1Ese80d
GT1MECH-2-004 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Chilled water valve command to be clarified. It functions as "Read" point which deviates with point schedule | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204108&prj=501&rqi=cjKfh4d7uBQWsM8Akn5jKompjG
GT1MECH-2-001 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Decimal for Supply air fan flow and Air flow sensor range to be checked with GC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204105&prj=501&rqi=ebDGSrqdG71X8zDHAurTNifcI0
GT1MECH-2-009 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Outdoor air damper command to be clarified. It shows in 'percentage' on GUI and functions as "Read" point which deviates with point schedule. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204113&prj=501&rqi=bTCCSMcysxMkzFmcJiAIKDv1YU
GT1MECH-2-012 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Supply air temperature setpoint is not available. MAU is controlled by supply air dewpoint temperature. Please clarify with GC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204117&prj=501&rqi=djzxsNmLRUXwDDWilolTgpfjij
GT1MECH-2-015 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | EC fan kW unit to be checked. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204120&prj=501&rqi=QRikraqyN2nK6Wryz4L2wzdoJ7
GT1MECH-2-010 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Outdoor air damper feedback to be clarified. It shows in 'percentage' on GUI which deviates with point schedule. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204115&prj=501&rqi=OBQ8vyeKrdif1VNhwFhHMtY3e9
GT1MECH-2-002 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Supply air static pressure is showing supply air flow rate reading. Please clarify the deviation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204106&prj=501&rqi=AQQVkiOxhAG7qjtkcGyMeYz1IS
GI-127 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | Mechanical Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that ATS alarm description is different with point schedule. Please clarify deviation with point schedule Normal source available (Rename as normal source not available) Alternative source available (Rename as alternative source not available) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204098&prj=501&rqi=FZzq27lz2GCc586Df5ChmWOugW
GI-129 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | It is observed that these points are not available on DCOS. Please clarify deviation with point schedule Entering Water Temp kW Leaving Water Temp Supply fan command | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204102&prj=501&rqi=Y3gIPlStIcbHG9ZxRg5kbxNNV6
GI-119 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS |  | system | Rblock R |  |  |  | DCOS power line issue - Some power line is not shown with color when it is energised, some is showing with color when it is not energised. In general, the DCOS power line graphic for each equipment has variation to the real-time situation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204085&prj=501&rqi=Ysw63h4bXBTQjk6zQudIzQSyZe | https://equinix.facilitygrid.co.uk/x/project/501/system/13010
GT1DCOS-30-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_35 | DCOS - Control Panels |  |  | Full point-graphic report outstanding. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221095&prj=501&rqi=fKOoS8BWD9RisXPRbcEZbcxlj1
GT1MECH-2-005 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Humidifier command to be clarified. It shows in 'percentage' on GUI and functions as "Read" point which deviates with point schedule | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204109&prj=501&rqi=XtfwZqIIYcJtDmoAm3CV53CCoL
GI-081 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | Electrical Contractor |  | General Design issue | Design | [6 empty] | Fuel pump system SOO issue - during scenario where more than 8 generators sent signal for refilling fuel and a fault occur, pumps were not able to start up or changeover | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199725&prj=501&rqi=LGb3PLiqj3nSw631nTAk3lsIP1
GI-085 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | FCU DCOS issue - further clarification required where one point on DCOS is not done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199731&prj=501&rqi=9YmnWy2qhsg0oheYoaxewRZR1U
GI-083 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS | [6 empty] | MAU graphic is not ready and self test has not done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199729&prj=501&rqi=OgoC21Mu3gaqDkSHI0cHYrve8v
GI-087 | HK06-1 | APAC | Closed | P3 Low DCOS | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | BTMS DCOS communication issue - server is not ready and point is not checked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199734&prj=501&rqi=xZQVH8kCKJzU75PVbVvzhkqoQy
GI-084 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | VRV point to graphic issue (control card issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199730&prj=501&rqi=7K2YoCO8HblF9fKGJuUr802vpQ
GI-086 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | VER - Vertiv Electrical |  | Commissioning Issue | Commissioning | [6 empty] | RPP DCIM point mapping issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199733&prj=501&rqi=K0xEMrF9HXCHk6w7eSuEw5CmDj
GI-088 | HK06-1 | APAC | Closed | P3 Low DCOS | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | Chiller logic on DCOS is not ready - some of the logic is not following the SOO even though it can run in auto mode | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199735&prj=501&rqi=TdQyH6s2lh8p4PEzk1YL1lEjil
GI-082 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | It is observed that CRAH ATS alarm cannot be reset by "acknowledge" button after power resume. Please double check the logic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199728&prj=501&rqi=HuukZTCCXmdKCBxfdbidPzLfOA
GI-080 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Fuel pump system Cx L4 - A total of 8 to 15 nos. of Genset hall fill requests, the full system cannot be operated if A1 & B1 of the pumps have a fault. - The full system cannot be operated if Special Changeover scenarios (Already 2 Pump Running, Possible request more than 3 Pump). Because the logic can let both pumps A1 & A2 run or both pumps B1 & B2 run. But it cannot operate any swap combination pattern, both pumps A&B running together. The system will be in â€œHungâ€ Status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199632&prj=501&rqi=7ZOuNeg8pTYxHvZ3SrPuX6DM2I
GI-079 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS |  | system | eWall A |  |  |  | DCOS power line issue - Some power line is not shown with color when it is energised, some is showing with color when it is not energised. In general, the DCOS power line graphic for each equipment has variation to the real-time situation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199630&prj=501&rqi=jdb2qwYPA4oYIMzy6NyEZT6fIZ | https://equinix.facilitygrid.co.uk/x/project/501/system/13007
GI-075 | HK06-1 | APAC | Closed | P3 Low CX | keymanchan@commtechasia.com | 2026-02-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | BTMS (Busduct temperature monitoring system) 's DCOS part outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199257&prj=501&rqi=p0d39hfXG0wQ6jOqqxvVKIz8dT
GI-074 | HK06-1 | APAC | Closed | P3 Low CX | leocheng@commtechasia.com | 2026-02-16 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | STSSB test report DCOS cap screen not fully completed. Pending Vertiv to coordinate with Schneider to collect all cap screen to finished test report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199253&prj=501&rqi=XDxVZmljZA0pE5wVC1qHvTbPCw
RT1MECH-3-001 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | HVAC | equipment | 1MAU_M2R1_3 | AHU - Air Handling Unit |  |  | Nameplate of 1MAU-M2R1-3 is showing different model number to the approved material submission. Approved model: A1(C)1330H-1050W, while onsite model number on nameplate is showing A1(C)1330H-1200W. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199229&prj=501&rqi=wjXqtDtMt5d3kRLpEH2IeVjQUS
GI-072 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | It is observed site legend shows critical, high, medium, low alarm. In DCOS SICD document for CRAH, alarm severity is shown as urgent, high, low, inform. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199237&prj=501&rqi=Uw7XcjdcryFL8QXdZRpdvdtHm0
GI-073 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | Mechanical Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | Entering Water Temperature kW Leaving Water Temperature Supply Fan Command Normal source available (Rename as normal source not available) Alternative source available (Rename as alternative source not available) Please provide clarification and confirmed with EOR for any changes | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199238&prj=501&rqi=SJeCgF3AKlqeGYuGjJj0LqUAuT
GI-068 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that CRAH ATS alarm cannot be reset by "acknowledge" button after power resumption. Please double check the logic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199232&prj=501&rqi=aTm2PqGjGoQDfSubZH3jvmXthU
GI-071 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that no reading under column kW. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199236&prj=501&rqi=isjCSnXTMUlDoHPvJdYBNcyjsz
RT1MECH-2-001 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | 1MAU_M3R2_2 panel affixed with un-updated equipment ID: 1MAU_M2R1_2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199234&prj=501&rqi=QyyaBEa2cNNLjfQ7miIXtZ9RB8
GI-069 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | ATS alarm log description should be aligned with the graphic description. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199233&prj=501&rqi=rrygnZ2UFV6LkyJJUqJoJMRY4z
GI-070 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that there is no status update under column "Total" and "Active". Please clarify any status when unit is running or having alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199235&prj=501&rqi=dV7ulfd5GIHpXPJBgKKOs9ZBcA
GI-067 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-13 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS | [6 empty] | Gen set L3 Fuel pump system point to point test & logic test issue 1. Is the global design graphic for the "Main Tank X lockout" point and alarm show in the pump information? Please clarify. (image 1) 2. In the DCOS graphic during whole fuel pump logic test & point test, all fuel running path are outstanding (image 2, image 3) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199208&prj=501&rqi=mz1hR0EunrQoSlidrtce4RgPdZ
GI-066 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-02-13 04:00:00.000 +0400 | General Contractor |  | Component/Equipment failure | Commissioning | [6 empty] | During dummy load test, dummy loader failed to startup. Was first reported that the unit control power shut down during testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199177&prj=501&rqi=ZuTsZEMf2T093qcvQFZ0S0B4Gj
GI-064 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | BTU 24 hr discharge test were not able to follow as per the playbook intention. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199105&prj=501&rqi=pQWbgYTkEh9XkJzSMHAkVCp748
GI-065 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | HVAC | equipment | 1EF_M3_7 | EF - Exhaust Fan |  |  | The exhaust fan type of 1EF_M3_7 in SOO not align with approved fan equipment schedule. In-line fan type approved in equipment schedule, however EC fan type approved in DCOS fan SOO | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199113&prj=501&rqi=VFN3rpaV2yEoD4fsc3GpEa8xRT
GI-063 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS | [6 empty] | RMU power path is incorrect. During Cx L4 testing for the RMU, when both of the incoming VCB is open, the power path connecting between both of the RMU is showing to have power floating, whereas the RMU is also shown to be energise to the downstream. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199102&prj=501&rqi=yYEfiylKNzDjufKTXAsZKGrzYI
GI-061 | HK06-1 | APAC | Closed | P2 Medium DCOS | PerryLee@commtechasia.com | 2026-02-11 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | HVAC | equipment | 1CHWSTR_M1R1_1_CWP_1 | CWP - Condenser Water Pump |  | Ebara | WCC and CHWP fail to start but fault alarm not triggered on DCOS due to incorrect set point | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198976&prj=501&rqi=e49t1ELudDDUWaDnaUZs4HB4ls
GI-060 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-06 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS General Issue | DCOS | [6 empty] | DCOS graphic for chiller is not ready, immediately fix and solution must take action | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198686&prj=501&rqi=YBbRCYlvekGVPLHyuPUYGDSQNo
GI-058 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | UPS did not exit ESS mode when it is performing 0% to 50% step load | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198323&prj=501&rqi=Z8A8CN9H5RPQM1ZRCXxG1n1Hti
GI-059 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS | [6 empty] | RMU point has issue during Cx L4 During the Cx L4 test for RMU, when one of the VCB is opened, the DCOS graphic for the RMU went offline. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198474&prj=501&rqi=v48CBMm7swGfFOG4vRYPtKLtk6
GI-056 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | DCOS and the network is super slow which it has slowed down the T&C process | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198319&prj=501&rqi=iM3KjAyLudaP4ejMTI3n6VstQg
GI-057 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | SCH - Schneider MV |  | General Design issue | Design | [6 empty] | BTU for SUDB not able to do 24hr discharge | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198320&prj=501&rqi=rO1OdDgCuz4PuIwHvMbVosnwuL
GI-043 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Please confirm remote temperature setpoint in UPS Room. As per SOO, the setpoint is 27degC. It is observed that CRAH in UPS Room is operating at 60% at low load conditions. Return air temperature (from remote temperature reading) is around 25 degC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198215&prj=501&rqi=0w4ziBVqmvQAxcjLgXbsDhMC7l
GI-055 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | It is observed that CRAH ATS on alternative status is off when normal source is resumed and ATS is counting down to transfer back to the normal source. (DCOS) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198233&prj=501&rqi=qauCOFoidBMqRFqX4OnPEbhVS6
GI-048 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | As per SOO, fan speed will ramp to meet the setpoint if remote temperature reading is higher than setpoint, vice versa. It is observed that fan speed will ramp when remote temperature is getting closer to setpoint. Please clarify PID / proportional band setting for CRAH fan speed control and update equipment setting table for fan speed control. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198223&prj=501&rqi=4rAq4p9BFvEENlSPfh6Io24JsU
GI-046 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | As per SOO, CRAH equips with in-built return air temperature sensor in Lv Switch Room and in-built return air temperature sensor with humidity in DataHall. It is observed that in-built return air temperature reading is excluded. Please clarify whether it fulfills design intent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198219&prj=501&rqi=xSv83OI7uuop9vwQTQeNUtLSkx
GI-045 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | It is observed that CRAH supply and return air temperature in group mode is showing the group control temperature on DCOS(All units have the same reading on DCOS). Individual CRAH unit temperature reading cannot be shown on DCOS. Please clarify whether it fulfills design intent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198217&prj=501&rqi=KoGcEUIltIgqycEVn3IiCxT3xg
GI-052 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | As per SOO, CHW valve will be opened to Vmax position. It is observed that CHW valve will close after lost of command signal. Please clarify the deviation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198229&prj=501&rqi=fzccFLPhpBK3nltKLuFRYiSCSz
GI-040 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | Missing cover for remote air temperature sensor for CRAH. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197702&prj=501&rqi=QU83LnQRBAKrfCr2GZhHLA3ngr
GI-049 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | As per SOO, remaining fan will ramp up to maximum speed. It is observed that CRAH unit in group control mode will be ramp up to maximum fan speed and stop running afterward when single fan within CRAH is failed. Please clarify the discrepancy. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198224&prj=501&rqi=S6JdSUnyV2rEXvMcB3FIUuIm4X
GI-051 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | It is observed that CRAH unit requires a close contact for VAC trip while â€œNOâ€ contact is a common practice for fail safe purpose. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198228&prj=501&rqi=izZeISu3bUd3UOSK1vk88PP470
GI-044 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | CRAH fan speed is controlled by return air temperature reading while return air temperature consider highest CRAH unit average remote temperature reading in group for calculation. Please clarify whether it fulfills design intent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198216&prj=501&rqi=CIYLRSgEu9HIK8ACJLGIBXwvfI
GI-042 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Please confirm ATS setting for CRAH in UPS Room that is not supplied by UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198208&prj=501&rqi=elRzHEXbqWiLgEVjrqj4q8GJ7E
GI-041 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | General Design issue | Design | [6 empty] | When the transformer is de-energized with high temperature trip, power loss to the transformer control power because the incoming control power is coming from one of the DB in MSB which does not have any UPS power back up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198186&prj=501&rqi=EoYDOKXZ9GHvFyOehthSdk5cFB
GI-050 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | It is observed that no alarm will be raised on controller under dual power failure condition. It is deviated with SOO. Please clarify the discrepancy. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198227&prj=501&rqi=Yg96uKyzcOIz36XkToRqUifcyB
GI-054 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | It is observed that multiple CRAH units supply air grille are damaged and the condition of SAGs are deteriorating. Please provide a schedule for replacement work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198231&prj=501&rqi=fjTy7M2dx7BJHyN7ymqxGkSy3Y
GI-047 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | It is observed that CRAH unit in group mode consider highest RAT and SAT reading for fan speed and valve control. High / low return air temperature and supply air temperature alarm activation also follow the same logic. Please clarify whether it fulfills design intent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198221&prj=501&rqi=RY3hRabuEud7A8cJw6oD65Vmjv
GI-039 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-01-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | DCOS network is not stable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197602&prj=501&rqi=QJRrvGyWTMRTOp6kwmyIiT919O
GI-038 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-01-26 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | UPS physical damage for UPS L12, L13, L15, L17 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197553&prj=501&rqi=sNiBtLbnGdCOXHGgzTx1akSV4a
GT1ELEC-32-001 | HK06-1 | APAC | Closed | P3 Low CX | lawkwokfai@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Construction Manager | L3 | Commissioning Issue | Commissioning | Electrical | equipment | 1ATSMI_M1R1_26 (1ATSMI_M1R1_33) | ATS - Automatic Transfer Switch |  |  | ATS ID number do not match DCOS; B-C & A-C have 54V shown on display and DCOS when power off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197441&prj=501&rqi=OmzC3vI7OLkCBqeipbFSAiTHbC
GT1ELEC-36-001 | HK06-1 | APAC | Closed | P3 Low CX | lawkwokfai@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Construction Manager | L3 | Commissioning Issue | Commissioning | Electrical | equipment | 1ATSMI_M1R1_27 (1ATSMI_M1R1_34) | ATS - Automatic Transfer Switch |  |  | ATS ID number do not match DCOS; B-C & A-C have 54V shown on display and DCOS when power off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197442&prj=501&rqi=bLu9IaN3ngOpe0zfbeetccy69y
GT1ELEC-30-001 | HK06-1 | APAC | Closed | P3 Low CX | lawkwokfai@commtechasia.com | 2026-01-21 04:00:00.000 +0400 | Construction Manager | L3 | Commissioning Issue | Commissioning | Electrical | equipment | 1ATSMI_M1R1_24 (1ATSMI_M1R1_31) | ATS - Automatic Transfer Switch |  |  | Communication alarm test with DCOS fail, device name matched drawing and FG but not match DCOS, B-C and A-C have 54V shown on display and DCOS when power off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197306&prj=501&rqi=83eNiAy1co8MQQqqM67jORdkmU
GI-037 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that ATS Alarm - Normal source not available and alternative source not available alarm was shown on DCOS graphic which are deviated with point schedule. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197243&prj=501&rqi=bKvTpQNjUXNQKmq0RC5AcWEBGb
RT1MECH-210-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | HVAC | equipment | 1EF_L_1 | EF - Exhaust Fan |  |  | Installation of motion sensor will be verified at Cx3 after completion of fitting out work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197097&prj=501&rqi=bKNRusRe02PAyxYV8Jyyhb688k
RT1MECH-211-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | HVAC | equipment | 1EF_L_2 | EF - Exhaust Fan |  |  | Installation of motion sensor will be verified at Cx3 after completion of fitting out work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197098&prj=501&rqi=iS1vkbA3nHvCkxagUgx9a63Z8V
RT1MECH-102-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | HVAC | equipment | 1EF_A_1 | EF - Exhaust Fan |  |  | Installation of motion sensor will be verified at Cx3 after completion of fitting out work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197096&prj=501&rqi=QctikOtrt7g7NiWu0Jni4ZmSU5
GI-036 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-01-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | 1. ATS equipment ID not aligned between DCOS and on-site layout. 2. Communication alarm only response when both sources is detected with 0V which it should not be the case. 3. When the main source of the ATS is simulate with lose of power, main source still detect with around 50V on phase to phase, this happen same to the alternative source of the ATS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197062&prj=501&rqi=Xoc7kr2qeFJ0nUV1KryK5Mqpd9
GT1ELEC-31-001 | HK06-1 | APAC | Closed | P3 Low CX | lawkwokfai@commtechasia.com | 2026-01-16 04:00:00.000 +0400 | Construction Manager | L3 | Commissioning Issue | Commissioning | Electrical | equipment | 1ATSMI_M1R1_25 (1ATSMI_M1R1_32) | ATS - Automatic Transfer Switch |  |  | Communication alarm test fail, device name match drawing and FG but not match DCOS. B-C & A-C have 54V shown on display and DCOS when power off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197312&prj=501&rqi=jAqu0k3uRNXxlQqQ47MOrSmg7x
YT1MECH-247-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-02 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | HVAC | equipment | 1FCU_M3R2_53 | FCU - Fan Coil Unit |  |  | Scratches were found on LMCP casing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196248&prj=501&rqi=bAdQ1lGds7QFZLeTvrl1rVI2eB
YT1MECH-237-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-02 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | HVAC | equipment | 1FCU_R2_54 | FCU - Fan Coil Unit |  |  | Scratches were found on LMCP casing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196249&prj=501&rqi=8kResN7i7aokMdhvo2eBx8LBbM
GT1MECH-378-001 | IL03-1 | S-EMEA | Open | P3 Low CX | s.collier@core-group.me | 2026-09-15 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | General Design Issue | Design | Electrical | equipment | 1HWS_C_1 | HWS - Water Heater |  |  | The access to maintain HWS C1&3 is very limited and may need ceiling removed to replace the Heater if required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638114&prj=609&rqi=dwR2WE048YTybly4FsX57jHlyb
YT1ELEC-419-001 | IL03-1 | S-EMEA | Open | P3 Low CX | o.alemdag@core-group.me | 2026-09-15 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | Trace Heating (Chilled Water) | TRACE - Trace Heating |  |  | L2b_Elec_OA: There are defects on this panel as follows. Pictures are also attached. * Cables routed on earth bar * Two cable lugs connected at a single termination point * Deep cleaning required * Missing bolt connection * Missing cable tray covers * Missing covers at panel bottom * Sealing issue identified * Missing torque marks on connections * Improper cable lug installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638086&prj=609&rqi=02AbF89IZj4Oi7rxinUbtLVPEw
GT1MECH-136-001 | IL03-1 | S-EMEA | Open | P3 Low CX | k.erbay@core-group.me | 2026-09-03 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_R_01 | CRAH - Technical Room CRAHs |  |  | The ventilation grille's louver is damaged and the mounting screws are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636649&prj=609&rqi=66yiwrdtT9kz9VnAia2DrSFOrr
GT1FS-222-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | o.alemdag@core-group.me | 2026-08-18 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Component/Equipment Failure | Commissioning | Fire Suppression | equipment | 1MFD_C_62 | FD - Fire Damper |  |  | L3_Electrical_OA: There is an issue during L3 test, C _62 damper open-close status could not be completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634100&prj=609&rqi=ytlNwzuvhyq4kRSibz5dVaope0
L2L3 Sun-159-002 | IL03-1 | S-EMEA | Open | P3 Low CX | o.alemdag@core-group.me | 2026-08-18 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning |  | equipment | PAVA Main Equipment Rack | PAVA Main Equipment Rack |  |  | L2b_Electrical_OA: During L2b inspection, following issues are found the PAVA panel in the security room. * Panel fans, some bolts and covers are rusted. Please check Image 1. * Battery connections are not completed. Check Image 2. * There is still un-terminated cable in the panel. Check Image 3. * There is high dust, foreing objects inside and around the panel. * Cable entry from above is not sealed. Covers in bottom side of the panel is not completed. Check Image 4. * Panel humidifier or thermostat setting must be set as per required value. Check Image 5. * It is not clearly visible which cable connection is done each zone. There is no label on the panel racks etc. Check Image 5. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634095&prj=609&rqi=MQpBpS0wOWlZv85n87ttPC8iXF
YT1SEC-37-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | o.alemdag@core-group.me | 2026-08-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Electrical | equipment | NIRB.0101 | ICT Racks |  |  | L2B_Electrical_OA: Missing equipment ID tags especially AV sockets etc. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632728&prj=609&rqi=xdtr5D4SiBMj2KPJFvJbhw8Iow
GT1MECH-44-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-08-03 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_17 | CRAH - Technical Room CRAHs |  |  | The equipment label on the CRAH unit is damaged and partially illegible. It needs to be replaced. This applies to the CRAH units listed below. -1CRAH_A_17 -1CRAH_A_18 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631994&prj=609&rqi=f4KRLiCLT5bOdSpCWp23x2fmuD
YT1ELEC-34-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | a.tuysuz@core-group.me | 2026-07-20 04:00:00.000 +0400 | CMM - Cummins | L2B | Component/Equipment Failure | Commissioning | Electrical â€“ MV | equipment | 1-GEN-B | GEN - Generator (MV) |  |  | During the MV route checks from 1-GRMU-C to 1ZZTRMU_A, cracks were observed on the MV termination kits (Euromold type) installed at the incomer connection from the Gen-B alternator to 1-1GRMU-B. The MV cable connection between the generator alternator and the GRMU incomer shall be thoroughly inspected. The cracked termination kit shall be replaced with a new approved termination kit and the cable shall be tested following the replacement. A cable test report shall be prepared and submitted for all generator-to-GRMU incomer cables. The report shall include, at a minimum, two clear photographs demonstrating that the cable termination kits are installed correctly and are free from defects. This comment is applicable to all Generator sets and their respective GRMU incomers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630007&prj=609&rqi=Be8ThpP4ctMCvKH8gCdaKSrCIb
RT1ELEC-32-005 | IL03-1 | S-EMEA | Closed | P3 Low CX | a.tuysuz@core-group.me | 2026-07-08 04:00:00.000 +0400 | CMM - Cummins | L2A | Design not as specified | Design | Electrical â€“ MV | equipment | 1-GEN-A | GEN - Generator (MV) |  |  | Regarding the ARUP / Generator Earth Bar technical submittal and the design correspondence below dated 07/07/2026 at 10:17 AM, the earth bar inside each genset container shall be rectified in accordance with the approved technical submittal and the requirements outlined in the email. This requirement is applicable to all Gensets. "The removable link shall be incorporated into the generator earth bar arrangement as indicated in the approved Cummins shop drawings. This requirement was raised during the QA/QCâ€“FAT visit, formally noted, and subsequently reminded. To remain fully aligned with the design intent, the incomer connections originating from the transformer room, local earth rods, and the serial bonding conductors between generator earth bars shall be terminated on the opposite side of the removable link, as shown in the shop drawings. This arrangement is necessary to maintain compliance with the approved design." | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628430&prj=609&rqi=ZVOnIEw2KYfhWCD4CZYCE0yCDQ
RT1ELEC-32-006 | IL03-1 | S-EMEA | Open | P3 Low CX | a.tuysuz@core-group.me | 2026-07-08 04:00:00.000 +0400 | CMM - Cummins | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1-GEN-A | GEN - Generator (MV) |  |  | Regarding the ARUP exit signage and emergency lighting fixtures used in the GEN-SET area, and with reference to the correspondence below dated Thursday, 21 May 2026, at 3:47 PM, please note that the lighting fixtures inside the containers shall be fully replaced with self-contained emergency luminaires,And external lights to be provided over all acces doors. This requirement is applicable to all GEN-SET containers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628431&prj=609&rqi=V7h37api28I0NTsAj0osGqdh9H
L2L3 Sun-159-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | w.tavares@core-group.me | 2026-06-26 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning |  | equipment | PAVA Main Equipment Rack | PAVA Main Equipment Rack |  |  | During the L2B inspection it was found that same PAVA speakers need to be replaced, and the Cleaning has not been Completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627061&prj=609&rqi=46MnkL6tCodajoHyrDrd5NPTmI
GI-027 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-19 04:00:00.000 +0400 | SCH - Schneider MV |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Closing interlock logic in C264: mismatch between software and wiring. There seems to have been a wiring change in the C264 interlock output contact (change from NC to NO). These wires have different labels than factory wiring. Now the latest software update in 264 matches the original wiring Even the drawings are confusing. On one page there is NC contact, on another page is NO contact. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626239&prj=609&rqi=vCSSJzGZSfDDnVgIsbwrqINREu
GI-024 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-17 04:00:00.000 +0400 | General Contractor |  | General Design Issue | Design | [6 empty] | Personel cannot be evacuated safely in case of an urgent, rapid evacuation. if someone goes out rapidly from the gemerator enclosure it would find itself trapped on the plantform, on the side without ladder | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625750&prj=609&rqi=zpV9IcfRu75c53tSMXJ0VQHmDy
GI-023 | IL03-1 | S-EMEA | Open | P3 Low CX | i.vasilescu@core-group.me | 2026-06-17 04:00:00.000 +0400 | CMM - Cummins |  | Installation not correct | Commissioning | [6 empty] | MV cable tray is not secured against seismic risks. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625749&prj=609&rqi=E0p4kAttSaaHgSpwuN6o0GSmKi
GI-022 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-17 04:00:00.000 +0400 | SOC - Socomec |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Internal STSSB power connection found not torqued during ispection. (section right after the bus bar flange - see attached picture). This was torqued and marked during the inspection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625585&prj=609&rqi=2Gu8LNdCTSbVyWJDrYrlzsm8uv
GT1ELEC-15-005 | IL03-1 | S-EMEA | Closed | P1 High CX | m.yerkoylu@core-group.me | 2026-06-16 04:00:00.000 +0400 | SCH - Schneider MV | L3 | Component/Equipment Failure | Commissioning | Electrical â€“ MV | equipment | 1PUSP_2 | PUSP - Primary Utility Supply Panel |  |  | The L3 phase connection to the Voltage Transformer (VT) experienced an arc flash event. The VTs appear to remain structurally intact; however, arc flash marks were observed on the top surface of the L3 VT and around the L3 cable boot. The protective top cover at the L3 cable termination on the VT side was found dislodged following the incident. The VT enclosure sustained mechanical damage, with localized outward bending of the panel, but no internal components were exposed. Inspection of the L3 VT secondary wiring revealed no apparent damage to the cables themselves; only the protective sleeving showed signs of arc flash damage. It should be noted that the L3 VT and its associated cabling were factory-installed, terminated, and tested by the MCE vendor, and were delivered to site as a complete assembled package. No personnel were present in the room at the time of the incident, and no injuries were reported. Photos are attached. MCE/GC to provide RCA accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625471&prj=609&rqi=icADCGmddgXBBlBOUP7g4qC89B
GI-021 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-11 04:00:00.000 +0400 | SCH - Schneider MV |  | General Design Issue | Design |  | equipment type |  |  |  |  | MV commissionability: trip signals should be made available through the test block. otherwise, with each maintenance these wires will be tampered with | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625308&prj=609&rqi=yC46jJHuDl8aievxl03P20ZlJs
GI-018 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider MV |  | Incomplete Connections | Commissioning |  | equipment type |  |  |  |  | trip circuit supervision inputs are both active when according to schematics only one should be active (return path through CB position) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623669&prj=609&rqi=iS8Q7t6CRPcRqHB6tg9cfskHE2
GT1ELEC-15-004 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider MV | L3 | Design correction needed | Design | Electrical â€“ MV | equipment | 1PUSP_2 | PUSP - Primary Utility Supply Panel |  |  | spare contact for trip lockout is wired to a NC contact. this should be wired to NO contact. change in PUSP1 as well | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623666&prj=609&rqi=IfQQHg4J5oYvAiqNTTpVl5xwDs
YT1MECH-412-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-06-02 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Design correction needed | Design | Fuel | equipment | Fuel -Oil System-GEN-R | FFIL - Fuel Fill System |  |  | Access to the daily fuel tank is inadequate. The piping/valves structures installed in front of the access area restrict maintenance access and should be reviewed against the clearance requirements specified in the approved drawings. In addition, sufficient access is not available to fully open the louvre doors on the generator enclosure. A permanent access platform shall be provided to ensure safe operation, inspection, and maintenance activities in accordance with HSE requirements and the manufacturer's recommended clearance requirements. Applicable to all GEN Sets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623642&prj=609&rqi=3PrjcCOl5MOxKobRENftbyWext
GI-016 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  | equipment type |  |  |  |  | this contact needs to be NO. to be modified in PUSP1 as well. attach picture with evidence to close it | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623667&prj=609&rqi=cnbaqr2lvGasGNH5fD10bzORpZ
GI-017 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  | equipment type |  |  |  |  | TRIP OUTPUT needs to LATCHED! | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623668&prj=609&rqi=7aTRH9CV8g09FIcJ61J78l5Isy
GT1ELEC-15-003 | IL03-1 | S-EMEA | Closed | P3 Low DCOS | i.vasilescu@core-group.me | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS Design Issue | DCOS | Electrical â€“ MV | equipment | 1PUSP_2 | PUSP - Primary Utility Supply Panel |  |  | this "alarm" needs to be properly defined. at the moment, with cb open, the alarm changes its status just by changing the disconnector | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623665&prj=609&rqi=kagjt3BACrDUKdAr6qRmcSZksD
GI-014 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-21 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | system | MV System |  |  |  | Cables from Control circuits need the have their screen earthed on one end. attached, in the picture, are current measurements from SUDB. to PUSP. its screen is not earthed on any side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622687&prj=609&rqi=whsCHsh7vk2ng9IxWa25sTvblJ | https://equinix.facilitygrid.co.uk/x/project/609/system/12241
GI-013 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-21 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  | equipment type |  |  |  |  | Current measurement circuits need to have one point of earthing on star point. currently, the circuits coming from SUDB to PUSP is not earthed. a temp link has been made in PUSP1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622686&prj=609&rqi=Wl4QrmWnkuSFSfB3ZqCGIF9C5P
GI-012 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-21 04:00:00.000 +0400 | SCH - Schneider MV |  | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1PUSP_1 | PUSP - Primary Utility Supply Panel |  |  | current measurement cable cannot be of a colour identical to grounding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622675&prj=609&rqi=z6kpF6cQw3AOe1nQVt6VtpA1s4
YT1MECH-48-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_17 | CRAH - Technical Room CRAHs |  |  | The grilles of the CRAH unit was damaged (see attached photo) and needs to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622541&prj=609&rqi=IMv0WlLwymOi8FZsjdsGNSwukU
YT1MECH-49-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_18 | CRAH - Technical Room CRAHs |  |  | The left panel/cover of the CRAH unit was damaged (see attached photo) and needs to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622539&prj=609&rqi=0Es9TEVenRHOEtCzojf7gNDF7S
YT1ELEC-35-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | a.tuysuz@core-group.me | 2026-05-18 04:00:00.000 +0400 | CMM - Cummins | L2B | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1-GEN-C | GEN - Generator (MV) |  |  | During the L2B inspection of 1-GEN-C comments are listed below. 1- GEN SETs pressure test reports for pipework and day tank shall be added to the L2B documentation. (Previous phase test document is attached.) 2- Pressure gauge calibration certificates shall be added to the L2B test documentation. 3- Sleeves shall be installed at the each MV cable tray joints, and the sections which is contact on MV cables shall be cut/trimmed accordingly. 4- The gap between the deck ladder and the walking platform shall be closed. 5- The GRMU MV cable glands shall be tightened at the bottom. 6- Floor openings shall be closed. ( General comment ) 7- It was observed that particles are present inside The batteries and alternator.Cleaning is done not enough. 8- Rusted IMC conduits shall be cleaned in accordance with the applicable procedure/standard. 9-Emergency lighting fixtures and signage have not been installed on the doors.( Please provide tech submittal ) 10-LV and ELV cables shall be properly rectified, as the current installation is not sufficient. 11-General and detailed cleaning of all equipment parts shall be completed. 12-Equipment (lighting switches, power outlets, etc.) shall be labeled according to the DBL circuits, not according to the cable schedule. The items listed above are applicable to both 1-GEN-C and 1-GEN-B. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622152&prj=609&rqi=RaYsUektbGHkuubXqyiqLep6Gz
GI-006 | IL03-1 | S-EMEA | Closed | P3 Low DCOS | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS | Electrical â€“ MV | equipment | 1PUSP_1 | PUSP - Primary Utility Supply Panel |  |  | PUSP Bay numbers (Q01, Q02) don't match the ones from DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621857&prj=609&rqi=1eeI0zYHIDPrYwfo7QJrQca49z
GI-005 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  | equipment type |  |  |  |  | Breaker failure protection functionality in PUSP is reversed. Incomer sends trip to Feeder, when it was supposed to be the other way around. (executed as per drawing) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621852&prj=609&rqi=Q3mbFVpemSkNwI1x1ybTS1WpIa
GT1ELEC-14-001 | IL03-1 | S-EMEA | Open | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV | L3 | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1PUSP_1 | PUSP - Primary Utility Supply Panel |  |  | Pendant CB status not working (light bulbs are missing) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621853&prj=609&rqi=LG78dT6HNOBlXEG3uxYqUyWTUo
GI-008 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Design correction needed | Design |  | equipment type |  |  |  |  | PUSP - Tx Feeder- Isolator Switch Position is not present in DOCS Every HV equipment position needs to be present in DCOS one way or another | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621864&prj=609&rqi=MPb6doP6gf1tCqEVDmXpXfieLX
GI-004 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  | equipment type |  |  |  |  | P643 Current circuits: 34kV outgoing cable Core Balance CT is not wired as per relay manual. NER CT not present in the design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621792&prj=609&rqi=UoG4ugblenHiG3PQcv1adFAWZM
GI-007 | IL03-1 | S-EMEA | Closed | P3 Low DCOS | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | PUSP - "Alarm" The tag of this signal should be changed to be self explanatory. It is supposed to be voltage presence. Both alarms are active if the Voltage Transformer is not energized - Bus without voltage. As a minimum, the "Alarm" should be changed to "Bus voltage absent". Need to clarify the actual function of this button | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621859&prj=609&rqi=onVFOhieQDmM2DM5Tz3Ny8NuPe
GI-003 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Three wires are are not permitted in the same terminal. RON should get in contact with SCH and ARUP to check the two options: - add extra terminals in PUSP control panel (preferred method) - use a 4wire measurement circuit. A ready for verification status from RON should be set once an answer from ARUP is obtained | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621790&prj=609&rqi=sN25GmUf1vB7l2zXbWAtIT91fJ
GI-010 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  | equipment type |  |  |  |  | PUSP - TX Feeder - Local/Remote button not wired into relay, can't be made available in DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621867&prj=609&rqi=HxqTWAAExg8vsPDAXokyzxA7oE
GI-002 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | The wires connecting the Current Transformers from SUDB to PUSP have a cross section of 2.5sqmm and they might be too thin (but as per design IL031-RON-ZZ-ZZ-SH-E-POWR-6103). Schneider to confirm that the used wire on site is the correct one by updating the IL31 - MV Network CT/VT Calculation document (IL031-SCH-ZZ-ZZ-CA-IC-MVSWGR-7009.pdf). At the moment this situation is not covered in the design. Add a calculation chapter for the CT connecting SUDB to PUSP., prove calculation with a 2.5sqmm and the length from SUDB to PUSP is within limits | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621786&prj=609&rqi=cbijLkX9g7gxTCayKKtJ6bLnP3
GT1ELEC-14-002 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ MV | equipment type | PUSP - Primary Utility Supply Panel | PUSP - Primary Utility Supply Panel |  |  | PUSP Power Meter shows a frequency alarm when the line is simply disconnected. Alarm should be filtered if it's out of range during operation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621854&prj=609&rqi=shj1JL8hIKnvSkY5XaVlCY7uuw
GI-011 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | PUSP - Trip Lockout signal is not latched in the relay. DCOS status won't show if a relay tripped the Circuit Breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621870&prj=609&rqi=XZr4RqSceVi8wDHXn29pI6iYeb
GI-009 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | Electrical â€“ MV | equipment | 1PUSP_1 | PUSP - Primary Utility Supply Panel |  |  | PUSP - Feeder - current measurement cables don't have labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621865&prj=609&rqi=YkFzPBUgHfm9Vx07mfWYeeFmNq
YT1MECH-405-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-05-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Design correction needed | Design | Mechanical â€“ Water | equipment | 1TST_1 | CHWBT - Chilled water buffer tank |  |  | It was observed on the buffer tank recharge line that a sudden reduction from DN200 to DN80 may create an excessive increase in velocity and pressure loss. In common site practice, a maximum reduction of two nominal pipe sizes is considered acceptable. For larger reductions, a staged reduction is recommended. Confirmation by the EOR is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620694&prj=609&rqi=T3eHa2hDyMboOt1WxzRoZnljRm
YT1FS-94-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-05-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Fire Suppression | equipment | 1MFD_C_1 | FD - Fire Damper |  |  | Permanent asset label is missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620354&prj=609&rqi=GXVKsHbKT3d6joyHcni0UO1ZIJ
RT1ELEC-332-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-04-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | LD-FO-GEN-B | LEAK - Leak Detection (Fuel) |  |  | Carry out full visual inspection of panel and found that metal gland shall be installed prior to the final connections of the tubes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618376&prj=609&rqi=J1wkLrxrTGkV8FHuvQBHGIn3jt
RT1FS-259-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-04-15 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Fire Suppression | equipment | 1MFD_LB_04.3 | FD - Fire Damper |  |  | The duct connections of the fire dampers do not comply with QA/QC standards and are applicable to all transformer room dampers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618194&prj=609&rqi=4tf2M1XTITQqym6v0Jh7Wju3iv
RT1FS-260-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-04-15 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Component/Equipment Failure | Commissioning | Fire Suppression | equipment | 1MFD_LB_04.4 | FD - Fire Damper |  |  | It has been observed that the fire damper cannot be opened manually. This must be rectified prior to the L2B inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618196&prj=609&rqi=mjV9CDYrn2C1LanBif1BuDTn4j
RT1FS-180-002 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-04-02 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning | Fire Suppression | equipment | 1MFD_R_8 | FD - Fire Damper |  |  | The open/closed position labeling on the fire damper actuator is missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617135&prj=609&rqi=qKVSTW9rrtvtBgxY03Ya6z6x8R
RT1FS-180-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-04-02 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Fire Suppression | equipment | 1MFD_R_8 | FD - Fire Damper |  |  | The damper does not open due to a clash between the duct elbow and the damper blade. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617134&prj=609&rqi=TsDlJuoG07t5RtnPxPjFdlNxOW
RT1FS-257-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-03-31 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Design correction needed | Design | Fire Suppression | equipment | 1MFD_LB_04.1 | FD - Fire Damper |  |  | Inadequate maintenance access in LB-Transformer room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616923&prj=609&rqi=qqejzEqAfYWgq2eCvYcSzkNZiR
RT1FS-255-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-03-31 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Missing Components | Commissioning | Fire Suppression | equipment | 1MFD_LB_02 | FD - Fire Damper |  |  | Missing component. Kit WE has not yet been installed yet. Applicable to all LB fire dampers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616922&prj=609&rqi=XdtOXszvDjXQaR2zOQnGpzrTy7
RT1MECH-385-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-03-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Incomplete Connections | Commissioning | Electrical | equipment | 1HWS_C_5 | HWS - Water Heater |  |  | Equipment should be installed complete with reinforced flexible connections. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615223&prj=609&rqi=0LWPxNVZv98XEOU12PufRudMnb
RT1FS-53-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-02-25 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Fire Suppression | equipment | 1MFD_A_62 | FD - Fire Damper |  |  | Fire damper installed has not been supported in accordance with the approved benchmark details and project requirements. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204131&prj=609&rqi=0dVK6nijuG3HOT1Q5ipBsEOMIU
RT1FS-4-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Fire Suppression | equipment | 1MFD_A_5 | FD - Fire Damper |  |  | This installation of the following MFDs: 1MFD_A_5, 1MFD_A_62, 1MFD_A_75, 1MFD_A_76, 1MFD_A_77, 1MFD_C_30, 1MFD_C_42 and 1MFD_E_02 are not as per the approved BENCHMARK. The installation of these MFDs shall be rectified to proceed for the L2A inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204130&prj=609&rqi=4x6Z7Kcp2cACE5GaXQEajd54X7
RT1FS-81-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-16 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Fire Suppression | equipment | 1MFD_B_27 | FD - Fire Damper |  |  | 1MFD_B_27 is not accessible due to its installation above the busbars (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199264&prj=609&rqi=6e6JOrcQjfkcb02vYuZcQuFihR
YT1FS-119-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-16 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Fire Suppression | equipment | 1MFD_C_28 | FD - Fire Damper |  |  | Earthing cable is connected the MFD support system. However, bonding between the support system and the MFD body is not yet done. GC to complete the installation of the missing bonds. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199270&prj=609&rqi=KSibxyoQpzINZD6UdYMbYBsKou
YT1FS-29-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-06 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Fire Suppression | equipment | 1MFD_A_31 | FD - Fire Damper |  |  | Body bonding is not installed. This case has been identified in many of the MFDs installed. GC to re-inspect all the MFDs and make sure that bonding is installed as project specs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198687&prj=609&rqi=8Us8JOQSENITa0O2NpCoi8Nigc
RT1MECH-121-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-03 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_17 | CRAH - Technical Room CRAHs |  |  | The seismic bracing cables installed on 1CRAH_C_17 at four corners do not conform to any single one of the four installation alternatives provided by the seismic design supplier. Instead, the current installation is a hybrid configuration combining elements from both Alternative 1 and Alternative 2. Vertiv is requested to provide official confirmation on whether this mixed installation is acceptable and approved by the seismic designer. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198209&prj=609&rqi=OjqQ5TzAdfLrUyfSPdAqHCtrD1
RT1MECH-122-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_18 | CRAH - Technical Room CRAHs |  |  | One seismic cable is in direct contact with the C channel support of the cable tray installed above the CRAH unit. The C channel support shall be relocated by the GC team to ensure proper clearance for the seismic cable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198220&prj=609&rqi=dnF2LXyl7yow6Z1K1ufyv1m1HM
RT1MECH-121-002 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-03 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_17 | CRAH - Technical Room CRAHs |  |  | 1CRAH_C_17 has a visible gap between the structural frame and the black protective sheet attached to it. This defect requires correction or replacement by Vertiv. (Please refer to the attached photo for additional clarification.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198212&prj=609&rqi=SvBapylj12FRIbpjzAStXHqAat
RT1MECH-122-002 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_18 | CRAH - Technical Room CRAHs |  |  | One of the bottom covers of the CRAH unit is damaged and must be repaired or replaced by the GC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198222&prj=609&rqi=m5xLMisu1zzkawPtwY7k4FwPTH
RT1ELEC-15-008 | IL03-1 | S-EMEA | Closed | P2 Medium CX | m.yerkoylu@core-group.me | 2026-01-28 04:00:00.000 +0400 | SCH - Schneider Electric |  | Missing Components | Commissioning | Electrical â€“ MV | equipment | 1PUSP_2 | PUSP - Primary Utility Supply Panel |  |  | SF gas level is found low. Close to critical level as per gauge. To be rectified prior to power on. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197726&prj=609&rqi=UUek7KHBeQ5IysTHt20aboRy5v
RT1FS-176-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-01-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning | Fire Suppression | equipment | 1MFD_R_4 | FD - Fire Damper |  |  | The firestop label should be applied to both sides. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197246&prj=609&rqi=Ti2paxmCtb4jYZ4RHGuxQNxPg4
GI-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | m.yerkoylu@core-group.me | 2026-01-12 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning | [6 empty] | Damaged MV Cables (2 nos) observed at PUSP-2. GC to investigate further and propose the way forward. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196679&prj=609&rqi=GaJwn0c0HRzDPzGIzgMfSTGbDS
RT1ELEC-32-004 | IL03-1 | S-EMEA | Closed | P3 Low CX | t.marculet@core-group.me | 2026-01-05 04:00:00.000 +0400 | CMM - Cummins | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1-GEN-A | GEN - Generator (MV) |  |  | General issue for all Gensets - Earthing cables missing from the starpoin connection to the local earth bar. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196317&prj=609&rqi=HZ6aaUs9b5q90R57FwCm96iO6W
RT1ELEC-35-005 | IL03-1 | S-EMEA | Closed | P3 Low CX | t.marculet@core-group.me | 2026-01-05 04:00:00.000 +0400 | CMM - Cummins | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1-GEN-R | GEN - Generator (MV) |  |  | Generator container has a dent by the door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196318&prj=609&rqi=RlVvWQFUCwdSJ82hwbXauOO6KD
YT1MECH-40-002 | IL03-P1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-09-01 04:00:00.000 +0400 | CMM - Cummins | L2B | Installation not correct | Commissioning | Fuel | equipment | Fuel -Oil System-GEN-E | FFIL - Fuel Fill System |  |  | During inspection, it was observed that the tension cable of the fire safety fusible link valve system is in direct physical contact with an adjacent metal support bracket (as highlighted in the attached image). The bracket is obstructing the free movement and direct path of the cable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636415&prj=625&rqi=qepPpdGVVNIjRJwm8nIBco7AvB
YT1MECH-40-001 | IL03-P1 | S-EMEA | Open | P3 Low CX | k.erbay@core-group.me | 2026-09-01 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Design correction needed | Design | Fuel | equipment | Fuel -Oil System-GEN-E | FFIL - Fuel Fill System |  |  | Access to the daily fuel tank is inadequate. The piping/valves structures installed in front of the access area restrict maintenance access and should be reviewed against the clearance requirements specified in the approved drawings. In addition, sufficient access is not available to fully open the louvre doors on the generator enclosure. A permanent access platform shall be provided to ensure safe operation, inspection, and maintenance activities in accordance with HSE requirements and the manufacturer's recommended clearance requirements. Applicable to all GEN Sets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636414&prj=625&rqi=o5YsBOtTtdVNzmjtEuZUwso7SH
GI-001 | IL03-P1 | S-EMEA | Open | P3 Low CX | j.shaw@core-group.me | 2026-08-24 04:00:00.000 +0400 | TRN - Trane |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Cap ends missing from pipework on Chillers. This could lead to accidental drainage of the system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634889&prj=625&rqi=67KSTGLjeVsR0JnWxrpMCrKeoU
RT1MECH-34-001 | IL03-P1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-06-28 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1EF_E_03.2 | EF - Exhaust Fan |  |  | The fan panel door mechanism is damaged and must be repaired. Scratches and paint defects on the panel door shall also be rectified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627220&prj=625&rqi=oeAPtGdtqft2ab71QZukPL54Do
GI-278 | JH02-1/2 | APAC | Open | P2 Medium CX | junkaichan@commtechasia.com | 2026-09-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Doubtful Input power reading on JCI Chiller Control Panel. Observed WCC is reading 40kW input power at 30% motor amp on JCI chiller controller. This value is illogical and different to FWT result of 110kW input power at 31% motor ampere. Action: Please correct the reading on all JCI controller. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638065&prj=632&rqi=xwIZOqyX8636J8qjtl1HHrEMPp
GT1ELEC-177-002 | JH02-1/2 | APAC | Open | P2 Medium CX | charitysamar@commtechasia.com | 2026-09-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | Pending DCOS point-to-graphic verification for Q16. DCOS is unable to monitor Q16 voltage (AB, BC, CA, AN, BN, CN), current (A, B, C, N), power (kW, kVA, kVAR, kWh), and power factor due to a communication/connection issue. Power meter communication interface/components require replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638077&prj=632&rqi=o2JFrpTPeecgBoEe2NbgkKU7J3
YT1MECH-532-001 | JH02-1/2 | APAC | Open | P3 Low CX | KaiJetSim@commtechasia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Fuel | equipment | FPPUMP1 | FPMP - Fuel Pump |  |  | FPPUMP1 No pump labeling and rotation direction on pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637871&prj=632&rqi=t63CFwdQTIEIHti2WxA1YROwwF
YT1MECH-533-001 | JH02-1/2 | APAC | Open | P3 Low CX | KaiJetSim@commtechasia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Fuel | equipment | FPPUMP2 | FPMP - Fuel Pump |  |  | FPPUMP2 No pump labeling and rotation direction on pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637873&prj=632&rqi=dEdKKYSB5ZBMb3Q9KDLkJu8vd1
YT1ELEC-225-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-09-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1RPP_F1R1_2_1 | RPP - Remote Power Panel |  |  | 1RPP_F1R1_2_1 Incoming cable and earth cable not attached with label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637562&prj=632&rqi=CD7JteuE33DvlD5JWMNaA4nhA4
YT1MECH-257-001 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_10 | EF - Exhaust Fan |  |  | 1EF_M1_10 calibration certificate serial number for cable test on Accesstech side is not tally with the one mentioned inside checklist. Please take a necessary action. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637440&prj=632&rqi=CHyst3CrtlaHWQF2LgNsMSEkch
YT1ELEC-116-001 | JH02-1/2 | APAC | Closed | P3 Low CX | charitysamar@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STS_D1R1_2 | STS - Static Transfer Switch |  |  | Remove white paint splashes from the STS panel door and clean the affected surface. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637432&prj=632&rqi=Ue8b6rPqNNl0rVbzUiWOZs2yRS
GT1DCOS-10-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Controls | equipment | 1DCOS_RIO_1 | DCOS - Control Panels |  |  | TT sensor mapping on graphic is wrong. when plug out sensor 1, both sensors 1 and 3 give out alarm. this is identical for other sensor inside the chw loop. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637410&prj=632&rqi=WIfNC3acJZMTpe6idPyMWlySwe
GT1DCOS-10-002 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Controls | equipment | 1DCOS_RIO_1 | DCOS - Control Panels |  |  | DPT mapping for ewall riser 01 and 04 is wrong. onsite the dpt is connected to different riser not as per mapping. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637411&prj=632&rqi=dr3pKKXX8G74tHpXbxMjz9DjGZ
GT1ELEC-104-001 | JH02-1/2 | APAC | Ready for Verification | P2 Medium CX | charitysamar@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STS_E2R1_1 | STS - Static Transfer Switch |  |  | During the STS (Static Transfer Switch) Functional and Burn-in Test, a significant load discrepancy of approximately 60 kW was observed following the transfer from Source S1 (E Block) to the alternate Source S2 (R Block). The observed discrepancy is considered abnormal and requires further investigation. Contractor shall investigate and identify the root cause, verify the accuracy of the load measurement/metering and associated power distribution, and implement the necessary corrective actions to rectify the issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637145&prj=632&rqi=ermHQwCb8oQFQGEyIvCuZ7DRMp
GT1ELEC-127-006 | JH02-1/2 | APAC | Open | P3 Low DCOS | AliHazmeerHamdan@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | UPS_A1 - Line animation still not fully configured correctly. Honeywell to rectify and ensure the animation accurately reflects the actual system status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637142&prj=632&rqi=nF2CO2z5OrDday75jO5YMTqMmP
GT1ELEC-127-005 | JH02-1/2 | APAC | Ready for Verification | P3 Low DCOS | AliHazmeerHamdan@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | UPS_A1- Eaton shall provide the applicable threshold or range values to Honeywell to ensure that the displayed values are correctly configured and identifies any out - of range conditions or abnormal status indications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637140&prj=632&rqi=wjUUTnG6cijb1qArQt6TikbPzm
GT1ELEC-127-004 | JH02-1/2 | APAC | Open | P2 Medium DCOS | AliHazmeerHamdan@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | UPS_A1 - Refer to DCOS graphic, some item / equipment not fully configured or still shows undefined value. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637139&prj=632&rqi=RaZFJYqUCEqnytNL2n25DpcI11
GT1ELEC-5-001 | JH02-1/2 | APAC | Open | P2 Medium CX | charitysamar@commtechasia.com | 2026-09-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_R | RMU - Ring Main Unit |  |  | The RMU ring circuit breaker position is currently not indicated on the DCOS monitoring interface. Honeywell shall configure and integrate the circuit breaker position (Open/Closed) into the DCOS for remote monitoring. (This applies to MV Overview, see attached photo for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637057&prj=632&rqi=fldIzBlOnupQ606oNanIbqefXr
GT1DCOS-3-006 | JH02-1/2 | APAC | Open | P2 Medium DCOS | MuhammadHaziqZakaria@commtechasia.com | 2026-09-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/Equipment Failure | Commissioning | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | DCOS graphic for FCV_03 keep flicking On and Off when the feedback is at 0%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637066&prj=632&rqi=CzMZWBjzLnUo2hXOaRkrktPgUj
GI-268 | JH02-1/2 | APAC | Ready for Verification | P2 Medium CX | junkaichan@commtechasia.com | 2026-09-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_F1 | UPS - Uninterrupted Power Supply |  |  | During Cx3 Testing for UPS F1 for 10. UPS OVERLOAD - (SINGLE) - LB ramped up to 1400kW for 10 mins to trigger Static Bypass transfer (L2 overload alarm), after Static Bypass transfer immediately L3 overload alarm triggered and offloaded the UPS. Action Required: To preform investigation and submit RCA. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636944&prj=632&rqi=JD39i0ZCobtNNWNOpbt9j4v87B
GI-270 | JH02-1/2 | APAC | Open | P3 Low DCOS | junkaichan@commtechasia.com | 2026-09-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_A | MSB - Main Input Switchboard |  |  | Phase-N signal of voltage and current show on graphic as per required in SPL, but designed breaker is TPN. Action required: HW please confirm with EOR to remove these unnecessary items on graphic. and attach final screenshot to proof this is removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636949&prj=632&rqi=SRgNrHvJvc81qr4TkcMmzqVb4j
GT1MECH-165-001 | JH02-1/2 | APAC | Open | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-09-04 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_06 | EF - Exhaust Fan |  |  | During Cx3 Temperature Validation, found the temperature sensor for 1EF_M1_06 show (27.7Â°C) which is a different reading (29.3Â°C) from a calibrated temperature meter. The different is higher than the acceptance tolerance (Â±0.5Â°C). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636801&prj=632&rqi=CdSQ74FBeTBkAewuxOqsrxh6zU
GT1MECH-172-001 | JH02-1/2 | APAC | Open | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-09-04 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_05 | EF - Exhaust Fan |  |  | During Cx3 Temperature Validation, found the temperature sensor for 1EF_M1_05 show (37.1Â°C) which is a different reading (31.3Â°C) from a calibrated temperature meter. The different is higher than the acceptance tolerance (Â±0.5Â°C). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636798&prj=632&rqi=yHRh6LUzQ9KWNtNH6pTqOzaoua
GT1MECH-137-005 | JH02-1/2 | APAC | Open | P2 Medium DCOS | samintarajarujunan@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | Supply Fan Command Mismatch alarm unable to simulate. SE does not have fan feedback data provided to DCOS. This point is DCOS calculated and based on the onsite testing it was found that this point unable to be simulated for testing. Please recheck the logic and get the point tested to close this issue. Applies to all CRAH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636675&prj=632&rqi=LY63D3XdhEBPoL4zC03vYdEMvv
GT1MECH-137-006 | JH02-1/2 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | All CRAH units fire cable yet to be terminated to the units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636677&prj=632&rqi=8uXcWP6himztgOUX4hjjDg4xfz
DCIML2B-1-001 | JH02-1/2 | APAC | Open | P2 Medium DCOS | sganeshmahadik@ap.equinix.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L2B | DCIM Maximo Issue | DCIM | Controls | system | DCIM |  |  |  | Maximo and Location Vectors list is not ready as Cx activities are going on. It's essential to DCOS/DCIM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636679&prj=632&rqi=o2DCMzjbTdLPeVDgtVJL8el0Ob | https://equinix.facilitygrid.co.uk/x/project/632/system/12791
GT1DCOS-3-005 | JH02-1/2 | APAC | Open | P2 Medium CX | imanuddinhamdan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | Line animation and buffer tank mode is wrong when the open the FCV 03, the buffer tank mode is not changing. Line animation also | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636483&prj=632&rqi=3AeO8vqNUhVlT25I1Xht1iDQDV
GT1MECH-137-002 | JH02-1/2 | APAC | Ready for Verification | P2 Medium DCOS | samintarajarujunan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | Valve Mismatch is a DCOS calculated Alarm. 30s delay has been added however during testing it was identified that the mismatch still be triggered on multiple occasion. To recheck the programming on the implementation. Applicable for all CRAH Units | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636388&prj=632&rqi=TxoHsIVhWhVvjbbd8OHIhHdqoC
YT1ELEC-108-001 | JH02-1/2 | APAC | Closed | P3 Low CX | charitysamar@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STS_F2R1_2 | STS - Static Transfer Switch |  |  | Damaged STS ventilation/insect mesh at roof support. CSPM to rectify and reinstate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636393&prj=632&rqi=l1eAtLkHUvrP2ECxahdiQSraGy
GT1MECH-137-001 | JH02-1/2 | APAC | Open | P2 Medium DCOS | samintarajarujunan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | Resilient and Resiliency Vote Calculation to recheck. Once 1 of the Units from the group receive summary alarm, all the units in the group loses its resiliency vote. however, based on the approved calculation, resiliency vote is calculated individually for each unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636386&prj=632&rqi=4WfLFlCUl0zaXhc9YXM22PSaI4
GT1MECH-137-003 | JH02-1/2 | APAC | Open | P2 Medium DCOS | samintarajarujunan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | Num of Units in Group is still computed based on the configuration point. This means the number is based on how many units has been configured in a group rather than a live value. During testing one of the grouping cables has been removed to observe the change in number units in group. However, found that it does not reduce. The only way to reduce the number of units in group is to configure a different value from the CRAH HMI. Applies to all CRAH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636389&prj=632&rqi=s3smF6FMTuypteWPEgOmB30m1I
GT1MECH-137-004 | JH02-1/2 | APAC | Open | P3 Low DCOS | samintarajarujunan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | The Command screen has 2 submit buttons. Apply to All CRAH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636392&prj=632&rqi=SVCbXwwPfgkYdORKBKjiQG860q
GI-266 | JH02-1/2 | APAC | Ready for Verification | P2 Medium CX | junkaichan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS | Electrical â€“ LV | equipment | 1STS_A1R1_1 | STS - Static Transfer Switch |  |  | There is a list of boolean points informed by CSPM cannot be tested at P2G due to Socomec controller do not have simulation function. Please confirm with manufacturer with official letter confirmation on which point unable to be simulated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636427&prj=632&rqi=4wwwB7YE8Gh5kTCVc63R77lKKu
GT1DCOS-3-003 | JH02-1/2 | APAC | Closed | P2 Medium DCOS | junkaichan@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | CPR1 - AO - CT VFD speed command not working - DCOS can't send out command signal to VFD to control pump speed (P2-HW) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636224&prj=632&rqi=22caYjk389eSqClTdKMY2iwDKr
GT1DCOS-3-001 | JH02-1/2 | APAC | Open | P2 Medium DCOS | junkaichan@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | CPR1 - DO - CT1 and CT2 share same start/stop command from DCOS graphic - whichever faceplate of CT1/CT2 give command start/stop, both CT1 and CT2 will run/stop together - confirm with HW EOR if this is intended design (P2-HW) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636218&prj=632&rqi=QTJuZej78VP1Wp1GiqgsQdPV8l
GI-265 | JH02-1/2 | APAC | Closed | P2 Medium DCOS | junkaichan@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS | Electrical â€“ LV | equipment | 1MSB_A | MSB - Main Input Switchboard |  |  | MSB_A DCOS PQM unable to communicate during official P2G witness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636171&prj=632&rqi=C9TzV87eVoMZC3QfuXRvsxIKw6
GT1DCOS-3-002 | JH02-1/2 | APAC | Open | P2 Medium DCOS | junkaichan@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | CPR1- AI - FT-01 on site not performed flowrate verification and P2G - no flowmeter ready by HW. (P2-HW) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636223&prj=632&rqi=BFxDUfB7U2oZf05jRtaB1vg1iT
GT1DCOS-3-004 | JH02-1/2 | APAC | Open | P3 Low CX | junkaichan@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | CPR1 - All Belimo valves in chiller plant no proper tagging, and some with wrong tagging. ACT to rectify based on approved schematic. (P3-ACT) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636225&prj=632&rqi=O3fcoxIpm872cWcbZwa0uAqmgy
GT1ELEC-95-001 | JH02-1/2 | APAC | Open | P2 Medium CX | charitysamar@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STS_A1R1_2 | STS - Static Transfer Switch |  |  | During the STS Point-to-Graphic Test/Functional Test, no DCOS line animation (energized/white indication) was observed on the STS Source 2 Bypass path while the system was in S2 Bypass Mode and STS Q42 breaker was in the Open position. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636216&prj=632&rqi=v0tnswQfipVlHkoTtjjA7IqJPO
GT1ELEC-215-001 | JH02-1/2 | APAC | Closed | P1 High CX | charitysamar@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LBSB_1 | LBSB - Loadbank Switchboard |  |  | Water ingress into the Load Bank Switchboard occurred due to incomplete cable installation associated with the Mobile Generator. Contractor shall provide an Incident Report identifying the root cause, extent of water ingress, and corrective actions taken. Contractor shall also assess and confirm which electrical tests are required to be repeated prior to re-energization of the switchboard and resumption of load bank testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635215&prj=632&rqi=Vgh1yl2KAKv7CyETRQJVY2ltV0
YT1MECH-308-001 | JH02-1/2 | APAC | Open | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_5 | FPMP - Fuel Pump |  |  | The cable from 1FP_M1_5 to Overflow Pump connected to the single phase circuit has been installed 3 phase color identification (RYB). the cable color arrangement does not comply with the required single phase identification, which should be Red (L), Black (N), and Green (PE) . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635231&prj=632&rqi=xAXtU3nugRFe2jpSDGl1l43zFU
GT1ELEC-128-001 | JH02-1/2 | APAC | Ready for Verification | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-08-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UPS_A2 | UPS - Uninterrupted Power Supply |  |  | During the load slowly increase until 100% (1200kVA) for UPS_A2, the UPS generated phase C Overload alarm at HMI. The overload event was triggered phase C (Blue Phase) only, while the overall UPS load remained below the configured overload threshold. the configured overload setpoint is 106%, however, the Phase C Overload alarm was triggered when measured load was still below 106% setpoint, this event occurs shows the phase is unbalanced. In addition, the DCOS did not receive or display any overload of phase unbalanced alarm from UPS_A2 when the alarm was active on the UPS HMI. The DCOS alarm indication is critical for operational operation. Any abnormal or protection event detected by the UPS should be correctly transmitted and displayed on the DCOS to alert the Operations team. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634558&prj=632&rqi=6Cy0kxHjHDCtHTXWPCtki32a8H
YT1MECH-216-001 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_D_1 | EF - Exhaust Fan |  |  | Found the tagging for DCOS cable is not tally between its own pair and the cable name inside checklist. Please do the necessary rectification to close the issue. Please check on all EF before close issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634571&prj=632&rqi=JKnF3t3924gq6Y1Mg9b49QT4kB
GI-263 | JH02-1/2 | APAC | Ready for Verification | P2 Medium DCOS | AliHazmeerHamdan@commtechasia.com | 2026-08-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | The trend logging for the electrical system, particularly for the UPS systems, has not been fully configured in DCOS. The trend logs for the UPS and overall electrical system parameters are still incomplete. This limitation prevents DCOS from properly recording and trending the electrical parameters during the UPS Burn In Test. Honeywell required to complete configured and setup the trend logs for all UPS system and the overall system in DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634559&prj=632&rqi=Y0crI73ZXN6u4gx0MMIZbAoSpx
GT1ELEC-135-004 | JH02-1/2 | APAC | Open | P2 Medium DCOS | AliHazmeerHamdan@commtechasia.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_E2 | UPS - Uninterrupted Power Supply |  |  | During UPS_E2 Burn in Static Bypass, DCOS graphic just remain at Double Conversion (online mode). The graphic does not reflect with UPS status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634164&prj=632&rqi=ODey8UYLpYF2IxDO4v00gDqjal
GT1MECH-194-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-08-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M2_1 | EF - Exhaust Fan |  |  | When fire alarm is triggered at the M2_1 , M1_1 also triggered the fire alarm. Same goes to the refrigerant leak simulation same fan triggered as well. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634021&prj=632&rqi=ZOx9lZhgBlYUEbzc6auUMc0ML2
GT1MECH-193-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-08-18 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M2_2 | EF - Exhaust Fan |  |  | Fan running time and time taken to trigger is not tally for all the fans. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634045&prj=632&rqi=lpXeKzJ6nYWskiLCnzoZqISTfI
GT1ELEC-135-003 | JH02-1/2 | APAC | Ready for Verification | P3 Low DCOS | AliHazmeerHamdan@commtechasia.com | 2026-08-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_E2 | UPS - Uninterrupted Power Supply |  |  | The breaker status Q01, Q08 and MSB_E_PQM displayed on the DCOS is incorrect. The status indication needs to be checked and rectified before proceeding with the Gen Source transfer testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634115&prj=632&rqi=2czSC7zQHmwlwaZXkrr2cG63MV
GT1ELEC-133-001 | JH02-1/2 | APAC | Open | P2 Medium DCOS | AliHazmeerHamdan@commtechasia.com | 2026-08-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_M1 | UPS - Uninterrupted Power Supply |  |  | The DCOS is displaying an incorrect value for Gen_M1, and the breaker status is also not being reflected correctly in DCOS. Please verify all the points at MSB Graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633914&prj=632&rqi=Cfxw1NnitXtCeXzrlfXnXfwOXn
YT1MECH-237-003 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_03 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the cable tagging for DCOS is not tally as per checklist. Please refer photo attached for the discrepancy. Understand the one from checklist is the correct one. If so, please change accordingly. Please do check for other cable as well. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633871&prj=632&rqi=kuVpvvyXsYRAa7NTLoGkcwkqVG
YT1MECH-237-002 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_03 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found there is missing terminal block inside panel for 24 VDC and possible missing cable termination since SLD and GA drawing mention for 24 VDC. Please clarify the issue and close the issue immediately. ISSUE APPLIED TO ALL EF | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633869&prj=632&rqi=gQwPkoY7WSyMe7trDqgP0Lg8dR
YT1MECH-229-002 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_R_1 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found there is missing terminal block inside panel for 24 VDC and possible missing cable termination since SLD and GA drawing mention for 24 VDC. Please clarify the issue and close the issue immediately. ISSUE APPLIED TO ALL EF | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633868&prj=632&rqi=APUeB3lvWpjP4vSeTnYXSMeJ8k
GT1ELEC-132-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-08-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_R12 | UPS - Uninterrupted Power Supply |  |  | The line animation on the DCOS graphic is not fully aligned with the actual system status. Please verify and rectify the animation accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633760&prj=632&rqi=Af9KoJaphzP60pO4Ziwn2x9NCG
GT1ELEC-132-002 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-08-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_R12 | UPS - Uninterrupted Power Supply |  |  | The reading shows at MSB_R_Q_04 for KW and PF are still incorrect. The Value required tally with DPM MSB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633761&prj=632&rqi=5X9MWEMlmGcwvuAfAWlkhYrdE4
GI-261 | JH02-1/2 | APAC | Ready for Verification | P1 High DCOS | AliHazmeerHamdan@commtechasia.com | 2026-08-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS | [6 empty] | Issue: DCOS/CPOS graphics development, deployment, and validation are significantly behind schedule. SFAT-validated graphics and database evidence are no longer valid, requiring substantial rework. Multiple graphics remain incomplete or contain errors, trending configuration is not fully implemented, equipment integration and handshaking activities are outstanding, and no consolidated tracker exists to monitor completed versus pending works. These deficiencies are preventing chiller plant testing, sensor validation, TAB verification, burn-in testing, and other commissioning activities from progressing as planned, creating a significant risk to the project RFS milestone. Honeywell is required to provide a comprehensive recovery plan, resource allocation strategy, outstanding works register, and milestone-based schedule recovery actions. Impact: Delay to Cx activities, inability to complete planned testing, risk of repeated testing effort, and potential RFS schedule slippage. Required Action: Honeywell to submit RCA and execute a detailed recovery plan with clear ownership, resource augmentation, daily progress tracking, and prioritized completion of critical DCOS/CPOS graphics and integration activities. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633763&prj=632&rqi=rGnyFqKdKb50RDG8Z4Vbpdm5l4
YT1ELEC-607-001 | JH02-1/2 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_D_1_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q04 to "SPARE". Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633188&prj=632&rqi=HpD0BWBom9Umw64X9nVswb290D
YT1ELEC-152-001 | JH02-1/2 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_C_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q09, Q10, Q11 and Q12 to "SPARE". Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633192&prj=632&rqi=fqoqobE2v9vdBs2W5Mqq8AQm5w
YT1ELEC-608-001 | JH02-1/2 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_F_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q02 and Q03 from "SPARE" and Q11 from "SPACE". Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633194&prj=632&rqi=Vj2PxJhnddr6yNRcSlj6y6ntlw
YT1ELEC-607-002 | JH02-1/2 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_D_1_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q04 to "SPARE". Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633189&prj=632&rqi=1ADsJ7CAYhyRhAz71t1jIQFtbj
YT1ELEC-606-001 | JH02-1/2 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_C_1_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q04 to "SPARE". Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633191&prj=632&rqi=s4cdDj2sPzBFsJmJxBppTNbWt6
YT1ELEC-389-001 | JH02-1/2 | APAC | Closed | P3 Low CX | charitysamar@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_C_06 | LVSB - Low Voltage Switchboard |  | i-Box | Update the as-built drawing to incorporate the changes and place the approved revised drawing in the designated document pocket of the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632994&prj=632&rqi=HMWaLeVFL9BdrOGoMNYBRiBAO5
YT1ELEC-367-001 | JH02-1/2 | APAC | Closed | P3 Low CX | charitysamar@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1_27 | LVSB - Low Voltage Switchboard |  | i-Box | Update the as-built drawing to incorporate the changes and place the approved revised drawing in the designated document pocket of the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632989&prj=632&rqi=0p0kCVhJe56EVbzy6cQjLiyMCt
GT1ELEC-177-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | MSB_R. During simulate utilities failure (Open Breaker). The Gen_R breaker at MSB not automatic close and the genset not kick in to start. The UPS_R1 in discharge Mode (Battery Discharge). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632831&prj=632&rqi=F0ZbcgcGjbI09CKpF8fT2d3XRZ
GI-259 | JH02-1/2 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-08-07 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_D | MSB - Main Input Switchboard |  |  | HMI panel already install by GC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632701&prj=632&rqi=f8I0jjGKsg0EWJKrZ1UCiBMcXt
GI-260 | JH02-1/2 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-08-07 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_F | MSB - Main Input Switchboard |  |  | HMI panel already install by GC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632704&prj=632&rqi=7pwfFMSZMOFdyyRN9dBF4OIeqL
GI-258 | JH02-1/2 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-08-07 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | HMI panel aready install by GC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632696&prj=632&rqi=kCag0BLnxJHOvFasXjNDy6op9h
GT1ELEC-135-002 | JH02-1/2 | APAC | Open | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_E2 | UPS - Uninterrupted Power Supply |  |  | During the Burn In test UPS_E2 (Double Conversion), UPM 2 and UPM 3 experienced an overtemperature trip due to the elevated supply air temperature from CRAH system. The high CRAH supply air temperature resulted in an increase in the ambient temperature around the UPS, causing the UPM operating temperature to exceed the allowable limit. Please verify and confirm the condition of UPM 2 and UPM 3 following the overtemperature trip event. Kindly check whether the event has caused any abnormality, derating or impact the UPM efficiency and output capacity. I believe this UPM can operate 0â€“40-degree Celsius without derating based on technical specifications. it would be appreciated if Eaton could provide the UPM temperature history or trend prior to the overtemperature trip, including the final temperature recorded before the trip. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632709&prj=632&rqi=uowHD7TCeFHOoRRqNsbwcV8Pt1
GI-257 | JH02-1/2 | APAC | Closed | P2 Medium CX | junkaichan@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_R11 | UPS - Uninterrupted Power Supply |  |  | - load up UPS to 35%~420kw - â engineer check for meter verification between PQA and UPs HMI - â found imbalance current at UPS HMI (output meter -blue phase) while PQA showing healthy reading Please submit RCA report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632500&prj=632&rqi=qSWauuiJMstU7u8LYbt3ICulDv
GT1ELEC-135-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-08-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_E2 | UPS - Uninterrupted Power Supply |  |  | The UPS_E2 HMI current indication is abnormal. The blue phase current reading is significantly lower than the red & yellow phase. R = 175A, Y=172A and Blue=86A. Please verify the current measurement and CT wiring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632265&prj=632&rqi=kHkyH0LNdLVnDmhAZVllVDOqvM
YT1MECH-199-001 | JH02-1/2 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-08-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | To complete installation of field sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632070&prj=632&rqi=RhCTTMI5bfg8LLU15fnrBzpXgn
GT1ELEC-180-001 | JH02-1/2 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-08-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_M2 | MSB - Main Input Switchboard |  |  | Test 27- Flex initiated transfer to Fixed Generator (Closed Transition). The Generator started and the utilities breaker were in closed position. However, the system did not receive the Sync Ready status signal. As a result, the synchronization sequence could not proceed, and the transfer to the Generator source was inhibited. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632082&prj=632&rqi=wM0WU4Y5Wa13YQdgWlTb9H6VHQ
YT1MECH-227-002 | JH02-1/2 | APAC | Closed | P2 Medium CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_06 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the end of fire cable is left hanging from the junction box. Please complete the fire cable installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631963&prj=632&rqi=MYvwhPiWDjalh5NzpHLe8jyH1P
YT1MECH-227-003 | JH02-1/2 | APAC | Open | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-02 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_06 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the TS glass cover is broken. Please rectify to close the issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631964&prj=632&rqi=NrNm1PvmIQiXmReuKInlE9RXmf
YT1MECH-227-001 | JH02-1/2 | APAC | Open | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_06 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the cable for DCOS is missing however the DCOS is mentioned inside the SLD. PIC claims the drawing is wrong. Please attached any relevance document to show proof DCOS cable is not to be terminated on this panel. Please amend the drawing if necessary. APPLIED TO ALL EF | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631962&prj=632&rqi=KSuAAQGnww0Jx6aM4AynGwDN1C
YT1MECH-260-001 | JH02-1/2 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1TEF_M1_1 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, noticed fire cable is missing from the drawing attached inside the pocket drawing. Please discuss with relevance party to clarify the fire cable termination. Issue for panel LCP_1TEF_M1_1&2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631716&prj=632&rqi=fyhLMeIVv4rfjxSn1WLgZqQ2IM
YT1MECH-237-001 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_03 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the breaker size is larger than SLD and GA Drawing. On site breaker install 20A while in all drawing mention breaker size is 10A. Please verify and amend as necessary. APPLIED TO ALL EF | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631357&prj=632&rqi=QIS53oImMjOSIDkCNvLoqYA6G3
YT1MECH-236-001 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-30 04:00:00.000 +0400 |  | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_A_1 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the breaker size is larger than SLD and GA Drawing. On site breaker install 20A while in all drawing mention breaker size is 10A. Please verify and amend as necessary. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631349&prj=632&rqi=WbfLs7eqtWYIl0Usu4jD75I5Aw
YT1MECH-230-001 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_B_1 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the breaker size is larger than SLD and GA Drawing. On site breaker install 20A while in all drawing mention breaker size is 10A. Please verify and amend as necessary. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631359&prj=632&rqi=t2Lr3e3MkTbKYaNTOoDtkIC5tl
YT1MECH-229-001 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_R_1 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the breaker size is larger than SLD and GA Drawing. On site breaker install 20A while in all drawing mention breaker size is 10A. Please verify and amend as necessary. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631361&prj=632&rqi=7EvLfm6gkXoCQOvYHj7JiC0m8N
YT1MECH-223-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | junkaichan@commtechasia.com | 2026-07-29 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_E_1 | EF - Exhaust Fan |  |  | Signal cable from fan control to LiB Block E (E_ 1-7) and (E2_1-7) is not installed, tested thus termination at LiB is incomplete. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631123&prj=632&rqi=8aTZIywcKry1rMN8sVeHI1NPJN
YT1MECH-183-001 | JH02-1/2 | APAC | Open | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_1 | CRAH - Computer room air handler |  |  | Pressure Testing and flushing documents are approved on Project Portal and attached to the correct section of Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630833&prj=632&rqi=HHhr0ddZC2M4fwSJoO28iVs1MK
YT1MECH-177-001 | JH02-1/2 | APAC | Open | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_E_1 | CRAH - Computer room air handler |  |  | Pressure Testing and flushing documents are approved on Project Portal and attached to the correct section of Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630831&prj=632&rqi=hjf8dCsYbGm2nsvudGvsgtOeqk
YT1ELEC-154-001 | JH02-1/2 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_F_1_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q04 from "SPARE" to the correct load. Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630655&prj=632&rqi=wQKbKh1eOcJn0opg506YHtjOUA
YT1ELEC-107-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | charitysamar@commtechasia.com | 2026-07-23 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STS_F2R1_1 | STS - Static Transfer Switch |  |  | The tagging at the busduct connection point to the STS does not correspond to the tagging on the busduct body. If the discrepancy is limited to the busduct body tagging, a continuity test should be conducted to verify the connection, and the tagging shall be corrected afterward. However, if the discrepancy is at the connection point, the busduct will need to be modified to ensure the correct connection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630513&prj=632&rqi=JEKzmS1cJXoLP95333htL5oCjM
YT1ELEC-370-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1R_38 | LVSB - Low Voltage Switchboard |  | i-Box | 1LVDB_M1R_38 RCCB for each phase, to be swapped out for 2 pole MCB as confirmed by NV5 to avoid nuisance tripping. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630218&prj=632&rqi=geVqjP1W3uNgRyr20swb73pVki
YT1ELEC-106-001 | JH02-1/2 | APAC | Closed | P3 Low CX | iau@cspm.com.my | 2026-07-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STS_E2R1_2 | STS - Static Transfer Switch |  |  | White Glove Report is approved on Project Portal and appended to the document section of this checklist | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629708&prj=632&rqi=pyYxHRP5HmlXXakPO5a22dUbpI
YT1ELEC-103-001 | JH02-1/2 | APAC | Closed | P3 Low CX | iau@cspm.com.my | 2026-07-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STS_E1R1_1 | STS - Static Transfer Switch |  |  | White Glove Report is approved on Project Portal and appended to the document section of this checklist | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629712&prj=632&rqi=1suXssAoCSiby4FfxMOA4f91mR
GT1ELEC-129-001 | JH02-1/2 | APAC | Open | P2 Medium CX | charitysamar@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_B1 | UPS - Uninterrupted Power Supply |  |  | UPS DCOS SPL not in Honeywell Points List during Cx3 Testing: -DC Ground Fault -DC Over Voltage Shutdown -Input Current Unbalance -Maintenance Bypass Breaker Closed -Maintenance Bypass Breaker Open -Output Breaker Closed -Output Breaker Open -Over Temperature Shutdown -Overload Shutdown -Resiliency Vote -Resilient -Static Switch Disable -Synch Enable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629341&prj=632&rqi=cTHnlyyPAGZYCyMtGTTjnJlcE6
YT1ELEC-365-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | charitysamar@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1_25 | LVSB - Low Voltage Switchboard |  | i-Box | Please attach/provide the calibration certificates for the exact test instrument used. The Cable Insulation Resistance Test conducted on the cables on July 13, 2026, was performed using a Kyoritsu test instrument with Serial Number E8528764. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628833&prj=632&rqi=mHd17ZRkVIPZIoH443lDa3q0v5
YT1ELEC-364-001 | JH02-1/2 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1_24 | LVSB - Low Voltage Switchboard |  | i-Box | During YT inspection, found 1 of the timers that located beside the contactor inside panel is not turn on. All the timers T2 and T3 is turn on while T1 beside the contactor C1 is turn off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628640&prj=632&rqi=O7N9edp4YUh1XmBPEoonIHxaFY
RT1MECH-625-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAK_C_1 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628687&prj=632&rqi=ipt7GIgQsOUODg3Ib8jxY7Rfn6
RT1MECH-277-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_07 | EF - Exhaust Fan |  |  | Permanent equipment labels affixed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628634&prj=632&rqi=oXgEKlqb7RmZtmgfm326cqGzZy
YT1ELEC-555-001 | JH02-1/2 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1ATSM_M1R_27 | ATS - Automatic Transfer Switch |  |  | During YT inspection, noticed the quantity for fuse inside the panel is not the same as in the drawing. Total quantity for fuse inside drawing is 9 nos while the total quantity inside the panel is 10 nos. Please confirm the nos of fuse and do some amendment if necessary. This issue is applied to all unit 1ATSM panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628642&prj=632&rqi=qvhuUjRN7f5sZIMU4whBWuGosl
YT1ELEC-603-002 | JH02-1/2 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_28 | LVSB - Low Voltage Switchboard |  | i-Box | During YT inspection with GC and vendor, found the termination for contact is not as per drawing. Drawing show termination from only 2 MCB (Y3 & Y4) while on site termination is connecting from 3 outgoing MCB to contactor C2 (1L2-21, 1L2-22, 1L2-23). Please advise. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628641&prj=632&rqi=jsKEGVfvqqzMnK7HvombR4VVwk
GT1ELEC-178-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_M1 | MSB - Main Input Switchboard |  |  | During the UPS_M1 Failure Mode Test Under Utilities Supply (Failure of UPS Batteries for 5min). The LiBattery breaker was switched OFF. Initially, the UPS transferred to Static Bypass mode. After the LiBattery breaker was isolated, the UPS transferred to Double Conversion mode. During testing 50% load. Approximately 1-2 mins later, the following breakers tripped due to Ground Fault Protection: 1) Incoming from Tx (Q_01) : Tripping A (1200A) : time (0.00sec) 2) Incoming for UPS_M1 (Q_10) : Tripping A (600A) : time (0.00sec) Additionally, the time and date settings in the micrologic protection units were not configured correctly, preventing accurate identification of the trip sequence and confirmation of which breaker operated first. The vendor shall carry out the detailed troubleshooting to the determine the cause of the Ground Fault Trips. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628638&prj=632&rqi=A07ObYFyduhZPToIQxBgVsbPDQ
YT1ELEC-603-001 | JH02-1/2 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_28 | LVSB - Low Voltage Switchboard |  | i-Box | During YT inspection with GC and vendor, found the termination for contact is not as per drawing. Drawing show termination from only 2 MCB (R3 & R4) while on site termination is connecting from 3 outgoing MCB to contactor C1 (1L1-21, 1L1-22, 1L1-23. Please advise. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628637&prj=632&rqi=INs5CU6guuz9J6Jcw1PdLs8uf1
RT1MECH-619-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_D_1 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628503&prj=632&rqi=VRmzEYRjGi8bdcWWUmb0v0RYF0
RT1MECH-614-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_B_4 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628494&prj=632&rqi=99m56M2sLxDK3zGVzvHL2imCGk
RT1MECH-622-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_D_2 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628504&prj=632&rqi=pMOC3IMznLaneAqNUSUugUSfNl
RT1MECH-624-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_M1_1 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628507&prj=632&rqi=jb417XMPC5I6jbz8NTTlr8pIrU
RT1MECH-621-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_D_3 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628509&prj=632&rqi=2RF03KM1NcExRjjpv21QqEIcfD
YT1ELEC-5-002 | JH02-1/2 | APAC | Closed | P3 Low CX | charitysamar@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_E | RMU - Ring Main Unit |  |  | The shielding cable has been cut and rejoined using a bolted connection (bolts and nuts). Confirmation from ABB is required to verify whether this repair method is acceptable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628515&prj=632&rqi=V9Relk3RkJ4VE6LNCn4DrR0Euq
RT1MECH-611-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_B_3 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628493&prj=632&rqi=9OZW7n6ne7baTD29sNT4Wutcji
RT1MECH-615-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_C_1 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628495&prj=632&rqi=jWSmWbAC4Q125jJHGUZPTHAKVa
RT1MECH-607-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_A_4A | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628467&prj=632&rqi=z0sFgruvNQjS2MzLwwZNtIR6Bf
RT1MECH-608-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_A_3 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628470&prj=632&rqi=IBUNdOVWV6wX3jr24xiNjpVJ6O
RT1MECH-620-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_D_4A | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628506&prj=632&rqi=T3nzcERq9EMvU4xojYrn0ESMGG
RT1MECH-616-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_C_4 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628502&prj=632&rqi=9WOHkAHVBZsDVWKR9sq8tQjelo
RT1MECH-623-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_D_4 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628505&prj=632&rqi=o0kVU6kJm1npPh25ku3YQALRy0
RT1MECH-613-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_B_2 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628492&prj=632&rqi=mwFvID01zgcvumt9LdCNydF7rj
RT1MECH-610-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_B_1 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628266&prj=632&rqi=0opuIP5Ver6boPD9LJXanJ41rN
RT1MECH-605-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_A_2A | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628269&prj=632&rqi=Xt5LjNZf3eExySEN6Dz3G4xMoY
RT1MECH-612-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_B_1A | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628267&prj=632&rqi=iAvlZRW8qtnGvwsjGQ6uPNEUjT
YT1ELEC-130-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_B1 | UPS - Uninterrupted Power Supply |  |  | GC need provide Photo Evidence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628112&prj=632&rqi=iS5P63mbU4JoUGISTivaV10bgi
YT1MECH-306-003 | JH02-1/2 | APAC | Closed | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | The wall penetration is still not fire sealed. This outstanding work is preventing us from issuing yellow tag for PUMP ROOM 1 & PUMP ROOM 2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628166&prj=632&rqi=rnvh95QmL88yFg6Q1okk0CX6Jl
YT1MECH-306-004 | JH02-1/2 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | The earth chamber still not tested yet & kindly place the labelling or tagging at Earth Chamber follow the Earthing Main Schematic labelling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628167&prj=632&rqi=2mGTrkg0mF7Q9VbslCv7FIcZ0n
YT1DCOS-10-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Controls | equipment | 1DCOS_RIO_1 | DCOS - Control Panels |  |  | Wrong tagging for power supply. Supposed to be B1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628263&prj=632&rqi=6LfqphLgLoa4YVLY3Ikv04WICp
YT1MECH-307-004 | JH02-1/2 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_2 | FPMP - Fuel Pump |  |  | All permanent earthing not complete installed & labelling in PUMP ROOM 1 & PUMP ROOM 2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627957&prj=632&rqi=TaMF6OfVNXk5KtwnRvaEUpBFam
YT1DCOS-12-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Controls | equipment | 1DCOS_RIO_3 | DCOS - Control Panels |  |  | Wrong power source tagging. supposed me 38-B6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628264&prj=632&rqi=xcTRKXrTd9sdZtNtrW147DLgOl
GT1ELEC-127-001 | JH02-1/2 | APAC | Closed | P3 Low DCOS | ahmadfuad@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | Battery time remaining status on DCOS to recheck formula as it does not indicate correct time as per UPS HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627490&prj=632&rqi=8CGt2dQDWFrmX5kqTsNLELek6c
GT1ELEC-127-002 | JH02-1/2 | APAC | Open | P3 Low CX | ahmadfuad@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | UPS is showing kWh/day status on HMI, however DCOS is using kWh as per approved SICD. Eaton to verify if the correct HMI status with per day status should be there or to be revise to kWh | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627491&prj=632&rqi=iwGR2WJZODsqAwad1sqN8ZzAvU
GT1ELEC-127-003 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | UPS has been verified with latest new firmware version CSB : 5.12.342. Eaton to ensure the latest version update is incorporated in new setting revision and submit to design consultant for approval. Please attached new approved setting document for record purpose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627493&prj=632&rqi=LMHAjoikpuix7KESTUJb02dg51
YT1ELEC-7-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_A | RMU - Ring Main Unit |  |  | During preparation of UPS_A1 load, test it was observed that RMU_A1 trip due to earth fault trip to Q_03 outgoing breaker to MLTX_A1. Further investigation, it was found cable shield for the 3C phase cables were found to be outside of ZCT. RYB to seek clarification via email from ABB. As for the solution to bring the cable shield inside the ZCT is acceptable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627190&prj=632&rqi=WJSdHcYr7U3fp3QDsQ32kKfJ72
GI-253 | JH02-1/2 | APAC | Closed | P3 Low CX | junkaichan@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | CRAY Isolator installed right below water flexible hose connection - risk of damage/safety during maintenance/accidental water leakage. Suggest checking with design team if the isolator design is acceptable or any modification required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626444&prj=632&rqi=d3elyzVvznTeBTxrSKuqTpFjbQ
YT1MECH-209-001 | JH02-1/2 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_M2_1 | CRAH - Computer room air handler |  |  | Confirm that Chilled Water has been pre-commissioned, flushed and treated to approved Method Statement and witnessed by GC/CxA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626304&prj=632&rqi=hSSaRQUaCV9SdegY65swOdXhv4
YT1MECH-209-002 | JH02-1/2 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_M2_1 | CRAH - Computer room air handler |  |  | Pressure Testing and flushing documents are approved on Project Portal and attached to the correct section of Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626305&prj=632&rqi=bOvu9AFqdcTfXD5FzQpKrhpKZv
YT1MECH-210-002 | JH02-1/2 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_M2_2 | CRAH - Computer room air handler |  |  | Pressure Testing and flushing documents are approved on Project Portal and attached to the correct section of Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626307&prj=632&rqi=URUu3xvHqeYFBYff65ccYlp6Az
YT1MECH-210-001 | JH02-1/2 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_M2_2 | CRAH - Computer room air handler |  |  | Confirm that Chilled Water has been pre-commissioned, flushed and treated to approved Method Statement and witnessed by GC/CxA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626306&prj=632&rqi=HHbQkz952LQfYPXuXeHUIbeF1N
RT1ELEC-245-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_C_1 (L1 near DG) | LEAK - Leak Detection |  |  | The panel no permanent tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626285&prj=632&rqi=UkbEgLSsgu7mV5rHTrk9RZR2Ql
RT1ELEC-240-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_M1_2 | LEAK - Leak Detection |  |  | The panel no permanent tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626280&prj=632&rqi=GYfnjSUjgzWsoAG1ZIMBljsuj6
RT1ELEC-248-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_B_2 | LEAK - Leak Detection |  |  | The panel no permanent tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626290&prj=632&rqi=HAglCo97Ue897WyL9ta6ylT7yL
RT1ELEC-244-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_D_2 | LEAK - Leak Detection |  |  | the panel no permanent tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626284&prj=632&rqi=PVfGGAs5aO23ZqcIGk7RvSmehh
RT1ELEC-239-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_M1_1 | LEAK - Leak Detection |  |  | The permanent labelling not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626278&prj=632&rqi=3KLVFQzJHN7bTmO4r8yW9MovZi
RT1ELEC-246-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_D_1 | LEAK - Leak Detection |  |  | The panel no permanent tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626286&prj=632&rqi=HKikyi6hSG16a6YyCZHP7JWRoq
RT1ELEC-242-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_M1_4 | LEAK - Leak Detection |  |  | The panel no permanent tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626282&prj=632&rqi=5bh97hb5Yn7TjwrsR5jz8Yq47i
RT1ELEC-246-002 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_D_1 | LEAK - Leak Detection |  |  | The panel alignment requires adjustment as it is slightly slanted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626288&prj=632&rqi=qKqoNDSTfOT3jijTS3iMZm21Lz
RT1ELEC-247-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_A_2 | LEAK - Leak Detection |  |  | The panel no permanent tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626289&prj=632&rqi=EksYnjHtjVz49mQR6FHnC7IB70
RT1ELEC-241-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_M1_3 | LEAK - Leak Detection |  |  | The panel no permanent tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626281&prj=632&rqi=NdxVSuIkh2tgYD3IV7UaXum5y3
RT1ELEC-243-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_C_2 | LEAK - Leak Detection |  |  | The panel no permanent tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626283&prj=632&rqi=aR8UwS6Ih9SEW4ZX59VaiEo99x
GI-249 | JH02-1/2 | APAC | Open | P1 High CX | pauljohnson@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_M2 | RMU - Ring Main Unit |  |  | 1BTU_M2 side of the unit is damaged and the door now not aligned to close. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625740&prj=632&rqi=TJkJqvdAiMSS3FA7PtVNaihGZ7
GI-250 | JH02-1/2 | APAC | Open | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M1R_03 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_M1R_03 bottom cover of the busbar section dented. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625741&prj=632&rqi=sBN5Yg3wX1IXnMa0U8KIKQX7W0
GI-247 | JH02-1/2 | APAC | Open | P3 Low CX | junkaichan@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1MWP_M1_1 | DOMW - Domestic Water Set |  |  | Pressure switch control cable no label. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625588&prj=632&rqi=9esBlhFDhqiKVrj1LwcuBNPN0U
GI-248 | JH02-1/2 | APAC | Open | P3 Low CX | junkaichan@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1MWP_M1_1 | DOMW - Domestic Water Set |  |  | coiled up cable in MCC cabinet not terminated - to be clarified the purpose. if unused to be wrapped up the exposed termination. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625589&prj=632&rqi=2UWmA04pQ8fdB5NMCdvIJ1mKqG
YT1MECH-310-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_4 | FPMP - Fuel Pump |  |  | Cable entry at the Fuel Pump Panel (bottom) of the panel is not properly gland and the cable need flexible conduit before entering the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625430&prj=632&rqi=NAjQq0wtd44gMElVikVL19uGpo
YT1MECH-310-002 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_4 | FPMP - Fuel Pump |  |  | the cable missing tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625431&prj=632&rqi=How62OcGlrc0NAw97ji6LPo440
YT1MECH-306-002 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | Cable missing the tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625420&prj=632&rqi=PEHNPlii9QNqdYl6UPE2cED8CM
YT1MECH-306-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | Cable entry at the Fuel Pump Panel (bottom) of the panel is not properly gland and the cable need flexible conduit before entering the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625412&prj=632&rqi=ad2YtQc2ZJsbSDFCcnvE5N11li
RT1ELEC-201-002 | JH02-1/2 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-06-16 04:00:00.000 +0400 | Commissioning Authority | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R_4 | MDSB - Mech Distribution Switchboard |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625415&prj=632&rqi=F2tFr6lLT4RiVwmvtrztXOQweF
YT1MECH-307-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_2 | FPMP - Fuel Pump |  |  | Cable entry at the Fuel Pump Panel (bottom) of the panel is not properly gland and the cable need flexible conduit before entering the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625417&prj=632&rqi=I0Bg59Hm9dM598xZVjWQLZcPHz
YT1MECH-307-002 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_2 | FPMP - Fuel Pump |  |  | The cabling missing tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625418&prj=632&rqi=RzvYsJtOqJfm03MKxUutZVYeMz
RT1ELEC-201-001 | JH02-1/2 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-06-16 04:00:00.000 +0400 | Commissioning Authority | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R_4 | MDSB - Mech Distribution Switchboard |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625413&prj=632&rqi=E1f6Ch0v3vBtW2KJTAH2aFjuWg
YT1MECH-307-003 | JH02-1/2 | APAC | Open | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_2 | FPMP - Fuel Pump |  |  | Cable dressing is not acceptable. Cable ties have been at the cable bend, causing excessive bending. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625419&prj=632&rqi=xhRdwiJsMgaP10SnH1yXztPrmu
YT1MECH-309-003 | JH02-1/2 | APAC | Open | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_3 | FPMP - Fuel Pump |  |  | Cable dressing is not acceptable. Cable ties have been at the cable bend, causing excessive bending. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625429&prj=632&rqi=Y8cwn3gPZfBuQL1Dh4sVw35O13
YT1MECH-309-002 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_3 | FPMP - Fuel Pump |  |  | The cable missing tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625428&prj=632&rqi=qWdHRRrbKmA9GWGxK6ohgO5xM0
YT1MECH-309-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_3 | FPMP - Fuel Pump |  |  | Cable entry at the Fuel Pump Panel (bottom) of the panel is not properly gland and the cable need flexible conduit before entering the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625427&prj=632&rqi=1gGwLFMT1H7387ZrdTTRsHQ7O0
YT1MECH-200-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_2 | CRAH - Computer room air handler |  |  | isolator for power source to be label to differentiate power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626192&prj=632&rqi=tNVRquzsutWPkldyN39sGjtDAU
YT1MECH-200-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_2 | CRAH - Computer room air handler |  |  | Conduit for fire is tear | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626191&prj=632&rqi=FZIB69gemp9j8cg79A67NHLr2z
YT1MECH-200-003 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_2 | CRAH - Computer room air handler |  |  | Conduit to be labelled serving whats trade/service | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626193&prj=632&rqi=MSFGchWZcYYc01PoDVd63N9sUG
GI-245 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_7 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624918&prj=632&rqi=PCPmehA3y3gwABBGAN6ISY90jT
GI-246 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_8 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624920&prj=632&rqi=1JqxLFLnGERXWrSd34mb7y7hbq
GI-244 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_6 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624917&prj=632&rqi=H35dQmVNnp54MhgsSyIvFHC6rY
GI-243 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_5 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624916&prj=632&rqi=fD0Nz966apNkxfws03GYGTAyMy
GI-241 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_2 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624912&prj=632&rqi=L1SiC4fW2e7QiEt8HA98UJ1G1q
GI-242 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_3 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624914&prj=632&rqi=l1RuKPqhfrUvkLZn7Zr6VEAklh
GI-240 | JH02-1/2 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-06-10 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_15 | LVSB - Low Voltage Switchboard |  | i-Box | Closed issue panel warning sign sticker refer photo attachment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624632&prj=632&rqi=tWYXWTBMf8S7jIxOFeUPs4JJt2
YT1MECH-203-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_5 | CRAH - Computer room air handler |  |  | Conduit to be done properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624821&prj=632&rqi=QU3HqAKiBs37pFCdbjCmTz9k7c
YT1MECH-201-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_3 | CRAH - Computer room air handler |  |  | isolator to be label at A and B source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624820&prj=632&rqi=NiiA66T7ck8Tm3vCZJDCakB155
GI-239 | JH02-1/2 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-06-10 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1_15 HVAC DB | LVSB - Low Voltage Switchboard |  | i-Box | Closed issue Panel warning sign sticker refer photo attachment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624631&prj=632&rqi=TT51mz3jP3HiG20V9aPJW8rtTc
YT1MECH-202-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_4 | CRAH - Computer room air handler |  |  | tear conduit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624819&prj=632&rqi=pda1lz5fJQp4Ul9VV2UIUzONvA
YT1MECH-299-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_6_CHWBT | CHWBT - Chilled water buffer tank |  |  | insulation to redo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624290&prj=632&rqi=b8YUACerUtCV1VYqgisvQFx0Ax
YT1MECH-295-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_2_CHWBT | CHWBT - Chilled water buffer tank |  |  | Valve clashing with tank | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624293&prj=632&rqi=QD1h0a6p2CnliSNZeRDcRVDoR0
YT1MECH-294-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_1_CHWBT | CHWBT - Chilled water buffer tank |  |  | valve clashing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624294&prj=632&rqi=EfGPPYGRmQxgxr5sHA5pmB0lmQ
YT1MECH-299-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_6_CHWBT | CHWBT - Chilled water buffer tank |  |  | Valve clashing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624289&prj=632&rqi=DmdxZOoRW83RW8GmT6JW9F45Nn
YT1MECH-300-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_7_CHWBT | CHWBT - Chilled water buffer tank |  |  | Accesories not intalled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624292&prj=632&rqi=1hQhGgtwC0wkIBBUq4OCHUJ6WV
YT1MECH-299-003 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_6_CHWBT | CHWBT - Chilled water buffer tank |  |  | flow direction label to be install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624291&prj=632&rqi=4yF7iEZrzbo2KqSK8kIKVyqGlb
YT1ELEC-214-001 | JH02-1/2 | APAC | Closed | P1 High CX | ahmadfuad@commtechasia.com | 2026-06-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_9 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_M2R_9 was energised prior obtaining Conditional Yellow Tag (CYT) or Yellow Tag (YT) given to the panel which deviate from the established Cx process and EQIX playbook. GC to submit RCA detailing the sequence of event and the corrective action plan to prevent same issue occurring again in future. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624228&prj=632&rqi=oASCgM81bo6uu8jHlAzdafZvC1
YT1ELEC-450-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-06-06 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_03 | LVSB - Low Voltage Switchboard |  | i-Box | Circuit tagging missing on plastic cover. To install circuit tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624229&prj=632&rqi=DrHjm2lq60X75d9gDyh1M59Z91
YT1MECH-192-005 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_R_4 | CRAH - Computer room air handler |  |  | Tear conduit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624277&prj=632&rqi=XHAEmfKe92NOxHes7CzqovCUNE
YT1MECH-192-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_R_4 | CRAH - Computer room air handler |  |  | Fire cable not terminated per standard and unlabelled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624273&prj=632&rqi=l8gCZ4GODc13qMnaYHaZHLqTyH
YT1MECH-192-002 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_R_4 | CRAH - Computer room air handler |  |  | Comm cable is not properly tagged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624274&prj=632&rqi=DcwyLK9IKx24jxomLILU0lOiUd
YT1MECH-192-004 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_R_4 | CRAH - Computer room air handler |  |  | equipment is coated with dust and cleaning to be done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624276&prj=632&rqi=jmdku0IvhbJ191mPaUHHhVZt5X
YT1MECH-192-003 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_R_4 | CRAH - Computer room air handler |  |  | Isolator to be labelled power source And B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624275&prj=632&rqi=NpkvgawtHxgRkKEI8o7KiulwY6
RT1ELEC-472-001 | JH02-1/2 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_15 | LVSB - Low Voltage Switchboard |  | i-Box | Panel warning sign stickers are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624104&prj=632&rqi=MAiCYp7lmhahDCQ6pIgrkHbuUV
RT1ELEC-378-001 | JH02-1/2 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1_15 HVAC DB | LVSB - Low Voltage Switchboard |  | i-Box | Panel warning sign stickers are missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624101&prj=632&rqi=BrQup9YNjyR5SasoQ5JbVdwlP2
YT1MECH-271-003 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_6_CHWP | CHWP - Chilled water pump |  |  | no cable gland | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624017&prj=632&rqi=bzncRr5tim1iPksLRjWT4RGc2s
YT1MECH-271-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_6_CHWP | CHWP - Chilled water pump |  |  | DCOS and Xinnetwork conduit not labelled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624014&prj=632&rqi=fLzr5VBAbTse68C1v8zgDElK7g
YT1MECH-272-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_7_CHWP | CHWP - Chilled water pump |  |  | torque mark misaligned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624021&prj=632&rqi=1IKYSFC3BB5bRu011JgjNq0quM
YT1MECH-268-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_3_CHWP | CHWP - Chilled water pump |  |  | labelling for trunking and conduit to be done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624011&prj=632&rqi=n8STRUx20k0buMAnDo1xYP8C5A
YT1MECH-268-003 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_3_CHWP | CHWP - Chilled water pump |  |  | cable tagging missing xinnetwork | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624013&prj=632&rqi=jh88Kvif1O1T5ZYL5mlngxSRp3
YT1MECH-272-003 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_7_CHWP | CHWP - Chilled water pump |  |  | missing cable gland | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624023&prj=632&rqi=m7W1ba4XnLAoojhcfa8OPJ098L
YT1MECH-269-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_4_CHWP | CHWP - Chilled water pump |  |  | cable tagging not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624031&prj=632&rqi=VTslBtZtsRdTmR0e3sDefmKJXu
YT1MECH-276-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_4_CWP | CWP - Condenser Water Pump |  |  | isolator cover missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624030&prj=632&rqi=kfkQlM6XjGbFCpIFW2i2uilbrI
YT1MECH-272-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_7_CHWP | CHWP - Chilled water pump |  |  | conduit to be labelled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624020&prj=632&rqi=VvDBGvwuyeM5gWZwhYJ2bI4J5l
YT1MECH-279-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_7_CWP | CWP - Condenser Water Pump |  |  | missing cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624024&prj=632&rqi=aT1hyHgv0hnf4Jt58RXHbyudV9
YT1MECH-271-002 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_6_CHWP | CHWP - Chilled water pump |  |  | cabel tag missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624015&prj=632&rqi=guk47F6lg5w58v0akNhmi9CnNs
YT1MECH-268-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_3_CHWP | CHWP - Chilled water pump |  |  | Torque marking not done properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624012&prj=632&rqi=39JQQMpOtKkubQ3BTOi0b8Xxkn
YT1MECH-246-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1PF_M1_7 | EF - Exhaust Fan |  |  | Ip rating compromise since coring on isolator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623880&prj=632&rqi=W9lEjmd7upL5wimAdJryasBKxA
YT1MECH-246-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1PF_M1_7 | EF - Exhaust Fan |  |  | Isolator not labelled serving to which panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623881&prj=632&rqi=ouR7wo0nNhSPt67pc1AVsiNPpU
YT1MECH-246-003 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1PF_M1_7 | EF - Exhaust Fan |  |  | cable labelling is wrong and swapped over damper and mv fan | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623882&prj=632&rqi=z4fcP48JhAkH94Z8Ei2iX0qknS
YT1MECH-244-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1PF_M1_4 | EF - Exhaust Fan |  |  | isolator IP rating compromise | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623874&prj=632&rqi=AVN6fS5PtO6XOxgZSR9JXwofPt
YT1MECH-243-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1PF_M1_3 | EF - Exhaust Fan |  |  | Isolator IP rating compromise | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623879&prj=632&rqi=mvHvQru4rhSWlJuVgfWKalXSAv
RT1MECH-317-001 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1TEF_M1_1 | EF - Exhaust Fan |  |  | GA and SLD not tally onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623756&prj=632&rqi=0fG3eekqHFEGUWYyNKLUrpVi6K
YT1MECH-296-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_3_CHWBT | CHWBT - Chilled water buffer tank |  |  | Valve clashing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622619&prj=632&rqi=S1Oyb4dmU2IZTHtO96Ba9Dk1fX
RT1ELEC-488-001 | JH02-1/2 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVSB_M1R_5 | LVSB - Low Voltage Switchboard |  | i-Box | The outgoing breaker tagging (Q_04, Q_06, Q_07) at 1LVSB_M1R_5 panel on site is not tally with the latest revision (Rev 02) of the SLD drawing. Please check and amend the drawing based on site condition. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622579&prj=632&rqi=MXZpbhJ3b7g7o3hWwjDoRdscvt
YT1ELEC-392-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_CR_09 | LVSB - Low Voltage Switchboard |  | i-Box | Electrical wiring drawing does not tally with FCU layout drawing. Electrical drawing has CCT R1 to FCU_A_30, but FCU layout has this as FCU_A_25. (All other circuits are the same as this) Electrical drawing & LVDB SLD to be red-lined (updated) as per the FCU layout drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622358&prj=632&rqi=kaSW6XaHvbLzwDNYzxuwAftm47
YT1ELEC-461-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_AR_09 | LVSB - Low Voltage Switchboard |  | i-Box | Electrical wiring drawing does not tally with FCU layout drawing. Electrical drawing has CCT R1 to FCU_A_02, but FCU layout has this as FCU_A_04. (All other circuits are the same as this) Electrical drawing & LVDB SLD to be red-lined (updated) as per the FCU layout drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622213&prj=632&rqi=0lk2Og1L7mgs3i3QhuqNZqU8Pg
RT1ELEC-213-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-05-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_4 | MDSB - Mech Distribution Switchboard |  |  | Outgoing breaker tagging Q_02 (To 1CHWSTR_M2_9_CWP) and Q_03 (To 1CHWSTR_M2_9_WCC) need to be revise to follow CWP (To 1CHWSTR_M2_3_CWP) and WCC number (To 1CHWSTR_M2_3_WCC). Typical to all 1MDSB_M2R_2 to 8 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621923&prj=632&rqi=7IZSZpc7rDmfG851AMLeGXkiqv
YT1MECH-275-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_3_CWP | CWP - Condenser Water Pump |  |  | no tagging at cat6 cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621772&prj=632&rqi=yjUS6AL3b91275TmkdjbglZCoz
YT1MECH-275-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_3_CWP | CWP - Condenser Water Pump |  |  | isolator box to change and label. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621773&prj=632&rqi=cwN50xyLLKICnnqwqIl3umiOrI
YT1MECH-278-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_6_CWP | CWP - Condenser Water Pump |  |  | no cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621778&prj=632&rqi=o0odGY61SIjSl0uI5QJIdK7wtl
GI-231 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | All bolted connections are not torque tightened and some pipe support brackets are not completely installed. Applied to HSD Yard, Pump Room 1 and Pump Room 2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620184&prj=632&rqi=PK2ekCPTXi7OYMKbcK9XoVY1iB
GI-232 | JH02-1/2 | APAC | Open | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | it was observed Check Valve (FR_CV2 & FR_CV3) are installed in the wrong direction. Applied in Pump Room 2 & Pump Room 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620186&prj=632&rqi=4WvI2vsMBUDVoPfyQXMDKNLlae
GI-229 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-05-04 04:00:00.000 +0400 |  |  | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | The pressure gauge, test point and flow switch are missing at Pump Room 2 & Pump Room 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620182&prj=632&rqi=yXHbEF8Jam6hYKtksxQvxzNTxM
GI-230 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | it was observed that all pipes in Pump Room 1 & Pump Room 2 are not labeled, identified and painted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620183&prj=632&rqi=fDvC3HzuTbcLeLq1nRvq7QgobV
GI-233 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Fuel | equipment | FPPUMP1 | FPMP - Fuel Pump |  |  | it was observed all pipes are no labeled, torque tightened, identified and painted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620188&prj=632&rqi=oo2F3JBMUf5rvohZAXJRxTELoh
YT1ELEC-65-001 | JH02-1/2 | APAC | Open | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1ATSM_M1R_02 | ATS - Automatic Transfer Switch |  |  | It was observed that there were no DCOS monitoring to 1ATSM_M1R_01 till 07 (supplying to CHW pumps). Honeywell to recheck with EoR and confirm if these ATSM panels supplying to CHWP require to be monitored or not in DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619676&prj=632&rqi=1dUHTz6YiLlEQ47Fs3mFiHPBvA
RT1MECH-186-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-24 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1AS_B_11 | FFU - Air Scrubber |  |  | isolator blocked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619443&prj=632&rqi=ToEoRx4gy6mbWaPR2cvQawronZ
RT1MECH-182-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1AS_B_09 | FFU - Air Scrubber |  |  | fan clashing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619444&prj=632&rqi=PTQ6891rr8Vm5RMvywY7VZ4yZk
RT1MECH-212-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1AS_B_03 | FFU - Air Scrubber |  |  | cable management to be done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619440&prj=632&rqi=YvNibQEPUZoOexCzcbj0udLWOG
YT1ELEC-212-001 | JH02-1/2 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_4 | MDSB - Mech Distribution Switchboard |  |  | Outgoing compartment Q_03 nameplate shows to 1CHWSTR_M2_9_WCC. Actual on-site outgoing goes to 1CHWSTR_M2_03_WCC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619159&prj=632&rqi=wqovMUlKafLQ136gylH94LqIbf
RT1MECH-210-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1AS_B_02 | FFU - Air Scrubber |  |  | Cement marks on unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619439&prj=632&rqi=UY56sfRWw6ZCqYMTnZ6ZybTBXR
RT1MECH-208-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1AS_B_01 | FFU - Air Scrubber |  |  | faulty isolator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619438&prj=632&rqi=lPA6An3KbhIyvK50nhIsF0MOMn
RT1MECH-200-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1AS_A_04 | FFU - Air Scrubber |  |  | power isolator blocked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619441&prj=632&rqi=EEhDy6WxWWvYECudGK3c4ogyIz
RT1ELEC-372-001 | JH02-1/2 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1R_33 | LVSB - Low Voltage Switchboard |  | i-Box | Permanent equipment labels missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619162&prj=632&rqi=YOBSBSOxCWBEUn2vGwpkAFrJJn
RT1DCOS-42-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Controls | equipment | 1DCOS_CP_1 | DCOS - Control Panels |  |  | Neutral bar only provided for protected earth ( power earth bar). No functional earth (signal earth bar) provided for the panel. Other panels PCP, SCP, RIO, LCP has both functional. HNY to get confirmation from EoR. Aoolicable to all CP panels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618967&prj=632&rqi=L33ArwuJjMPx5UvvyxzWcpG8oI
RT1MECH-230-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_3 | CRAH - Computer room air handler |  |  | Confirm clear access is available to all CRAH components and that sufficient withdrawal space has been allowed for maintenance, removal and replacement of parts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619165&prj=632&rqi=jYOaIjO2uIflvFcehLOMJKyoRQ
RT1MECH-243-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | imanuddinhamdan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_4 | CRAH - Computer room air handler |  |  | Valve bracket damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619168&prj=632&rqi=i2Jd7Fsfb4yw7mDHnloVr9iXbV
RT1MECH-229-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_2 | CRAH - Computer room air handler |  |  | Confirm clear access is available to all CRAH components and that sufficient withdrawal space has been allowed for maintenance, removal and replacement of parts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619163&prj=632&rqi=PvMSDVsM8SCLdHtDVwD691VqEg
RT1MECH-228-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_1 | CRAH - Computer room air handler |  |  | Confirm clear access is available to all CRAH components and that sufficient withdrawal space has been allowed for maintenance, removal and replacement of parts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619164&prj=632&rqi=QAMq53eQcEEcydgIIJCQ3MFpZ3
RT1MECH-232-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_5 | CRAH - Computer room air handler |  |  | Confirm clear access is available to all CRAH components and that sufficient withdrawal space has been allowed for maintenance, removal and replacement of parts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619166&prj=632&rqi=Yyt9f1keoFDpMDiWukbj3u4r8l
RT1MECH-320-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1MAU_M1_1 | AHU - Air handling unit |  |  | Observed dents and scratches on the bottom plate of the MAU. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618001&prj=632&rqi=wTwP5SGx6KLtScMSyy3SBd6nzV
RT1MECH-320-002 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1MAU_M1_1 | AHU - Air handling unit |  |  | The equipment labelling has not been fixed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618004&prj=632&rqi=yDfg9w9BvsJdfBp6NXQCFuYS24
RT1MECH-320-003 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1MAU_M1_1 | AHU - Air handling unit |  |  | To provide relevant project piping specifications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618005&prj=632&rqi=UWtDlSndtU9VmRUHd75wyzm76R
YT1ELEC-122-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | As per understanding from Siemens, the earthing from the TX to earth system, it should be 2 earths from the TX room earth bar to the TX LV side and 2 earths from the TX room earth bar to the TX MV side. Current onsite installation has all 4 earths from TX room earth bar to TX LV side. GC to confirm with vendor (Siemens) and NV5 that this is an acceptable installation method | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617768&prj=632&rqi=pow3hSJMOGSmkHSvpnaYZwNrJi
RT1MECH-374-003 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1DWBP_M1_1 | DOMW - Domestic Water Set |  |  | No Tagging for Pump and Panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617613&prj=632&rqi=eM3Mhr6xdNJfkfI9hd3zb8ITcX
RT1ELEC-382-001 | JH02-1/2 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_27 | LVSB - Low Voltage Switchboard |  | i-Box | Missing permanent nameplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617598&prj=632&rqi=oNJDwH9gcMMVtqa42nL4cDEP8Z
RT1MECH-376-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1TWSP_M1_1 | DOMW - Domestic Water Set |  |  | Single Line Drawing to be updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617335&prj=632&rqi=lrRRzSwsSfIPP0roSUR6lKgmEs
RT1MECH-255-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_6 | CRAH - Computer room air handler |  |  | No Permanent Tagging Installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617288&prj=632&rqi=S8YW9evuCtfldlm3LhAbTqYQh7
RT1MECH-251-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_2 | CRAH - Computer room air handler |  |  | Tagging for equipment is not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617289&prj=632&rqi=Om2okKI4vqFY2zYwpvpJlejQ45
RT1MECH-378-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1RWFP_M1_1 | DOMW - Domestic Water Set |  |  | Panel IP Rating to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617332&prj=632&rqi=DPT348NIOnvGvZbdSYOlJSBg80
RT1MECH-374-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1DWBP_M1_1 | DOMW - Domestic Water Set |  |  | Panel IP Rating to be clarified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617337&prj=632&rqi=DFA3gwopGCe3ltCRNY8WcKbb3D
RT1MECH-251-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_2 | CRAH - Computer room air handler |  |  | Internal tagging for the sensor to be updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617285&prj=632&rqi=Z9aXkWwf5K2UKk9ixzs92wMPr1
RT1MECH-374-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1DWBP_M1_1 | DOMW - Domestic Water Set |  |  | SLD Drawing to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617338&prj=632&rqi=e0p9UR0iLxFnrT57K0Yyl51tOZ
RT1MECH-378-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1RWFP_M1_1 | DOMW - Domestic Water Set |  |  | Panel naming and pump tagging to be updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617334&prj=632&rqi=Rnz596arDtZcXkqEJdyG4QqUBW
RT1MECH-368-003 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1MWP_M1_1 | DOMW - Domestic Water Set |  |  | Missing Labelling for equipment and warning sign | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617294&prj=632&rqi=cLcLUXlxeYspxXH8rPI4C8uczI
RT1MECH-294-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_03 | EF - Exhaust Fan |  |  | Exhaust fan duct support bracket is installed in a slanted and improper alignment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617303&prj=632&rqi=BxAxgjtNponM4JceHiObpLiU0h
YT1ELEC-93-003 | JH02-1/2 | APAC | Closed | P1 High CX | ahmadfuad@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1SUDB_1 | SUDB - Secondary Utility Distribution Board |  |  | During energisation site walk conducted on Friday (3/4/2026), it was observed that there is a potential SF06 gas pressure issue at K01 Outgoing Feeder of 1SUDB_1. The SF06 pressure gauge indicates the reading is outside of the acceptable (green) range. ABB to investigate and determine the root cause of the issue whether it is due to gas leakage or instrument faulty. ABB to submit RCA for the issue to outline the findings corrective actions and preventive measure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617355&prj=632&rqi=OsNVygLWGjrZXImthLMrt4SnGf
RT1MECH-368-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1MWP_M1_1 | DOMW - Domestic Water Set |  |  | MCB Rating to be clarify. Drawing shows 40A while however onsite shows 32A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617291&prj=632&rqi=OBxpoBhMmvg0q1NmpKrhW694O0
RT1MECH-376-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1TWSP_M1_1 | DOMW - Domestic Water Set |  |  | Panel tagging and Pump Tagging to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617336&prj=632&rqi=TwVQFCR2saNy7znpilSesCUx8x
RT1MECH-255-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_6 | CRAH - Computer room air handler |  |  | Internal Tagging for equipment to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617287&prj=632&rqi=0hbuxaYTnR0C87fh3q75T9JPt0
RT1MECH-368-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1MWP_M1_1 | DOMW - Domestic Water Set |  |  | IP Rating for Panel to be updated with supporting letter from Supplier | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617290&prj=632&rqi=BMVwKxuXvIdWNSD89C3QjKJqOh
RT1MECH-296-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_04 | EF - Exhaust Fan |  |  | Exhaust fan support bracket is in contact with the cable tray. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617214&prj=632&rqi=YbnbOzr5TRrK2WCxlBan1b4G7D
RT1MECH-292-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_B_3 | EF - Exhaust Fan |  |  | Equipment layout drawing needs to be updated as the panel name shown is incorrect compared to the onsite panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617217&prj=632&rqi=Sr5CBZFR0feAxwfMBbdEUe1333
RT1MECH-292-002 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_B_3 | EF - Exhaust Fan |  |  | Drawings missing from the panel. Applicable for all exhaust fan at Pre Action rooms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617218&prj=632&rqi=EzcSuJ0glPJz4p1woR5v8jEmxY
RT1ELEC-495-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVSB_M1_1 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign is not affixed to the panel. Applicable to all panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617000&prj=632&rqi=PAVjzX7CFDV00wyQfMav23hQdZ
RT1ELEC-486-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M2_06 | LVSB - Low Voltage Switchboard |  | i-Box | General arrangement and schematic Drawings not in the panel. Applicable to 1LVDB_M2_06 and 1LVDB_M2_07 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616783&prj=632&rqi=SQZFhdzPoR9pjquHiLG9jgjIN4
RT1ELEC-486-002 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M2_06 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign is not affixed to the panels. Applicable to all panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616784&prj=632&rqi=YSVVyXYfBWGN53XDDc8jXciHxk
RT1ELEC-592-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M2_10 | LVSB - Low Voltage Switchboard |  | i-Box | Panel nameplate is damaged. Applicable to 1LVDB_M2_10 and 1LVDB_M2_12 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616785&prj=632&rqi=RiUMA06jmtOsFJmEHj31Bfse0q
RT1ELEC-593-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M2_11 | LVSB - Low Voltage Switchboard |  | i-Box | Panel door knob is broken. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616786&prj=632&rqi=C45O4PGmqSsIRej3WaT15uSCRl
RT1MECH-351-004 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_1_CHWBT | CHWBT - Chilled water buffer tank |  |  | Permanent equipment labels not fixed. Apply to all Buffer Tanks. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615931&prj=632&rqi=Y1InPLnKJFyb6MgzF7dKr2k1qR
RT1ELEC-366-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1_25 | LVSB - Low Voltage Switchboard |  | i-Box | Latest revisions of both the General arrangement and schematic Drawings missing . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615497&prj=632&rqi=rxiOFdjjgHxmJZEA7OZ0vVCK0c
RT1ELEC-144-001 | JH02-1/2 | APAC | Open | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | HMI not yet positioned and installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615493&prj=632&rqi=Y6MGk9hX9zX0W899r1Vi6FDZuE
YT1ELEC-11-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | pauljohnson@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | CT for L3 phase is to be replaced and to be tested once installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615491&prj=632&rqi=GUu57rB4mhwLeIznKleqZQxtIO
RT1ELEC-145-001 | JH02-1/2 | APAC | Open | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_D | MSB - Main Input Switchboard |  |  | HMI not yet positioned and installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615495&prj=632&rqi=O3wzgOnYSqpAtTTmDRFBas4QXb
RT1ELEC-37-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1ATS_FR_02 | ATS - Automatic Transfer Switch |  |  | Panel door is unable to close properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615498&prj=632&rqi=wQJtMPJLUDFYzZ63rublZskpgN
RT1ELEC-146-001 | JH02-1/2 | APAC | Open | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_F | MSB - Main Input Switchboard |  |  | HMI not yet positioned and installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615499&prj=632&rqi=jT1Pra7lBxqVUF0ZTRVVKuq21v
RT1ELEC-33-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1ATS_DR_01 | ATS - Automatic Transfer Switch |  |  | Dual power supply sign is not affixed to the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615494&prj=632&rqi=NY7yWrYs6X48CnZnyTFmTxhLkn
YT1ELEC-13-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | pauljohnson@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | CT for L3 phase is to be replaced and to be tested once installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615490&prj=632&rqi=t6z17Bhu4J70HX9jug6B9cQLGh
YT1ELEC-128-001 | JH02-1/2 | APAC | Closed | P1 High CX | ahmadfuad@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | During busduct Cx2A was conducted between 1MSB_A to 1UPS_A1, it was observed the earth bar on UPS compartment and busduct N bar is too near to each other. It was observed that the spacing is less than 5mm spacing. GC to evaluate and make adjustment to ensure the safe gap of more than 25mm in between. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615338&prj=632&rqi=pIUrrcMNYGUK51k1mOtkQ9olUv
RT1ELEC-12-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615093&prj=632&rqi=cpYv6ZSFwpz2eO4xITI5bH0cDu
RT1ELEC-11-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615089&prj=632&rqi=4m3chzK6avCrfACruCqlnW5ntP
RT1ELEC-13-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615090&prj=632&rqi=4EPCrLojcNyezLzwjePnGANMmL
RT1ELEC-5-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_E | RMU - Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615091&prj=632&rqi=0P8sRmc25nbAEK6Z2lU0Acs0Gg
RT1MECH-330-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_1_CWP | CWP - Condenser Water Pump |  |  | Danger warning sign is not installed on panel. Apply for all CWP panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614869&prj=632&rqi=CM3zwgU8qLhbK7iyurZts0KhcP
RT1MECH-351-003 | JH02-1/2 | APAC | Open | P3 Low CX | ahmadfuad@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_1_CHWBT | CHWBT - Chilled water buffer tank |  |  | maintenance ladder to buffer tank stop short at plinth. However no access provided from ground to plinth. Suggest to extend the ladder to the ground. GC/ACT to confirm maintenance feasibility. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614748&prj=632&rqi=lKBhXRPISjvtU45iVi53P2rl0w
RT1MECH-351-002 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_1_CHWBT | CHWBT - Chilled water buffer tank |  |  | Bolting at the floor and end connection did not indicate torque mark. To ensure all bolting have torque mark and demonstrate to CTA on site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614747&prj=632&rqi=JZHxN2LGldbPM8itbe5IBbxhmX
RT1MECH-323-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_1_CHWP | CHWP - Chilled water pump |  |  | Danger warning sign is not installed on panel. Apply for all CHWP panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614787&prj=632&rqi=oGjwBo4ERNzahQlKUyLYJNhjQQ
RT1MECH-351-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_1_CHWBT | CHWBT - Chilled water buffer tank |  |  | Tank painting micron indicated 50 micron for external layer and 150 micron for internal layer as per document specification. GC to provide prove on painting micron. FAT document didnt shown the information. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614745&prj=632&rqi=TaMX5f90On4Thq9YuhujwxR28H
RT1ELEC-404-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_DR_8 | LVSB - Low Voltage Switchboard |  | i-Box | Proper circuit number tagging to install. Current installation is not acceptable. Refer to the sample as per attached. Typical for all LVDB panels. Please do one sample for review before proceed for other panels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614680&prj=632&rqi=DcSgWPPIFjC8t9Ilj4FR3ozSSl
RT1ELEC-129-004 | JH02-1/2 | APAC | Closed | P3 Low CX | fazdliabdulmubin@eaton.com | 2026-03-02 04:00:00.000 +0400 | Commissioning Authority | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483517&prj=632&rqi=D112j9CxzfFbvou9gHxHdd0Oem
RT1ELEC-96-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STS_A1R1_1 | STS - Static Transfer Switch |  |  | FAT report provided is without the Primary Injection test on ACB breaker. As per Cx playbook, PI test is require to be conducted on site for breaker >250A. CSPM to arrange manpower to complete the testing on site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483514&prj=632&rqi=y6D7zBYrxyQgA41svci5vIiPxb
RT1ELEC-129-005 | JH02-1/2 | APAC | Closed | P3 Low CX | fazdliabdulmubin@eaton.com | 2026-03-02 04:00:00.000 +0400 | Commissioning Authority | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | Installation checklist from MCE completed (signed off) and attached to this checklist as a document (where Applicable) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483520&prj=632&rqi=4Raa0bzgO4IpPpuHgqYUhYJttG
YT1ELEC-179-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-26 04:00:00.000 +0400 | Consultant | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_M1 | MSB - Main Input Switchboard |  |  | Q14 incorrect settings for the short time. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352255&prj=632&rqi=t6gLBeJZEasxCf6n4FgBevnUBn
RT1ELEC-181-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  |  | HMI not yet in position and wall mounted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204140&prj=632&rqi=f6MwT0hoA10DrnakA6LbNk83HP
RT1ELEC-178-002 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  |  | HMI not yet positioned and installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204138&prj=632&rqi=ENYZVGBWpx02GQMzM8U7QyY54d
RT1ELEC-180-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_M1 | MSB - Main Input Switchboard |  |  | HMI not yet positioned and wall mounted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204143&prj=632&rqi=wfm4YVHeVWPll5uAjtkMwoYdrI
RT1ELEC-177-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_A | MSB - Main Input Switchboard |  |  | HMI not yet in position and wall mounted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204141&prj=632&rqi=DA60gpmOrIOZxIewTUcrk9JsHx
RT1ELEC-129-002 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | Missing drawing pocket to install infront of cover plate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199814&prj=632&rqi=MAQ91jiXWEfX7bdXPjfsolesxd
RT1ELEC-129-003 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | Missing equipment tag for UPS to install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199815&prj=632&rqi=ANJlyARNNVpf7KzZfQZNSnsxTi
RT1ELEC-129-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | DC+ and DC- busbar to tag '+' in red color and '-' in black color. Current on site missing color tag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199812&prj=632&rqi=bsIA87ZjUp96Zl5LlDzfcptGxf
YT1ELEC-177-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | pauljohnson@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  |  | For the eWall Earthing Schematic, the schematic shows MSB, Transformer Room & Generator As a TNC (should be TNC-S) with a Neutral Earthlink shown inside the MSB. Also the schematic shows the LV cables from the TX & Genset as a PEN (Protective Earth & Neutral Combined) conductor. Current onsite LV cabling doesn't tally with the schematic and TNC set up, as cables installed have 14 earth cables from the TX to the MSB. GC to confirm with design. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198962&prj=632&rqi=G5yxi76T3v38PMRl2JVf34ikiW
RT1ELEC-158-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_8 | MDSB - Mech Distribution Switchboard |  |  | Control drawing missing in the pocket drawing. Control Cable tagging for control unable to check. Typical for all 1MDSB_M2R_2 to 8. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198963&prj=632&rqi=fBkqIv5IXU9rw0xsg9MBuojIyy
RT1ELEC-178-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  |  | MSB_B HMI panel not yet installed as part of MSB Cx2A. Arrange with GC to expedite installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198576&prj=632&rqi=prMJ9dOCEnHNTi79bG4mI2xDoS
RT1ELEC-520-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_11 (40A) | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign is not installed on panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198567&prj=632&rqi=IIpJECPceDEB4GUCkQSzuydw7e
RT1ELEC-56-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1ATSM_CR_02 | ATS - Automatic Transfer Switch |  |  | Danger warning sign and dual supply warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198583&prj=632&rqi=3aqh6Lbi4evmtxndZh4NwzOyaz
RT1ELEC-409-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_D_13 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign is not installed on panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198562&prj=632&rqi=b47WdnkfykJXwXgXJMnxJbokCY
RT1ELEC-405-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_DR_9 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign is not installed on panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198571&prj=632&rqi=givTLH7gtK6nHSRXRpbcg3we3H
RT1ELEC-60-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1ATSM_DR_02 | ATS - Automatic Transfer Switch |  |  | Danger warning sign and dual supply warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198582&prj=632&rqi=XNN3gHNjYCQHGhB6Dnf2tFZQgs
RT1ELEC-519-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_07 (40A) | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198579&prj=632&rqi=PcBiS4qldMDjEX7YQ9YxxJ6fdY
RT1ELEC-179-003 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | MSB_R HMI panel not yet installed as part of MSB Cx2A. Arrange with GC to expedite this installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198573&prj=632&rqi=r4N6pjc9VfwVEpddGy3Tx70hFa
RT1ELEC-521-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_12 (40A) | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198581&prj=632&rqi=G3szM2WghAeAeX1MDgo2bDXW9u
RT1ELEC-393-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_CR_09 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning is not installed on panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198575&prj=632&rqi=Qoxrgg6AT5TnLuAJQyLzatvoG7
RT1ELEC-518-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_06 (40A) | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198577&prj=632&rqi=7uwqwUjN5n9eU4RsukIQjTz0qj
RT1ELEC-397-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_C_13 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198578&prj=632&rqi=hnBa2JKdofqv8U7brR2BpwpWL2
RT1ELEC-473-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_09 | LVSB - Low Voltage Switchboard |  | i-Box | Verify Permanent equipment labels affixed and are as per approved colour scheme. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198289&prj=632&rqi=9PeYaJuwMUVX24ivgyZOVnFWgH
RT1ELEC-30-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1ATS_AR_02 | ATS - Automatic Transfer Switch |  |  | Permanent equipment labels are affixed and are as per approved colour scheme. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198288&prj=632&rqi=Qj5XicEereOchvI8g9g7KulFkT
GI-228 | JH02-1/2 | APAC | Closed | P1 High DCOS | ahmadfuad@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Controls | equipment | 1DCOS_PCP_1 | DCOS - Control Panels |  |  | (FWT) During DCOS and CPOS SFAT, it was observed that minimum testing readiness was prepared by Honeywell. The test was deemed Not Acceptable and re-SFAT required. Line animation and basic graphics requirement were not presented due to unreadiness. These items are mandatory and required to be tested during SFAT. The configuration is not based on signed off SICD. The DCOS HMI graphics were only presented for one typical set of equipment, which does not comply with the MOS requirement that 100% of graphics must be ready and tested. Finally, no proper Internal test report and QA/QC report with graphic screenshot were not provided before the SFAT date. Honeywell to submit RCA for detailed failure root cause and corrective action plan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197901&prj=632&rqi=qOJLCmHgAyTDwsc3xDHfnjBHVq
YT1ELEC-488-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVSB_M1R_2 | LVSB - Low Voltage Switchboard |  | i-Box | LV cables connection to isolator for LCP-1EF-M1-13 and LCP-EF-M1-12 to redo cables termination due to bending radius not acceptable. As per PB 5.1 Equinix allow a min bend radius of 12-15 times the cable diameter | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197322&prj=632&rqi=DGprfzw3wIL5QCBUq6uyJOsoYU
YT1ELEC-93-002 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1SUDB_1 | SUDB - Secondary Utility Distribution Board |  |  | 1BTU_1 Battery Charger have two charger namely Charger 1 and Charger 2. Incoming power for Charger 1 identified is from LVSB_M1_35 R2. However, no incoming cable identified for Charger 2. Please recheck with design EOR to confirm power source for Charge 2. Typical comments for 1BTU_2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197324&prj=632&rqi=3b9k55UfbUSv0bXwiDKRjWFtxN
RT1ELEC-216-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_10 | MDSB - Mech Distribution Switchboard |  |  | Discrimination setting. Refer marked in yellow changes from R4. To finalise setting with design consultant and update sticker where required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197172&prj=632&rqi=wCImwrJC30r4KTHKXpSiqzp9az
YT1ELEC-204-002 | JH02-1/2 | APAC | Closed | P2 Medium CX | pauljohnson@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M1_04 | MDSB - Mech Distribution Switchboard |  |  | For MCCB's Q02, Q03, Q04 & Q05 Discrimination study for instantaneous and ground faulty doesn't align with the Breaker Frame Size (In) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197146&prj=632&rqi=Ik3EncHGvZAGU6BDJCoErmSFhs
YT1ELEC-199-002 | JH02-1/2 | APAC | Closed | P2 Medium CX | pauljohnson@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R_3 | MDSB - Mech Distribution Switchboard |  |  | For MCCB's Q02, Q03, Q04 & Q05 Discrimination study for instantaneous and ground faulty doesn't align with the Breaker Frame Size (In) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197154&prj=632&rqi=Wyg6Kpoo6FG8jm9WJ5Au9L2RVz
RT1ELEC-215-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_9 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_M2R_9 Q_06 breaker size onsite is 160AF/40AT. Discrimination Study for Q_06 show 100AF/40AT. Breaker size installed on site correct as per SLD. To reconfirm with design consultant which to follow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197163&prj=632&rqi=ajuIO5sr3iKBfWD6Vz8EhueI28
RT1ELEC-182-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_M2 | MSB - Main Input Switchboard |  |  | MSB_M2 HMI panel not yet installed as part of MSB Cx2A. Arrange with GC to expedite installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197175&prj=632&rqi=tjmvLrQ4K3F3Fj5AL5pDJ5JHnf
YT1ELEC-204-001 | JH02-1/2 | APAC | Open | P3 Low CX | pauljohnson@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M1_04 | MDSB - Mech Distribution Switchboard |  |  | Confirm all labels and safety labels are present | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197141&prj=632&rqi=zjdeTTUo7rA7AgBpdBlc9uiKQw
YT1ELEC-199-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R_3 | MDSB - Mech Distribution Switchboard |  |  | Confirm all labels and safety labels are present | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197153&prj=632&rqi=e8WKnLOPJbad7NRBflFckpjswM
RT1ELEC-182-002 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_M2 | MSB - Main Input Switchboard |  |  | Tagging for switches K01 to K05 pending installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197178&prj=632&rqi=ECt0svNbY1uKJ3UjPZjn5tNg9y
RT1ELEC-10-003 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Permanent ladder or movable ladder or platform are required to be position inside the RMU. Current testing was conducted using temporary ladder. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197102&prj=632&rqi=JVwOYlHtoI9uFnaMLeT5LbGbY1
RT1ELEC-10-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | 1RMU_B panel tagging pending installation. Typical for 1RMU_M1, 1RMU_M2, 1RMU_R and 1RMU_A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197100&prj=632&rqi=Ov5Rj5TBNRka7v7ThDhaj1VEnf
RT1ELEC-10-002 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | ZCT and Moxa BMS card pending installation inside RMU. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197101&prj=632&rqi=FyEVztPfpMPY2yn3hELU36FJk3
YT1ELEC-93-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1SUDB_1 | SUDB - Secondary Utility Distribution Board |  |  | Current Setting for below was tested on site without actual setting. However, to confirm if setting require to be set on site and If required please confirm the setting with design consultant. Typical comments for SUDB1 and SUDB2. 27- undervoltage 59- Overvoltage 81U - underfrequency 81O - over frequency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196866&prj=632&rqi=5k8f8Rje5qkZJLjCwZiC6aM4Ml
YT1ELEC-94-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1SUDB_2 | SUDB - Secondary Utility Distribution Board |  |  | Current Setting for below was tested on site without actual setting. However, to confirm if setting require to be set on site and If required please confirm the setting with design consultant. Typical comments for SUDB1 and SUDB2. 27- undervoltage 59- Overvoltage 81U - underfrequency 81O - over frequency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196867&prj=632&rqi=kJLeAhYmZ8mAtjfETtgzpIenQB
RT1ELEC-94-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1SUDB_1 | SUDB - Secondary Utility Distribution Board |  |  | Approved Schematic drawing SLD yet to place inside SUDB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196759&prj=632&rqi=deuHxstE5fu9C2iZGqrhoioBs1
YT1ELEC-372-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1_34 | LVSB - Low Voltage Switchboard |  | i-Box | Incoming cable test pending installation and Cx2 document signed off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196544&prj=632&rqi=EPNu5BYQVfWsJ8SM68cByAThTm
YT1ELEC-372-002 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1_34 | LVSB - Low Voltage Switchboard |  | i-Box | Pending incoming cable test Cx2B. To expedite cable installation and testing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196557&prj=632&rqi=izUcn38tRGbM9k34h2Y82dElDt
YT1ELEC-198-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R_2 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_R_2 discrimination setting not tally with PDC report 1) Q_02 Please confirm I Instantaneous should be (6.0 x 100A (breaker frame size) = 600A) instead of 240A from discrimination studies. 2) Q_02 to 05, 07 to 12, 16 to 20 setting Ground fault at 0.4 x 100A = 40A which typical to trip setting? Otherwise, should this be typical to Q_01 which is 0.2 x 100 = 20A setting? 3) Q_14 I instantaneous 6.0 x 160A = 960A however setting shown is 600A. Please confirm Once NV5 revert, to update and retest accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196556&prj=632&rqi=pg8K0LcZl2dNzQLZaMrb9YlaLj
YT1ELEC-178-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | HMI_R is yet to position and start Cx activity. To expedite wall mount installation and start Cx2A and Cx2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196555&prj=632&rqi=bTHBQ4IYGVDtyEALGKAgUl9DoH
RT1ELEC-179-002 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | HMI R have yet to position and start Cx2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196416&prj=632&rqi=b5LlFdkmhQ7OqeZIoDkAxiLOq0
RT1ELEC-179-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | Key switches tagging missing on panel to install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196305&prj=632&rqi=T8c2St4NAfKrgddzSgOS3vmQzP
RT1ELEC-1-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-11-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Nameplate found rusty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615404&prj=626&rqi=pC6KUKM0v3cVxAZL9ME6vQniFn
BT1FD-6-001 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-09-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | During the 1st alarm simulation, there was a delay in alarm signal detection/indication at the DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638410&prj=626&rqi=6Y21WIv0C8fr6yVy9GaE1uLwre
BT1FD-4-002 | JK01-2 | APAC | Open | P2 Medium CX | wellyjulian@commtechasia.com | 2026-09-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | During General Alarm, the motorized fire damper at the fire riser did not open. MFD FOH B panel indicated Floor 6, whereas it should indicate 4 dampers. LCP indication showed Floor 4 MFD ON. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638416&prj=626&rqi=LsWtrMMgXpRWxPNcbMmLXDfZKs
BT1ELEC-4-001 | JK01-2 | APAC | Open | P1 High CX | fauzanfikri@commtechasia.com | 2026-09-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | During test generator under 100% load condition, abnormal noise and vibration were observed at the generator exhaust. On second start-up attempt, the generator was found hunting condition Testing could not be continued and further investigation from Altrak is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637827&prj=626&rqi=ZheV7n3ThmXZqeKoGG3pY7R78g
BT1FD-5-001 | JK01-2 | APAC | Open | P1 High CX | wellyjulian@commtechasia.com | 2026-09-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_5.01 | PAV - Pre-Action Valve |  |  | During 1st Alarm simulation, SAP Fire Panel L5 indicated â€œCARD 3 LOOP 2 â€“ CARD MISSING/FAILED,â€ resulting in failure of the required interlocks, including CRAY ramp-down and other systems, following the General Alarm sequence. Orient to provide RCA and confirm whether card replacement or troubleshooting is required, followed by full re-testing of the interlock sequence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638412&prj=626&rqi=NuB9tFrHAi4X3oB4hZR0j0k6uh
BT1ELEC-38-001 | JK01-2 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-09-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | CxL4 â€“ 1MLTX_F can't be performed due to an issue with temperature control component. In addition, the communication cable to DCOS is still showing communication loss (commloss) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637790&prj=626&rqi=sPVseT5EfIKa6HZ8gJcN9nrZ3Q
GT1FD-39-001 | JK01-2 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-09-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Fire Detection | equipment | ASDSP-7.10 | VES - Vesda |  |  | During P2G with DCOS, Description in alarm shows ASDSP-7.09 instead of ASDSP-7.10. DCOS team to fix this issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637728&prj=626&rqi=vmMxupQ63129i6CpX3LEz5ghUa
BT1ELEC-5-001 | JK01-2 | APAC | Open | P1 High CX | fauzanfikri@commtechasia.com | 2026-09-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | During CxL4 testing for scenario â€œEarthing Switch State Checking for Maintenance 1RMU,â€ the earthing switch coil on 1RMU_B was not working. This is second time the same issue has occurred. The same issue also happened previously when 1RMU_B was energized | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637764&prj=626&rqi=YrpNoRMoh5R85rMhgB364emGbR
GT1ELEC-155-002 | JK01-2 | APAC | Open | P2 Medium DCOS | DimasKurniawan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Controls | equipment | 1PANEL_I/O_Motorized Damper | CP - Control Panel |  |  | DCOS have to provide additional register (regarding new SoO of MAU Motorize Damper) that need to integrate to DCOS monitoring: - High Temperature Alarm - Bypass Damper Fault - Room Damper Fault Level 2-7 (Cool Spine) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637448&prj=626&rqi=4p7TPBs24MDKXH3i8UQiPCjCFL
GT1ELEC-155-003 | JK01-2 | APAC | Open | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Controls | equipment | 1PANEL_I/O_Motorized Damper | CP - Control Panel |  |  | GC need to perform Air TAB for MAU and provide report Air TAB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637453&prj=626&rqi=yDCpHYzFCWYTPmZ4Z3C1B4SuKA
GT1MECH-81-001 | JK01-2 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_6.01 (Existing) | PAV - Pre-Action Valve |  |  | Seismic Bracing not yet installed and will be planned to install asap by GC. (This issue for all floor) Ensure that when installing those, there will be not affect piping and support pipe. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637418&prj=626&rqi=r1Nt8MSdplpodZAXPkgF3bzfoe
BT1MECH-57-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | During the Fire Alarm Signal Test, the fire alarm status on the LCP HMI remained "False." | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637250&prj=626&rqi=IdjN3WKVtL1t6KPD5ILu4hkvtj
BT1MECH-60-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | There is a discrepancy in the Hâ‚‚ sensor reading. The value displayed on the HMI-LCP is 1, whereas the sensor indicates 0. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637251&prj=626&rqi=bl61T73RIf3DjjvTVLm35VX49H
BT1MECH-60-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | During the Fire Alarm Signal Test, the fire alarm status on the LCP HMI remained "False." | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637249&prj=626&rqi=YTkNK4ypndSOBcgWYPilGgYKXS
BT1MECH-67-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-04 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | During the manual ON/OFF on HMI operation, when the selector switch is moved to Manual, the unit immediately starts running. However, according to the SOO flow for Manual Mode, the selector switch should first be moved to Manual, followed by pressing the Start button on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636797&prj=626&rqi=kOQWXKAAJPX5G8eEC3FJglszZ4
BT1MECH-64-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-04 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | During the manual ON/OFF on HMI operation, when the selector switch is moved to Manual, the unit immediately starts running. However, according to the SOO flow for Manual Mode, the selector switch should first be moved to Manual, followed by pressing the Start button on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636785&prj=626&rqi=bCvc2fOGAxvQlfiO4yO1svAtl5
BT1MECH-67-001 | JK01-2 | APAC | Closed | P2 Medium DCOS | MulyaSitanggang@commtechasia.com | 2026-09-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | There is a discrepancy between the room temperature sensor reading and the temperature displayed on the DCOS graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636795&prj=626&rqi=kz3PT9puOiYSULR6cn2I6F209m
BT1MECH-62-003 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_C_54 | EF - Exhaust Fan |  |  | During the manual ON/OFF on HMI operation, when the selector switch is moved to Manual, the unit immediately starts running. However, according to the SOO flow for Manual Mode, the selector switch should first be moved to Manual, followed by pressing the Start button on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636655&prj=626&rqi=jQznKHZXlMIxnKnlds9C5MSAX4
BT1MECH-62-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_C_54 | EF - Exhaust Fan |  |  | The room temperature reading on the HMI LCP not fluctuating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636654&prj=626&rqi=qIj6aCvHzwA9m551D1hj1eivim
BT1MECH-61-001 | JK01-2 | APAC | Closed | P2 Medium DCOS | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_C_53 | EF - Exhaust Fan |  |  | There is a discrepancy between the room temperature sensor reading and the temperature displayed on the DCOS graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636651&prj=626&rqi=Zrm52i2ovYwgrjb74sVWCJzapy
BT1MECH-62-001 | JK01-2 | APAC | Closed | P2 Medium DCOS | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_C_54 | EF - Exhaust Fan |  |  | There is a discrepancy between the room temperature sensor reading and the temperature displayed on the DCOS graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636652&prj=626&rqi=xmC8ukHN0Zu61x7yC9OJ03VVhO
BT1MECH-58-001 | JK01-2 | APAC | Closed | P2 Medium DCOS | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_B_31 | EF - Exhaust Fan |  |  | There is a discrepancy between the room temperature sensor reading and the temperature displayed on the DCOS graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636667&prj=626&rqi=AAp44H0kMCdGDSwXYrQSefLKMR
BT1MECH-58-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_B_31 | EF - Exhaust Fan |  |  | During the manual ON/OFF on HMI operation, when the selector switch is moved to Manual, the unit immediately starts running. However, according to the SOO flow for Manual Mode, the selector switch should first be moved to Manual, followed by pressing the Start button on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636668&prj=626&rqi=TGcqAr7J28mEqmrh9dV8h9WFSX
BT1MECH-50-005 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_22 | DXID - FCU/DX Indoor Unit |  |  | When Start Hot Standby Sequence test, Second FCU units in the same room are not operating normally (B_22) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636443&prj=626&rqi=sWSuNl7CQ1HIZzP2lTaT8mSrAx
GT1ELEC-49-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Please revise the graphic for STSSB_C_2 refer to STSSB_B_1, as they are one integrated equipment, not separate equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636452&prj=626&rqi=i4eRNaqAadbCJWV2WkuOtKSzvd
BT1MECH-50-004 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_22 | DXID - FCU/DX Indoor Unit |  |  | During Dx FCU Functional Test, when Simulate the space/room temperature Lower than current set point by changing the Setpoint at Thermostat, set point temperature does not trigger to Centralize LCP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636430&prj=626&rqi=hHZwbX0oACzWInAR3A1em8v4MT
GT1ELEC-52-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Please revise the graphic for STSSB_F_1 & F_2 refer to STSSB_B_1, as they are one integrated equipment, not separate equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636454&prj=626&rqi=SCnxuCjO81cFK6vnxwj0dZuFlB
BT1MECH-50-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_22 | DXID - FCU/DX Indoor Unit |  |  | There was no change in the set temperature on the LCP and DCOS when the set temperature was changed on the thermostat. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636421&prj=626&rqi=wHYYs4e1SESF1El03YuiyhgaQI
GT1ELEC-50-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | Please revise the graphic for STSSB_D_1 refer to STSSB_B_1, as they are one integrated equipment, not separate equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636453&prj=626&rqi=tLnFunfOCD2Z1CbFpcFpDTuMrZ
BT1MECH-50-003 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_22 | DXID - FCU/DX Indoor Unit |  |  | During Dx FCU Functional Test, when Simulate the space/room temperature Higher than current set point by changing the Setpoint at Centralize LCP, set point temperature does not trigger to thermostat | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636426&prj=626&rqi=RBmgI0eaDB22GI9qw6wWnOuGMr
BT1MECH-50-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_22 | DXID - FCU/DX Indoor Unit |  |  | During the compressor failure test, the compressor power was intentionally switched off. After the power was reinstated, the VRFOD did not immediately resume automatic operation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636409&prj=626&rqi=AvMzPfHWKexne79QVbI62jSVfi
GT1ELEC-48-004 | JK01-2 | APAC | Closed | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Please revise the graphic for STSSB_C_1 refer to STSSB_B_1, as they are one integrated equipment, not separate equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636447&prj=626&rqi=mpBMU60PUGKWt1SUntfBMBmNlj
BT1MECH-52-003 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_42 | DXID - FCU/DX Indoor Unit |  |  | There is a discrepancy in the room temperature readings between the thermostat and the LCP/DCOS (The readings on the LCP and DCOS are the same) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635587&prj=626&rqi=SEeooLDHh5XOc3K1FSqJrdhYUy
BT1MECH-54-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | There is a discrepancy in the room temperature readings between the thermostat and the LCP/DCOS (The readings on the LCP and DCOS are the same) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635569&prj=626&rqi=h5gZWQHTCcggkloOMsk388LLpq
BT1MECH-53-003 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_B_41 | DXID - FCU/DX Indoor Unit |  |  | During Simulate power failure for PICV actuator by disconnect power supply to the PICV actuator from control panel. After re-connect power supply, PICV closed first then open again to last position. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635490&prj=626&rqi=ToTgAY1Ryl9CMIFlMtNZePNgkW
BT1MECH-54-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | During alarm test, upon DXFCU power loss the alarm appeared for approximately 8 minutes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635489&prj=626&rqi=EfjVoFqcUj09zEPO55f7X6YgKO
BT1MECH-52-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_42 | DXID - FCU/DX Indoor Unit |  |  | During Start Stop Sequence (Auto Mode) LCP unit cannot be switched to Auto Mode (Need To Confirm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635586&prj=626&rqi=6g87nufIBwgQ2ZyMFPqTIttzul
BT1MECH-52-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_42 | DXID - FCU/DX Indoor Unit |  |  | During alarm test, upon DXFCU power loss the alarm appeared for approximately 8 minutes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635580&prj=626&rqi=PXHw96Q8zMcuwCvx8dqPhxGPXG
BT1MECH-53-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_B_41 | DXID - FCU/DX Indoor Unit |  |  | During alarm test, upon DXFCU power loss the alarm appeared for approximately 8 minutes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635488&prj=626&rqi=hHBXadGME5lGABkaUxk6fDmMVO
GT1MECH-86-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Fuel | equipment | 1LCP_FPUMP_A2 | FT - Fuel Tanks |  |  | Actual test regarding existing Pump function cannot perform due to incomplete PRV setting. Once it already done and can be test, please invite CTA to witness | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635227&prj=626&rqi=qCl7oacCvnq8He5g6apwcmZKrp
BT1MECH-53-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_B_41 | DXID - FCU/DX Indoor Unit |  |  | During Start Stop Sequence (Auto Mode) LCP unit cannot be switched to Auto Mode In SOO mention can Auto Mode Operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635234&prj=626&rqi=8Hc4Rhhs0sBp0myv2beXFBgJCw
GT1MECH-87-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Fuel | equipment | 1LCP_FPUMP_B2 | FT - Fuel Tanks |  |  | Actual test regarding existing Pump function cannot perform due to incomplete PRV setting. Once it already done and can be test, please invite CTA to witness | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635230&prj=626&rqi=lPYD4AXSX06liZNJx8qgJMJM9u
BT1ELEC-41-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | During CxL4 1RMU_D, Power meter at 1MSB_D_1 shows an inaccurate kW reading compared to the actual load | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634714&prj=626&rqi=m8qvfMBzBaJ4s5PRBVbddlZCdJ
BT1MECH-51-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | During indoor trip alarms no alarm verified at DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634345&prj=626&rqi=WcTZs4OEwCelFBYfxR5EoeRqnz
GT1MECH-25-003 | JK01-2 | APAC | Ready for Verification | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634312&prj=626&rqi=ORHBkofdroWfLPVk1eMo59neiP
GT1MECH-79-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_2.01 (Existing) | PAV - Pre-Action Valve |  |  | Integrated testing with CRAY has not been performed when the 1st alarm, CRAY will ramp down. Orient to perform this test with Vertiv and make a report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634257&prj=626&rqi=fPv54ozhboKQaAvMjzQft8pprl
GT1FD-1-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Fire Detection | equipment | 1FAS_2 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634252&prj=626&rqi=Srt0C8JCLAIP14M4bWlQqc41L6
GT1MECH-27-003 | JK01-2 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634306&prj=626&rqi=S8mO3tvi6d2XjwLM67BjyMFGxY
GT1MECH-26-002 | JK01-2 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634307&prj=626&rqi=uYrBymqeRURz8urAAlO5umM7cV
GT1MECH-26-003 | JK01-2 | APAC | Ready for Verification | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634308&prj=626&rqi=HCVR4wR0JHA9acdT4Y1j8URlOx
GT1MECH-27-002 | JK01-2 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634305&prj=626&rqi=9afTKc0FTIbIMcZrKcoTUJAXmY
GT1MECH-24-003 | JK01-2 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634309&prj=626&rqi=3zJoYG6rM7CMCsm6yx0WnSqwtn
GT1MECH-24-004 | JK01-2 | APAC | Ready for Verification | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634310&prj=626&rqi=c2WMJiebvwE7H513RAk84gMImk
GT1FD-6-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Fire Detection | equipment | 1FAS_7 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634256&prj=626&rqi=KQR6nUPEIQ04hduIH5lpITm9GQ
BT1MECH-51-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | During Fail compressor by failing power to compressor. Verify Loss Communication alarm at DCOS. FCU remain running on site is off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634360&prj=626&rqi=hwxlYlAIHjXDJJEuuOrCI3Hyf7
GT1FD-5-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Fire Detection | equipment | 1FAS_6 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634255&prj=626&rqi=hJNVy3wvcFFmISGEI2AdgMMqEm
GT1FD-4-001 | JK01-2 | APAC | Open | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Fire Detection | equipment | 1FAS_5 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634254&prj=626&rqi=6ECL0hHNNSHhQzUgWQINLCQk0i
BT1MECH-51-003 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | During Start Stop Sequence (Auto Mode) LCP unit cannot be switched to Auto Mode In SOO mention can Auto Mode Operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634361&prj=626&rqi=qBkeyWju6LpITChMEFbXSEdhEG
BT1MECH-51-004 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | During Start Stop Sequence (Manual Mode) PICV water flow 1.5 (PICV water flow available (â‰¥1.6 lps)) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634362&prj=626&rqi=JLUKsHTlrkMaJMe3ggGAtSBZGF
GT1MECH-25-002 | JK01-2 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634311&prj=626&rqi=rHGzbbZVTxdvGnxts9JPx0iHb7
GT1FD-3-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Fire Detection | equipment | 1FAS_4 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634253&prj=626&rqi=sMztyw6RlmBIs9GrrxXcOp8zpH
GT1MECH-77-004 | JK01-2 | APAC | Ready for Verification | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634166&prj=626&rqi=ddudyyRDdXVJsBG5TFRIRxMr4J
GT1MECH-78-002 | JK01-2 | APAC | Ready for Verification | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634167&prj=626&rqi=AYzVrpSEw3l8MeTepno0okfv4B
GT1MECH-75-002 | JK01-2 | APAC | Ready for Verification | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634165&prj=626&rqi=YHPkPaMn1pxdxfWXouOoYExLuN
GT1MECH-76-006 | JK01-2 | APAC | Ready for Verification | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634080&prj=626&rqi=JUzVhCiNMdDy42ZcUqv4G7C7f8
GT1MECH-35-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-08-18 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | During airflow measurement test, blanking panel beside Cool Array unit are bend / curved when running 100% fan speed of Cool Array test | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634048&prj=626&rqi=2NdFb4gxK1EOnDJxBS5m7YuweL
BT1FD-5-002 | JK01-2 | APAC | Open | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_5.01 | PAV - Pre-Action Valve |  |  | During CxL4 (Water Discharge Test) some issues are discovered; - The LED indicator floor mimic panel doesn't ON during 1st & 2nd alarm (DONE) - There's a water leak/splash on water gong (DONE) - Need to add support for drain pipe at sprinkler Control Valve Room (DONE) - install flow direction sticker for fire pipe at some point (DONE) - Seismic Bracing not installed yet (DONE) - Wire burn in HAC & CAC will be test during IST (FYI) - Need to add installation isolation valve after flow switch (suggestion from FMG) --> for future maintenance (FYI) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638414&prj=626&rqi=Ft4P2bkIdeSwJHQ6m0vTQ8xVu2
BT1FD-6-002 | JK01-2 | APAC | Open | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | During CxL4 (Water Discharge Test) some issues are discovered; - There's a water leak/splash on water gong 7th floor (DONE) - Need to add support for drain pipe at sprinkler Control Valve Room (DONE) - install flow direction sticker for fire pipe at some point (DONE) - Seismic Bracing not installed yet (DONE) - Wire burn in HAC & CAC will be test during IST (FYI) - Need to add installation isolation valve after flow switch (suggestion from FMG) --> for future maintenance (FYI) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638411&prj=626&rqi=0LRe5xJaiHTOYfnCKeer3cGVig
BT1FD-4-001 | JK01-2 | APAC | Open | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | During CxL4 (Water Discharge Test) some issues are discovered; - Need to add support for drainpipe at the Sprinkle Control Valve Room (DONE) - install flow direction sticker for fire pipe at some point (DONE) - Seismic Bracing not installed yet (DONE) - After the test, leakage was found in 1st floor piping that makes Jockey Pump starts running continuously (DONE) - Wire burn in HAC & CAC will be test during IST (FYI) - Need to add installation isolation valve after flow switch (suggestion from FMG) --> for future maintenance (FYI) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638415&prj=626&rqi=j9gRTkkRS5C10HFJHrZyAvXAhz
BT1ELEC-30-005 | JK01-2 | APAC | Open | P1 High CX | fauzanfikri@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Based on discussion between Aurecon, CTA, TnT, Altrak & GC regarding the phase unbalance issue during CxL4 1UPS_D_1, Altrak is required to investigate the issue and provide an RCA (Root Cause Analysis) for the phase unbalance observed when step load using generator source Issue related: During load step-up to 75% with Generator source, MSB panel detected a phase unbalance, causing power source automatically transfer from Generator to Utility. The same 75% load step-up was repeated using Utility source, and no phase unbalance was detected and remained stable at 75% load | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633390&prj=626&rqi=MjTFaR2P9t94VK2y6T7wdj6aN3
GT1MECH-76-005 | JK01-2 | APAC | Open | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633408&prj=626&rqi=1l5UuGN74Px2IRWeXqtWoSAYOI
GT1MECH-77-003 | JK01-2 | APAC | Open | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633412&prj=626&rqi=vtcqq9CFDCmpYyX0mRs6Va3qxN
GT1MECH-75-001 | JK01-2 | APAC | Open | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633411&prj=626&rqi=LpP4bvpseesgMSLPqm0lyJTRMf
GT1FD-2-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Fire Detection | equipment | 1FAS_3 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633417&prj=626&rqi=lk2KZwweIaW2PWySHB2SctWKDH
GT1MECH-78-001 | JK01-2 | APAC | Open | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633410&prj=626&rqi=tFzX2VYndeEhQLkv6k6qUmmhLe
YT1ELEC-155-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | ( Issue CxL2A Laying cable from DB_FOH_7_L to DB_DALI_L7) Need install labelling at FOH side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633151&prj=626&rqi=X0oaryyCZEpkgbSkDOcScZDQGq
GT1ELEC-155-001 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Controls | equipment | 1PANEL_I/O_Motorized Damper | CP - Control Panel |  |  | During the HRA activity for the MAU motorized damper programming and commissioning activity, the following items were identified: 1. Update the SoO flowchart to reflect the actual operating condition and obtain approval from the AE. 2. During a power failure, the actual motorized damper remains closed, rather than returning to the last position as currently stated in the SoO. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633221&prj=626&rqi=2kecMiH7CQbkDPdt1bOI1zFfPR
YT1ELEC-152-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L4 | DB - Distribution Boards |  |  | ( Issue CxL2A Laying cable from DB_FOHA_4_L to DB_DALI_L4) Need install vinyl netral and grounding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633150&prj=626&rqi=rnlKjPQmO9WBQFMv7R5oZs1FDu
GT1ELEC-9-001 | JK01-2 | APAC | Closed | P2 Medium DCOS | DimasKurniawan@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | For (FDAY) DCOS P2G verification related to Valve Command and Valve Feedback, GC need to coordinate with related parties to perform those tests. And after test already perform, Orise need to revise their report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633011&prj=626&rqi=CiU7lcXyWiyVPwTw6JhSvvn3wW
GT1ELEC-7-003 | JK01-2 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | For (FDAY) DCOS P2G verification related to Valve Command and Valve Feedback, GC need to coordinate with related parties to perform those tests. And after test already perform, Orise need to revise their report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633006&prj=626&rqi=DoCp2AcP8ajXF4eoy30x7SOghS
GT1ELEC-6-001 | JK01-2 | APAC | Closed | P2 Medium DCOS | DimasKurniawan@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | For (FDAY) DCOS P2G verification related to Valve Command and Valve Feedback, GC need to coordinate with related parties to perform those tests. And after test already perform, Orise need to revise their report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633009&prj=626&rqi=9FynJmU8HWMrn8Zp1WKOGelRxN
GT1ELEC-8-001 | JK01-2 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | For (FDAY) DCOS P2G verification related to Valve Command and Valve Feedback, GC need to coordinate with related parties to perform those tests. And after test already perform, Orise need to revise their report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633010&prj=626&rqi=9Bw0KZQiw4pfr5ogx9uIoENon2
BT1ELEC-40-001 | JK01-2 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Key "K3" on Solenoid box can't take out during process reinstate the maintenance bypass for UPS, because UPS OFF conditions and thereâ€™s no power on HMI, so that can't send the signal to Solenoid box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633008&prj=626&rqi=xry6eN4p0EmqmZAWOdmMaC88f5
GT1MECH-73-002 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_5.01 | PAV - Pre-Action Valve |  |  | (Only for Record) During the PASCV C&E Matrix testing, a smoke detector was triggered in the data hall. At that time, the CRAY team had not yet confirmed whether the CRAY unit would ramp down as expected. Therefore, Orient and Vertiv conducted an internal test and invited CTA to witness the test and close this issue. (Orient already installed the cable and module). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632818&prj=626&rqi=yOpcBapUpUMwu0a16My0ZywD9z
GT1FD-7-002 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-2.04 | VES - Vesda |  |  | Based on the current ASDSP point list, new loop-3 integration to DCOS points have not yet been configured and programmed. See the HLI Modbus List for reference. Be sure to retest after configuration. (Responsibility Orient and Orise, with escort by GC) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632821&prj=626&rqi=pWGYIuHemTahXeUTHTJ9oa3fRP
GT1MECH-72-002 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | (Only for Record) During the PASCV C&E Matrix testing, a smoke detector was triggered in the data hall. At that time, the CRAY team had not yet confirmed whether the CRAY unit would ramp down as expected. Therefore, Orient and Vertiv conducted an internal test and invited CTA to witness the test and close this issue. (Orient already installed the cable and module). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632817&prj=626&rqi=sTMmw1dJEopoBmN0p02ZpnuJSl
GT1MECH-74-003 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | (Only for Record) During the PASCV C&E Matrix testing, a smoke detector was triggered in the data hall. At that time, the CRAY team had not yet confirmed whether the CRAY unit would ramp down as expected. Therefore, Orient and Vertiv conducted an internal test and invited CTA to witness the test and close this issue. (Orient already installed the cable and module). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632819&prj=626&rqi=hjB8yalMwSKaPNpLW2Ouuqlp4w
BT1ELEC-39-001 | JK01-2 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Key "K3" on Solenoid box can't take out during process reinstate the maintenance bypass for UPS, because UPS OFF conditions and thereâ€™s no power on HMI, so that can't send the signal to Solenoid box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632779&prj=626&rqi=EwhU0OtzdbFvfpoZ50PhhvIem6
BT1ELEC-32-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | During CxL4 1UDP_F_2 testing, abnormal sound/noise was observed from UPS unit during operation at 100% load on inverter mode | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632777&prj=626&rqi=O2dU70sSBmujI4ohDEBkZbvN2d
GT1MECH-72-001 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | When the solenoid valve and PASCV are activated, the flow switch is active but the monitoring on the MIMIC and panel does not match with C&E Matrix. Need to check and retest and invite CTA for closing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632730&prj=626&rqi=jAfCA22VyUjdxyl63BNFZW1AZu
BT1MECH-6-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | During Fan Speed Control (Group Control) Unit CRAH not response (Simulate the Return Temperature sensor set point lower than the current Return Temperature Sensor Value (Average sensor value) Fan speed does not increase | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632690&prj=626&rqi=1XZkCtItMcp1kYbtxnsOnU2HqJ
BT1MECH-6-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | During Fan Speed Control (Group Control) Unit CRAH not respone (Simulate the Return Temperature sensor set point higer than the current Return Temperature Sensor Value (Average sensor value) Fan speed not decrease (STULZ) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632691&prj=626&rqi=BQJaFGCd22vQE69bUROntYSqws
GT1MECH-73-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_5.01 | PAV - Pre-Action Valve |  |  | Need to touch-up painting pipe and install flow direction. Manual Call Point (Z3-MP-10) need to install ID tag. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632655&prj=626&rqi=o00VUtpb8noJyjIFaH7V7xDpIp
BT1ELEC-26-002 | JK01-2 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Key "K3" on Solenoid box can't take out during process reinstate the maintenance bypass for UPS, because UPS OFF conditions and thereâ€™s no power on HMI, so that can't send the signal to Solenoid box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632752&prj=626&rqi=Iu3ypWTv39k0O20uhIF5pBauNp
GT1MECH-2-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | Please provide report cable for sensor CH4, H2 and CO. And revise acceptance criteria (on the MoS) of these 3 tests according to Approve SoO. Attach photo once it done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632735&prj=626&rqi=LzrynMk3scU9Rnwue0cDkX34Ay
BT1MECH-6-003 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | During Grouping Failure / Lost Communicationâ€ alarm not appears DCOS, and on CRAH display not have sign alarm, only sound alarm on CRAH Unit (STULZ) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632692&prj=626&rqi=5RmHzUeqe7SU72BSAncRfqrkk9
BT1MECH-11-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | During Water Leak Alarm test, the module sensor did not respond (usually the indicator lamp is on, but this off) Stulz to rectify this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632499&prj=626&rqi=Xns42CN6M4V3safNCz05t8rPtN
BT1MECH-1-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | During Fan Speed Control (Group Control) Unit CRAH not respone (Simulate the Return Temperature sensor set point higer than the current Return Temperature Sensor Value (Average sensor value) Fan speed not decrease (STULZ) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632492&prj=626&rqi=VD7jFz0pL5r0iqSmNB5kc3lvVB
BT1MECH-1-003 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | During Grouping Failure / Lost Communicationâ€ alarm not appears DCOS, and on CRAH display not have sign alarm, only sound alarm on CRAH Unit (STULZ) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632493&prj=626&rqi=w9nYhfPscdVYsAiIOi634OVxoH
BT1MECH-1-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | During Fan Speed Control (Group Control) Unit CRAH not response (Simulate the Return Temperature sensor set point lower than the current Return Temperature Sensor Value (Average sensor value) Fan speed does not increase | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632277&prj=626&rqi=TW6s0uj9dUjrjfoBCKgekcZxpT
BT1MECH-12-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-08-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | During simulate of supply air temperature sensor failure, CHW Valve cannot modulate open to Vmax | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632102&prj=626&rqi=ZD7NyAnZQU1G0bqrmGevJ7BgiR
GT1MECH-72-003 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | During the low-pressure simulation, a discrepancy was identified between the actual panel status and the C&E Matrix Rev. 04. The actual panel status is shown as Supervisory, while the C&E Matrix indicates an Alarm. Please clarify the intended status and confirm the correct sequence. If the C&E Matrix requires revision, the updated C&E Matrix shall be reviewed and approved by the Design Team. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633020&prj=626&rqi=7N5Ehrvc5Zb5WaK5ZmQtRwx4YS
GT1FD-7-001 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-2.04 | VES - Vesda |  |  | (For All ASDSP issues) During the L3 ASDSP testing, the ASD workstation was not ready, as an additional VHX 1200 module was required for configuration and programming. After the installation is completed, the vendor and GC shall retest the ASDSP functionality. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632820&prj=626&rqi=y3FO3gc5c39UA3Cf82y4SKsNkA
BT1ELEC-29-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | On DCOS & HMI UPS input phase-to-phase voltage displayed phase-to-neutral voltage values | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631945&prj=626&rqi=lmrIooy3W2ZxyVyiws7t2im8Vg
YT1ELEC-123-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Discrepancy between drawing and actual labelling, need update drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631736&prj=626&rqi=kdvq0NnE6JEthsJ1H1g0rnRFM2
YT1ELEC-14-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_A_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A 1UPS_A_2 to Libattsys_A_2) Labelling cable is incorrect, please change from 1UPS_A_2 to Libattsys_A_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631741&prj=626&rqi=hSKscQ26kG1ni5LxsCb4lccaYw
YT1ELEC-123-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | elevation socket outlet not align with shop drawing (refer attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631737&prj=626&rqi=T9PR3Kd6uJo78WTGTSV3G5NKPM
YT1ELEC-120-004 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Elevation socket outlet not align with shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631731&prj=626&rqi=C1CAQQd0iptlYxMUYrA5qDelBn
YT1ELEC-120-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Discrepancy between drawing and actual labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631728&prj=626&rqi=qrkWIa9ryvjEtuYahFYtFGd3CJ
YT1MECH-39-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | During Cx activity, found that one of support for return pipe (near PICV) are loose and not securely tight. Attach photo from same angle once already rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631727&prj=626&rqi=MJ3jV20v7Sk37WsX3wcNtFYqPf
BT1ELEC-30-004 | JK01-2 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Key "K3" on Solenoid box can't take out during process reinstate the maintenance bypass for UPS, because UPS OFF conditions and thereâ€™s no power on HMI, so that can't send the signal to Solenoid box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631944&prj=626&rqi=7cqkjQKNCy3ZtC2xNuymJlu2mP
YT1ELEC-23-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_G_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A 1UPS_G_2 to Libattsys_G_2) Vinyl install for cable (+) is incorrect . Please replace it with the black color | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631751&prj=626&rqi=gzMFNL4UKRRKbVxls8tyZNBayW
YT1ELEC-23-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_G_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A 1UPS_G_2 to Libattsys_G_2) Labelling cable is incorrect, please change from 1UPS_G_2 to Libattsys_G_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631753&prj=626&rqi=Uqm9Y5l1EEm04agjvhz5dUDGlW
YT1ELEC-14-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_A_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A 1UPS_A_2 to Libattsys_A_2) Vinyl install for cable (+) is incorrect . Please replace it with the black color | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631739&prj=626&rqi=w4oHOYp7U5UbXcQQBo0WAX5gaF
BT1ELEC-30-003 | JK01-2 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | During load step-up to 75% with Generator source, MSB panel detected a phase unbalance, causing power source automatically transfer from Generator to Utility. The same 75% load step-up was repeated using Utility source, and no phase unbalance was detected and remained stable at 75% load | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631943&prj=626&rqi=lLmGVdj8xpjhJrrWx6xSehlEav
BT1ELEC-33-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Inconsistent overload alarm threshold was observed between UPS units. UPS F2 (Mechanical UPS) triggered the overload alarm at 107% load (above 100% load), while UPS D2 (Mechanical UPS) triggered the alarm at 112% load (above 110% load). The overload alarm setting shall be standardized across all UPS unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631724&prj=626&rqi=UNpFc77A8jRiHYXlug6Lu48E3r
GT1MECH-64-002 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_41 | CRAH - Computer room air handler |  |  | During Waterflow Verification (PICV VMax) the HMI cannot show the value of Opening Chilled Water Valve, while in DCOS it appears. Stulz needs to rectify, attach photo once it already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631444&prj=626&rqi=x3yEJ1eGcp4RBmelGYVG0B6bNy
GT1MECH-74-002 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | During Low Air Pressure Switch Function + 1st Alarm Test, Solenoid and Flow switch is not triggered, need to check and re-programming with latest Cause and Effect Matrix | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631443&prj=626&rqi=0vrVfBfIh2WwwC5Cdtp2Bx02BM
GT1MECH-74-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | During CxL3 activity, ID tagging valve for PASCV 7.01 are not installed yet. Pipe direction sticker also not installed yet, please provide. Once all been done, please attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631429&prj=626&rqi=rstk9WWqpGSfNnZL5uvZotdfr6
GI-031 | JK01-2 | APAC | Open | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | The gaps between CA need to be sealed off (for all floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631105&prj=626&rqi=LkbKwQTeW1AEsdxRE7I6n91Cez
GT1ELEC-51-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631012&prj=626&rqi=QUu04Vf4OrbC9a4Jyux7EhO606
YT1ELEC-167-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630863&prj=626&rqi=XXd0KQqd7zsDPip4DzbQjmZpzJ
BT1ELEC-30-002 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | During UPS overload test, DCOS indicated "Battery Discharge" alarm even though the UPS was not operating on battery mode (ORISE) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630999&prj=626&rqi=4MOI9ALHtpBeZQhIdkfzpKDsfH
GT1ELEC-49-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631008&prj=626&rqi=2eBBiP20Mbzl1YBmt7uE2JkLvM
GT1ELEC-49-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631009&prj=626&rqi=jsoorpfIqnet3yOfVHSspVIYnV
GT1ELEC-50-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631174&prj=626&rqi=Jhdvv8USzCdfmzRZW8TCFZ1ND4
GT1ELEC-51-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631011&prj=626&rqi=Z7YgA1eM64JsDNvWgUU1RpzV2U
YT1ELEC-170-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630874&prj=626&rqi=4ft8J0VI9XUgi63c3vs4ZFxbiN
GT1ELEC-50-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631010&prj=626&rqi=yZBvXICjfsE5c6FZML1plMWbWu
GT1ELEC-46-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631003&prj=626&rqi=zvjsxeAY0qQP77Bo1K0bJp0sgK
YT1ELEC-164-007 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630864&prj=626&rqi=SZ9eB6DBqrYoQQ8MfcVT7fYgQA
GT1ELEC-47-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631005&prj=626&rqi=X6C7d1EPHIRDBVk46sOn2CSTFG
GT1ELEC-48-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631007&prj=626&rqi=QvgIP3dbKahKFaCXv4zTgTDNaE
GT1ELEC-48-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631006&prj=626&rqi=OBz66Czq7A4EiEH12rjZLHkMVf
GT1ELEC-46-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631002&prj=626&rqi=FBAaQnECviYzChFXWZgy5lFi5Y
YT1ELEC-166-007 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630869&prj=626&rqi=mHvi43xdZ9uYdUZ9DV4k793P5s
YT1ELEC-165-004 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630866&prj=626&rqi=jJKz82iDUgmBbXL0kYXGX80dMc
BT1ELEC-30-001 | JK01-2 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | During 50% load step-up on Generator source, 1MSB_D_1 panel unexpectedly switched back to Utility. When trying to transfer the power source back to Generator, Breaker QE (Generator incomer) failed to close even though the Generator was running | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630998&prj=626&rqi=qMh64GXYg2YmmWyDwCDZhyp2qw
YT1ELEC-169-008 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Rrom readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630873&prj=626&rqi=Sxog0DOnuNpD643Kabc3E0A3VU
BT1ELEC-33-001 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Status of operation mode UPS after Overload Test, UPS status is Static bypass (Load on Bypass in DCOS), but in DCOS shows Load on Inverter | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630835&prj=626&rqi=2IS2brsHxjMkJT3cKSxqfEyWzK
GT1ELEC-52-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631013&prj=626&rqi=DeP7sDkrjT4PoIMVxD5u6O8yWY
YT1ELEC-168-005 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630868&prj=626&rqi=TJodAsM2oBYj0JWPMxw0T9IhJr
GT1ELEC-53-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631176&prj=626&rqi=kZS9OS0ITYz4LRP2gAMPehNhUa
YT1ELEC-171-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630875&prj=626&rqi=tHhAVn7wv0NBbZOK7uhQdfQqu8
GT1ELEC-53-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631177&prj=626&rqi=CpqtpW1xPoCLHxypukPHpQtf3p
GT1ELEC-52-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631014&prj=626&rqi=8TBfavxcr5oXLAaiWSxHHn5yJV
GT1ELEC-47-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631004&prj=626&rqi=BAnF5Nh7fuyYJMOzbSEj3CMV1M
GI-030 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | All the sharp edges (which is in contact with the cable) need to be protected with rubber protection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630627&prj=626&rqi=OjxkNodgBwYoCNHSJPzoNRAmsE
GT1ELEC-7-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Voltage Dip during Block Load Test 0%-100%-0% out of tolerance. 418 to 280 Volt (above 20%) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630674&prj=626&rqi=t6jSIcWuVZtDo5qltRp0GwBKNi
BT1ELEC-28-002 | JK01-2 | APAC | Open | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | During UPS transition from Normal Mode to Dynamic Mode, the DCOS graphic did not update. The operating mode remained displayed as "Load on Inverter" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630608&prj=626&rqi=4btz5G1BXMKOKzMCyEY9pUUgzb
BT1ELEC-28-004 | JK01-2 | APAC | Open | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | During the Maintenance Bypass test, Key K3 at MSB solenoid box could not be released after switching sequence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630610&prj=626&rqi=MlTy937BgmiwXQ5JW4EZAXKJbh
GT1ELEC-7-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Frequency Dip during Block Load Test 0%-100%-0% out of tolerance. 50Hz to 41.88 Hz (above 10%) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630675&prj=626&rqi=nb1yyAI4hX8sp7pwFjUGlxMEFG
BT1ELEC-28-001 | JK01-2 | APAC | Open | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-07-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | During UPS transition from Normal Mode to Eco Mode, the DCOS graphic did not update. The operating mode remained displayed as "Load on Inverter" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630607&prj=626&rqi=3xAXSfIou88nfbIozPda5vt40b
BT1ELEC-28-003 | JK01-2 | APAC | Ready for Verification | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | During UPS overload test, Overload Alarm was not triggered even though the UPS load reached 110% of rated capacity | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630609&prj=626&rqi=eSckdtArAfHnJfPocnem6lppUf
YT1MECH-60-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | Tidy Up Fire Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630228&prj=626&rqi=sETMzxtQdPeKbwi5yJ9l4DV9K2
YT1MECH-62-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | Take Out Material Not Use | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630238&prj=626&rqi=pF9s4yr7D0RrkUDC39AGWScNv6
YT1MECH-62-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | Completed Termination Cable PICV | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630237&prj=626&rqi=gEobiXflCEabqnwLAx9CevANyp
YT1MECH-59-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | Tidy Up Fire Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630224&prj=626&rqi=YCa7MwSZW9iVGeSnLAL9xbO2Nn
YT1MECH-60-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | Completed Termination Cable PICV | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630226&prj=626&rqi=cmTgrmo4kptWgF0yh24xRwH6Cz
YT1MECH-62-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | Tidy Up Fire Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630239&prj=626&rqi=KzjaEqqCT0Q2TORKBtiVadDXlJ
YT1MECH-61-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | Completed Termination Cable PICV | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630230&prj=626&rqi=0nscpArOZmJNmeiTGP1EL3jpLJ
YT1MECH-60-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630225&prj=626&rqi=aHIpkj9vRTnzsPWkxC6F2TsUNk
YT1MECH-59-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | Take Out Material Not Use | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630223&prj=626&rqi=lNdUMDOIlG0BhxkxWixUlSAvBt
YT1MECH-59-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630221&prj=626&rqi=hpn7ruSWQgRV83vlhxCIFik00Q
YT1MECH-60-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | Take Out Material Not Use | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630227&prj=626&rqi=FxLvwyUIxf3m8youtXT30RWV1M
YT1MECH-61-005 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | Tidy Up Flexible Installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630233&prj=626&rqi=lSd3UXpQSorq0d4pKC2Daxon1e
YT1MECH-61-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | Take Out Material Not Use | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630231&prj=626&rqi=FWIUWfksOw4bmubHAjdW1rI8HL
YT1MECH-59-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | Completed Termination Cable PICV | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630222&prj=626&rqi=NCaP91zSLiplMCvkQy5Bg7atJp
YT1MECH-62-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630236&prj=626&rqi=xE6EWCBYds3g4UAxmJLgctFnXZ
YT1ELEC-6-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630310&prj=626&rqi=j0yZooXlYbFXE7escYpjpT2NrL
YT1MECH-61-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630229&prj=626&rqi=GilWXjUiKlHIVNaVfy5PqdHH6R
YT1MECH-61-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | Tidy Up Fire Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630232&prj=626&rqi=fhKKODUrwjrELPDSrizN5Y5mZA
GT1MECH-76-004 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | During the verification of the flow reading between FM and the handheld tools, witnessed by CTA. The flow readings from FM and Pump HMI are consistent. However, the handheld measurement at the orifice balancing point does not match and shows fluctuating results, indicating a potential issue with the orifice. GC is required to obtain a formal statement letter from the orifice manufacturer/principal to clarify and justify the discrepancy. Compare with CHWP 2: with the same tools (the results are good and not much different) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630095&prj=626&rqi=KXvGgoh99jIbhtRvwJ1A8sQ5rq
GT1ELEC-17-002 | JK01-2 | APAC | Open | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Several points have not been tested: This includes all UPS units. - Output Overload - Output Alarm - Overload Shutdown - Rectifier Fuse - Total Output kW - Input Breaker Open - Low Battery Alarm - Battery Amps - Battery Time Remaining Status | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630169&prj=626&rqi=hAdTgkxNiQSTYIQPdiq3mKbq0A
GT1MECH-77-002 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | During the verification of the flow reading between FM and the handheld tools, witnessed by CTA and attended by the Orifice Balancing principal, an anomaly was identified between the FM and handheld readings. GC shall investigate the discrepancy and provide clarification/ statement letter with principle regarding the observed measurement results. CHWP 4: FM: 43 l/s ¦ Handheld: -0.1 kPA (appx. 7 l/s) Compare with CHWP 2: with the same tools (the results are good and not much different) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630074&prj=626&rqi=WHAiaZWpQa0qeEX9xyRqDN1R0a
YT1MECH-57-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | Completed Termination Cable PICV Valve | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629981&prj=626&rqi=Hw8uqhDq0pARMoTrn0TiImcZWH
YT1MECH-57-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629980&prj=626&rqi=fTqTMjgkFpO3JXdg4IHVh6uEBD
YT1MECH-58-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | Completed Termination Cable PICV | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629984&prj=626&rqi=S4w8pVkwOVuteKpDFCJA3imkNA
YT1MECH-58-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | Tidy Up Fire Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629986&prj=626&rqi=HmR40045cfKOY7Z4IXZlWH9Wrk
YT1MECH-57-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | Tidy Up Fire Cable at CA unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629982&prj=626&rqi=mHBjX2J7BKr9G9fLOs0tdDMRJM
YT1MECH-58-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | Take Out Material Not Use | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629985&prj=626&rqi=pmqXBDMfgzLH3jWagxGgDPfbCz
BT1ELEC-26-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | During the preparation for the UPS B_1 L4 (Burn-In) test, a cable was found to be in contact with the busbar. Once finish burn-in, install additional rubber protection on the cable, as over time the cable may come into contact with the busbar again. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629978&prj=626&rqi=ZVCG7tS6f5iTW1xcuNyoTvs2mW
YT1MECH-58-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629983&prj=626&rqi=HB4MsKom4uJIDVHxYr106AErW7
YT1MECH-43-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Completed Install PICV Cable_CA Response in issue must take evidence each of equipment in Block D (5th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629354&prj=626&rqi=8jvlT78hIWwGFBgbC49h5UjOVA
YT1MECH-43-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Completed Termination Cable Sensor_CA Response in issue must take evidence each of equipment in Block D (5th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629356&prj=626&rqi=WZUAwopt69pubrONFXxTo9ZDFS
GT1MECH-76-003 | JK01-2 | APAC | Closed | P1 High CX | MulyaSitanggang@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | A leakage has been identified on the CHWP-03 pipeline. Please provide an explanation of how this issue could have occurred, including a detailed Root Cause Analysis (RCA). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629352&prj=626&rqi=slzdsLlREpOqZLkvaX2NIZonPO
YT1MECH-43-005 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Take out material not Use_CA Response in issue must take evidence each of equipment in Block D (5th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629357&prj=626&rqi=bZ0jQRJvMLomuLUv6A8JHjRuy7
YT1ELEC-162-002 | JK01-2 | APAC | Closed | P2 Medium DCOS | DimasKurniawan@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | General Contractor | L2B | DCOS Installation not complete | DCOS | Electrical â€“ LV | equipment | 1Fuel Leak_L3 | LEAK - Leak Detection |  |  | The DCOS cable hasn't been pulled to the panel, even though the drawing shows a DCOS connected to the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629412&prj=626&rqi=Z3eiUIHJbJzzLShzJWtSYKs1vN
YT1MECH-43-006 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Tidy Up Flexible Installation_CA Response in issue must take evidence (report) each of equipment in Block D (5th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629359&prj=626&rqi=pjdBaAYPal6PKqGl9d2w8OVYzt
YT1MECH-50-004 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_C_01 | CA - Cool Array |  |  | Kindly Provide Report for Installation Flexible pipe (completed sign off TNT and CTA) Response in issue must take evidence/report each of equipment in Block C (4th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628858&prj=626&rqi=BoBiHQV27vuqqqqAm2hhi0vWsP
GT1ELEC-48-001 | JK01-2 | APAC | Open | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L3 | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Key interlock on ACB is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630617&prj=626&rqi=FQB54apHvfm0SROPnFoqMxQhBI
YT1MECH-50-003 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_C_01 | CA - Cool Array |  |  | Kindly Termination All Cable Installation at Sensor unit Response in issue must take evidence each of equipment in Block C (4th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628855&prj=626&rqi=bRxikHyANzJKEtKVqYZMfIeQv4
GT1MECH-76-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | During CxL3 Running Pump, leakage in flange connection pipeline | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628844&prj=626&rqi=f2Rmshp7nulI3E2s9WGe1RE9lm
GT1ELEC-50-001 | JK01-2 | APAC | Open | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L3 | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | Key interlock on ACB is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630618&prj=626&rqi=tcmXbx36sTD246ww1B3Yg8J5Ei
GT1ELEC-53-001 | JK01-2 | APAC | Open | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L3 | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Key interlock on ACB is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630619&prj=626&rqi=CfZgqU6n1nbojWdCAAJkdEy7PW
YT1MECH-50-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_C_01 | CA - Cool Array |  |  | Kindly Tidy Up All Cable Installation (Cable Sensor) Response in issue must take evidence each of equipment in Block C (4th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628854&prj=626&rqi=wHQfZ3WmFxxyWdkdlnTL5ZD8Yc
GT1MECH-77-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | During CxL3 Running Pump, leakage in connection pipeline | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628846&prj=626&rqi=ntl4PQByAJHHUdvTAfoiIbkqjK
YT1ELEC-9-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628852&prj=626&rqi=8OZTPzo9swCOTCPHUMS9M98eEZ
YT1ELEC-46-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628735&prj=626&rqi=Vg9Qc8zrSa1zgOPvin9QH3gSgW
YT1ELEC-7-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628725&prj=626&rqi=TVUB2LVYKsLJYwQJyFvC6W0tgk
YT1ELEC-47-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628736&prj=626&rqi=6VfDfsE3kLewCqnevILddBM6kR
YT1ELEC-168-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Wrong cable termination location. The cable from 1MDSB_R1_2 to 1TOU_F_2 has been terminated at the wrong breaker Q1-3 at 1MDSB_R1_2 side. The correct termination point is breaker Q1-6. Please rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628708&prj=626&rqi=R3j1OYJdDZWe9KiUteGXtRcQxf
YT1ELEC-165-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Wrong cable termination location. The cable from 1MDSB_R1_2 to 1TOU_C_2 has been terminated at the wrong breaker Q1-6 at 1MDSB_R1_2 side. The correct termination point is breaker Q1-3. Please rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628706&prj=626&rqi=yyQbl3iifg213HIZh4DX6spKL3
GT1ELEC-17-001 | JK01-2 | APAC | Open | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Based on UPS Point-to-Graphic (P2G) test results, several DCOS points have not yet been tested. Please complete the testing for the following points: (will be verify during CxL4 ) 1. Battery Amps 2. Battery Discharge 3. Blower Fan 4. Alarm 5. DC Cap Fuse 6. Output Overload 7. Overload Alarm 8. Overload Shutdown 9. Rectifier Fuse 10. Total Output kW | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628675&prj=626&rqi=QCCPJefARSw6INdLpG8u5dOO9w
YT1MECH-40-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_06 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628569&prj=626&rqi=tUbAttpMlF7Dnnq6jwEsPQfFae
YT1MECH-79-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_1 | FFU - Air Scrubber |  |  | Cable Straight Not Straiht | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628531&prj=626&rqi=Ko5GrCXvZOHAwiktwBT93QCUXZ
YT1MECH-38-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_B_03 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628554&prj=626&rqi=VWEKJA7eDkt9L2pPT6uhxPVZCJ
YT1MECH-36-004 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH already pulled but need to tidy up and installed properly. Cable test also not perform yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628543&prj=626&rqi=KjQofd35ht9lZVkybw4JsUveE1
RT1ELEC-169-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Controls | equipment | 1PANEL_I/O_Motorized Damper | CP - Control Panel |  |  | equipment name / labelling onsite does not match with name on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628512&prj=626&rqi=SBr2b5EloN2cKfBZ9q2CK303OS
YT1MECH-41-004 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH are not yet pulled. When the cable already pulled, please do the installation properly and attach photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628560&prj=626&rqi=8mKfCY9pNDDRPdK6KdykWhPqeY
YT1MECH-40-005 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_06 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628576&prj=626&rqi=wOnoOS0Owd3PK3DJ61WUEZFwZ4
YT1MECH-41-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628570&prj=626&rqi=J7om1aVk1xUVGaRDEjssMma73b
YT1ELEC-18-010 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | kattyrachmawati@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | White glove inspection/FOD report not yet submitted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628491&prj=626&rqi=KPJUArLvxRlgOvbgbsQBsU8H6l
YT1MECH-41-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628557&prj=626&rqi=ygyiBauMIWdSHYtq8jVx9Cbujb
YT1MECH-41-006 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628575&prj=626&rqi=9Kj3dHfAa33mPkPv5mlHGgo0fj
YT1MECH-39-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628555&prj=626&rqi=OWNLNV2LRqanOjJddURgUwvJUy
YT1MECH-38-003 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_03 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH already pulled but need to tidy up and installed properly. Cable test also not perform yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628564&prj=626&rqi=FJzgfX0r7mCosmTbHhj6h9tkdw
YT1MECH-79-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_1 | FFU - Air Scrubber |  |  | Completed Cable Installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628533&prj=626&rqi=mVEiKWLyocBGaSGD1hWTwCIe0W
YT1MECH-42-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628558&prj=626&rqi=hz4ILi11QTWz5njSD72ttMBoUp
YT1MECH-36-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628544&prj=626&rqi=anJbPi5EcbY7XJTWmHr6ujQv1T
YT1MECH-39-003 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH already pulled but need to tidy up and installed properly. Cable test also not perform yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628563&prj=626&rqi=qPzfEbl3t5aF4xy69WoRznkoDt
YT1MECH-36-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628528&prj=626&rqi=cPL4dmQBM540RN58i8Yk2lOzFz
YT1ELEC-8-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628548&prj=626&rqi=7i6JKTJsTtswKggf4TQU6Zy74k
YT1MECH-37-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_02 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628566&prj=626&rqi=lXk9CNW2nTkSOIvj8YhYeGIzm5
YT1MECH-42-006 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628574&prj=626&rqi=iuJMnGtC6zzD45VsfYUL2V2r9a
YT1MECH-39-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628568&prj=626&rqi=828phVZakVywSuwd3tJ8Zm0cB3
YT1ELEC-50-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628551&prj=626&rqi=k7AWmwthO0QSHzrf8NVdp0IEtC
YT1MECH-39-005 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628577&prj=626&rqi=5LABmi9SwAkM3mUz35OfSX1vtj
YT1MECH-38-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_03 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628567&prj=626&rqi=BSMQJICUp22jZQSI1um3L4gI55
YT1MECH-37-003 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_02 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH already pulled but need to tidy up and installed properly. Cable test also not perform yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628565&prj=626&rqi=EZM2DqdnMPL98Ta16qFPLKOGo8
YT1MECH-37-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_B_02 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628552&prj=626&rqi=V1rY7M76aLE4FxBCIKrflst1b6
YT1ELEC-49-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628550&prj=626&rqi=B5XOGeBFdSrLPU0TuoEdVCVNCf
YT1MECH-38-005 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_03 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628579&prj=626&rqi=TMWQLZfndJ6aHrY2w6KcuM6Um8
YT1ELEC-51-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628553&prj=626&rqi=VJ170aLnHjNAeUWJPpzvmVEYQB
YT1MECH-40-003 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_06 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH already pulled but need to tidy up and installed properly. Cable test also not perform yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628562&prj=626&rqi=7tMhNsNCZElZpXZ73oimfN1j0X
YT1MECH-40-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_B_06 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628556&prj=626&rqi=Mx0R4GcoQGZeE4giDepmRdH7U6
YT1MECH-42-004 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH are not yet pulled. When the cable already pulled, please do the installation properly and attach photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628559&prj=626&rqi=y6CIFbLT7sJULiwAK7vo9g2U8A
YT1MECH-42-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628571&prj=626&rqi=Ib82GBFB47UdT3DccSSby2Ckwf
YT1MECH-37-005 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_02 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628580&prj=626&rqi=NtnH22oaZHdycqEBR3e46pCUqw
YT1MECH-36-006 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628549&prj=626&rqi=nT2FdoYfg5UgkRkpSw4OBLLfkf
YT1MECH-79-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_1 | FFU - Air Scrubber |  |  | Label Equipment Not Straight | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628534&prj=626&rqi=UAoYydB53XThn8EkuceeM94IQo
RT1ELEC-29-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1UPS_G_2 | UPS - Uninterrupted Power Supply |  |  | Please upload following documents: 1. RFIT documents 2. Certificate calibration of Torque Wrench | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628300&prj=626&rqi=LrP4xikgqEROx6LALOuH4ehQdx
YT1MECH-76-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | Remove Silica From FFU Unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628308&prj=626&rqi=DdRDEppSweYeOl9XzkscqJNMTQ
YT1ELEC-30-007 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Please upload Torque Report Earthing Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628411&prj=626&rqi=eJQbVZSYyQpzuWAH5URk2yE4fq
YT1ELEC-29-011 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Please upload Torque Report Earthing Cable (not include on CxL2B earthing cable report) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628402&prj=626&rqi=8LLEOakaicgdKT2oopYP30k5C8
GT1ELEC-1-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L3 | Cleaning | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Top of panel found dusty. Please re-clean to minimize dust ingress into panel and busbar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628306&prj=626&rqi=eOFJt6oGjggyswgAmnYPZHzJRx
YT1MECH-69-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | Adjust Door FFU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628309&prj=626&rqi=iXlaJ0y2PABkQPYe7ujWyPXL5n
YT1MECH-78-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | Clean the dirt from the FFU unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628307&prj=626&rqi=y0qhvRNfRQSMNt9SAWcXBVZs8P
YT1MECH-67-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_4 | FFU - Air Scrubber |  |  | The FFU door is not closing tightly. Please adjust the door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628165&prj=626&rqi=966njXtdkBTTtdvDcayieckREP
YT1ELEC-25-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628182&prj=626&rqi=2PFUScDHqNQt9mIMIcUCN1l96N
YT1ELEC-26-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628183&prj=626&rqi=ekRgzWP6zAz6ap9gX6GZIYODXH
YT1ELEC-32-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628185&prj=626&rqi=8Fx8GEsk3apXbwTUstqErIiI1Q
YT1MECH-66-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_3 | FFU - Air Scrubber |  |  | The FFU door does not close smoothly. Kindly adjust the door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628164&prj=626&rqi=LNgQAtbIz0rMFUSydgcwJDUMbO
YT1MECH-65-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_2 | FFU - Air Scrubber |  |  | The FFU door does not close smoothly. Kindly adjust the door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628163&prj=626&rqi=3797DVWgkYRlZqf9h3VNkWP4mM
YT1ELEC-31-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628184&prj=626&rqi=KMg6QjheRdPqJKrrVyrLFAOyyG
GT1MECH-76-001 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | During the Internal CxL3 Pump Performance Test witnessed by CTA, a discrepancy was observed between the flow rate reading displayed on the Flow Meter/SCP Panel and the Pump HMI. (SCP Display: 46 Hz --> 64 L/s and HMI Pump: 46 Hz --> 11.43 L/s) Further investigation is required to verify which reading accurately represents the actual flow rate and to ensure the displayed values are correct and consistent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628111&prj=626&rqi=CCJaxhr2jw7HFW133J1tBZDGFb
GT1MECH-62-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | During Air TAB inspection, some of grille section on the unit was loose and cannot remain steady when the airflow CRAH blows. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628033&prj=626&rqi=jHZKFoMUorRwfZmTvQ3k2kPln0
GT1MECH-60-004 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | When conduct P2G CRAH, parameter "Waterflow" cannot be simulated (STULZ need to be check and clarify) This issue is for ALL CRAH UNIT | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627986&prj=626&rqi=c7xMaS8yTrmLM3nt3arY3kvuYX
GT1ELEC-122-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Unused hole must be close | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627971&prj=626&rqi=N6HYMNhMXQfqclNvoDRjJpY8Qe
YT1ELEC-168-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628175&prj=626&rqi=oiCrOnwVjlhYMNRZ8SGdB1kK7l
YT1ELEC-166-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to attached images | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628171&prj=626&rqi=jXtvlfNTCvmJQ60BEe8zvE9GyB
YT1ELEC-170-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628177&prj=626&rqi=L7nMXimJBhwWrwCV5H8QNmPpVG
YT1ELEC-164-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628172&prj=626&rqi=fVuuqqvkYWoy8ER254zQVCrbH7
RT1ELEC-131-006 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | The uploaded drawing of panel is an old version. Please replace it with the latest updated drawing, old version must be unlink/removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627967&prj=626&rqi=7QVKn1DnctuwuJUlEJGzwJggeD
RT1ELEC-122-007 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | The uploaded drawing of panel is an old version. Please replace it with the latest updated drawing, old version must be unlink/removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627961&prj=626&rqi=Yx2XvJai4T1Ewp40Uo6LjoNPMt
YT1ELEC-165-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628173&prj=626&rqi=tCZ9vu31himPLzjQYMQF7TARxz
YT1ELEC-48-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628181&prj=626&rqi=Nn3GODG4sFaqPtImABwCiXGcvj
RT1ELEC-125-010 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | The uploaded drawing of panel is an old version. Please replace it with the latest updated drawing, old version must be unlink/removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627964&prj=626&rqi=LCuI9TcA9i73n6GLphqffGkauQ
YT1ELEC-171-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628178&prj=626&rqi=QMj6syYvRRzxwJsvj4T7E1s3hT
YT1ELEC-169-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628176&prj=626&rqi=vPyOu65DY2pbD9wDwteU1c6CqC
GT1MECH-60-003 | JK01-2 | APAC | Closed | P2 Medium DCOS | DimasKurniawan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | Discrepancy between SICD and actual measurement (SICD = airflow , actual = waterflow) Orise needs to change the parameter and approval. This for all CRAH units | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627984&prj=626&rqi=a8MYmcQwTlpiv1V6d4IGHBH6oe
RT1ELEC-128-013 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | The uploaded drawing of panel is an old version. Please replace it with the latest updated drawing, old version must be unlink/removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627966&prj=626&rqi=fB2sImkCf0rCVy2ZcmgUsCj5mb
YT1ELEC-167-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628174&prj=626&rqi=8M4qBlpUeMR4KQJ03IZRIkeUAT
GT1ELEC-10-002 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Based on the MSB Point-to-Graphic (P2G) test results, several DCOS points for breakers QE, QN, Q1-1, Q1-3, Q1-4, Q1-5, and Q1-6 are not available. This issue is applicable to all MSB units. Please refer to the attached picture for details. The unavailable points are as follows: 1. Current N 2. Voltage AN 3. Voltage BN 4. Voltage CN | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627856&prj=626&rqi=OOmBLu36tvn6CdnvcpMSQwNHRw
GT1MECH-27-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | The DS sticker has not been installed. JCI must implement a DS-approved sticker on the chiller's DB panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627852&prj=626&rqi=l3C9ToEVBoD7l8dDYDBRA9Xvfl
GT1ELEC-11-002 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Based on the MSB Point-to-Graphic (P2G) test results, several DCOS points for breakers QE, QN, Q1-1, Q1-3, Q1-4, Q1-5, and Q1-6 are not available. Please refer to the attached picture for details. The unavailable points are as follows: 1. Current N 2. Voltage AN 3. Voltage BN 4. Voltage CN | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627869&prj=626&rqi=WBW0HyNDSYwFgt5Ypl2FQiNjMA
GT1MECH-24-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | The DS sticker has not been installed. JCI must implement a DS-approved sticker on the chiller's DB panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627849&prj=626&rqi=5Tcf3OqiNK5aCOAusYO8izNpDJ
GT1MECH-25-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | The DS sticker has not been installed. JCI must implement a DS-approved sticker on the chiller's DB panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627850&prj=626&rqi=0VqrsRuf0ce5rfGh4sws1JeFCY
GT1MECH-26-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | The DS sticker has not been installed. JCI must implement a DS-approved sticker on the chiller's DB panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627851&prj=626&rqi=S5vRn5MC3VpWW3i1Dc0loAIT7y
YT1ELEC-125-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Issue White Glove Inspection, please close all issues on WGI form and provide photo evidence for all issues already closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627968&prj=626&rqi=VhaTRQ5pnw5Pfl2aPAQH3CU1Zc
GT1MECH-24-002 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Lesson learned from phase 1) The evaporator leaving temperature setpoint can only be adjusted when the HOA is in Hand Mode. JCI shall implement the software update in Phase 2 to enable remote setpoint control in Auto Mode, then notify CTA for verification onsite. Implement for all chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627853&prj=626&rqi=3qBdA1JtmqUnAiT3sP6q3AKauE
YT1MECH-27-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | Cable communication not connected yet to existing unit (VRFOD G_61) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627774&prj=626&rqi=2ryoi8khvEZ7I7APFPYNVK0Gdu
YT1ELEC-119-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Issue White Gloves Inspection, please check the attached images. Make sure all issues already closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627763&prj=626&rqi=F6rthW85uZXC1TiJlaam3GzY7Y
YT1ELEC-16-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Issue White Glove Inspection, please check the attached images. Make sure issue already closed and please provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627814&prj=626&rqi=ZZa1BAa5bBFnZ0b1XCBmALIO5u
YT1ELEC-122-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Issue White Gloves Inspection, please check the attached images. Make sure all issues already closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627761&prj=626&rqi=SYxy21c9vMPiZpUt1E3xRG0n4K
YT1ELEC-27-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | Issue White Glove Inspection, please check the attached images. Make sure issue already closed and please provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627811&prj=626&rqi=ioVumt7kMGLZ1DWIXtaNrTNtF6
YT1ELEC-15-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Issue White Glove Inspection, please check the attached images. Make sure issue already closed and please provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627813&prj=626&rqi=zlgsrL1lK9n42SXWLNLMtkNcou
RT1ELEC-15-028 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Factory Test Data including Calibration certificates not uploaded to FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628021&prj=626&rqi=QsxrL2PsbqiihhyudwKWSjaR8T
YT1ELEC-22-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Issue White Gloves Inspection, please check the attached images. Make sure all issues already closed and please submit photo evidence after closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627770&prj=626&rqi=mDRVOnQk0Y05c8gZKLgT25WZQ4
YT1ELEC-21-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Issue White Gloves Inspection, please check the attached images. Make sure all issues already closed and please submit photo evidence after closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627760&prj=626&rqi=eiku8OiG1tKiiGMIXmtBEJZRun
RT1ELEC-13-028 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Factory Test Data including Calibration certificates not uploaded to FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628018&prj=626&rqi=nkOmVuj2IVqfOGMomZszcf2YBc
YT1MECH-20-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_B_22 | DXID - FCU/DX Indoor Unit |  |  | Cable communication not yet connected to existing unit (VRFOD A_21) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627771&prj=626&rqi=pqNW4YtnyzcNWk6iRiT1uxU33A
GT1MECH-16-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_B_22 | DXID - FCU/DX Indoor Unit |  |  | issue from CxL2B. cable communication not yet connected to existing unit (VRFOD A_21) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627773&prj=626&rqi=Cvt1IaPqHVMEGUmpp02ekPVFJH
GT1ELEC-1-005 | JK01-2 | APAC | Closed | P2 Medium DCOS | dickyhermawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Re-assigned to Orise) Need to update latest SICD approved. Based on the RMU Point-to-Graphic (P2G) results, several mandatory DCOS points from the Outgoing RMU MVBCM are not available: See attached picture 1. IED Test Mode 2. Voltage AB 3. Voltage BC 4. Voltage CA 5. Power Factor 6. MW 7. MVA 8. MVAR 9. Frequency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627772&prj=626&rqi=QOyvo36Qj38lJLM5OfZhopLUcg
GT1MECH-22-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | issue from CxL2B. Cable communication not connected yet to existing unit (VRFOD A_21) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627778&prj=626&rqi=rLbD6AWAmtBZtnAOT5aQhtgzIT
YT1ELEC-30-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Issue White Glove Inspection, please check the attached images. Make sure issue already closed and please provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627810&prj=626&rqi=2YneMPBYMIKqsmhk7YNmVEjijw
YT1ELEC-28-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_2 | LIBATT - UPS Battery |  |  | Issue White Glove Inspection, please check the attached images. Make sure issue already closed and please provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627812&prj=626&rqi=7tgi5prqBUvDpz0kbi1vmrDoXm
RT1ELEC-12-011 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | Factory Test Data including Calibration certificates not yet uploaded to FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628017&prj=626&rqi=w8c8EBVzu2rNxj2NZXksKgvQDm
RT1ELEC-14-028 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Factory Test Data including Calibration certificates not uploaded to FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628020&prj=626&rqi=z6lGHwVAia46q56WynlTpLwbV8
YT1MECH-26-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | Cable communication not connected yet to existing unit (VRFOD A_21) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627776&prj=626&rqi=joosyeiEyxtAloI5884iRqKgU3
YT1ELEC-29-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Issue White Glove Inspection: Please refer to attached image and provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627809&prj=626&rqi=7ZGrlTP9AEXdzrwv6mIgI6o9zW
GT1MECH-23-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | issue from CxL2B. Cable communication not connected yet to existing unit (VRFOD G_61) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627775&prj=626&rqi=IydY2IKmJxrX3w3Umno7krJFmY
RT1ELEC-36-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Temp. sensor not installed at cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627532&prj=626&rqi=lBRewepGAktKR7xKlzYcaOEP37
YT1MECH-5-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of Daily Tack is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627518&prj=626&rqi=uzMMvUj90O9MQUC3bQ6Yv0fNSD
YT1ELEC-20-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Please close issue White Glove Inspection (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627541&prj=626&rqi=kNrqaZHMWBi9FNyISgeW5bfonn
YT1ELEC-18-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Please close issue white glove inspection (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627540&prj=626&rqi=MQWWou4RPe1uC3He6EPwFhut6r
YT1MECH-25-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627505&prj=626&rqi=ybihF2J15VAK67e3uZLNgnrENT
GT1ELEC-10-001 | JK01-2 | APAC | Closed | P2 Medium CX | JoshuaPrasatyaGani@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Incoming and outgoing single-core cables to Panels MSB_B and MDSB_B are not installed in trefoil arrangement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627551&prj=626&rqi=VI2HdkjbxSfaY00meCQfRmtnuv
YT1MECH-2-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of Daily Tack is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627522&prj=626&rqi=8SgfipgU8xIKIuJqDmKCfnfljU
YT1MECH-24-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_B_41 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627506&prj=626&rqi=hiVUzKGjS4FtU7K58pM4Zq2ndx
YT1ELEC-17-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Please close the issue white glove (refer to attached photo): 1. Busbar still dusty 2. Need re-torque & double mark to all bolts 3. Missing bolt (9 pcs) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627537&prj=626&rqi=bdqG0oCKQVB0CgAqxLLCChKX5x
RT1ELEC-33-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | Temp. sensor not installed at cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627533&prj=626&rqi=L42wn6enQccF4FT2eLJZeIE32H
YT1MECH-19-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of Out Door is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627498&prj=626&rqi=yZsZ2TmiIxSpHMnoZU5YAotyyn
YT1MECH-23-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_42 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top all of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627507&prj=626&rqi=pkpFH26jq53V2n60Wt4cOno4Ey
YT1MECH-22-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top all of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627553&prj=626&rqi=gowNerUnnXkPvcJcSI5GZDGOAv
YT1MECH-27-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627496&prj=626&rqi=H8f2TYNsoahEEo78TMD4bNC7xL
YT1MECH-4-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of Daily Tack is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627521&prj=626&rqi=lCiPrkfkM9Mw4SZadWXQq7y2kM
YT1MECH-26-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top all of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627508&prj=626&rqi=CBw0xjIxh4Ub3ayRwtkxEvC8XG
YT1ELEC-13-014 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of all panel is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627514&prj=626&rqi=SDJtwAsa8toZJwc6qYYUp7GNqr
GT1MECH-61-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627414&prj=626&rqi=ppu26LnpFLeL8fYRVJ6Kirnf24
GT1MECH-59-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627410&prj=626&rqi=uuyIeLNwmh79iEf0hdEf3yoZ1j
GT1MECH-60-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | (Issue move to CxL3) External pipe arrow/ direction not installed yet. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627273&prj=626&rqi=Td2YzrbgSQywk3t1LXjjvoQZSh
GT1MECH-69-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_62 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627431&prj=626&rqi=ErxmT9ybds4QSPbeTQQtKo9fZV
GT1MECH-68-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627430&prj=626&rqi=YNggi0pgmNYaUIGltTaFlpDr9u
GT1MECH-57-002 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_21 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627274&prj=626&rqi=n2P42W2IFSQQTUuZrCMGXJ2bo0
GT1MECH-63-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627418&prj=626&rqi=XtJnIqoyc0AaEZDHWvaOX3QmZY
GT1MECH-71-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627434&prj=626&rqi=GKLgZ5EzCVNevUTUuyBx0TvGRl
GT1MECH-70-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627432&prj=626&rqi=VESnoi5ZHjjSE32SB1fjPsis3b
GT1MECH-64-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_41 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627424&prj=626&rqi=icTY3Cblgo7SBaoCPwjjonACz6
GT1MECH-56-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627405&prj=626&rqi=aYBBNIkaSiSXJg6KO21JWAepNY
RT1ELEC-30-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_A_2 | LIBATT - UPS Battery |  |  | Please upload following documents: 1. RFIT Report 2. Approved Layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627326&prj=626&rqi=deftavy60FTI0KTy47TlC7MP7T
GT1MECH-67-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627428&prj=626&rqi=Qhld73AwwOKdjgSIk1hCMQiuXz
GT1MECH-65-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_41 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627425&prj=626&rqi=wgSBL65hdrKOaLBQXnzfq4J6vi
GT1MECH-66-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627427&prj=626&rqi=71yRKHocuXDLgTk8KMNMkOcYSL
GT1MECH-60-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627412&prj=626&rqi=OnKtFLNbgiwKtjiYXUAXxmtMsu
GT1MECH-58-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627406&prj=626&rqi=3IYkBl4QyY5HaPXayHSxogDZlR
GT1MECH-62-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627417&prj=626&rqi=GvoAUjRSeAdON97qexSJIV0ur4
GT1MECH-57-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_21 | CRAH - Computer room air handler |  |  | (Issue move to CxL3) External pipe arrow/ direction not installed yet. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627216&prj=626&rqi=QeerggS7rl8LkqxDgHoVESmhzK
YT1ELEC-119-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Please note that the CxL2B LV Cable Report for 1MDSB_D_2 to 1DB_D_CRITICAL (photo on DB panel side) is still based on a temporary cable installation. Please update the report once the permanent cable has been installed and re-upload the revised report to this checklist. Kindly remove/unlink the previous report that contains the temporary cable installation evidence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627855&prj=626&rqi=a38k9b8ruJEqvN7DSAGfuWUekh
YT1ELEC-125-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Please note that the CxL2B LV Cable Report for 1MDSB_F_2 to 1DB_F_CRITICAL (photo on DB panel side) is still based on a temporary cable installation. Please update the report once the permanent cable has been installed and re-upload the revised report to this checklist. Kindly remove/unlink the previous report that contains the temporary cable installation evidence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627854&prj=626&rqi=kmbcHlvjgxyZo1BU4zWzs5mV8A
YT1ELEC-22-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627332&prj=626&rqi=RJsECmSemqV0ukovbhuOweTueq
YT1ELEC-22-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627333&prj=626&rqi=P6irigNtmApmrGPoNdUqDixUQo
YT1ELEC-22-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Grounding busbar is not sufficient for all grounding cable terminations. Please extend the busbar to avoid cable stacking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627331&prj=626&rqi=qjPHFpor1AYdL5Tl2Y5YzlhyWp
GI-025 | JK01-2 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_5 | ERTH - Earthing |  |  | Lev 2. MV Riser 2. Grounding tray size does not accommodate all the grounding cables in the riser, so the cables pile up and cannot be tied up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627025&prj=626&rqi=V6pwAmlhvB89YEu43bk1NWvaWV
GI-029 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | The existing water leak cable is trapped between the Li-Batt racks. Based on site walk with Aurecon, the cable must be pulled and re-laid to cover the new Li-Batt racks | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627030&prj=626&rqi=CneiIdens2MHNPWudNEkwoqjiB
YT1ELEC-20-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Grounding busbar is not sufficient for all grounding cable terminations. Please extend the busbar to avoid cable stacking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627110&prj=626&rqi=G5EGzR4iOEdeiSRSheE6Arf6N9
RT1ELEC-153-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue STS Room D) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627147&prj=626&rqi=AdmZBfcgmJp0XZOJoJFFyuFapO
RT1ELEC-152-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue Battery Room B) Vinyl cable loose & cable tagging not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627145&prj=626&rqi=qsldKtAQNUMxwAn1XBmKK6MpeM
YT1ELEC-18-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Grounding busbar is not sufficient for all grounding cable terminations. Please extend the busbar to avoid cable stacking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627109&prj=626&rqi=hNPq31NozX7HnHwuDNBZ7bfuNg
YT1ELEC-18-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627114&prj=626&rqi=vBgpwtIOkc2rWgPdp0Gl94kKxo
GI-028 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_A_2 | LIBATT - UPS Battery |  |  | The existing water leak cable is trapped between the Li-Batt racks. Based on site walk with Aurecon, the cable must be pulled and re-laid to cover the new Li-Batt racks | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627028&prj=626&rqi=ADqmJmGqznnc5RNh2QLEqWxuzp
GI-027 | JK01-2 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | Lev 2. MV Riser 2. Grounding tray size does not accommodate all the grounding cables in the riser, so the cables pile up and cannot be tied up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627027&prj=626&rqi=WcIrSZgHWPdEnBZ0FSEC1sjRz2
YT1ELEC-18-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Control cable needs proper dressing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627108&prj=626&rqi=5q4eXNlJzoJ4jGYCLp3iNHfi4F
RT1ELEC-152-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue STS Room B) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627144&prj=626&rqi=9DDUiSwo7sHe0V41SjGD2ZnXw7
YT1ELEC-13-013 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Busduct) Busduct LBSB 3200A 1MSB_F_1 & 1UDP_F_1 clash with sprinkler pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627128&prj=626&rqi=WkjluMCeTPbJmhUOTDgENSdCNG
YT1ELEC-16-007 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | DCOS cable has not been terminated at the UPS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627106&prj=626&rqi=uR0MIObtQ78tNYMYXQVqbVcywd
YT1ELEC-16-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627105&prj=626&rqi=pyeWjk8CoDIIjUBi8rWtxzwZy0
RT1ELEC-153-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue STS Room D) Need to add flat & belleville/spring washer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627146&prj=626&rqi=7Bkp5WjmcSijIJHzyW4gIEy9GU
YT1ELEC-16-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Minimum 3 threads shall be visible beyond the nut | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627103&prj=626&rqi=pXeg8lfHnoyIcyBpACLMGgvkOQ
YT1ELEC-16-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Control/Auxiliary cables are not connected and need proper cable dressing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627107&prj=626&rqi=x767BDvWDZK7r7ZiFgWW8TEBJB
RT1ELEC-153-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue Battery Room C) Minimum 3 threads shall be visible beyond the nut and need to install spring washer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627143&prj=626&rqi=QlYlFmmT33tEOvLq725AByTjpp
RT1ELEC-153-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue EWALL Room D) Minimum 3 threads shall be visible beyond the nut and need to install spring washer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627141&prj=626&rqi=gc8vh5BgNt1jwOSKIDDbjuUqXr
YT1ELEC-19-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627113&prj=626&rqi=tBHlcCYLQnjqtC2iuYB2g5FnCf
RT1ELEC-153-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue EWALL Room D) Need to install cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627142&prj=626&rqi=f3fiIvqzz1XsP3G0MzsRHItrT0
YT1ELEC-20-002 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | DCOS cable has not been terminated at the UPS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627111&prj=626&rqi=rCBrCR536KCA7lrDklVxHxUMin
YT1ELEC-20-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627112&prj=626&rqi=D2UeeMLE1lhsaxIJ8AgC3I928R
YT1ELEC-15-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627102&prj=626&rqi=w0fq2l1NVNRuJYFBDroYgOGYuW
YT1ELEC-47-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Earthing Cable) Cable Tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627050&prj=626&rqi=fzxFIgxxpFfGMAwinteKpHeKdi
GI-024 | JK01-2 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | Lev 2. MV Riser 2. Grounding tray size does not accommodate all the grounding cables in the riser, so the cables pile up and cannot be tied up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627022&prj=626&rqi=7PGOzNgzMHbr7U08MiXtWUiqwy
YT1ELEC-15-001 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | DCOS cable has not been terminated at the UPS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627101&prj=626&rqi=dvXEc7OjzaTdWd8mGp2ttOgu3g
YT1ELEC-10-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Earthing Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627049&prj=626&rqi=sdQr6LPJxM6vEhYMvRVxpmiM7c
GI-026 | JK01-2 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | Lev 2. MV Riser 2. Grounding tray size does not accommodate all the grounding cables in the riser, so the cables pile up and cannot be tied up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627026&prj=626&rqi=2PrMOi78KC6a1OXlU6jgXRVG0d
YT1ELEC-16-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Grounding busbar is not sufficient for all grounding cable terminations. Please extend the busbar to avoid cable stacking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627104&prj=626&rqi=p0Klr6RR3Q94ED4qON5VNvXTih
YT1ELEC-21-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Please tidy up the control cable conduit installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627043&prj=626&rqi=ENPNajsv0EnmEpG4yQLJOVEZnh
YT1ELEC-21-002 | JK01-2 | APAC | Closed | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Please tidy up the DCOS cable installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627045&prj=626&rqi=k1nq3JUyvSBTvfM7LIBXxxeaRY
YT1ELEC-21-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Control cable UPS to LIBATTSYS not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627046&prj=626&rqi=vAZLAD8Xwm4Zx22qtFTEvpMJj0
YT1MECH-14-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1EF_D_53 | EF - Exhaust Fan |  |  | (Issue CxL2A LV Cable) Cable over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626843&prj=626&rqi=0KjHdGtmay64axFKUDJPZhV2Lw
RT1ELEC-52-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | Minor dents & scratch, need to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626854&prj=626&rqi=EzdzzR3hIBVVTMHWPhVtNIMQ8b
RT1ELEC-52-005 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | Need to upload calibration certificate for torque wrench | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626858&prj=626&rqi=EaEq6urrYa15AxB139hOzXn7he
YT1ELEC-125-003 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Incorrect cable termination for grounding (refer to attach photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626881&prj=626&rqi=oeT66WZ8VlxB3Nv6uZYZL5CuAp
YT1MECH-106-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | Pipe not connected yet, and also for Cable not yet for Tamper Switch, Solenoid and Flow Switch. Trim set also not done yet. Attach photo once already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626879&prj=626&rqi=vyvmArsouq3nRp2qbWUOtMU0Q8
YT1ELEC-117-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Incorrect label outgoing (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626842&prj=626&rqi=4X3MvphiYEgSrasUPT7sws0WpO
GT1ELEC-11-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626688&prj=626&rqi=e5pLDl893miurX1YgTJmk4mARc
RT1ELEC-20-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_A_2 | UPS - Uninterrupted Power Supply |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626853&prj=626&rqi=DcRuS5kVOJ4JcYRfQGW3ZH5c7K
RT1ELEC-56-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | Anchor bolt loose cannot be tightened and not properly for anchor (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626859&prj=626&rqi=LmLu8LRGmRQArJOyH2ol18d3RQ
RT1ELEC-22-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Need to torque verification & mark for rear anchor bolt | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626457&prj=626&rqi=i0cyqORC85zVIP5P3rl5V4NebV
RT1ELEC-26-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Please protect HMI display to prevent from construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626467&prj=626&rqi=QBZpnApBdNlQ1e0ZNpyt8lj46Z
RT1ELEC-26-009 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Need torque verification & mark for rear anchor bolt | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626464&prj=626&rqi=fcyatoUCFh4BiVzKHvqr5KDIs6
RT1ELEC-26-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Door foam damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626465&prj=626&rqi=4FK3GvSsq0rLNEeN3H8XtTBIHP
RT1ELEC-26-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Missing bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626466&prj=626&rqi=uT63cKIRxT1hSGa7jIi30gn7QJ
RT1ELEC-21-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Minimum 3 exposed threads required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626452&prj=626&rqi=0Xr7dVPrGhxUWn6zsIMkJAtth8
RT1ELEC-21-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Minor dents, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626451&prj=626&rqi=skd0v3zQ6t9VtqLmzTWrtMjsFT
RT1ELEC-21-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Door foam damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626453&prj=626&rqi=9BSpm2goCQFnVdtDgLSizTYZjM
RT1ELEC-22-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Discrepancy between drawing & actual position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626455&prj=626&rqi=PNbKaPvvcfDUmm4SbNdSnR1PUC
RT1ELEC-24-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Minor dents, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626459&prj=626&rqi=LNXpnFEg6UCpKvxuZNqgFrgXTP
RT1ELEC-24-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Door foam damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626461&prj=626&rqi=44IScvvOMsgmdRmYp8KHcaOQTG
RT1ELEC-24-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Please protect HMI display to prevent from construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626460&prj=626&rqi=i0qlPc5mQUywN2mCXQ1Fl4B69C
YT1MECH-18-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | cable tagging not installed yet for cable communication for outdoor to indoor unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626462&prj=626&rqi=YkE9iMRv1iMGLgNGw9BGiJFSQZ
RT1ELEC-22-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Minor scratch & dents, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626458&prj=626&rqi=2K2PRPhbiMLoSiyeEVK0eJU121
RT1ELEC-26-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Discrepancy between drawing & actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626463&prj=626&rqi=Epusrjye5u2tqofXFmIhURdUwT
GI-023 | JK01-2 | APAC | Closed | P3 Low CX | ariagandanegara@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | Please rectify and repaint the peeled off pipe coating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626450&prj=626&rqi=x0Ng0nsCB8pzUTvCICb2rUscGs
YT1MECH-43-002 | JK01-2 | APAC | Closed | P1 High CX | DimasKurniawan@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor | L2B | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | During Tie-in activity for CHW Pipe Cooling Array Level 4th floor, leak was discovered at CHWF mainline pipe. Please provide RCA for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626357&prj=626&rqi=NP6ilmksLgxWUJoG86XCHWLJ1R
YT1DCOS-14-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Controls | equipment | 1DCOS_1_SCP_04 | DCOS - Control Panels |  |  | (Issue CxL2A LV Cable) Cable over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626248&prj=626&rqi=Asv9ZGtnpe6mH8wSagU5mPrUTm
YT1DCOS-12-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Controls | equipment | 1DCOS_1_SCP_02 | DCOS - Control Panels |  |  | (Issue CxL2A LV Cable) Cable over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626246&prj=626&rqi=DNo0QRTPFvA1BQAKFOc6UjYQEV
YT1DCOS-15-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Controls | equipment | 1DCOS_1_SCP_07 | DCOS - Control Panels |  |  | (Issue CxL2A LV Cable) Cable over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626249&prj=626&rqi=rv9StLdnkBuMzsGXFKwSlCZ3tb
YT1ELEC-16-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable) Incorrect cable tagging, should be from 1UPS_B_2 to 1LIBATTSYS_B_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626242&prj=626&rqi=KoW79viXvQK2W8AD7YzrIlmaTv
YT1ELEC-19-005 | JK01-2 | APAC | Closed | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | DCOS cable installation is not neatly arranged. Please tidy up and secure all DCOS cabling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626245&prj=626&rqi=RVogC4hSykbdkQ0S0G9oWguNDt
YT1ELEC-26-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | (Issue CxL2A LV Cable) Incorrect cable tagging, should be from 1UPS_B_2 to 1LIBATTSYS_B_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626243&prj=626&rqi=M61Dni3KYXkSvPeHZjLYbQLgKu
YT1DCOS-9-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626241&prj=626&rqi=g91B51sZgcHuCRFmzoENoFoWys
YT1ELEC-116-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | Incorrect breaker label, please follow new breaker outgoing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626244&prj=626&rqi=azA3cMqKre7QcqeV3yscadOS6f
GT1ELEC-2-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Several point lists included in the approved Point List could not be verified in DCOS during RMU CxL3 P2G testing. LS Electric confirmation and Statement Letter are required. Potential impact to all similar RMU units. Need to update SICD approved and signed by Orise, LS, and GC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625636&prj=626&rqi=78PTDAfU6DhyjTxQi7D9VDt7AU
YT1ELEC-17-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Auxiliary and DCOS cables are not properly connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625634&prj=626&rqi=HFIea7wMABfy9XZHJgoVOKDlrM
RT1FD-6-001 | JK01-2 | APAC | Closed | P2 Medium CX | ariagandanegara@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Fire Detection | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | 1. Solenoid Cable is not Installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625779&prj=626&rqi=IkUcyjBycJPxGTiZIybWTPpmAx
YT1ELEC-17-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Control cable UPS to LIBATTSYS not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627048&prj=626&rqi=1HHbMG2reI6EPH0ine57s1UpcU
RT1FD-6-002 | JK01-2 | APAC | Closed | P2 Medium CX | ariagandanegara@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Fire Detection | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | The Pipe is not Installed yet. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625782&prj=626&rqi=Obss7d0MsUaBEwcJDZVwAzKORO
YT1ELEC-117-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Incorrect label outgoing breaker, should be: - Q1-3: to 1EF_B_31/32 - Q1-4: to 1EF_B_21 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625790&prj=626&rqi=Xvld9e2E9EflpeGthlUWY8jaiC
RT1SEC-15-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Security | equipment | 1CCTV_level_7_DH | CCTV - Closed Circuit Television |  |  | issue CCTV C:07-43 not installed yet because cable tray is not installed yet by GC, the CCTV shall be installed under tray | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625797&prj=626&rqi=r7IFNXanADMPKEMpDWa0t3fEwu
YT1ELEC-17-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | General Contractor | L2B | Torque required | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Bolt torque under 3 threads under the nuts & please perform re-torque verification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625635&prj=626&rqi=epFERsOgtmrXVHVqU7vyztgxOO
YT1MECH-35-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Labelling / equipment name tag not yet (Issue from L2A) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625581&prj=626&rqi=X27yPsBa4sp7oFmIO7YCCSzPVm
YT1ELEC-171-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625305&prj=626&rqi=Z6gnNjGpBxf6QdVYy8hErE3Cnx
YT1MECH-72-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_4 | FFU - Air Scrubber |  |  | (Issue CXL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625331&prj=626&rqi=OjlYG3khLJaN5WwwbX3Mjr0Soq
YT1ELEC-168-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | (Issue CxL2A LV Cable) Ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625306&prj=626&rqi=6wscDPv63K2LGuQB00cn1vmNkL
YT1MECH-73-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_5 | FFU - Air Scrubber |  |  | (Issue CXL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625332&prj=626&rqi=9WvtvUb2V7I8SZjsa6rZ572irV
YT1MECH-71-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_3 | FFU - Air Scrubber |  |  | (Issue CXL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625330&prj=626&rqi=7Z31ckrngLpibH0ha3Hmy5eGYW
YT1ELEC-52-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable) Ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625316&prj=626&rqi=q6ZsDHR1CJ6A9fssqa7j3QC3sH
YT1MECH-74-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_1 | FFU - Air Scrubber |  |  | (Issue CXL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625328&prj=626&rqi=Qw1HfbiF5R2mFQcOO1nPq71pOi
YT1ELEC-52-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable) Remove temporary marker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625315&prj=626&rqi=zijfYQm18AyHI9OHNz4dxcsJ9H
YT1MECH-70-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_2 | FFU - Air Scrubber |  |  | (Issue CXL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625329&prj=626&rqi=VcGpvM41thhOdCK8Aco9CfmXGB
YT1ELEC-168-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625304&prj=626&rqi=0Ynav3O5LRK1h3X9wnFkfbywyt
YT1ELEC-53-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Cable) Cable insulation damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625317&prj=626&rqi=rz5si8nGKj3h9eIikGkKuAxqA3
YT1MECH-89-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625221&prj=626&rqi=4c2aZzXJzD3aw9VkixcaJgHvZK
YT1ELEC-117-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Ensure the gland is properly covered and sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625204&prj=626&rqi=feFjesLwGpvScn6mrpWhu6HVW0
YT1MECH-44-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_D_03 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625223&prj=626&rqi=12kydMfElAtO6WOBrGIUNjvf9w
YT1MECH-95-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cable tray not finished yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625211&prj=626&rqi=OU6CWonAJ1JmLzL6kXefM6uqa7
YT1ELEC-119-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1DB_D_CRITICAL to 1CRAH_D_42) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625212&prj=626&rqi=wQ9HG7NBncXjG5XwTBbh7VbAM0
YT1MECH-98-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Bonding jumper on tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625218&prj=626&rqi=gvbEE76a7I6zbeYupeb0cRXUi0
YT1MECH-46-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_D_06 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625225&prj=626&rqi=0FvTHyGyuYvAcTWpyo5toSFMhI
YT1MECH-47-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_D_07 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625226&prj=626&rqi=JPKGoH4alBFioo9hNIvHuqULBx
YT1ELEC-117-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625203&prj=626&rqi=8mbGxoEDc8bXlhVa45M4oFVYAS
YT1MECH-96-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | (Issue Cxl2A LV Cable) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625210&prj=626&rqi=HtbJD3HwvvY8KXBQsUXJWcTL0x
YT1MECH-40-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_B_06 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625234&prj=626&rqi=3l9egXbokmaWeU8Ilgx8w8ARbH
YT1MECH-97-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_62 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cable installation is not neat and several cables are over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625219&prj=626&rqi=hycKsIS4xA2pp9sEF3DcGrEDp3
YT1MECH-42-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625237&prj=626&rqi=dL1St4RPyuW71rEMLdIvXbz6hu
YT1MECH-91-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625217&prj=626&rqi=JkdxjFbZVDCfffsrcgzbsVMt9c
YT1ELEC-125-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625216&prj=626&rqi=PihtoMD61inBgqygc197TgCEqk
YT1MECH-45-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_D_05 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625224&prj=626&rqi=iwMFsLeEuXZgncSHujoPyCGyih
YT1MECH-49-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_D_11 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625229&prj=626&rqi=WPhN70PYpPwMDlvS1JspUgkJFY
YT1MECH-96-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cable installation is not neat and several cables are over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625220&prj=626&rqi=zkKAydHQVcOpAgff79l1IHyq6G
YT1ELEC-119-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1DB_D_CRITICAL to 1CRAH_D_42) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625213&prj=626&rqi=FNmgZG8v8CRiBNnwPQB6gFac8o
YT1MECH-39-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625233&prj=626&rqi=CTpgv8LnKZHDku3soRZinvsn1O
YT1MECH-41-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625235&prj=626&rqi=8EqFMwyQGDu8pNYWxWt8cvl4rW
YT1MECH-43-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625222&prj=626&rqi=zktubdNpdaTAUe6AM5msrYE15P
YT1MECH-6-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | (Issue CxL2A LV Cable 1DB_B_EWALL to LCP_EF_B_21) Cable over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625199&prj=626&rqi=Tm6B16fCPvxA69h0ugv7fm5xNN
YT1MECH-48-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_D_09 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625228&prj=626&rqi=S6rYRxQPwPRvHZYOc7bDWr9cbP
YT1MECH-6-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | (Issue CxL2A LV Cable 1DB_B_EWALL to LCP_EF_B_21) Cable & conduit needs to install labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625200&prj=626&rqi=3xqs6DiHIsRH2zztqCHwPk7plW
YT1MECH-38-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_B_03 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625232&prj=626&rqi=Zx1uxGoLTMdktatUSFF3WNZWEC
YT1MECH-99-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cable installation is not neat and several cables are over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625215&prj=626&rqi=AZ6cvQBjV4agGaPF3xo2PnGGCV
YT1MECH-36-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625230&prj=626&rqi=hgTMquOLvGUtuvFe32dZuWLaV0
YT1ELEC-16-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_B_1 to 1UPS_B_2) Several cable gland caps are damaged (torn) and not properly covering the gland, please ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625208&prj=626&rqi=epbW3lCFIcNUZVVypTm8ARdqnD
YT1ELEC-16-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_B_1 to 1UPS_B_2) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625207&prj=626&rqi=g0MUQWtwjeLTfoLAXmPzk1c6Ia
YT1MECH-37-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_B_02 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625231&prj=626&rqi=XxDpFKGfFD1Ueu2y73zpHtRIXe
YT1ELEC-117-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1DB_B_EWALL to LCP_EF_B_21) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625202&prj=626&rqi=TuYA8bANZsJ8psbspbEuarEWWf
GT1SEC-12-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning | Security | equipment | 1ACS_level_6 | ACU _ Access Control |  |  | Door handle not yet installed (D:06-09 E-wall room & D:06-38 Battery room) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625059&prj=626&rqi=SpETcN5O4ewq9szyidatqnLAkO
YT1ELEC-126-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Discrepancy identified between the breaker protection settings applied in the panel and the latest approved Discrimination Study. Short Time Delay (STD) and Ground Fault Protection settings do not match the approved study (Refer to the attached images) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624922&prj=626&rqi=yJ2ODIQ1DXu8CDFfp1ZOGO4Jfm
YT1ELEC-125-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Discrepancy identified between the breaker protection settings applied in the panel and the latest approved Discrimination Study. Short Time Delay (STD) and Ground Fault Protection settings do not match the approved study (Refer to the attached images) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624913&prj=626&rqi=c2G4BINYZN26WCTiqgxEEyFcHt
YT1ELEC-8-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Incorrect vinyl cable color at Panel DB Aux. Vinyl cable color for L1=Black, L2=Brown, L3=Grey, Neutral=Blue, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624881&prj=626&rqi=nf6059fPnsyHoJFbTEyiqN9mT9
RT1ELEC-153-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue EWALL Room C) Cable Tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624886&prj=626&rqi=3nXJLReyehzdwoWMI1MLkJGncJ
YT1ELEC-7-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Incorrect vinyl cable color at Panel DB Aux. Vinyl cable color for L1=Black, L2=Brown, L3=Grey, Neutral=Blue, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624879&prj=626&rqi=tNE3iG2CK2CRiBCLHyyLeKY8Xi
YT1ELEC-6-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | Incorrect vinyl cable color at Panel DB Aux. Vinyl cable color for L1=Black, L2=Brown, L3=Grey, Neutral=Blue, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624878&prj=626&rqi=5v4PAKcwdBB2bXnYRSvEXWJcFK
YT1ELEC-170-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | (Issue CxL2A LV Cable 1MDSB_D_2 to 1TOU_D_1) Missing bonding jumper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624873&prj=626&rqi=pD6u31XpTx0gxXGAg0exXaar6D
YT1ELEC-9-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Incorrect vinyl cable color at Panel DB Aux. Vinyl cable color for L1=Black, L2=Brown, L3=Grey, Neutral=Blue, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624876&prj=626&rqi=egdsXCAEWojuzW2HBVubZHk7H3
RT1ELEC-153-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue EWALL Room C) Cable tag naming does not comply with the project standard. Please correct accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624884&prj=626&rqi=56kv9PnIRZdUm21J4NysBYVTcs
RT1ELEC-153-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue EWALL Room C) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624883&prj=626&rqi=Vxo9pYiTuYwBACrnuSnHpUteTm
YT1ELEC-50-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Cable Aux) Cables are not neatly arranged. Please tidy up and secure all cables properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624861&prj=626&rqi=COdHEmyRYZPl9Jnys6iFLJD3ye
GT1MECH-80-001 | JK01-2 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_3.01 (Existing) | PAV - Pre-Action Valve |  |  | Seismic Bracing not yet installed and will be planned to install asap by GC. (This issue for all floor) Ensure that when installing those, there will be not affect piping and support pipe. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624812&prj=626&rqi=5pcdjbBAE8p4RuPkS12CYbyn5h
RT1ELEC-155-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | (Issue EWALL Room F) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624887&prj=626&rqi=UBtPixcbVDPs4XKscklRjLWeNU
YT1ELEC-50-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Cable Aux) Cable conduit label not installed. Please provide the label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624862&prj=626&rqi=aEE2FpqDMXE5RwZ83HMarSfWIp
YT1MECH-18-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | (Issue CxL2A LV Cable) Missing bonding jumper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624866&prj=626&rqi=Bhwlxa5DLyOuSTpNDT65NVePgp
YT1ELEC-52-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Cable Aux) Need to install label at conduit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624860&prj=626&rqi=yVrU6hOztAAaORKkTmN0wru4Cj
RT1ELEC-155-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | (Issue EWALL Room F) Incorrect cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624888&prj=626&rqi=iqUhtt6qslXc7GaFTxYdNSa742
YT1ELEC-9-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MDSB_D_1 to Panel DB Aux) Incorrect vinyl cable color. Vinyl cable color for L1=Black, L2=Brown, L3=Grey, Neutral=Blue, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624875&prj=626&rqi=8y8fHHOQdMehpuMfAZbW81gWHS
YT1ELEC-52-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Cable Aux) Cables are not neatly arranged. Please tidy up and secure all cables properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624859&prj=626&rqi=25JzHnDOkEjgzw8veDTV4IBDxS
YT1MECH-65-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_2 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_2] Cable lug phase R is broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624506&prj=626&rqi=0ZUAOwO5Zu1TnihJ36lQDW6EHD
YT1MECH-65-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_2 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_2] tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624507&prj=626&rqi=rYp0HXZSJxbML050rHAfBrN8HU
YT1MECH-31-004 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A Laying cable 1DB_CHWSTR_B_07_CH1 to 1CHWSTR_B_07_CH1) Belleville washer size is larger than the cable lug size. Please replace it with the correct size. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624519&prj=626&rqi=bTQG4vxtHmOMdjocCIFtGLKiDT
YT1ELEC-166-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | [Issue CxL2A 1TOU_B1] Cable tagging blurry need rectify (phase N) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624499&prj=626&rqi=TVf1YuiMrn1L97PQxdem27v3fN
YT1MECH-92-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_41 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable DB_B_Critical to ISO 1CRAH_B_41) Labelling panel not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624492&prj=626&rqi=RdjumXRcyHGiPDkqemQUHe95hp
YT1MECH-84-001 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable DB_B_Critical to ISO 1CRAH_B_21) Cable scratch until insulation is visible all phase (R,S,T,N,G) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624485&prj=626&rqi=OFEPZlmuJwZQ8zLTtT0WorArCY
YT1MECH-64-001 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_1 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_1] Cable over bending, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624502&prj=626&rqi=XXUMFPvCznLEckQpDvO0ySNxHE
YT1MECH-65-001 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_2 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_2] Cable over bending, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624505&prj=626&rqi=pCS9Q6NFyPmsnU64E8Ro1xBmNO
YT1MECH-19-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | (Issue CxL2A LV Cable 1MDSB_F_1 to DB 1VRFOD_F_61) 1. Cable lug not yet installed 2. Cable gland not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624705&prj=626&rqi=nWARNZ4AxF9Fk50WsZYfUvpi1P
YT1MECH-88-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable DB_C_Critical to ISO 1CRAH_C_41) Cable tagging and cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624488&prj=626&rqi=WEYYcW1TZZ9AvOmsMRbEC6YGwa
YT1MECH-84-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable DB_B_Critical to ISO 1CRAH_B_21) Need install cover tray and tagging cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624486&prj=626&rqi=PojaOHGKUewEiNwWgYkX1KKQCF
YT1ELEC-166-004 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | [Issue CxL2A 1TOU_B1] Protection neutral not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624500&prj=626&rqi=zXy0gqNO0T8uzdFBdAomwgCY75
YT1MECH-41-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1CA_B_7] Grounding cable was incorrectly terminated on the panel body, need rectify it according to the attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624514&prj=626&rqi=t1Q0Abb6Ffoximf0eY4Utmf4t3
YT1ELEC-166-005 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | [Issue CxL2A 1TOU_B1] Vinyl grounding not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624501&prj=626&rqi=jOdjec1STCDTHTMhRYvJNew1mH
YT1MECH-30-004 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A Laying cable 1DB_CHWSTR_D_04_CH1 to 1CHWSTR_D_04_CH1) Vinyl cable need tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624557&prj=626&rqi=LFOLRnE8DcqIPjmwNFKqDI7xWg
YT1MECH-19-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | (Issue CxL2A LV Cable 1MDSB_F_1 to DB 1VRFOD_F_61) Bonding jumper not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624708&prj=626&rqi=Xmf8aPxTnvi96wsW1Git9pUoqi
YT1ELEC-126-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1MDSB_F_1 to 1DB_F_EWALL) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624703&prj=626&rqi=mc9063mYaG3RUPQjbTIJEO3uw8
YT1MECH-87-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable ISO 1CRAH_C_22 to 1CRAH_C_22 ) tagging cable phase R not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624495&prj=626&rqi=sMnWHMcLnjrcShNxVaSMWu3pgQ
YT1MECH-30-005 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A Laying cable 1DB_CHWSTR_B_07_CH1 to 1CHWSTR_B_07_CH1) Vinyl cable identification for Phase R and Phase T has been installed incorrectly. Please revise according to the cable tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624558&prj=626&rqi=WWHDxiyDMJAlUshV9aCfl3cs5M
YT1MECH-93-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_41 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable ISO to 1CRAH_D_41) Label isolator not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624716&prj=626&rqi=H0NYqNNFk4ddCpQ5VWDduWL4Ka
YT1MECH-67-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_4 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_4] Tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624511&prj=626&rqi=7CZVANwIY2yMJd7Pj4odW0mtFN
YT1MECH-66-001 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_3 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_3] Cable over bending, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624508&prj=626&rqi=CbldfKrXtnTmU3LzcLRNht7e7t
YT1MECH-67-001 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_4 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_4] Cable over bending, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624510&prj=626&rqi=zJ32d5hTMItmqbvKfQytOo5N9g
YT1MECH-68-001 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_5 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_5] Cable over bending, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624512&prj=626&rqi=sANZ5RTWx8Wr3YScBsdlOv0UXI
YT1MECH-66-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_3 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_3] tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624509&prj=626&rqi=Jd4oXM6x0eSbWld0nUNO5acSZU
YT1MECH-31-005 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A Laying cable 1DB_CHWSTR_B_07_CH1 to 1CHWSTR_B_07_CH1) Vinyl need tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624556&prj=626&rqi=e8vdwtd2En8jjt3fs1XV2v0T3n
YT1MECH-86-001 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable ISO 1CRAH_B_22 to 1CRAH_B-22) Cable over bending at phase T, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624489&prj=626&rqi=WhCZFtVlPED7WPLDHAFaglNSoO
YT1MECH-91-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable ISO to 1CRAH_F_42) Bonding jumper not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624717&prj=626&rqi=9VlRAkGQD8pEpGTcGo40T3doZo
YT1MECH-110-004 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV CABLE ISOLATOR_1CHWSTR_B_07_CHWP_1 to AHF 1CHWSTR_B_07_CHWP_1) Grounding Cable Scratch until copper wire is visible | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624559&prj=626&rqi=FnIr85t4JSQmS42X59Uq8JDTk0
YT1MECH-87-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable ISO 1CRAH_C_22 to 1CRAH_C_22) Vinyl Cable was installed in reversed, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624494&prj=626&rqi=VTKBjuwgPTde9lNnL5juVGHzRQ
YT1MECH-64-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_1 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_1] tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624503&prj=626&rqi=xLh0RkryEJVVK1VtagJcU4FxbI
YT1MECH-68-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_5 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_5] Tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624513&prj=626&rqi=Dn2Oco3kpOeJeASg1ABdBiR8Gu
YT1ELEC-122-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable DB_C_Critical to ISO 1CRAH_C_22) Protection Neutral not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624487&prj=626&rqi=JiEquNPcWBH2ocfN4HH7nfsRYY
YT1MECH-110-005 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV CABLE ISOLATOR_1CHWSTR_B_07_CHWP_1 to AHF 1CHWSTR_B_07_CHWP_1) Cable end caps rubber need to be properly installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624560&prj=626&rqi=qQMBo9ILBwRgbWDs0N43FXfZIp
YT1ELEC-10-009 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Breaker Q1-3 protection settings are not in accordance with the latest approved Discrimination Study. Please update all breaker setting values and re-testing to match the approved protection coordination study and resubmit the report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624388&prj=626&rqi=wCBe53B5tLET4iCZuIUlUaNXVa
YT1ELEC-116-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable DB_B_Critical to ISO 1CRAH_B_21) tagging cable not yet installed for Q-2, Q-3, Q-4, Q-5 DB side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624444&prj=626&rqi=QLcS08BvoWQkaBoUsqNm6MoSJT
GI-022 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-06-08 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | pressure gauge does not match the unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624427&prj=626&rqi=ccUBtZuJm6y6ZMBiFZ1fPcw6rm
GT1ELEC-1-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Arc flash label on the RMU is still temporary. Please replace it with the permanent label as per the approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624417&prj=626&rqi=95oT8ExbRnKIJIcFbtvn0hu1Vx
GI-019 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-06-08 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | pressure gauge does not match the unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624422&prj=626&rqi=iA2VRk8mZmIX7mCWmZqQqElzNR
GI-020 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-06-08 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | pressure gauge does not match the unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624424&prj=626&rqi=xLtYoQ3qAhTl8yPo4LrTIPM0p2
GI-021 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-06-08 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | pressure gauge does not match the unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624426&prj=626&rqi=xrWrS55VWemdd7AXxDgGL84WPG
GT1ELEC-3-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Arc flash label on the RMU is still temporary. Please replace it with the permanent label as per the approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624420&prj=626&rqi=RsNpoOYHpL1rlDfvcNg1P88JqO
GT1ELEC-2-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Arc flash label on the RMU is still temporary. Please replace it with the permanent label as per the approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624419&prj=626&rqi=u8Hnhk7a6McDvFsfn3368CSLnS
GT1ELEC-4-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Arc flash label on the RMU is still temporary. Please replace it with the permanent label as per the approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624421&prj=626&rqi=huF6bAUpnRhNVDb3Zlq3nh9FcI
YT1ELEC-13-011 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Please re-check the contact resistance test results for ACB Q1. Based on the acceptance criteria (deviation shall not exceed 50% of the lowest measured value), the recorded values exceed the allowable deviation limit. Kindly perform retesting if necessary | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624393&prj=626&rqi=qOZ1ve5pfwLh2crrtMw7s6SDHm
YT1ELEC-13-012 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Breaker settings in 1MSB_F_1 do not match the latest approved Discrimination Study. Please update the settings accordingly and perform retesting if required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624395&prj=626&rqi=oU9Zrkiqqi3uBYRYd4yAKhJBq3
YT1ELEC-11-011 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Breaker settings in 1MSB_C_1 do not match the latest approved Discrimination Study. Please update the settings accordingly and perform retesting if required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624409&prj=626&rqi=oPiMMKCe8YsfiKxX0PjxNm9rpF
YT1ELEC-12-015 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Breaker settings in 1MSB_D_1 do not match the latest approved Discrimination Study. Please update the settings accordingly and perform retesting if required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624411&prj=626&rqi=e1jw8Qxq0LPxtRpvNECcCM37R0
RT1MECH-34-002 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-06-06 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | During the Chiller 4 tie-in activity, water leakage was observed from the Buffer Tank. Later found out that the source of the leakage as a torn flange gasket at the venting connection. The issue was promptly rectified by replacing the damaged gasket. Following the rectification, the tie-in activity resumed and was successfully completed in a safe and controlled manner. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624247&prj=626&rqi=2BH0iKAgXncRIM2KDc73kXvSqu
YT1ELEC-17-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) This is a DC cable. Cable tagging is incorrect; please replace all "L" and "N" identification with "+" and "-" accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624082&prj=626&rqi=5lrVvbIU7pk3xNIjbMxdaRAKCf
YT1ELEC-17-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Apply correct DC cable identification: Red vinyl for DC+ and Black vinyl for DC- | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624085&prj=626&rqi=ikpqbDcekpvmMskEdLNvmTUSRt
YT1ELEC-29-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Apply correct DC cable identification: Red vinyl for DC+ and Black vinyl for DC- | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624095&prj=626&rqi=zA7cbvrLFLacGvddHlLtkjmP4L
YT1ELEC-19-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) Washer size is larger than the cable lug. Please replace with the correct washer size | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624120&prj=626&rqi=6ctg8J1gbG2dP9NfASyZTg9zuq
YT1ELEC-19-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) Flat washer and Belleville washer are missing at cable terminations. Please install as required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624106&prj=626&rqi=lE6wb4YMwjvAeQA5tOu86SbkNS
YT1ELEC-17-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624084&prj=626&rqi=C10r5173cxMoSHzmOy6evIh8hu
YT1ELEC-29-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624094&prj=626&rqi=wDreLILCOUr6NSTYQCeF3UGCMY
YT1ELEC-29-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) This is a DC cable. Cable tagging is incorrect; please replace all "L" and "N" identification with "+" and "-" accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624091&prj=626&rqi=Af1If2byTA9oxIpZhL7dtTvi4P
YT1ELEC-17-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Glanding is not fully covering the cable entry. Ensure proper sealing and full coverage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624087&prj=626&rqi=xrK3W7iy7FTVoL2zM11dugcvu0
YT1ELEC-19-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) Apply correct DC cable identification: Red vinyl for DC+ and Black vinyl for DC- | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624118&prj=626&rqi=Yi09JfLnY5eiJaxwZi0T2C5uvR
YT1ELEC-19-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) This is a DC cable. Cable tagging is incorrect; please replace all "L" and "N" identification with "+" and "-" accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624105&prj=626&rqi=onfCTCSjoekUuFGigXgO0lZu0Q
YT1ELEC-27-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) Remove all temporary markings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624119&prj=626&rqi=2vTj8JKpza8zUlw1stS5JEV3Dt
YT1ELEC-27-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) Apply correct DC cable identification: Red vinyl for DC+ and Black vinyl for DC- | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624102&prj=626&rqi=OtcZiCravU8gJUgCEwpUFxPfLx
YT1ELEC-17-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Cable tray cover is not installed. Please complete the installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624086&prj=626&rqi=3o4O8wSKHmv0Zu0CBQlzlBVr57
YT1ELEC-27-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) This is a DC cable. Cable tagging is incorrect; please replace all "L" and "N" identification with "+" and "-" accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624100&prj=626&rqi=0aeRszkTfWFxmyVgTFhwnqZOFu
RT1ELEC-160-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L6 | DB - Distribution Boards |  |  | Need provide labelling inside panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623918&prj=626&rqi=8R02gl43CZYdX3rNkW26zFwDvc
YT1MECH-28-005 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | During the Chiller 2 tie-in activity, leakage was observed at a tee reducer connection that had previously been used for temporary flushing. GC shall inspect and properly tighten all tee reducer connections following flushing activities to ensure system integrity and prevent recurrence of similar issues | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623911&prj=626&rqi=3YGpDbFZKgNkMAouHJVMhiMyir
YT1MECH-28-006 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Discrepancy noted between the approved MAR and the installed Pressure Gauge (PG). The approved pressure range is specified in kgf/mÂ², while the installed gauge scale is in kPa. Please provide clarification and justification for acceptance. Note: for all Chiller. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623913&prj=626&rqi=Zx0dJE9xLt0ThwiW1JstZIVBds
YT1MECH-110-003 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_B_2 To ISOLATOR 1CHWSTR_B_07_CHWP_1) Cable scratch until exposing the copper wire | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623695&prj=626&rqi=JkJ2JhBi7RVUiPav3Yds0b8gNq
YT1MECH-107-011 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_C_2 To ISOLATOR 1CHWSTR_C_02_CHWP_1) Nut broken on the upper neutral side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623701&prj=626&rqi=bR09I3eNxWCUBtuzQKDgV5EmP7
YT1MECH-107-010 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_C_2 To ISOLATOR 1CHWSTR_C_02_CHWP_1) vinyl damage, please rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623700&prj=626&rqi=MNHI5crFyHnnn84TBppIH450uz
YT1MECH-107-008 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_C_2 To ISOLATOR 1CHWSTR_C_02_CHWP_1) Need to install ferrule cable connector for termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623697&prj=626&rqi=kn6vXOGwnAhVu6uo6kEpPgDb8L
YT1MECH-107-009 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_C_2 To ISOLATOR 1CHWSTR_C_02_CHWP_1) Please ensure that the grounding and neutral termination positions are in accordance with the design, as on the other isolators the grounding termination is installed on the top side while the neutral termination is installed on the bottom side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623698&prj=626&rqi=u1fXI7HcUqqGJiZpFRsacEYZq4
YT1MECH-107-012 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_C_2 To ISOLATOR 1CHWSTR_C_02_CHWP_1) Need cleaning inside Iso panel, too many foreign object | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623702&prj=626&rqi=9HO1BEbBypNn0VzLhWQL5q2DVd
GT1ELEC-1-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | During energization of 1MLTX_B, for power, voltage, and current readings could not be displayed on the RMU panel. Please to investigate and rectify the issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623759&prj=626&rqi=PPVmb4bkRSYUVPJ4d9EYne1HWE
YT1MECH-110-002 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_B_2 To ISOLATOR 1CHWSTR_B_07_CHWP_1) Need to install ferrule cable connector for termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623690&prj=626&rqi=kLwwGhez1pGYxWhuhw5lmJE8EN
YT1ELEC-12-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cables with insufficient bend radius, cable is over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623588&prj=626&rqi=dzHLWJdOauF2hiEUkJiTvFNBeo
YT1ELEC-10-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Incorrect cable tagging, should be "High Temp / Over Temp" and cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623596&prj=626&rqi=jNUCg3TK9PrMnglloUigCHUxuV
YT1ELEC-11-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623586&prj=626&rqi=vKBdrn7AoCmaDCjWXyveE8ypwK
YT1ELEC-13-009 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cable termination not yet completed and cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623584&prj=626&rqi=TFJGGnpB22CylO03WpEF7KkJZg
YT1ELEC-11-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Incorrect cable tagging, should be "High Temp / Over Temp" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623593&prj=626&rqi=gU8tOxZXMSVS2sJjUD1INi9nrT
YT1ELEC-12-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Outgoing nameplate should be to "1CHWSTR_D_04_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623592&prj=626&rqi=mC9HETgkTZZxYxjfFkgptyKcK9
RT1ELEC-12-010 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable From 1MSB_B_1 to 1GPC_B) Tagging Cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623606&prj=626&rqi=QnLtsS971n1LzuHHcErgDA9DvU
YT1ELEC-12-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cable termination not yet completed and cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623590&prj=626&rqi=DA7ZvjDuGeDZfK6fLQKHeTogaB
YT1ELEC-12-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Incorrect cable tagging, should be "High Temp / Over Temp" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623589&prj=626&rqi=eaoqLsDHqg2qW0Xyu5F8MzdOGk
YT1ELEC-11-009 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cable termination not yet completed and cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623587&prj=626&rqi=65OQ9jBUxcif6jMHt8JCZyZgRZ
YT1ELEC-10-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cables with insufficient bend radius, cable is over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623594&prj=626&rqi=UFgCJ6Wbu6HFOFXyBfpsTxoxKc
YT1ELEC-12-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623591&prj=626&rqi=rIAuseIDPKkGLl3dgm9VrkpetG
YT1MECH-108-008 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_F_2 To ISOLATOR 1CHWSTR_F_03_CHWP_1) Nameplate Panel ISO Not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623617&prj=626&rqi=yROIYejqdGtLrGoobRpcZpUoYH
RT1ELEC-150-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue CxL2A BD R-Block Lv. 5) Label not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623639&prj=626&rqi=WGf6eE7YABXb76vPAycYu2BuQR
RT1ELEC-150-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue CxL2A BD R-Block Lv. 5) Incomplete bolts bracket support busduct, please check all bracket support | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623638&prj=626&rqi=sdgM0WlRipS8nHFEyUzUHfRVGy
YT1ELEC-10-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cable termination not yet completed and cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623595&prj=626&rqi=EZv03gmK33p5jIojgbjYe2C67x
YT1ELEC-13-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cables with insufficient bend radius, cable is over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623583&prj=626&rqi=4JcUjGqRxrfeLu7jGNFInXkqTI
YT1MECH-109-005 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_D_2 To ISOLATOR 1CHWSTR_D_04_CHWP_1) Cable insulation is damaged/scratch until exposing the copper conductor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623620&prj=626&rqi=IHjYGUYZxQAV59aaVh1Qia1SDS
YT1ELEC-13-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623585&prj=626&rqi=TekyHgNGBgOd35l4i6O3g6MpUI
YT1MECH-109-006 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_D_2 To ISOLATOR 1CHWSTR_D_04_CHWP_1) Need install Ferrules cable connector | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623635&prj=626&rqi=BaJhbqar5Tc59t6uH9JKyqwhWV
YT1ELEC-5-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Busbar joint between MLTX busduct and MSB not yet torqued and marked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623440&prj=626&rqi=lWBhIS8ijpc0NKrNk7sT3VPZ9M
YT1ELEC-18-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_C_1 to 1UPS_C_2) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623459&prj=626&rqi=fOJQ1ZE7KsGDzkYesf3w7W3NYB
YT1ELEC-18-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_C_1 to 1UPS_C_2) Several cable gland caps area damaged (torn) and not properly covering the gland, please ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623458&prj=626&rqi=2MSETg69nw3KZ1y9UtWzqvc3cG
YT1ELEC-18-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_C_1 to 1UPS_C_2) Cable vinyl not yet installed & missing bolt termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623460&prj=626&rqi=827ErAEYdExQASpcHhtPnidLIS
YT1ELEC-5-010 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Grounding cable from MSB panel to earth bar and from earth bar to SUDB need to be checked to ensure ready for MLTX energization | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623443&prj=626&rqi=6HPfMSpv1kUSTOB4Ar5uOfLLgC
YT1ELEC-5-009 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Busbar inside MLTX incomer cubicle in MSB panel still dirty and dusty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623442&prj=626&rqi=B3R41HYI4OvIL9563yjKqpyG9H
YT1ELEC-119-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1MDSB_D_1 to 1DB_D_CRITICAL) Please ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623456&prj=626&rqi=hpaHm9GMSp3CPJcgtZbWkLtJH7
YT1ELEC-120-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1MDSB_D_1 to 1DB_D_EWALL) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623455&prj=626&rqi=Eai1liVI5B8wEUoZlr2KeGYJ7t
YT1ELEC-120-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1MDSB_D_1 to 1DB_D_EWALL) Several cable gland caps area damaged (torn) and not properly covering the gland, please ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623450&prj=626&rqi=ET26bpGb3XApXuVQzQzjEiUEm6
RT1FD-32-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-6.09 | VES - Vesda |  |  | Pipe affected by paint | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623304&prj=626&rqi=mr4i8EFl7McxaHHkvS3yPb0yny
YT1ELEC-10-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_B_1 to Chiller) Standardize the cable tagging from "1MSB_B_1 to LBS 1CHWSTR_B_07_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623303&prj=626&rqi=4Pvf2n746QtPt6TJG37TZySr6P
YT1MECH-96-001 | JK01-2 | APAC | Closed | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | DCOS cable has not yet been pulled into the CRAH unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623307&prj=626&rqi=DzcJMRICcLBFIcndfCjJQrYeGs
YT1ELEC-11-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Aux power control cable inside MSB panel found over-bent. Please rectify the cable routing/installation Also, GC to clarify the reason why this cable was skipped during CxL2A & CxL2B process | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623300&prj=626&rqi=G3O2YK1D2rFKQp5peLslip2wIB
YT1ELEC-10-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_B_1 to Chiller) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623306&prj=626&rqi=XnVmVvOag3KqOPcEqLZvsCY8Y7
YT1MECH-32-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to Chiller) Standardize the cable tagging from "1MSB_C_1 to LBS 1CHWSTR_C_02_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623316&prj=626&rqi=0fEkGZJxz6kCeyYbhPJogQGk68
YT1ELEC-11-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to Chiller) Standardize the cable tagging from "1MSB_C_1 to LBS 1CHWSTR_C_02_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623309&prj=626&rqi=ztRUO6GFwL8ourZMS47Trmq5u9
YT1ELEC-11-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to Chiller) Please ensure glanding cap fully properly sealing & cover tray installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623314&prj=626&rqi=iJjZKZxT4bK7FncLRTBesTaPw5
YT1MECH-31-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A LV Cable 1MSB_B_1 to Chiller) Standardize the cable tagging from "1MSB_B_1 to LBS 1CHWSTR_B_07_CH_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623308&prj=626&rqi=eOh7w4crCAKRLFH9UTXcAljZ8a
YT1MECH-88-001 | JK01-2 | APAC | Closed | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | DCOS cable has not yet been pulled into the CRAH unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623298&prj=626&rqi=2Mls5KWeAxZD3pjgICRmkoozYt
RT1MECH-35-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | anchor bolts need re-torque and re-mark (it still moves when perform torque check) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623310&prj=626&rqi=k44CwHMvyUpasqyw52K6sxlVD7
RT1FD-32-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Fire Detection | equipment | ASDSP-6.09 | VES - Vesda |  |  | support pipe misalignment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623305&prj=626&rqi=q39SH4NbRY3n1M66XUv3bNuar4
YT1ELEC-11-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Outgoing nameplate should be "to 1CHWSTR_C_02_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623312&prj=626&rqi=47MlrJ4OvyqK4QoyjbQUXgnZtE
YT1MECH-89-003 | JK01-2 | APAC | Closed | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | DCOS cable has not yet been pulled into the CRAH unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623299&prj=626&rqi=cCHpmM2mc2L5atfF9mIc1jxH5C
RT1SEC-20-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_5_DH | ACU _ Access Control |  |  | door 05:11 & 05:13 door contact not yet install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623286&prj=626&rqi=yyiVHyZmmOPw06Oka5cIFjwIBZ
RT1SEC-20-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_5_DH | ACU _ Access Control |  |  | door 05:10 not yet install at all | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623284&prj=626&rqi=KhpeAuft7K6ZIBpfM8ZBuffHQS
YT1ELEC-12-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to Chiller) Please remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623319&prj=626&rqi=wtFh90HDPYBqNpO0ZdCEPOG2iv
YT1MECH-30-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to Chiller) Standardize the cable tagging "from 1MSB_D_1 to LBS 1CHWSTR_D_04_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623320&prj=626&rqi=Gd8uY0RigqcrvSxCoSQepbv0AH
YT1ELEC-12-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to Chiller) Standardize the cable tagging "from 1MSB_D_1 to LBS 1CHWSTR_D_04_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623318&prj=626&rqi=4jLAMW6aVuCKEyu15LQ8Vx3jem
RT1SEC-20-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_5_DH | ACU _ Access Control |  |  | reader not yet installed, door 05:16 Note: it's because GC's work (flushing pipe), that make the door cannot close so there will also become GC scope to rectify this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623273&prj=626&rqi=1LfCPNeDmQOvSm48keksLOapqb
RT1SEC-20-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_5_DH | ACU _ Access Control |  |  | door 05:12, 05:17 handle and accessories not installed yet. door 05:11, 05:13 accessories not yet. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623287&prj=626&rqi=VuralMR8qNAnhUzYs3M83EzONk
RT1MECH-35-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Labelling / equipment name tag not yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623315&prj=626&rqi=owy0jlLQ9dt9s3jd2gTwR9y03M
YT1MECH-85-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_21 | CRAH - Computer room air handler |  |  | Incomplete insulation and jacketing observed at several points along the CHW piping | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623302&prj=626&rqi=rSdzeFmerZiRZmsLuXjSkBSf8v
RT1SEC-20-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_5_DH | ACU _ Access Control |  |  | door 05:16 cannot close because of temporary flushing pipe, it causes the reader for this door cannot installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623281&prj=626&rqi=zsjXizgaDJ4GltHS61B8cji0ob
RT1SEC-7-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_2 | ACU _ Access Control |  |  | door 02:19 wall finishing around the pinpad installation require proper finishing, temporary flushing pipe are blocking the door so it cannot close, and also door accessories not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623297&prj=626&rqi=a1nDLSznGyyAYesONXp3KEsWMO
RT1MECH-35-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | manhole and drain pipe not yet insulated and jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623313&prj=626&rqi=aKH7vC54TR0Ha5G6EBt95FmEBU
RT1FD-32-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-6.09 | VES - Vesda |  |  | please upload Factory Test Data & Material submittal document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623110&prj=626&rqi=MAWCuQhaNQtpeVl29IW5DJi6Iq
RT1MECH-108-008 | JK01-2 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-05-25 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | LCD display is damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622964&prj=626&rqi=9kuAOtSu42gLIViOQYqQ3P8fck
GT1ELEC-3-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623032&prj=626&rqi=sHxdLlVDJuWtiQD96uYRPDRxa1
RT1ELEC-52-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_1 TO 1RPP_BRI_01_01] Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623003&prj=626&rqi=WGjgD3VmvpR20qHsSwE8iy5Yoj
RT1ELEC-52-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_1 To 1RPP_BRI_01_04] Cable Tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623002&prj=626&rqi=0HFmRKS5CtqcH663I6HfLY9mlY
RT1ELEC-52-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_1 To 1RPP_BRI_01_01] Dressing cable need to tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623004&prj=626&rqi=p3mCip5adZw45pWkr5Lvu9skoV
GT1ELEC-2-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623034&prj=626&rqi=saliDGbTrh1eq2wrOS9c7ZfD4k
GT1ELEC-2-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | BTU of RMU_D energized from temporary power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623035&prj=626&rqi=YzoQJ4s4fdFHdGhWkLninGRxf8
YT1ELEC-166-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | [Issue CxL2A LV Cable 1MDSB_B2 to Cooling Array Fan 1TOU_B1] Need to add belleville/spring washer on both side (Phase N,R,T) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622986&prj=626&rqi=ni8hmPXCHp1Y4e1OLsQ8AqpwVn
RT1ELEC-22-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | [issue CxL2A LV Cable 1UPS_B_2 to 1MDSB_B_2] Need to add cover tray | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622970&prj=626&rqi=60N98Mmqrt4kS8B054xxeXMc1a
RT1ELEC-22-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | [issue CxL2A LV Cable 1UPS_B_2 to 1MDSB_B_2] Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622968&prj=626&rqi=0gpa3QurqSlhsQxm4n7xXViQZN
RT1ELEC-22-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | [issue CxL2A LV Cable 1UPS_B_2 to 1MDSB_B_2] Belleville need to installed in two side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622969&prj=626&rqi=fY8fO7Xj9OGmrNA9INBFyYGXqH
YT1ELEC-166-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | [Issue CxL2A LV Cable 1MDSB_B2 to Cooling Array Fan 1TOU_B1] Need to remove temporary marking cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622984&prj=626&rqi=JNK8eCgtRoozhfeTC8RayDrPyN
RT1ELEC-22-004 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | [issue CxL2A LV Cable 1UPS_B_2 to 1MDSB_B_2] 3 Grounding cables are stacked on one busbar. (for All UPS Mech & possible IT) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622971&prj=626&rqi=bBOwkDHMmskf6JOyJTLYM3Mqmc
YT1ELEC-47-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_2 TO 1RPP_BRI_02_01] Need to remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622988&prj=626&rqi=TALS2FBCx5nhbqJSGl35iVFAtO
YT1ELEC-47-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_2 TO 1RPP_BRI_02_04] Grounding Vinyl loose, need to add cable ties | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622992&prj=626&rqi=tsmZxkcWZPFv74xZ1mivi0AFqG
YT1ELEC-51-001 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A Laying Cable 1STSSB_D_2 To 1RPP_DR1_02_05] Cable scratch damage until the insulation is visible. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623009&prj=626&rqi=xczvug02N5fTLFZ1mowDZ6gbEE
YT1ELEC-3-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | During white glove inspection, equipment body bolts are missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623037&prj=626&rqi=3ZTCPZZkNlPz2SQ4NtniDNFHxB
RT1ELEC-56-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A Laying Cable 1STSSB_D_1 To 1RPP_DR1_01_05] Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623013&prj=626&rqi=MG5O1JlM7aRadU6o8GV5zUWydy
YT1ELEC-47-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_2 To 1RPP_BRI_02_01] Grounding has not been fitted with a cable lug and has come loose. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622991&prj=626&rqi=7L1dqYxYqQTwnmCIop0hhvdzyW
RT1ELEC-56-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A Laying Cable 1STSSB_D_1 To 1RPP_DR1_01_05] Vinyl need to rectify and cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623014&prj=626&rqi=ZAMFX8mD4816Y4MwxnK5XGpXZt
YT1ELEC-51-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A Laying Cable 1STSSB_D_2 To 1RPP_DR1_02_05] Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623011&prj=626&rqi=rmU5MiTj0PAMjZoyoWtaqwlR35
YT1ELEC-51-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A Laying Cable 1STSSB_D_2 To 1RPP_DR1_02_05] Vinyl need to rectify and cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623012&prj=626&rqi=NH5cvJhFlPuf78Rxx15Fr05Cee
YT1ELEC-4-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | During white glove inspection, equipment body bolts are missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623036&prj=626&rqi=rnODpAvjA0An3tLsogWCSOi3mG
RT1ELEC-26-006 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | [Issue CxL2A Laying Cable 1UPS_D_2 to 1MDSB_D_1] Vinyl need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623025&prj=626&rqi=VaBX8Z6WzhssnXwRbRJeLW8H9S
RT1ELEC-26-005 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | [Issue CxL2A Laying Cable 1UPS_D_2 to 1MDSB_D_1] Cable tagging is incorrect, need to rectify revise to: from 1UPS_D_2 to 1MDSB_D_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623023&prj=626&rqi=wh2rpfgOHwx7xjggCVYqz0UzG9
RT1ELEC-26-007 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | [Issue CxL2A Laying Cable 1UPS_D_2 to 1MDSB_D_1] Need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623026&prj=626&rqi=EsnWbDM5ZT9R4arEaHBKGUPFTo
YT1ELEC-30-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | (Issue CxL2A LV Cable 1UPS_C_2 to 1LIBATTSYS_C_2) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622910&prj=626&rqi=jRFkPXbCvcJPIUt2dEBsGRDGXS
GT1ELEC-1-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622895&prj=626&rqi=ZL0jneUsJ1HbNJybYG2VqgMiBe
YT1ELEC-18-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1UPS_C_2 to 1LIBATTSYS_C_2) Incorrect cable tagging, should be "to 1LIBATTSYS_C_2" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622907&prj=626&rqi=qAJioCMaRZcS2ftdpOfneYnPxd
YT1ELEC-18-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1UPS_C_2 to 1LIBATTSYS_C_2) Cable inside UPS has not been provided with cable tagging, cable termination is not properly installed, and cable vinyl is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622908&prj=626&rqi=qIRqPj1TYgFuyvVyn2nn7pRS95
GT1ELEC-4-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622894&prj=626&rqi=G2sQFjtK0NnQotfHmG6cdkMZrZ
RT1ELEC-15-026 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Need to install cable tagging & remove temporary marker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622905&prj=626&rqi=DukIBEi5eZ7KOLI8LTDzY2mo9P
RT1ELEC-15-020 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Corrosion observed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622898&prj=626&rqi=VfSRciipb4K43zzWJCx3Ro5BnX
RT1ELEC-15-025 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | All bolts need to torque & marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622903&prj=626&rqi=Y51vj3RjsHeFkFlaFhvPg83Q8h
RT1ELEC-15-023 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Temporary marking need to remove | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622901&prj=626&rqi=ml8UWFGDn67dDQSXa6141fh0Y5
RT1ELEC-15-021 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Generator dirty & dusty. Need deep cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622899&prj=626&rqi=TgQJuynojKatL2Np0bPImR1NkN
RT1ELEC-15-024 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Need to add additional base frame as per design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622902&prj=626&rqi=r0auXIEJBkBJMu8TrtivF51Ii4
YT1ELEC-5-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Incorrect cable tagging external cable to MSB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622792&prj=626&rqi=xwWTxXm3dGRJJAOQWiZjbIS0K1
RT1ELEC-13-027 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Need remove straps and blocks for shipping (Cleaning) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622767&prj=626&rqi=S5DgX8qmZoJc9fJ1atBBTEcEHp
RT1ELEC-13-026 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Need to rectify the corossion pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622766&prj=626&rqi=w4M2UaI00SB4NfewbDSMkgG7hH
RT1ELEC-15-022 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Equipment tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622900&prj=626&rqi=7KgW2yPHXDd2awDHDnnrJg6qQU
RT1ELEC-13-025 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | many scratch on body generator, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622765&prj=626&rqi=7AwD4FiGneX7EnYcYAlPcGjlwu
RT1ELEC-15-027 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Generator cable not yet torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622906&prj=626&rqi=eaShmf13sZUTB6WygMhn6ODvgq
YT1MECH-56-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_C_11 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622438&prj=626&rqi=w2zGyiRxnbG5QCzlEyMKMUKAUQ
RT1ELEC-13-024 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Please add labelling cable to GCP Gen_D | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622597&prj=626&rqi=GbJwG9tk3BGZrZ0wG14NQPlPb5
YT1MECH-69-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622457&prj=626&rqi=MrwfNiEgNTqGPLFn7fekPZlfUp
YT1ELEC-4-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | During white glove inspection, flexible busbar was found disconnected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622656&prj=626&rqi=KVwZ8nV9DTvNcB4l3sMEkxa8kc
YT1MECH-55-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_C_09 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622437&prj=626&rqi=XdFoLhwPRFVc6n0jceSJAXBWGN
YT1MECH-77-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622451&prj=626&rqi=yp9OUw2QFQeWc1KA6fwthmn6te
YT1MECH-78-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622450&prj=626&rqi=MCYWwUC0kJ5FHFP5rwSrSDO8IG
YT1MECH-51-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_C_03 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622430&prj=626&rqi=FGUnW7nXmfOvQrj8Aj4aojbmxD
YT1ELEC-169-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) Cable tagging not yet installed & please rectify the cable vinyl | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622414&prj=626&rqi=jMdPMnrbGsbpwdZXW2o3XC1zC9
YT1ELEC-169-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622416&prj=626&rqi=ymg8hvO8Qckv94t7Tj9UVLM2Fw
YT1MECH-50-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_C_01 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622426&prj=626&rqi=cE60SpGTXw21yZtdlkHLediJK1
YT1MECH-78-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622448&prj=626&rqi=TsdUkvYQ0Z4HtvajcmOc6X9Vws
YT1ELEC-4-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | During white glove inspection, control cable was found disconnected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622668&prj=626&rqi=9GLS4AGkPIFREw1fGSRWoyeIyM
YT1MECH-54-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_C_07 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622434&prj=626&rqi=RiOvqEP7kTgDgUlXghB6iO8eEW
YT1MECH-69-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622442&prj=626&rqi=EpSg48stz1z2xhTgdVIlSUrw6n
YT1MECH-75-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622456&prj=626&rqi=noWSSS6Vsx1G7ZGxMynzchxoaL
YT1ELEC-169-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) Cable tray end sections are open. Please confirm and install end caps where required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622425&prj=626&rqi=LZKRXBkxSqvGsNFAIWHJw0ztky
YT1MECH-52-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_C_05 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622431&prj=626&rqi=owlOEMvP3RfLTrZLNzyhEVQeYm
YT1ELEC-165-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_2 to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622459&prj=626&rqi=inNUcdQvlJ4H6XhcG7ppOVExch
YT1MECH-75-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622444&prj=626&rqi=1bx8r9X9AqiqO2QUVYcCsLnjsg
YT1MECH-76-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622445&prj=626&rqi=BcOH4kFA9PMgz9qSUd1218UQJ5
YT1ELEC-169-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) Cover trunking not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622417&prj=626&rqi=kpGnvP4Ly9maeECu7r81t7rJrq
YT1MECH-53-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_C_06 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622432&prj=626&rqi=cLCFIyR05AmadFKx7GZjOGyOfW
YT1ELEC-169-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) Bonding jumper not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622419&prj=626&rqi=xrNEoX19hhHqdcyOtTDkbqstz6
YT1MECH-77-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622446&prj=626&rqi=7PQR5pDwaELGKWmvXsDhynYYfL
YT1ELEC-169-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) incorrect cable tagging feeder name | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622415&prj=626&rqi=El23uRpROxVPvhsARnh72Y7RtN
YT1MECH-76-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622455&prj=626&rqi=vofNu36yw1VPgRLlwfPXraJNvv
YT1MECH-89-002 | JK01-2 | APAC | Closed | P1 High CX | DimasKurniawan@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | \e observed during Cx activity (CRAH_F_41) that the HMI was damaged due to impact during ongoing construction work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622382&prj=626&rqi=MXqHu7HqIfw9zMoRTYi6VlbqRK
YT1ELEC-1-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | General Contractor | L2B | Missing Components | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Rear panel bolts of the RMU are still missing and not yet installed (around 10-15 pcs) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622361&prj=626&rqi=3dSyxRGmL7II5pI1SyMXb1VLsi
YT1ELEC-1-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622277&prj=626&rqi=4iyBfGxtWwW5uqS2GxIDBDw44S
YT1ELEC-1-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | During site walk for RMU energization readiness, solenoid was found not functioning properly resulting in energization activity unable to proceed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622274&prj=626&rqi=p39MAQrPeTc76BpYQaNBEvlh4f
YT1ELEC-4-014 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | The panel door lock cannot function properly due to the earthing key not being removable and causing the panel door unable to close normally | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622276&prj=626&rqi=MyVSTVPvHNWt9pW15QUO14LuHj
YT1ELEC-4-015 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | During RMU energization readiness inspection, several panel bolts were found loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622362&prj=626&rqi=m9Kxa9No52bXj1alrurmdGstZ5
YT1ELEC-4-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622275&prj=626&rqi=NRg0HiGB0Nz0iyHWjRmgXmna6y
YT1MECH-89-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | Need to add water flow direction labeling on the inner pipe of the CRAH unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622378&prj=626&rqi=nVyAEEC45Mq9HPLVQja1Ouu1tC
GT1ELEC-1-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | BTU_B Energized using temporary power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622911&prj=626&rqi=oeKPMwYE88CbrnLtdHE4neMIzh
RT1ELEC-14-023 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Please add labelling grounding + tidy up heat shrink | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622259&prj=626&rqi=PYl9oBAhauyBu09TbI0JfsySiP
RT1ELEC-14-022 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Need remove straps and blocks for shipping Gen (Cleaning) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622258&prj=626&rqi=ZnrZk6odXmrtA5djojxvmXPlct
RT1ELEC-14-024 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Spring mounting need rectify, cannot be tightened to the specified torque | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622260&prj=626&rqi=i6y6jdfxgepuplYleeRMSoe671
RT1ELEC-14-025 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Please install cover tray grounding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622262&prj=626&rqi=nKOr2tWXuD7YD9hYqBjB21tr4j
RT1ELEC-14-026 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Need install jumper grounding tray cable containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622263&prj=626&rqi=QhGTeTXii5eHbXiZ7TznYu6twN
GT1ELEC-3-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | BTU_C energized using temporary power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622159&prj=626&rqi=1uInYU6PXBqUgaErIkA1AgfzCf
YT1FD-13-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Fire Detection | equipment | ASDSP-3.10 | VES - Vesda |  |  | need to clean and provide proper cover for equipment to minimize debris, dust and also need to repaint pipe which affected by wall painting | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622268&prj=626&rqi=w8kU6hH4PpgQtyIpOgj8tropl9
YT1FD-38-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Fire Detection | equipment | ASDSP-7.09 | VES - Vesda |  |  | Please provide more proper labelling name for isolator switch, refer to phase 1 (photo attached) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622267&prj=626&rqi=Ei57WTnEHAcVfpoLZZSHfQTXS4
RT1ELEC-14-020 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Need to rectify the corrosion pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622255&prj=626&rqi=2L0mCRy0LNJbFn1eLoobZOw8Ev
RT1ELEC-14-021 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Please provide shop drawing for inspect dimension panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622257&prj=626&rqi=YroFFJqEsHmhe3OpEO0R0Wnp19
RT1ELEC-14-019 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Equipment damage (body scratch) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622252&prj=626&rqi=KM9atmrEh8eaB1ftMWEbbAaHmu
RT1ELEC-14-027 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Need install vinyl properly and cable ties | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622264&prj=626&rqi=a9EtfsSNzOJSudOm6TPsLwKIKG
GT1ELEC-4-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | BTU_F energized using temporary power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622158&prj=626&rqi=Fgb2Vq57g2OtsD4fTDwdXu1HkE
YT1ELEC-1-002 | JK01-2 | APAC | Closed | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | DCOS conduit pipe damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622156&prj=626&rqi=yyrJAfJtW8zJqsMsljymueFaIO
YT1ELEC-1-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Please update the breaker nameplate numbering to follow the approved nameplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622155&prj=626&rqi=rG3SNcaFOOcyleSYCWRwYjFZUE
YT1ELEC-4-010 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Need install Cover rubber cable gland, because make debris inside panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622101&prj=626&rqi=HBkrGb5uVgQJp19X8jpmrbvgM3
YT1ELEC-4-011 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Need replace connection grounding system at 1SUDB Side to 1RMU_F_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622102&prj=626&rqi=RGsHhVd8lw6JM4xtgCalZ9ktqw
YT1ELEC-4-009 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Tagging Grounding incorrect, Revise to: 1RMU_F_1 to EB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622100&prj=626&rqi=KNLB9f3lt2PTVtfQXvV94Yjg6U
YT1ELEC-4-008 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Tagging MV Cable incorrect, Revise to: 1SUDB to 1RMU_F_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622099&prj=626&rqi=QJ75mAdQh3hQAz5xSrphfjc2Ph
YT1ELEC-2-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Please provide the termination point cover at the RMU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622113&prj=626&rqi=bb5jWrtmJ9Wu9X3EwIuzaZSMOG
YT1ELEC-3-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Please update the breaker nameplate numbering to follow the approved nameplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622110&prj=626&rqi=HtnJBG49nMvhsRjEQyz5HgUSzP
YT1ELEC-4-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please update the breaker nameplate numbering to follow the approved nameplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621953&prj=626&rqi=4nG4L0MrtnqM8VOa2cPymxulEZ
YT1ELEC-4-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please provide the termination point cover at the RMU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621955&prj=626&rqi=EbZnDbGMuWl75FkqsuSqtE6Qio
YT1DCOS-15-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Controls | equipment | 1DCOS_1_SCP_07 | DCOS - Control Panels |  |  | During the site walk, CTA observed damage to the conduit at the SCP07 panel to sensor, and please add support to the conduit for reinforcement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621956&prj=626&rqi=eiu78xYkXvHksMzeMtGRaclZ6D
YT1FD-12-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-2.10 | VES - Vesda |  |  | Report CxL2A need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621583&prj=626&rqi=4eCA6VP9mekcxiVFomYXBg25yl
RT1ELEC-27-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Drawing inside panel not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621615&prj=626&rqi=HQz67b0oo6Rkc3CCVwOEesRYGe
YT1FD-7-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-2.04 | VES - Vesda |  |  | Report CxL2A need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621572&prj=626&rqi=tx5y5nYItR68ySrDkAANICyDwa
RT1ELEC-152-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue Tx Room B) Please follow Equinix standard for cable termination, not yet installed flat washer & spring/belleville washer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621343&prj=626&rqi=IVOxGA5pm97ITG4ZIGl7kf0UyY
RT1ELEC-27-005 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Add temporary protection to prevent for construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621633&prj=626&rqi=ln7SigWOtJJl64H8KPI4vQN0cP
YT1FD-11-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-2.09 | VES - Vesda |  |  | Report CxL2A need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621582&prj=626&rqi=4eMRVbHMDHAJGdGTj3bi4pxono
RT1ELEC-27-003 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621631&prj=626&rqi=ML6V5tYSNoQHTkp8uGHW8sBOQo
RT1FD-10-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-2.08 | VES - Vesda |  |  | upload RFIT doc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621570&prj=626&rqi=NdgYDfm6J2XDUND0wtFujrvlQf
RT1ELEC-54-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_1 to 1RPP_CR1_01_05) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621585&prj=626&rqi=lmasaepJhCcfBSVCe8CeLcvZ2z
RT1ELEC-152-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue Tx Room B) Earth bar label not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621344&prj=626&rqi=AsBISbKMSP0eAVwyf2kbrzItYw
RT1ELEC-15-019 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual breaker rating: - Breaker Q3: 6A actual 16A - Breaker Q4: 6A actual 16A - Breaker Q5: 6A actual 16A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621339&prj=626&rqi=pAWw84DS833Gd6qL1j4Cq1DtOh
YT1FD-10-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-2.08 | VES - Vesda |  |  | upload report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621581&prj=626&rqi=g3YP9WvENjKi2V3k742CPD5AcN
RT1ELEC-152-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue Tx Room B) Grounding cable size for the RMU & MLTX is not in accordance with the design. The installed cable is 300 mmÂ², while the approved design requires 240 mmÂ² | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621342&prj=626&rqi=l0oD3c0pfAnDpymblbjBzgrjzq
RT1ELEC-27-006 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Equipment is dirty with dust and foreign object, Cleaning (FOD) is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621634&prj=626&rqi=fEXyVuEjlOYe0vYWKN59fzez3R
RT1ELEC-152-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue Tx Room B) Please ensure all grounding cable tagging consistent as per standard | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621345&prj=626&rqi=72TqDoZ1S65VULrsjZAHa5rhN5
RT1ELEC-27-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Any scratch on body panel 1UPS_F_1, need to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621608&prj=626&rqi=aE8hY5LsrZznPkhg2CJbivmi9Y
RT1ELEC-55-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_2 to 1RPP_CR1_02_03) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621593&prj=626&rqi=c15kI7EI2K7PxoYRoN984nVwIM
RT1ELEC-27-004 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Nameplate panel not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621632&prj=626&rqi=oOWhmlj0LFVhmaZCz5pnI9SmdE
RT1ELEC-54-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_1 to 1RPP_CR1_01_05) Remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621587&prj=626&rqi=K2tCzy5AAZuWqCl6uyzYRotkpZ
RT1FD-16-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-4.03 | VES - Vesda |  |  | need to upload doc: 1. Technical Submittal 2. Factory Test Data 3. RFIT 4. Drawing (already approval) 5. Report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621065&prj=626&rqi=v9ntEi92GTWveI0Jo9Gb9JBK0s
RT1SEC-19-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_4_DH | ACU _ Access Control |  |  | door contact sensor has not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621047&prj=626&rqi=PqKyEBwv3VmiVwGE0uIVMz8unX
RT1SEC-19-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_4_DH | ACU _ Access Control |  |  | issue for CSA GC team; door accessories have not installed yet, such as door handle, door loop, mortise lock, door closer, and even there is one set of complete doors have not been installed yet (one of door at caging door) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621046&prj=626&rqi=CEukIm8BhjLCol5luH7MEBIta1
RT1MECH-9-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | issue LCP panel. labelling cable not yet complete | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621049&prj=626&rqi=ZM0idg6Cudxhm64rfPxzGpVxSy
RT1MECH-2-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | Pipe overflow does not install yet. attach photo once already done. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621072&prj=626&rqi=utKrashLfimhCorYIVNTsi6lLY
RT1FD-18-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-4.05 | VES - Vesda |  |  | need to upload doc: 1. Technical Submittal 2. Factory Test Data 3. RFIT 4. Drawing (already approval) 5. Report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621066&prj=626&rqi=Mesrao3Ioada4K8x8Q2MuloIlB
RT1FD-14-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-4.01 | VES - Vesda |  |  | need to upload doc: 1. Technical Submittal 2. Factory Test Data 3. RFIT 4. Drawing (already approval) 5. Report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621063&prj=626&rqi=tnS1sAkHRqME8905JBQq9Qj7pl
RT1MECH-6-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | issue LCP panel. labelling cable not yet complete | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621048&prj=626&rqi=kOOOzmBCHi67bGNtrfJeJCSfwR
YT1ELEC-2-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable 1RMU_A to 1RMU_D) Need to add tray/support cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621093&prj=626&rqi=QMynrmv6QdHT1K5KNyZBxgk08Q
YT1ELEC-2-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable 1RMU_A to 1RMU_D) Need to add cable tagging/label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621090&prj=626&rqi=KiHgJjWniWY7cjHo4UDue3rw57
RT1FD-15-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-4.02 | VES - Vesda |  |  | need to upload doc: 1. Technical Submittal 2. Factory Test Data 3. RFIT 4. Drawing (already approval) 5. Report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621064&prj=626&rqi=445kn7HuvJxficXm5gPdsw9LD0
RT1SEC-21-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_7_DH | ACU _ Access Control |  |  | door contact sensor has not been installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621045&prj=626&rqi=LKt8fATBs7VbSWevmy2dSpUKSv
RT1FD-23-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.01 | VES - Vesda |  |  | Factory Test Data need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621042&prj=626&rqi=Qj5BFnDVA74pVD933u4n9tWZcZ
YT1ELEC-2-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable 1RMU_A to 1RMU_D) Cable cleats not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621092&prj=626&rqi=1Xh7CksF8OzZ5tHDmRSW6J7KEu
RT1MECH-2-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | need to upload doc: 1. O & M Manuals 2. Shipping & Delivery Receipt (if any) 3. Approved SoO 4. Report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621067&prj=626&rqi=JH1ayyGsq5dXIYRG3NUNsZq2Zy
RT1SEC-21-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_7_DH | ACU _ Access Control |  |  | issue for CSA GC team; door accessories have not installed yet, such as door handle, door loop, mortise lock, door closer, and even there is one set of complete doors have not been installed yet (cool spine area) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621043&prj=626&rqi=icvafugVuvrdZjiBdWVTMT0BCN
RT1SEC-21-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_7_DH | ACU _ Access Control |  |  | issue for CSA GC team. a long thread blocking the door so it cannot close properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621044&prj=626&rqi=EAQZKIPpcjzJuMLGEL7HfAJ0kk
RT1MECH-2-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | Fusible link cable issue. attach photo once already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621069&prj=626&rqi=wGZxbw9r6vOQKFJjaaJcqSGc2o
RT1MECH-2-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | Pipes need to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621068&prj=626&rqi=yQI8AgzObYONwefQYNGNzWIVZg
RT1MECH-2-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | solenoid cable issue. attach photo once already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621074&prj=626&rqi=yipHNDADFlId1NypNv3BzVvMPE
YT1ELEC-12-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Vinyl cable color for Phase S / L2 should be brown, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621025&prj=626&rqi=XaQ1r7TGm0JMa66YwIjfVWMI56
RT1ELEC-154-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_5 | ERTH - Earthing |  |  | (Issue Tx Room C) Conductor still exposed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621031&prj=626&rqi=ossnBWOpPzYysIBku2BawcxFDb
RT1ELEC-154-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_5 | ERTH - Earthing |  |  | (Issue Tx Room D) Please follow Equinix standard for cable termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621033&prj=626&rqi=ir7FIhbPAjOmSqvkIHJEMIFFvz
RT1ELEC-13-021 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Please remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621028&prj=626&rqi=9Tg7yi4nksfMtcSuOwMttGlp1a
YT1ELEC-12-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Missing bonding jumper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621027&prj=626&rqi=L9HmXQwqFomEvERjmJ75XJupac
RT1ELEC-154-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_5 | ERTH - Earthing |  |  | (Issue Tx Room C) Please follow Equinix standard for cable termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621032&prj=626&rqi=hjkKO85huhjFRdFZFIllNFNWlZ
YT1ELEC-11-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to 1GEN_C Panel GCP) Need to add belleville or spring washer on the bolt termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621018&prj=626&rqi=wWO5dDUMoX6d5iIV67o0vi9Fcw
RT1ELEC-13-023 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Vinyl cable color for Phase S / L2 should be brown, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621030&prj=626&rqi=3mjoofa8bAiTQdEmrotSU7t43C
RT1ELEC-13-022 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Cable vinyl loose & not properly covering the lug | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621029&prj=626&rqi=xeehV7N82s4SOZk4DS6UDRxIfi
YT1ELEC-11-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to 1GEN_C Panel GCP) Cable vinyl is not properly covering the termination area between the cable and cable lug | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621019&prj=626&rqi=jr7oJI4I2oxBIdWbhcapyozpeN
YT1ELEC-12-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) 1. Cable tagging not yet installed 2. Glanding cap is torn. Ensure the gland is properly covered and sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621026&prj=626&rqi=MYTUNP2c1mJJhHxcLKhAxCmihz
YT1ELEC-11-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to 1GEN_C Panel GCP) 1. Cable tagging not yet installed 2. Glanding cap is torn. Ensure the gland is properly covered and sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621020&prj=626&rqi=EXY0HTBUda2ryPCTjRO6Rj3ZLE
RT1ELEC-14-018 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to 1GEN_C Panel GCP) Vinyl cable color for Phase S / L2 should be brown, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621021&prj=626&rqi=q4AilsYVGWOo7yYmKPMdPBpa1i
YT1ELEC-12-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Cable vinyl is not properly covering the termination area between the cable and cable lug | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621023&prj=626&rqi=IuF8MP3iDlJQyP7ZQjRF2C5wzB
YT1ELEC-12-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Need to add flat washer & spring washer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621024&prj=626&rqi=sqMQCruNTtslCIuriM5kpQGLI2
RT1ELEC-15-017 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620750&prj=626&rqi=p29e9xiUpL3Xme6ronocVUWmz3
YT1ELEC-13-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1MDSB_F_1) Tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620731&prj=626&rqi=rVFnKABBFCYiZ3eKaTQuixtwgC
YT1ELEC-13-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1MDSB_F_1) Conductor still exposed & cable vinyl loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620728&prj=626&rqi=nMhLN5We3OQR8xHU6PtTfLp0po
YT1ELEC-13-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Glanding cap is torn and not properly sealing/covering the gland | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620739&prj=626&rqi=TbTPZTjen8wAib5LrthSMm3yYp
YT1ELEC-13-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Cable vinyl broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620737&prj=626&rqi=BK5qi94wBSwAXgZpt9MPPCbLM7
YT1ELEC-13-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620738&prj=626&rqi=MIdXSVwwc0KF9cX3fx8EXEBC4Z
YT1ELEC-13-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Need to add spring washer on the bolt termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620740&prj=626&rqi=ZBbIqLG8LIqNqG3Q4477VmNXrZ
YT1ELEC-13-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Vinyl cable color for Phase S / L2 should be brown, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620747&prj=626&rqi=1OpPLy7yQCqpzJC6adGdVbFCGV
YT1ELEC-12-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1MDSB_D_1) Glanding cap is torn. Ensure the gland is properly covered and sealed & please remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620911&prj=626&rqi=GCb1N5V3tsaHL9wf96Ozi4V8CM
YT1FD-28-003 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Fire Detection | equipment | ASDSP-5.07 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620872&prj=626&rqi=cV5OnpmNdtOXIKWaacDswn2hHS
YT1ELEC-48-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_1 to 1RPP_CR1_01_03) Cable vinyl & cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620917&prj=626&rqi=Qqo0zrSdAjCGYsHkCB3prYiCNc
YT1ELEC-48-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_1 to 1RPP_CR1_01_03) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620916&prj=626&rqi=WIAnG0CFQZFg36YhyUOTfKRjm3
YT1ELEC-48-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_1 to 1RPP_CR1_01_03) Please add grommets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620918&prj=626&rqi=cAMcatlEckEc6uKir5JAu5qyQi
YT1FD-29-003 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Fire Detection | equipment | ASDSP-5.08 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620874&prj=626&rqi=nZRqhLtNromWa8V0RfzpwWqaJy
RT1ELEC-15-016 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Need to add flat & spring washer on the bolt termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620749&prj=626&rqi=hoOeWDBBCa7zsiCPJSVKouExGL
RT1ELEC-15-018 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Vinyl cable color for Phase S / L2 should be brown, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620751&prj=626&rqi=dAFuD2xiDHit2JE46oqaCcgdQg
YT1FD-25-003 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.03 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620869&prj=626&rqi=9BBJWrlyQBwxQ5azh7YWi9HhhH
YT1FD-33-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Fire Detection | equipment | ASDSP-7.01 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620867&prj=626&rqi=DMbAvWV1kUpxwCypiyJb3IyJRt
YT1FD-24-002 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Fire Detection | equipment | ASDSP-5.02 | VES - Vesda |  |  | 1. Isolators switch existing but cabling not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620868&prj=626&rqi=I4WNkNK7XRa81Xkn8gHyrYonzo
YT1FD-34-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Fire Detection | equipment | ASDSP-7.02 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620890&prj=626&rqi=FsAnTa2kVshHAewHAsYd83Davb
RT1ELEC-28-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_F_1 to 1UPS_F_2) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620727&prj=626&rqi=jOcsOIBcjrdUYXaQYe8nidlKZr
YT1FD-26-003 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Fire Detection | equipment | ASDSP-5.04 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620870&prj=626&rqi=AqWhb8yWvTwK5wXbGv4BJNslZq
YT1ELEC-12-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1MDSB_D_1) Please add grommet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620912&prj=626&rqi=7GVKq9AjkbL41X44eSTxgauV9k
RT1ELEC-26-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1UPS_D_2 to 1MDSB_D_2) Temporary marker to be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620905&prj=626&rqi=9XCe3bdBPY7y6zVTZR4RvCCBRq
YT1FD-27-003 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Fire Detection | equipment | ASDSP-5.05 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620871&prj=626&rqi=S4666a898gs676t7d0IwG4agKL
RT1ELEC-26-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1UPS_D_2 to 1MDSB_D_2) Glanding cap is torn. Ensure the gland is properly covered and sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620907&prj=626&rqi=hy64UeM8pmcasaPwowFF2USc7u
RT1ELEC-26-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1UPS_D_2 to 1MDSB_D_2) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620906&prj=626&rqi=5kDHhHnAVJRFR83PFEJ0sJDO5Q
RT1ELEC-12-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing and actual breaker size: - F5: 6A (actual 10A) - F6: 6A (actual 10A) - F7: 6A (actual 16A) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620655&prj=626&rqi=tsS5qopwlOnRA4wZc1mWplDjJg
YT1ELEC-162-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Fuel Leak_L3 | LEAK - Leak Detection |  |  | issue from L2A. permanent equipment labelling issue. attach photo once it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620650&prj=626&rqi=riHFLIjPqPZ1zhGXBRJposekph
RT1FD-39-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-7.10 | VES - Vesda |  |  | Installation and Start-up Manual document need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620656&prj=626&rqi=HqoL736jzAYPanNfkpLAv8N6OZ
RT1ELEC-12-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Panel surface need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620651&prj=626&rqi=y0zihdFIRlbX5BTuT8zQxnug17
RT1ELEC-12-009 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GCP) Discrepancy between drawing & actual panel length | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620658&prj=626&rqi=oPC4osBLlwiJadsuAs7p24BGFo
RT1ELEC-12-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Missing bolt | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620653&prj=626&rqi=FfALWF4SI3ZKvS8vJkT9WNR1JL
RT1ELEC-12-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Dual Battery Charger) Please revise drawing to match with actual condition for panel door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620649&prj=626&rqi=TMh0j5dt4k9F7UQeNVA0ozGdlA
YT1ELEC-128-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1WLEAK_L2 | LEAK - Leak Detection |  |  | issue from L2A. permanent labelling equipment issue. attach photo if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620646&prj=626&rqi=nLaxdwKFYblBRR4QRaGKNHOVtA
YT1ELEC-31-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | UPS temperature sensor has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620394&prj=626&rqi=mSFKIfukddaucb92Y4gAN0VFCE
RT1ELEC-12-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620510&prj=626&rqi=G80v6NcGcqrwONxOYRDht6t89l
RT1ELEC-149-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1MSB_C_1 to 1UPS_C_1) Busduct support is not aligned / tilted. Please adjust to ensure proper alignment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620380&prj=626&rqi=8bVJGwNOTQy0TqR4xtU12uwdvV
RT1ELEC-155-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | (Issue Tx Room Area) Missing bonding jumper on cable containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620378&prj=626&rqi=MeNItuBwyjzHuoHd4knzC6y3HS
RT1ELEC-155-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | (Issue Tx Room Area) Cable termination bolts are not in accordance with Equinix standard. No flat washer at the back side and no Belleville washer before the nut at the front side. If Belleville washer is not available, use spring washer. Please comply with Equinix standard, refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620379&prj=626&rqi=P8mKwtwCiJ2F6Odag1M3pduUNd
YT1ELEC-31-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | External cable to the AC/DC converter has not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620395&prj=626&rqi=ITWS6XGbRjHMuw8XdOU5IJzdfT
RT1FD-13-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Fire Detection | equipment | ASDSP-3.10 | VES - Vesda |  |  | The equipment nameplate labels for ASDSP and PSU are incorrectly swapped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620479&prj=626&rqi=b7RuvtO1LVw7tC820NgHYycQbl
YT1ELEC-31-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Communication cable between Module 2 & Module 3 in panel 1LIBATTSYS_F_1 not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620396&prj=626&rqi=mRJgn26XRmI2cwEzAqTRgghxtY
YT1ELEC-31-002 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | DCOS control cabling to panel 1LIBATTSYS_F_1 has not yet installed and terminated at Battery cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620392&prj=626&rqi=fShkZgfXbOyNIbueImZfIaOHel
YT1ELEC-31-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | MCCB AUX 1 cable has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620389&prj=626&rqi=1oUiKw3Letgw4m2l2Y1e9kE2wV
YT1ELEC-31-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | DC power supply from external AC/DC converter polarity has not been verified yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620397&prj=626&rqi=9UrHD4SxZAYb41kYRKe8w1E6AT
RT1ELEC-13-017 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual breaker capacity: - Breaker Q3: 6A actual 16A - Breaker Q4: 6A actual 16A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620381&prj=626&rqi=rigCmkQ5lH9lQHqgusb0jFar10
RT1ELEC-13-018 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Missing cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620382&prj=626&rqi=IDQNaQGWYCIgfn2oY7NOblVlqJ
RT1ELEC-13-020 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A - 1GEN_D Panel Battery Isolator) Discrepancy between drawing & actual breaker capacity: - Breaker F3: 25A actual 10A - Breaker F4: 25A actual 10A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620385&prj=626&rqi=OqkqJxoPwjs8zOEdTD44K9CPvj
RT1ELEC-155-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | (Issue Tx Room Area) Please confirm the new grounding cable tagging and ensure all grounding cable tagging is consistent as per standard. Kindly attach the latest grounding cable tagging standard document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620377&prj=626&rqi=nCQOQpOYpIOUlYSpvXRpzRWMM2
RT1ELEC-13-019 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual position. Refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620384&prj=626&rqi=6xFcwylViY3NEneeVLgyw1lX4O
YT1ELEC-32-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | MCCB AUX 1 cable has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620398&prj=626&rqi=oEsSAGoqmTMREP1Jauc9vjcvL3
YT1ELEC-32-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | UPS temperature sensor has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620400&prj=626&rqi=aV8BM2IxUipzNWTZG1UnST5HHu
YT1ELEC-32-002 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | DCOS control cabling to panel 1LIBATTSYS_F_2 has not yet installed and terminated at Battery cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620399&prj=626&rqi=qAkPmhQ4qZANgJ3vT8M72yhXqL
YT1ELEC-32-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | External cable to the AC/DC converter has not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620401&prj=626&rqi=nRpw514Cr34SAHRz9DZCd9EkTA
YT1ELEC-32-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | DC power supply from external AC/DC converter polarity has not been verified yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620402&prj=626&rqi=53qWPB1DZkEHgc5qWJr4rMpIIF
RT1ELEC-12-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual breaker size: - Q3: drawing 6A (actual 16A) - Q4: drawing 6A (actual 16A) - Q5: drawing 6A (actual 16A) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620509&prj=626&rqi=iTfzhGEfxXIRmv1Ol2wiZYbk8w
RT1ELEC-12-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Isolator) Discrepancy between drawing & actual position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620512&prj=626&rqi=I9VCFWxfRmUHDwWsv6HkGvtJ25
RT1ELEC-54-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-03 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Discrepancy between drawing & actual position. Refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620204&prj=626&rqi=94rCiv6ABsMYXr5bBXE6KbZXMy
RT1ELEC-54-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-03 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Dents & scratches on panel surface observed, need touchup | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620200&prj=626&rqi=4efz52UJhEI5po79vi0A3r1zxP
RT1ELEC-54-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Drawing not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620203&prj=626&rqi=85YVD8fox7EaEyplk0wYV2wfi6
RT1ELEC-54-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-03 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Missing bolt on back side panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620202&prj=626&rqi=AreIDdiocmdBhiSbaqD9ZMOAkz
RT1ELEC-54-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Please ensure all ACB & HMI are properly protected to prevent construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620201&prj=626&rqi=zS6O6HgGiXTZrz0I7pFVG9C0mS
YT1MECH-108-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) Ensure that the cable routing is uniform and consistent for all isolator switches, pay attention to cable neatness, disconnect cable which unused and isolated accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619972&prj=626&rqi=oZA5MtnYAIa0358y7JVcewaEuj
YT1MECH-109-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) need to install vynil cable accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619974&prj=626&rqi=vA3KnDohooAhYVeGJeykgVLSYa
YT1MECH-109-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) Ensure that the cable routing is uniform and consistent for all isolator switches, pay attention to cable neatness, disconnect cable which unused and isolated accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619973&prj=626&rqi=O5OyV0FhAduAzd6SNNz6ilUMlY
YT1MECH-108-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) provide cable label inside isolator switch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619971&prj=626&rqi=ffGCpb48NhhB1gsUlHQLb6UMvd
YT1MECH-109-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable AHF to Chiller Pump) provide vynil cable and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619980&prj=626&rqi=A8dFEh51of5BZthmGW4qig8BZg
YT1MECH-107-007 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable AHF to Chiller Pump) provide vynil cable and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619978&prj=626&rqi=SKCThHAV9yhW2KMs2VLqbVXzBx
YT1MECH-110-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable AHF to Chiller Pump) provide vynil cable and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619981&prj=626&rqi=prlbGuDbfqAvnK3HOxVAp3rx2z
YT1MECH-108-007 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable AHF to Chiller Pump) provide vynil cable and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619979&prj=626&rqi=eLzz7t0x68RTx6Xf911xLudWxs
RT1ELEC-158-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L4 | DB - Distribution Boards |  |  | Each component shall have two labels (terminal and component body). Proper component labelling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619983&prj=626&rqi=cKsm33WyeH8ONSQwe4dvBho1Sy
YT1MECH-109-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) provide cable labelling inside iso switch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619975&prj=626&rqi=JzMY9gRFySbIQU2w6Urrzgn4I1
RT1ELEC-158-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L4 | DB - Distribution Boards |  |  | Discrepancy between drawing & actual position for grounding & neutral location inside the panel (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619985&prj=626&rqi=ldQycJf5lpHINxcXdAiPytvwVi
YT1MECH-108-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) need to install vynil cable accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619970&prj=626&rqi=KaxCjfHQhoRbezo1U7T1EzEuxa
RT1ELEC-158-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L4 | DB - Distribution Boards |  |  | Please confirm the correct equipment tagging as per design: 1DB_DALI_L4.1 or 1DB_DALI_L4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619982&prj=626&rqi=irrSkWO0biCKflcu3qTn7S09Dl
RT1ELEC-158-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L4 | DB - Distribution Boards |  |  | Minor dents need to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619984&prj=626&rqi=69dyReJlWnbhmRVEgL42r6lQ0G
YT1MECH-30-002 | JK01-2 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | inside the rusty chiller pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619860&prj=626&rqi=CegNaxDovDnPLqiM1GTJzEKR6j
YT1MECH-13-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | YT tagging status changed, some documents missing 1. Cx Report 2. Ducting visual inspection report 3. Grounding test report 4. O&M | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619826&prj=626&rqi=YpxzgdS0ytBJQgmuxGbqaiRMet
YT1MECH-31-002 | JK01-2 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | inside the rusty chiller pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619855&prj=626&rqi=oO0WsuvgU0OtkEYIYPxHonyvrw
YT1MECH-28-004 | JK01-2 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | inside the rusty chiller pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619859&prj=626&rqi=5SPdes2gx7MLuBkPDkFDtpAVEn
YT1MECH-29-001 | JK01-2 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | inside the rusty chiller pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619861&prj=626&rqi=VvEB19Bp4edi63eVPc84fHxHdx
RT1ELEC-14-015 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual position. Refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619834&prj=626&rqi=8VVy8sszlll7PE2KTL90bJXU7E
RT1ELEC-14-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Isolator) Please provide drawing pocket & as built drawing in panel door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619829&prj=626&rqi=2UnsSeTmXSzFdwqgGncybY9DoU
RT1ELEC-14-017 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Please update drawing to match with actual door component location | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619837&prj=626&rqi=3sS5TcIcCUvq3t0Ja9QLmj2Ifs
RT1ELEC-14-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Isolator) Please provide protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619830&prj=626&rqi=8kHbl0U96v0tSy68rQU0OnoCBY
RT1ELEC-14-016 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy breaker size rating on Q3, Q4, Q5. In drawing 6A actual 16A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619836&prj=626&rqi=7yFuFnQGnl8J9JSObjN5TBE7MN
YT1MECH-14-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_D_53 | EF - Exhaust Fan |  |  | YT tagging status changed, some documents missing 1. Cx Report 2. Ducting visual inspection report 3. Grounding test report 4. O&M | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619821&prj=626&rqi=Jz3BQ7JygQ5tXneZgu2RFGU8qw
YT1MECH-107-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) Ensure that the cable routing is uniform and consistent for all isolator switches, pay attention to cable neatness, disconnect cable which unused and isolated accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619847&prj=626&rqi=CcHcPBj9ykVmKIroNvd2q08abG
YT1MECH-107-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) need to install vynil cable accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619841&prj=626&rqi=kDBox46ZWhAApoQLrvOO9FuNzh
YT1MECH-11-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_C_54 | EF - Exhaust Fan |  |  | YT tagging status changed, some documents missing 1. Cx Report 2. Ducting visual inspection report 3. Grounding test report 4. O&M | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619827&prj=626&rqi=5wTEYJ9gNQiHw56os0XqoRk8z5
RT1ELEC-122-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | Cable tubing/tagging faded need to replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619812&prj=626&rqi=832shtU2YpCfFVP92Vgao5pRyW
YT1MECH-10-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_C_53 | EF - Exhaust Fan |  |  | YT tagging status changed, some documents missing 1. Cx Report 2. Ducting visual inspection report 3. Grounding test report 4. O&M | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619825&prj=626&rqi=q0xm2mja8dRmNb8s6BV22j9Nxy
YT1MECH-107-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) need to install labelling inside isolator switch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619845&prj=626&rqi=8LfocjXZBKMZxrONbBrkrgfY3P
YT1MECH-30-001 | JK01-2 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | inside the rusty chiller pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619852&prj=626&rqi=WPCGSGtCCnDKw7vQaea5FsoX8a
YT1ELEC-164-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | (Issue CxL2A LV Cable) Several cable tags are mismatched (should be labeled as CA_B_1 but tagged as CA_B_2). Kindly recheck all and correct accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619666&prj=626&rqi=uSvMw4qkDSVuZ9kAm6hDd8koK6
YT1MECH-36-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tray covers are not yet installed. Please ensure all covers are properly closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619668&prj=626&rqi=ukDOBw20HJrMXXrMkTUnhgKCFb
RT1ELEC-157-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L3 | DB - Distribution Boards |  |  | Each component shall have two labels (terminal & component body). Proper labelling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619685&prj=626&rqi=iHKNK8v3O6jpRhF97vYZZq3aVI
RT1ELEC-157-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L3 | DB - Distribution Boards |  |  | Please confirm the correct equipment tagging as per design: 1DB_DALI_L3.1 or 1DB_DALI_L3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619686&prj=626&rqi=7aNHyyWAhOmFYWEfG83CvwDRHC
YT1ELEC-142-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_2 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue CxL2A BD 1UDP_B_2 to 1STSSB_B_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619663&prj=626&rqi=CpG3i46LTu7aDteJjH51yJxkKe
RT1ELEC-122-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Several cable gland caps are damaged (torn) and not properly covering the gland. Replace all damaged gland caps and ensure proper installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619673&prj=626&rqi=8fidyZU0Fj9dJNp7fzfg8PvH2C
YT1ELEC-164-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | (Issue CxL2A LV Cable) Incorrect cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619665&prj=626&rqi=24DyK5uvN8WvQl9DKBj4tEvBd4
YT1ELEC-143-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue CxL2A BD 1UDP_D_2 to 1STSSB_D_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619560&prj=626&rqi=lM9DpT2PKUub5IbChlAXUFnXZJ
YT1ELEC-164-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | (Issue CxL2A LV Cable) Several cable gland caps are damaged (torn) and not properly covering the gland. Replace all damaged gland caps and ensure proper installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619671&prj=626&rqi=Huo6Q8MIlvf1UHz837bKyaLV7b
YT1ELEC-164-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | (Issue CxL2A LV Cable) Cable conductor is still exposed. Please ensure proper termination is completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619664&prj=626&rqi=crisYt2w44Er97XHRZh1ofdcqE
YT1ELEC-164-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | (Issue CxL2A LV Cable) Bolt supports have not been properly tightened & unistrut support is found cut. Please adjust to match other unistrut installations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619667&prj=626&rqi=Nt0MdR6YC3lCGfnzCPijclEG5Z
YT1MECH-42-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tray end sections are open. Please confirm and install end caps where required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619670&prj=626&rqi=BvxCrUjLvis9391uQspB0q6PQu
YT1ELEC-143-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue from CxL2A BD 1UDP_C_2 to 1STSSB_C_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619542&prj=626&rqi=TARI7ZNZKtIh3ka0aYSbIgT2og
RT1ELEC-122-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Please remove all temporary markings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619672&prj=626&rqi=NTck9aYQW5VSGGAQpG6Ss5mscn
YT1ELEC-143-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue CxL2A BD MLTX_D to MSB_D) Sleeve and firestop at wall penetration are not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619558&prj=626&rqi=R48qy08hofDxSmCxTfsrTZgXRd
RT1ELEC-157-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L3 | DB - Distribution Boards |  |  | Discrepancy between drawing & actual position. Refer to the attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619682&prj=626&rqi=sCG5OyuGyksCzrGKDWUqsAK99E
YT1MECH-7-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_B_31 | EF - Exhaust Fan |  |  | Upload calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619459&prj=626&rqi=yguoSwiKewpTo6eVgoQvE11iLa
YT1MECH-17-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_F_74 | EF - Exhaust Fan |  |  | Provide MoS CxL3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619464&prj=626&rqi=OdZ3hw3kfuluDRxUwaOKB2Raya
YT1MECH-7-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_B_31 | EF - Exhaust Fan |  |  | Provide MoS CxL3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619457&prj=626&rqi=I9nrTELbebR0yxhZcwRLatWJnV
YT1MECH-16-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | Provide calibration certificate of test tools been used for CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619462&prj=626&rqi=hPkDSEwp0ao58CdDMySR8LfjjT
RT1DCOS-15-001 | JK01-2 | APAC | Closed | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Controls | equipment | 1DCOS_1_SCP_07 | DCOS - Control Panels |  |  | Please add label for incoming power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619475&prj=626&rqi=jGflrQHVm00bl36lZ6CBRR5Kqc
YT1MECH-17-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_F_74 | EF - Exhaust Fan |  |  | Provide calibration certificate of test tool used for CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619465&prj=626&rqi=kmuj7YQzf0dzS6YDHHXtOYT384
YT1MECH-8-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_B_32 | EF - Exhaust Fan |  |  | Provide calibration certificate of test tools been used in CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619460&prj=626&rqi=rSvbb1G0hI2Ml6osf1TctQJpMH
YT1MECH-8-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_B_32 | EF - Exhaust Fan |  |  | Provide MoS CxL3 doc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619458&prj=626&rqi=0HvmZ1pKEGWb95qqzphufdIhj7
RT1DCOS-15-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_1_SCP_07 | DCOS - Control Panels |  |  | Provide MoS CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619477&prj=626&rqi=Jsn8vwup6vJKcyGxEyawQArrjt
RT1ELEC-148-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_2 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1UPS_B_1 to 1UDP_B_2) Laser measurement shows about 15 mm elevation difference (not level). Please adjust to make it straight and level. Refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619292&prj=626&rqi=CuWdYlWaD7BkarARUOQbXn0p3T
YT1ELEC-10-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Short time protection test for breakers Q1â€“3 was skipped during testing. Kindly perform the required test to verify proper protection functionality | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619280&prj=626&rqi=fiFT8X23jgMN9LWNQJDzxFG9ht
YT1ELEC-10-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Input/Output PLC verification test has not yet been conducted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619282&prj=626&rqi=azaIpWz6SWgXiawR9p7Y01NstM
RT1ELEC-148-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_2 | BUST - Bus Duct Temperature Monitoring |  |  | [Issue BD 1UPS_B_1 to 1UDP_B_2] Please clarify with engineering, busduct support location different from the drawing. Confirm if this is approved and safe? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619293&prj=626&rqi=auPgHrfn9IVT6bL4161tvYQuxR
YT1ELEC-10-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | MCCB Q1-4 long time trip test result indicates a failure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619281&prj=626&rqi=8LnD5M0NU09DI9hbp5TkSJ0k44
YT1MECH-111-003 | JK01-2 | APAC | Closed | P2 Medium CX | JulianJensen@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_2.01 (Existing) | PAV - Pre-Action Valve |  |  | Pressure drop during pipe hydrostatic pressure test (STS Room B & C-Wall B). Refer to the attached image. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619170&prj=626&rqi=5Tpc3JjTyGnV9OHHC0jFJ0ksQ9
YT1MECH-18-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | Provide as built drawing because there was discrepancy between shop drawing and actual layout | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619171&prj=626&rqi=1NMnPQrwlDdTH1Aq99E8wRqh2a
GI-018 | JK01-2 | APAC | Open | P3 Low DCOS | dickyhermawan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS | [6 empty] | Configuration "Asset Data" is currently in progress by DCOS program Orise. After finish need to verify with CTA Note: - The Maximo asset data from GC has been completed, and Orise has confirmed that the data is complete, except for the ID numbers, which will be provided by the Ops Equinix team. FG GC issue GI-016 (Closed) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619210&prj=626&rqi=SUEOMesQEmvGsYlLCz2sInzcrb
RT1ELEC-15-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A GPC Panel) Please add temporary protection to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619044&prj=626&rqi=OzNTRX49zjm6vIuEfxCM2hJA39
RT1MECH-131-001 | JK01-2 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_2.01 (Existing) | PAV - Pre-Action Valve |  |  | Pipe has white paint residue. Refer to the attached image. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618991&prj=626&rqi=vrbInxuLopuxDA8zi0B33LEJRJ
RT1FD-3-002 | JK01-2 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | 1FAS_4 | FP - Fire Panel |  |  | Cable tagging not installed. Refer to the attached image. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618997&prj=626&rqi=Bw2pCivPKU0FUus2EnBOO9wODD
RT1ELEC-15-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Based on the RFIT inspection results, a discrepancy was identified between the drawing and the actual panel position (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619036&prj=626&rqi=54z8onGsuypyk2Zkked73RNawC
RT1ELEC-15-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add component RSH1 & RSH2 in the drawing component list | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619051&prj=626&rqi=I6v3I1i9wijbH155qw2vCypHoE
RT1ELEC-15-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Cable entry/exit location is not in accordance with the approved drawing. As per drawing, cable routing shall be from the bottom of the panel. However, actual installation is from the top of the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619053&prj=626&rqi=xxPlPmpohT77kzkvtVmLSiiEcD
RT1ELEC-15-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Missing bolt on the panel body | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619021&prj=626&rqi=ahoKNZuzgD2qvMWGDdpRIHnDjC
RT1FD-3-001 | JK01-2 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Fire Detection | equipment | 1FAS_4 | FP - Fire Panel |  |  | Spilled white paint on Fire Alarm and the cable cover pipe. Refer to the attached images. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618994&prj=626&rqi=WPJ1UYMkCHmwLbR5RPaf7xM6tN
RT1ELEC-15-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add labels above pilot lamps for â€œBattery Charger 1â€ and â€œBattery Charger 2â€ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619049&prj=626&rqi=e2wSYdy39KyvOihSb7L7yU1jVD
RT1ELEC-15-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Drawing and actual panel are not the same: location of voltage and ammeter is different. Please update the drawing to match actual condition | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619047&prj=626&rqi=gJNinY0AuRt4c1bj3jiuLwRusd
RT1ELEC-15-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Incorrect generator rating at panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619019&prj=626&rqi=TlSsSVwr7gUOj8IBXqbYbHFhy3
RT1ELEC-15-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add clear labels for ammeter and battery to show which one is Battery 1 and Battery 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619050&prj=626&rqi=3xoPd7RBefopLbT3yaBaLNNptN
RT1ELEC-15-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Minor dent found on panel surface, please touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619022&prj=626&rqi=7NJ1hAAKH74PBdERMhPRAB4zRe
RT1ELEC-15-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Drawing not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619023&prj=626&rqi=OUe4FTzbTlbNWKAzVQUmitFBzB
RT1ELEC-15-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Rear anchor bolts have not been torque tightened | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619020&prj=626&rqi=PMdI2aw4B2wmBbdS5bjmVQ6Txg
RT1ELEC-15-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Incorrect generator rating on the drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619030&prj=626&rqi=AAmCFlJM5FALheUKTYtn3mz4R1
RT1ELEC-15-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Discrepancy between drawing and actual breaker capacity: - Breaker F7: 6A (actual 16A) - Breaker F5: 5A (actual 10A) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619033&prj=626&rqi=Wh5kjNJkU8tWxxkGo6uFJG9r92
RT1ELEC-15-015 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add temporary protection to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619054&prj=626&rqi=EOPRDWLCD4xhIeztQyagSH7Ur6
YT1ELEC-29-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | External cable to the AC/DC converter has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618837&prj=626&rqi=feaL0Uq8vpDJIpbsp6G7GN18yh
RT1ELEC-134-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1WLEAK_L2 | LEAK - Leak Detection |  |  | permanent equipment labelling issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618811&prj=626&rqi=CII3pxOinQk2frxlDDzRAP6BVT
RT1ELEC-168-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Fuel Leak_L3 | LEAK - Leak Detection |  |  | document related need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618812&prj=626&rqi=8Xs9TLA9kDINyE1AgV2izlvYkn
YT1ELEC-29-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | MCCB AUX 1 cable has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618834&prj=626&rqi=42B610h26ZA1yOkHdBvgoFVLih
YT1ELEC-29-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Communication cable between Module 2 and Module 3 in panel 1LIBATTSYS_C_1 has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618839&prj=626&rqi=hhKlbkV5e6U2sPiMAVbH8eZkBx
YT1ELEC-29-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | UPS temperature sensor has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618836&prj=626&rqi=QZrNL2vtM2pVC1nmfJp8Rt8hSs
YT1ELEC-30-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | UPS temperature sensor has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618847&prj=626&rqi=mE2muBflcTO7UfdvPuj1RH35dY
YT1ELEC-30-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | External cable to the AC/DC converter has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618848&prj=626&rqi=h8a0jAzbqMAVOVOA9b6SgwLnOd
YT1ELEC-30-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | MCCB AUX 1 cable has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618843&prj=626&rqi=z9Yl2fVIPEgeiGhibBQ6oCs4e4
RT1ELEC-168-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Fuel Leak_L3 | LEAK - Leak Detection |  |  | Permanent equipment nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618813&prj=626&rqi=HiXRgU4N3hC3BNfRRqGCwrxlUh
YT1ELEC-29-001 | JK01-2 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | There is dust inside the battery rack. Refer to the attached image. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618832&prj=626&rqi=fyNjwk53w5vNAHNw9lBmn7s6sW
YT1ELEC-29-003 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | DCOS control cabling to panel 1LIBATTSYS_C_1 has not yet been installed and terminated at Battery Cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618835&prj=626&rqi=LmeJB8lUmQCbmVU4oONJodhiwJ
YT1ELEC-30-002 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | DCOS control cabling to panel 1LIBATTSYS_C_2 has not yet been installed and terminated at Battery Cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618845&prj=626&rqi=mB8J6QQQcDHKPsArGX4EwKBebA
RT1ELEC-134-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1WLEAK_L2 | LEAK - Leak Detection |  |  | need to upload document shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618810&prj=626&rqi=bAJNYit25Zh26zb6ZNggRhvy07
YT1MECH-28-003 | JK01-2 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Plastic cover not installed. Refer to the attached image. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618730&prj=626&rqi=KUDqw1Ytl3KoZ33UL5fGZRx0hE
RT1FD-25-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.03 | VES - Vesda |  |  | report L2A need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618682&prj=626&rqi=BUDAP47N57vphkZLKvAS1xiGMd
RT1FD-24-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.02 | VES - Vesda |  |  | issue and report document L2A need to comply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618680&prj=626&rqi=EAxMq900TifBLerXwWhjZl8k8b
YT1FD-27-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.05 | VES - Vesda |  |  | document related need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618687&prj=626&rqi=Hbl1dgJ7Y0CF9HB4r3GP4ok6kw
YT1MECH-28-002 | JK01-2 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Paint is not smooth. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618729&prj=626&rqi=ZxcTWKvo1ssya38C9GilfqPkOL
RT1ELEC-1-022 | JK01-2 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (BTU Issue); Missing washers on cover panel. Refer to the attached images. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618709&prj=626&rqi=9oQ57zqhd2hpsiOTFPVwj8dcT1
YT1FD-25-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.03 | VES - Vesda |  |  | related documents need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618683&prj=626&rqi=0VtX75YSKqTipaLEtRIJDhPq5p
RT1MECH-9-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | need to upload related documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618696&prj=626&rqi=Fsd4A3grfBGTqa8pg9lnJhO6pT
RT1MECH-9-002 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | Exhaust Fan ducting not connected yet to the opening wall and Wall Penetration not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618697&prj=626&rqi=HlOzGLJCb30ZnGjqoEZEogNbe0
RT1MECH-9-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | provide airflow direction | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618700&prj=626&rqi=VKjKl7XcqBl0ekJC8BUNi5VMJ6
YT1FD-29-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.08 | VES - Vesda |  |  | related documents need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618693&prj=626&rqi=DvXfUIU24j8LmcJdRglfNk2bHx
YT1FD-29-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.08 | VES - Vesda |  |  | L2A issue and report document need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618691&prj=626&rqi=fuOIOdZm5Fg7b45PUGCw7URWgi
RT1MECH-12-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_D_41 | EF - Exhaust Fan |  |  | need to upload related document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618703&prj=626&rqi=aNQ7OJP7Nfyj948a8siQUZiaGy
YT1FD-27-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.05 | VES - Vesda |  |  | L2A reports and issue need to close and comply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618688&prj=626&rqi=vg3ljSbsn256KrTzPFVJt268iw
YT1FD-24-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.02 | VES - Vesda |  |  | related documents need to upload on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618678&prj=626&rqi=ezy0Rs61OCLAIN9bTUZkomrA51
YT1FD-28-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Component/Equipment Failure | Commissioning | Fire Detection | equipment | ASDSP-5.07 | VES - Vesda |  |  | related documents need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618689&prj=626&rqi=3A0YUpYJ31UnEJ8HJIG6jvmOkc
YT1FD-28-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.07 | VES - Vesda |  |  | L2A issue and report document need to comply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618690&prj=626&rqi=jkW3Ns2TCEbydCaAoaULMumFZ3
RT1MECH-12-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_D_41 | EF - Exhaust Fan |  |  | provide airflow direction | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618705&prj=626&rqi=gzfe31ZmyhYbIi83YyOHqGlnvR
YT1ELEC-2-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Simulated trip from thermal relay to VCB cannot be performed due to incorrect wiring. GC to rectify the control wiring between MLTX and RMU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618720&prj=626&rqi=N6oh7rlVP2HnuzgJpPPZR6W4S8
RT1MECH-12-003 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1EF_D_41 | EF - Exhaust Fan |  |  | Exhaust Fan ducting not connected yet to opening and wall penetration not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618704&prj=626&rqi=Vdj83go6MNgGtSl4M8vyAMjbhD
YT1ELEC-2-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Control cable signal testing for alarm and trip contacts cannot be carried out. GC to confirm the cable routing and termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618714&prj=626&rqi=QcdBRqXCi6pN3kXLCHax0Lqti0
YT1ELEC-2-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Point to point testing for earth cables cannot be performed as the grounding cables have not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618713&prj=626&rqi=8PQGYchBsPUSZsGz3RVXIrpL9U
RT1MECH-12-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1EF_D_41 | EF - Exhaust Fan |  |  | vibration mounting need to adjust because it's not straight | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618702&prj=626&rqi=IOH1ThrX5mNgwllAs5sGtqsapo
YT1ELEC-3-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Control cable signal testing for alarm and trip contacts cannot be performed. GC to confirm the cable routing and termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618717&prj=626&rqi=EMQxljyIuMBEn5ZpajTKmUSY2M
YT1ELEC-4-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Control cable signal testing for alarm and trip contacts cannot be performed. GC to confirm the cable routing and termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618718&prj=626&rqi=ua3WGJexqf66xyDV9xYCD1pabg
YT1FD-26-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.04 | VES - Vesda |  |  | related documents need to upload on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618685&prj=626&rqi=erXmol9nYi1IypN8J3dH7ah5ZX
YT1FD-26-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.04 | VES - Vesda |  |  | issue and L2A report need to close and comply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618686&prj=626&rqi=vRn1v0e7P6OnEYlyDLncJ01wvI
YT1FD-25-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.03 | VES - Vesda |  |  | issue and document report L2A need to comply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618684&prj=626&rqi=RtFIQ3na7OezgHV1f6Wjx8fv2I
YT1MECH-28-001 | JK01-2 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Chiller side panel is dirty. Refer to the attached image | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618728&prj=626&rqi=Pp3ISd7WDR0fhvAB9ceiGB0xeJ
YT1ELEC-5-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Control cable signal testing for alarm and trip contacts cannot be performed. GC to confirm the cable routing and termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618719&prj=626&rqi=TRuAB3ADdd8Tbn10eYBPZ1lZJF
RT1ELEC-13-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add clear labels for ammeter and battery to show which one is Battery 1 and Battery 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618659&prj=626&rqi=gCAmzlx5oyuyoO9mW3WKgMuX0v
RT1ELEC-13-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Discrepancy between drawing and actual panel position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618654&prj=626&rqi=9IWnnrTAEsnKJK2X7dwujM2fDp
RT1ELEC-13-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Panel requires proper cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618650&prj=626&rqi=k3FEhyBLcnj5kpfoIdE0oT0gTG
RT1ELEC-13-015 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) GC please clarify why the positions of DB Aux panel and Dual Battery Charger panel are swapped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618661&prj=626&rqi=25yhr9uEJXdo0QkngDL9KYlkKG
RT1ELEC-156-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Grounding cable at panel door still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618640&prj=626&rqi=Zhtc7SEcSGEDrirfF2wBdgmGA0
RT1ELEC-161-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Each component shall have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618620&prj=626&rqi=TMuMfMA64EgUrygO1YU8VvIMcl
RT1ELEC-161-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | There is a discrepancy between the drawing and the actual installation position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618625&prj=626&rqi=ESTGREDyTHWU4FBMSYImLoS0Lc
RT1ELEC-13-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add component RSH1 & RSH2 in the drawing component list | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618660&prj=626&rqi=n1wGa6v6jb2fhtUKlgSIqjFtlW
RT1ELEC-13-016 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please provide temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618662&prj=626&rqi=B1M20WkYASsMO75GMDpb8c6pF8
RT1ELEC-13-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Drawing and actual panel are not the same: location of voltage and ammeter is different. Please update the drawing to match actual condition | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618657&prj=626&rqi=Xp0ZyThe2OA1v52yQafTWTQV1B
RT1ELEC-13-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Rear anchor bolts have not been torque tightened | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618653&prj=626&rqi=tRuBP1Lwj4LZlsR2iZ4TQ8eK29
RT1ELEC-156-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Internal panel bolts are still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618641&prj=626&rqi=7OqWinu0JxmACxeSlPCMM0L3Dg
RT1ELEC-161-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Panel surface is stained. Please clean the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618624&prj=626&rqi=SUOfkczPORgPJH74MLTeeh72zy
RT1ELEC-161-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Please confirm the correct equipment tagging as per design: 1DB_DALI_L7.1 or 1DB_DALI_L7 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618619&prj=626&rqi=X0FsWKgbigEIeK7aPrL1rvqs2I
RT1ELEC-13-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Missing bolts on the panel body | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618649&prj=626&rqi=oBGuQ2Ezaagy6HpMOXhS1qMUbT
RT1ELEC-13-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add labels above pilot lamps for â€œBattery Charger 1â€ and â€œBattery Charger 2â€ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618658&prj=626&rqi=a8auEMvQaSrFkHfebiOseENTju
RT1ELEC-159-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Please provide temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618634&prj=626&rqi=uV39yl1SjxvgmBZo9hL7xvYPEm
RT1ELEC-13-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Acrylic panel broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618651&prj=626&rqi=eVfOTEl719UvWJFL936PJMTNKt
RT1ELEC-13-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Length of panel actual 1480mm, please revise drawing panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618655&prj=626&rqi=pP94RXbBo8vv05Kk3NR0QM2hbB
RT1ELEC-161-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Please confirm the required torque value for the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618623&prj=626&rqi=wqNqSMxx0ymCoY9VkayV8Bhccj
RT1ELEC-161-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Please upload factory test data document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618618&prj=626&rqi=2PJ92if1b6zVBICZKiwHSQwqlV
RT1ELEC-156-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Please provide temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618644&prj=626&rqi=8VABjZ89D0cRGhL2DSMFRpecBc
RT1ELEC-13-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Incorrect label of capacity generator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618652&prj=626&rqi=H0MGPOEfaCBAJYgmmJsWfpkoxS
RT1ELEC-13-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Please provide temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618656&prj=626&rqi=RPh5nJ9ih1u0e88hJkss6xJJLU
RT1ELEC-159-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Internal panel bolts are still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618632&prj=626&rqi=KPqHg2vefcg83W1ibd5cLW89K7
RT1ELEC-13-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Dirt and dents found on panel surface, please clean and perform touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618648&prj=626&rqi=E3F39heXZ9OzShF03tJe8Idd6n
RT1ELEC-156-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Please confirm the required torque value for the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618642&prj=626&rqi=S0GSIiOngnXXOdEXmTyqiK5Inv
RT1ELEC-156-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Please confirm the correct equipment tagging as per design: 1DB_DALI_L2.1 or 1DB_DALI_L2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618637&prj=626&rqi=WuKKMLz8NmtfRTWA4vsXKzqYA8
RT1ELEC-159-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Please confirm the correct equipment tagging as per design: 1DB_DALI_L5.1 or 1DB_DALI_L5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618629&prj=626&rqi=pAX7w28fhgrweynbUar7vk6j13
RT1ELEC-159-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Please confirm the required torque value for the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618633&prj=626&rqi=eDVeQTFPZZAjxTw4dnvg6jcQ7F
RT1ELEC-161-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Internal panel bolts are still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618622&prj=626&rqi=NinFiio4cXE7yzd61lIwHO0l8P
RT1ELEC-159-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Each component shall have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618630&prj=626&rqi=1Jgc9ORFpj1TgUW7MhS3imPNid
RT1ELEC-159-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Grounding cable at panel door still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618631&prj=626&rqi=cyZxGwjNnyVE6Lfw17wqfKOfOt
RT1ELEC-161-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Grounding cable at panel door still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618621&prj=626&rqi=2HXpfUnW6Vt9qTKs2xuKNI4D2y
RT1ELEC-156-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Each component shall have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618638&prj=626&rqi=eeQDCe8hL81mW1nqhA5Es29xt8
RT1ELEC-156-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Please clarify the panel location for 1DB_DALI_L2 in the drawing. The yellow color means Phase P1, not Phase 2. If it should be Phase 2, please update the drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618643&prj=626&rqi=7BkUiqJc8zMTXsirNVki4kkkAw
RT1ELEC-156-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Please upload factory test data document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618636&prj=626&rqi=TqzSqlX5F0IDa3xqATHfYeTkPV
RT1ELEC-161-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Please provide temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618626&prj=626&rqi=3O5xtQ2L9tXGR19F1itkAaEQTn
RT1ELEC-159-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Please upload factory test data document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618628&prj=626&rqi=NkFFcrg41BQpaJdFrjNCEiJ3oG
RT1MECH-4-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Need to upload document related to the checklist; SoO, schematic drawing, O&M manuals, etc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618446&prj=626&rqi=ItKvqUkvbWqllYOgeUuXYR8far
RT1MECH-4-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Pipe overflow has not connected yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618448&prj=626&rqi=yraVqLTeycUy0IIbIulHoEErQH
RT1MECH-5-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Pipe overflow has not connected yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618455&prj=626&rqi=YhxPa6kvVBHA7j9lL7MN7jR1S6
RT1MECH-4-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Pipework needs to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618449&prj=626&rqi=JqWLZR1EChzeHY0pQEzPCn3Gbd
RT1MECH-4-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Equipment permanent label and tagging valve issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618447&prj=626&rqi=lJEsY3nctbQE97zVk1xGFjTmIW
RT1MECH-4-007 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Solenoid cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618451&prj=626&rqi=48sXaWpTndU1crVGzUKMBnaTCh
RT1MECH-4-008 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Discrepancy between shop drawing and actual measurement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618452&prj=626&rqi=lwbcdmx4Z5SprmKr9G27aqTL4y
GI-017 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [6 empty] | (Issue CxL2A MV Cable RMU C to F) Sleeve and firestop at wall penetrations have not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618460&prj=626&rqi=RBHqQvSSx1rWby8CGVi1Reo4oP
RT1MECH-5-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Need to upload document related to the checklist; SoO, schematic drawing, O&M manuals, etc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618453&prj=626&rqi=yOeIJVCr1IuRdROk53HcGRgz4f
RT1MECH-5-007 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Solenoid cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618458&prj=626&rqi=0CYXuvLSEcP8eLx9iCrZokCChy
RT1ELEC-14-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Minor dents found, please do touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618373&prj=626&rqi=OCbePFp63zw7p3vcoUdWIfqJ5m
RT1MECH-4-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Fusible link cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618450&prj=626&rqi=iYHyU4kseGPXMp7JSBPgk7wTnr
RT1ELEC-14-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add labels above pilot lamps for â€œBattery Charger 1â€ and â€œBattery Charger 2â€ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618370&prj=626&rqi=UUIkqvUReAmYeGdOgyZ0h2bXBy
RT1ELEC-14-011 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) GC please clarify why the positions of DB Aux panel and Dual Battery Charger panel are swapped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618372&prj=626&rqi=EUbp5Wau9FnizyelKwitA3n9MG
RT1MECH-5-008 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Discrepancy between shop drawing and actual measurement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618459&prj=626&rqi=PlvjKiY8gvuQfHzieLEKeoRktE
RT1ELEC-14-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add clear labels for ammeter and battery to show which one is Battery 1 and Battery 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618371&prj=626&rqi=ihpWOjDYbp6utf2oFvLVsUJZfI
RT1ELEC-14-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Drawing and actual panel are not the same: location of voltage and ammeter is different. Please update the drawing to match actual condition | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618369&prj=626&rqi=Wn1K0IiKfjqNRUFDhijoBiGxZW
RT1MECH-5-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Pipework needs to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618456&prj=626&rqi=3uvvCN66HuRJIG7ZG47GBOd9BQ
RT1MECH-5-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Fusible link cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618457&prj=626&rqi=4QJkUZUij1TGBQqbQwbIzZFYLX
RT1MECH-5-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Equipment permanent label and tagging valve issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618454&prj=626&rqi=i4HIWzVMByfunglLuHnZOGrBwB
RT1MECH-3-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | Equipment permanent label and tagging valve issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618347&prj=626&rqi=KpiEeWFNLSd0Wy8ShueaEL47Io
RT1ELEC-59-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Ensure all ACB & HMI are properly protected from construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618225&prj=626&rqi=lmf7UR8A6tkOwCIuzmmkgSgbvy
RT1MECH-32-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Dirt Air Separator issue; paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618483&prj=626&rqi=GdmJghT9kWNlhA2t3aEpjdfmOn
RT1ELEC-14-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Panel requires proper cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618365&prj=626&rqi=2jgebfbmtdb4rUDc8jD5NH3lpq
YT1ELEC-4-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Component/Equipment Failure | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Testing of the RMU control box panel could not be performed due to a fault in VCB. LS to clarify and take corrective action to resolve this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618363&prj=626&rqi=f1fTzTMF829VZLS8RN4zHCJlzK
RT1ELEC-14-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Rear anchor bolts have not been torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618367&prj=626&rqi=eeJ8JCcWyR2t5NyX4sJEpl2XPg
RT1ELEC-14-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Panel is not level based on waterpass checking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618366&prj=626&rqi=Dpu0XtVNQcquTwntO5lW6jmvK7
RT1ELEC-14-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Discrepancy between drawing and actual panel position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618368&prj=626&rqi=LF0oGXYAA7eBFrpZsVFKkaPtSC
RT1ELEC-14-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Dirt and dents found on panel surface, please clean and perform touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618364&prj=626&rqi=7DQGW7e31ye44gClMuHIb1AfjX
RT1ELEC-59-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Please provide correct GA & SLD drawings for 1STSSB_F_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618223&prj=626&rqi=AwqI4qRlCjlPgPuSOlYQoNEe4h
RT1MECH-28-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | DB Panel issue; Cable labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618358&prj=626&rqi=MfQp72NPtikEriYB1wMBDJgjzL
RT1MECH-34-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Dirt Air Separator issue; need to repaint | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618481&prj=626&rqi=nFVyzsVbFHRWpNcG8Ms4UVmdyR
RT1MECH-3-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | Pipe overflow has not connected yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618349&prj=626&rqi=bzckB8L2yv5lfxUYMeZhconpvQ
RT1MECH-3-008 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | Need to upload document related to the checklist; SoO, schematic drawing, O&M manuals, etc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618361&prj=626&rqi=QfgoCJLC1iwVw0gdVX9ekDpdrO
RT1ELEC-59-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Minor dents & scratches require touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618224&prj=626&rqi=ONg7QR85WtTyLiIlnCQbOm3mJh
RT1MECH-3-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | solenoid cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618357&prj=626&rqi=q4RniEYlRlNG7r1XBko8RDX2hC
RT1MECH-33-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Dirt Air Separator issue; paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618482&prj=626&rqi=cvfiK2anPl5PMQ5iJwFob2RKlt
RT1MECH-35-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | issue from Dirt Separator; paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618318&prj=626&rqi=SiG3VsDRn9rmmY77N93wB8mrwI
RT1MECH-3-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | pipework needs to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618353&prj=626&rqi=i70u2DGMOHX6FuFX08NYYilZ8D
RT1ELEC-149-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1UDP_D_2 to 1STSSB_D_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618259&prj=626&rqi=jGRUY2bHMYXOcTxIJJUWNl2re3
RT1ELEC-149-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1UDP_C_2 to 1STSSB_C_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618257&prj=626&rqi=p6ShkiQQfb62Yx49IDzhsbA3bj
RT1MECH-3-007 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | discrepancy between shop drawing and actual measurement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618360&prj=626&rqi=szwAKBFSumHwIBr4EsfAkozXe1
RT1ELEC-59-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Permanent equipment label/tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618222&prj=626&rqi=TI3sgG2459ecyhQkUTLUEPt8Dy
RT1MECH-3-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | Fusible link cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618354&prj=626&rqi=hyWDZ8MwfBIKrvHNwBEk1zUZ37
RT1ELEC-23-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Minor dents require touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618269&prj=626&rqi=tXfyzUyeYPaIDi91i1sYvHT5Nk
RT1ELEC-23-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Discrepancy between drawing & actual position (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618268&prj=626&rqi=uq22lQVGRynLJkswKnwNMFio5D
RT1ELEC-148-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_2 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1UDP_B_2 to 1STSSB_B_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618280&prj=626&rqi=TPOUL9l37sRb7noQXuOJLr3H5P
RT1MECH-29-008 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | DB Panel issue; Cable labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618359&prj=626&rqi=mTTmBmn2cMuXfcdYM9lrVirti5
RT1ELEC-23-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Please ensure HMI display is properly protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618270&prj=626&rqi=IGbzFgFzxvCAII1O7OVGMmfrrr
RT1ELEC-23-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Door foam damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618271&prj=626&rqi=pF0sn9xro74OdSqjak4eVCXVsq
RT1ELEC-23-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Deep cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618272&prj=626&rqi=AYjJdkUyUJvqwn8Xd1x9xwEl4V
RT1ELEC-59-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Provide temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618226&prj=626&rqi=afU17qWduXAFdJIKSWuYY8cldC
RT1ELEC-59-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Deep cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618221&prj=626&rqi=uySjSeSe63VxIL78IqZSgYzkeu
RT1ELEC-58-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Minor dents & scratches require touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618209&prj=626&rqi=1ZGn0pHWIU4qyVCYWLBv81banm
RT1FD-28-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.07 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618192&prj=626&rqi=mVaPrzQmp09ztpkYt1gR6uLBgG
RT1FD-27-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.05 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618191&prj=626&rqi=Dca1IKRYm7YC6r0xabb2QVIM8E
RT1FD-9-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-2.07 | VES - Vesda |  |  | Upload all related document to this checklist | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618198&prj=626&rqi=56geLnny59yW15wO5CqXaCzKQM
RT1FD-26-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.04 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618190&prj=626&rqi=Is3Zys5G52FhOHookvz57BAYLi
GI-016 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | DCOS graphic configuration for asset data equipment is pending due to missing data from GC and MCE. Please expedite submission of the required Maximo data so the DCOS team can proceed with configuration. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618202&prj=626&rqi=k7vPWdFqUNZ4UW2U7kMmUsQYpk
RT1FD-8-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-2.06 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618197&prj=626&rqi=PYfosMZ1OeybeHp7DtOn2b0oFF
RT1ELEC-58-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Please provide correct GA & SLD drawings for 1STSSB_F_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618206&prj=626&rqi=rewUsJCIoKqPrYFmVnIoeawvAj
RT1ELEC-58-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Provide temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618212&prj=626&rqi=2psI3zhkQfuFr5VBD18FwO4uN5
RT1FD-8-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-2.06 | VES - Vesda |  |  | Upload all related documents to this checklist | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618195&prj=626&rqi=S9rBqwVl9Pco2DYv7TKEDvvkgY
RT1FD-25-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.03 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618187&prj=626&rqi=r5cUWizPSLjdBRc9pmQnmN3qt7
RT1ELEC-59-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Discrepancy between drawing & actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618213&prj=626&rqi=DLxIl5HxhtdHTi0D1tBk49vbTQ
RT1FD-24-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.02 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618189&prj=626&rqi=DHBNXq584hep6janxLWqUC03XB
RT1ELEC-58-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Deep cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618208&prj=626&rqi=HRLAGYm2qaZ4lz44PG57V0iQDT
RT1ELEC-58-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Please upload calibration certificate of torque wrench | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618204&prj=626&rqi=noO3lcBXu2jV6WqpjKMee9pF1B
RT1ELEC-58-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | ACB has scratches | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618207&prj=626&rqi=FMyZiKo48xWmzhKiialhFlbvnr
RT1FD-9-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-2.07 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618199&prj=626&rqi=155mp6rk4w6OZQ0Ngds8gQm50G
RT1ELEC-58-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Permanent equipment label/tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618205&prj=626&rqi=3GnCSA9jZUUF0aqZzCCuaTrGnp
RT1ELEC-58-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Ensure all ACS & HMI are properly protected from construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618211&prj=626&rqi=Pi18pIqNuqBut5llB7NNKGBvO4
RT1ELEC-58-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Discrepancy between drawing & actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618210&prj=626&rqi=0sDC2tKyrnXhnay57dvrZcYViv
RT1FD-31-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.10 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618193&prj=626&rqi=tQc2rmf7Ztxe9XHLm3LqMR1slT
RT1MECH-100-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_4 | FFU - Air Scrubber |  |  | nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618040&prj=626&rqi=XEL8MB2LgLGhXH62f4DuoMwX2p
RT1MECH-102-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_5 | FFU - Air Scrubber |  |  | nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618042&prj=626&rqi=AI8CRF7aXCtQubW8FnYfCJzhlV
YT1MECH-82-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_4 | FFU - Air Scrubber |  |  | issue from L2A; nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618045&prj=626&rqi=mSbGOKfXKPzt4f9gCCzqR2dFG3
RT1MECH-96-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_2 | FFU - Air Scrubber |  |  | nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618038&prj=626&rqi=UzSyhGkWMyVFc3PgR8lL3dNszB
RT1MECH-98-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_3 | FFU - Air Scrubber |  |  | nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618039&prj=626&rqi=SdY57iK0VFK3ePIVzprgg4hwUv
YT1MECH-80-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_2 | FFU - Air Scrubber |  |  | issue from L2A; nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618043&prj=626&rqi=KypzTbIhyZolBpmSta17ey8pxk
YT1MECH-83-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_5 | FFU - Air Scrubber |  |  | issue from L2A; nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618047&prj=626&rqi=9E7nyd4skA6nTUCULESRUDAH4h
YT1MECH-32-001 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | jacketing not proper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618011&prj=626&rqi=chS1yNvkSVUJDZ6bqsGjzazFvm
YT1MECH-81-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_3 | FFU - Air Scrubber |  |  | issue from L2A; nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618044&prj=626&rqi=T9CFKVjkp5x2lIZuijOdbJaU60
RT1ELEC-149-010 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1MSD_D_1 to 1UPS_D_1) Please clarify with engineering, the drawing shows 5 busduct supports, but only 4 are installed. Confirm if this is approved and safe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617946&prj=626&rqi=tsvxNrjBYfgNlcqvAv3AD5AejN
RT1ELEC-124-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617891&prj=626&rqi=OxEaaYncMez7jbQ3JxFEue5SvA
YT1MECH-75-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | issue from L2A; provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617896&prj=626&rqi=IngzdoGLXPt5Dojl1uLFxXBWYX
YT1MECH-76-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | issue from L2A; provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617897&prj=626&rqi=zuCnKorc4sv5NXWs2bcwfGny7U
YT1MECH-78-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | issue from L2A; provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617899&prj=626&rqi=YjkFKucqpZPv0dH2FzTxXKy131
YT1MECH-69-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | issue from L2A provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617895&prj=626&rqi=c44Yteng5uh15G428Tdd1b27g9
YT1MECH-77-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | issue from L2A; provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617898&prj=626&rqi=k7eTGBePwGCjlZPD1TKelUe4hl
RT1ELEC-1-017 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Cable installation not yet completed? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617901&prj=626&rqi=mF5jUwcOfBDeYuATxiKg0DCaqf
RT1ELEC-176-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Door gasket panel broken/damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617914&prj=626&rqi=TZIZM6s2IUaCVvSFSHxUjSh7Oo
RT1ELEC-174-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | Cable tube marker is faded. Replace or re-label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617917&prj=626&rqi=b7Z7e3NvojFpBnJ6rmGtj8zvxm
RT1ELEC-1-020 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Busbar joint between battery not yet torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617904&prj=626&rqi=7nomnaWsVCRQvmUJlvrGizDguu
RT1ELEC-176-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617911&prj=626&rqi=JsVCXQIi70xJb5YCNjjSMa59ya
RT1ELEC-176-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Discrepancy between drawing and actual installation. In drawing this for 1TOU_C not 1TOU_D. Please clarify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617910&prj=626&rqi=LLJz0BApWu9pVAnWjxNW0rPoyU
RT1ELEC-1-019 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Incorrect cable connection between batteries (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617903&prj=626&rqi=TjqFjBboqQ04bQxIgHkgvfyQIs
RT1ELEC-123-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Sleeve and firestop at wall opening/penetration not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617888&prj=626&rqi=gjB6KyF7Q975Xmb94uTRLfanXa
RT1ELEC-176-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Please provide temporary cover to protect form construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617913&prj=626&rqi=1d4cx9wj8O2MjAP7NyYqgw75d3
RT1ELEC-1-018 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Battery stopper not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617902&prj=626&rqi=N1E4FvHiNENsH2ndmbKyvt0NYl
RT1ELEC-174-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | Discrepancy between drawing and actual installation. In drawing this for 1TOU_C not 1TOU_D. Please clarify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617915&prj=626&rqi=uvv2ajOLcC7T2SbfeTKPJxZ0gj
RT1ELEC-1-021 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Discrepancy between drawing & actual positioning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617905&prj=626&rqi=o7G47I4AKXYmhctDtx7zR0BAHv
RT1ELEC-176-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Cable tube marker is faded. Replace or re-label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617912&prj=626&rqi=r9f68FINBOtPRZ4R7JBUDWRUdT
RT1ELEC-1-016 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Equipment not level/titled, please refer to the attached water pass result photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617900&prj=626&rqi=q3EFDWj6G3HK6biOuoBRuCvGnK
RT1ELEC-123-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Glanding cap at cable gland not properly installed. Reinstall to ensure fully proper sealing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617889&prj=626&rqi=x7pQAFuHAkNYUcTLkedlZGs43q
RT1ELEC-174-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617916&prj=626&rqi=DSX1OuxYe5ZXwel4RTYnggzEWZ
RT1ELEC-174-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | Please provide temporary cover to protect form construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617918&prj=626&rqi=B7RdnrO7nHqdqNuQsHAQKCHKC1
RT1ELEC-124-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Glanding cap damage/broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617890&prj=626&rqi=uf0B12usvj8q8Czi8E5SkkeGMG
YT1MECH-108-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | some parts of the safety valve are rusty, need to replace/touch up, because some other valve seems ok with no rust at all | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617738&prj=626&rqi=QJVHfewdKrO8nfmYpj2HlSavGy
YT1MECH-107-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | some parts of the safety valve are rusty, need to replace/touch up, because some other valve seems ok with no rust at all | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617772&prj=626&rqi=cjG64B2cnlGqrJ5TuEsXivRNxB
YT1ELEC-3-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Earth cable point-to-point cannot be verified as the earth cable has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617656&prj=626&rqi=n5drWOcQKxmEa0QBCockdw1h38
YT1ELEC-4-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Earth cable point-to-point continuity cannot be verified as the earth cable has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617659&prj=626&rqi=nYV9bReAdX9M00uLYyFyC1l36j
YT1ELEC-5-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Improper grounding cable termination at BTU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617661&prj=626&rqi=13x8xOnOUtmFVZ9tkNJ2Bw2ZWy
YT1MECH-107-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | the bolt appears to have less than 3 thread and there is one bolt with no washer on it | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617739&prj=626&rqi=4zMVr01KsLaYI4W2TXgr1vi1id
YT1ELEC-5-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Earth cable point-to-point continuity cannot be verified as the earth cable has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617660&prj=626&rqi=IWxUkCm9xDeOPcr3oMYdfR9zHo
YT1MECH-108-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | Grouting base plate support pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617736&prj=626&rqi=sBFK9KKknjzRg9gfodV3pBGOsi
YT1MECH-107-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | Grouting base plate support pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617740&prj=626&rqi=dXhUmKjXtewOvFOIpTVUA49RtF
YT1MECH-108-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-08 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | some bolts appear to have less than 3 thread | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617619&prj=626&rqi=uu7Hq2FAWn09vtHPA63c2ziMHo
RT1ELEC-131-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breaker, similar to breakers Q1-1 to Q1-5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617494&prj=626&rqi=iRPkmlrpSUEcORDoJcxgOGYWRk
RT1MECH-2-001 | JK01-2 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | Fuel Tank not yet install sight glass, tagging and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617480&prj=626&rqi=01kDvS6TWfk84JPPuWoZStwjFh
RT1ELEC-132-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617513&prj=626&rqi=HBhJZxAFtpy8Gjxp0bfcYkrirr
RT1ELEC-132-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Equipment need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617505&prj=626&rqi=mBuZICldXoh0PcYDZt0c0ytXyU
RT1ELEC-132-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Discrepancy between drawing and actual positioning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617506&prj=626&rqi=ZHpLGMwnemryd5RJcZxlOw95u2
RT1MECH-4-001 | JK01-2 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Fuel day tank not install sight glass, tagging and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617486&prj=626&rqi=8OEhUJjLOm6tSIPey4gaBtWgK6
RT1ELEC-132-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (should be 1MDSB_F_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617504&prj=626&rqi=FfFD7I67e7OIOv3kefnDQ74jx8
RT1ELEC-132-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_F_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617511&prj=626&rqi=N3jnLt90waC4oRCfAthQ9kAJYG
RT1ELEC-14-002 | JK01-2 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Panel Isolator, DB Aux any part not tagging, cable not tight and cover acrylic not install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617489&prj=626&rqi=iFE4uZrfsEZYjqc0KG55ypH7LB
RT1MECH-5-001 | JK01-2 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Fuel day tank not install yet sight glass, tagging and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617487&prj=626&rqi=0c5Wj2Avc8E1WSXnXAUTUwWUXH
RT1ELEC-12-001 | JK01-2 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | Panel Isolator, DB Aux any part not tagging, cable not tight and cover acrylic not install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617488&prj=626&rqi=8FbllD25T89mMev4kAzCUtoBpp
RT1ELEC-131-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (should be 1MDSB_F_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617495&prj=626&rqi=1yf7nnqdXziLH1AsUnxRXwtc1T
RT1MECH-3-001 | JK01-2 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | Fuel day tank not yet install sight glass, tagging and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617485&prj=626&rqi=Ne9qA4AIzNj1FmCUxC1ZglwPlt
RT1ELEC-131-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Please add protection to prevent from construction damage, dust & debris also please protect HMI display | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617496&prj=626&rqi=E2EPD3hT6CVpa9IRvgUZ88ZoNH
RT1ELEC-131-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Discrepancy between drawing and actual positioning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617499&prj=626&rqi=kIvm64j0Ga9BuGsRkoKJwf2REe
RT1ELEC-131-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_F_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617497&prj=626&rqi=aEzVyESb8edOwVA1976ZXJvDjk
RT1ELEC-25-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Please ensure HMI display is properly protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617371&prj=626&rqi=PmWGi4Xu4KQrkoSuiiTpv3pLbX
RT1ELEC-25-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Minor dents require touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617370&prj=626&rqi=Qb1ezHQABtYowJhAHThdNo6LAX
RT1MECH-29-007 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | DB panel: there was some scratch inside, need to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617421&prj=626&rqi=0JyxyXfUtbaAj2ANWUIlhcp7oW
RT1MECH-28-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | the bolt appears to have less than 3 thread and there is one bolt with no washer on it | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617410&prj=626&rqi=H9zprHpN7SrXWQ2Sk7w2CPtWe0
RT1MECH-29-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | DB Panel anchor bolt seems not straight / tilted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617420&prj=626&rqi=OWC2m9FHVtXPMeq0b641E5Hi7f
RT1ELEC-25-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Latest drawings are not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617368&prj=626&rqi=r3CMVFOlsfc4OfnHaBmh04LBiw
RT1MECH-28-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Grouting base plate support | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617418&prj=626&rqi=sDLz7CBndq6arMlwxqqfcSXhHf
RT1FD-38-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-7.09 | VES - Vesda |  |  | provide Cause and Effect Matrix is approved document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617427&prj=626&rqi=tkQQOW0ZqMqSZNdtwu8GVPS6gd
RT1MECH-28-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | some parts of the safety valve are rusty, need to replace/touch up, because some other valve seems ok with no rust at all | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617419&prj=626&rqi=pQFc5Trq9hMoZalr7uUoGFYY6F
RT1ELEC-25-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Equipment permanent label/tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617374&prj=626&rqi=t8HSaA8ApXIn7tHgVmWBvdTHk8
RT1ELEC-25-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Deep cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617369&prj=626&rqi=q9QR8Wa5Mb40qq2o0GfvB2Iolz
RT1MECH-29-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Grouting base plate support | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617351&prj=626&rqi=ErUa7569h5xm87JMkxQm35KJjq
RT1MECH-76-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_2 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617321&prj=626&rqi=S04kpMUNcSJNPgX9AVkopI1Hfn
RT1MECH-74-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | provided Approved method statement for L2B static testing upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617306&prj=626&rqi=Mcve5z24b8c9PF3OCC9BROgXJT
RT1MECH-84-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_1 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617333&prj=626&rqi=vGSgyS4gS0pX10eWBI378RF7wf
RT1MECH-29-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | some bolts appear to have less than 3 thread | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617350&prj=626&rqi=Z1PP5XELUHLoPQADvAyZNbrMTS
RT1MECH-78-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_3 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617325&prj=626&rqi=qQajYdPE0DaYjPCEggkzGfwVHN
RT1MECH-86-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | provide permanent equipment label / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617310&prj=626&rqi=7fjfpB05IEcpA7inGEIapChrBg
RT1MECH-74-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617308&prj=626&rqi=qWVCInBnxrC3778kSdebMiuIlJ
RT1MECH-86-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | provide Approved method statement for L2B static testing upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617309&prj=626&rqi=7Q0BrNRH8suvfXlGIXWYbRDBUy
RT1FD-38-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-7.09 | VES - Vesda |  |  | minor scratch and paint damage at pipe vesda | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617304&prj=626&rqi=wKcpeiWzuCYQf4FV5UDArnIUHN
RT1MECH-74-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617307&prj=626&rqi=zxoRI0j1X3BnFBQQFL2Shbi2RT
RT1MECH-90-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | Cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617316&prj=626&rqi=wfnVJjxxZL9vkxV0CbdaJX1oIA
RT1MECH-90-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | Provide permanent equipment label / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617317&prj=626&rqi=ZnCZAhtnNoFAZx3DzWPACGwUSu
RT1MECH-92-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | provide Approved method statement for L2B static testing upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617318&prj=626&rqi=zopuWvvISjcFNqbhusrvc7fddJ
RT1MECH-92-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617320&prj=626&rqi=4h1Mhbro3InPHkySSiCI5yVwUY
RT1MECH-92-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | Provide equipment permanent label / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617319&prj=626&rqi=ay7yjobglschVTOwy7D43nGmRl
RT1MECH-86-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617311&prj=626&rqi=iQMYsw6Zajb4BkEDjWTqlBpda0
RT1FD-33-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-7.01 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617305&prj=626&rqi=W0MJZqzzsJVAIXSlmvV6dL48OF
RT1MECH-90-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | provide Approved method statement for L2B static testing upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617315&prj=626&rqi=DD4CswlAf7JGKUs1GmWzYHqtDo
RT1MECH-82-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_5 | FFU - Air Scrubber |  |  | cleaning issue and remove unused material inside equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617331&prj=626&rqi=UZqKDsOg9qC1zAHfQBvs5xViKu
RT1MECH-80-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_4 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617327&prj=626&rqi=VWt2TtA5VapNBpB30iPowce9t6
RT1MECH-88-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | provide Approved method statement for L2B static testing upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617314&prj=626&rqi=EOQ0JT5syuB9uh2nJWNGxwvWT3
RT1MECH-88-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617313&prj=626&rqi=pBjCEjxjXgGHROBfoPdLEIrkva
RT1MECH-88-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | provide permanent equipment label / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617312&prj=626&rqi=essEkJu3CQb1u5s9J14L3Ik0BW
RT1MECH-29-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | some parts of the safety valve are rusty, need to replace/touch up, because some other valve seems ok with no rust at all | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617352&prj=626&rqi=x4iOe9XbA34cimlF8tLnrUeYEY
YT1MECH-115-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1LCP_FPUMP_B2 | FT - Fuel Tanks |  |  | Invalid Testing Tools due to expired calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617136&prj=626&rqi=FxnxEyHt0RVojkrBoZBeU4fJPE
RT1MECH-15-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_F_61 | EF - Exhaust Fan |  |  | equipment name tag has not been affixed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617120&prj=626&rqi=ZwleRcEgdLKH4W45QS8ciPBDFb
RT1FD-34-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-7.02 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617147&prj=626&rqi=KtCCIvFMZjl8Dhlet0HDvGd80E
RT1FD-29-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.08 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617145&prj=626&rqi=UnLOdMNAFhi0XWABU5Udrgt2Qx
RT1MECH-15-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_F_61 | EF - Exhaust Fan |  |  | marking of support installation has not been applied | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617123&prj=626&rqi=pdmnFrHADLMaiDa8IkBoZwhD17
RT1FD-30-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.09 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617146&prj=626&rqi=3Zw9wBQifqelCnE9SvOTKXzLYX
YT1MECH-114-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1LCP_FPUMP_A2 | FT - Fuel Tanks |  |  | Invalid Testing Tools due to expired calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617131&prj=626&rqi=20ood7ZIZkIXyc5voYg9zA6Twk
RT1FD-36-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-7.04 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617149&prj=626&rqi=WQKjHiGr9uWzvgKqQNb9I901Z4
RT1MECH-15-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_F_61 | EF - Exhaust Fan |  |  | Airflow direction / orientation has not been affixed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617122&prj=626&rqi=KHbJeMr3OsQKdCWc3HZhOQhOWk
RT1ELEC-37-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Please add temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617130&prj=626&rqi=QmhTlzvzZxajtHwDiLJ1RiLKqk
RT1FD-35-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-7.03 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617148&prj=626&rqi=YG9LEbXkuFf7QRhtoc2lpP2zGg
RT1FD-37-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-7.05 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617150&prj=626&rqi=zUbFqzF0geUtjLWXzogX42LD0h
RT1ELEC-37-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617129&prj=626&rqi=IT4SoPnIRWpMQ8UWbfJ4PnbHh4
RT1ELEC-39-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Busbar joint marking not consistent. Standardize to red | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617015&prj=626&rqi=K8U78e8R5cmWwslTnn9UeR5Svu
RT1ELEC-39-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617012&prj=626&rqi=DAFMYOg26cKIRihDdSIzU5L58t
RT1ELEC-38-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | Busbar joint marking not consistent. Standardize to red | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617025&prj=626&rqi=MkNGoosQu3VgM004WzxR8sJDp3
RT1ELEC-129-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable containment penetration not firestopped. Provide firestop | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616956&prj=626&rqi=GBIxeFXeWkagI87qrmgy9VGriO
RT1ELEC-39-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Anchor bolts too long, torque wrench cannot be applied. Re-torque and re-mark all anchors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617014&prj=626&rqi=EI7EqiIOLWRj9Ih0PsaR7fp1Of
RT1ELEC-37-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Busbar joint marking not consistent. Standardize to red | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617031&prj=626&rqi=sBoaZhdzw8SUQ3KDNk1xc65Ojw
RT1ELEC-39-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Please add temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617018&prj=626&rqi=BIsIDW8ohcxzteXCLWfGsvYfEs
RT1ELEC-39-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Equipment labelling still temporary. Install permanent labels as per approved scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617013&prj=626&rqi=fCDZtgqTg3KJ8dOUlwNvh3Qs81
RT1ELEC-39-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | GC to upload following documents: 1. Certificate calibration of torque wrench 2. Approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617017&prj=626&rqi=x7qeV4kUFpNBycmxbKplksQ6Q6
RT1ELEC-37-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Please upload factory test documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617028&prj=626&rqi=6DkFOzTyMbOTRaLt44fX0EieHT
RT1ELEC-38-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | Anchor bolts too long, torque wrench cannot be applied. Re-torque and re-mark all anchors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617024&prj=626&rqi=qnrJX4PDLBv0wYN0L3PhES9z7G
RT1ELEC-37-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Anchor bolts too long, torque wrench cannot be applied. Re-torque and re-mark all anchors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617032&prj=626&rqi=yOULLT62IJXjQg1ZRkFBVwRJXZ
RT1ELEC-129-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Unused bolt observed at cable gland entry. Remove if not required. Glanding cap also not fully covering | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616955&prj=626&rqi=mtRtO2H2VxYGLiaQnWokNAhvmc
YT1ELEC-3-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2B | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | During function test of CxL2B, the alarm signal stayed ON and could not be reset due to incorrect wiring, the same issue also affected fault and trip signals. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617423&prj=626&rqi=EmF6Zb0epmx6mzr5tI01YAXoSb
RT1ELEC-38-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | Please upload factory test documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617020&prj=626&rqi=ShgfZmG47FPU6JdyOmAb9HPR1Y
RT1ELEC-39-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Please upload Factory Test documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617016&prj=626&rqi=YPKmwkvrPdMTOCmP5sx219wc1L
RT1ELEC-37-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Equipment labelling still temporary. Install permanent labels as per approved scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617030&prj=626&rqi=6GbQbUxG25CB9g2je0G0O90HF5
RT1ELEC-38-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | Equipment labelling still temporary. Install permanent labels as per approved scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617023&prj=626&rqi=2lWbZpoOXirCHtHkajdH8xsqPd
RT1ELEC-38-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | GC to upload following documents: 1. Certificate calibration of torque wrench 2. Approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617021&prj=626&rqi=alA6TP555vvIKS7vx88XWFEmrt
RT1ELEC-37-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | GC to upload following documents: 1. Certificate calibration of torque wrench 2. Approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617029&prj=626&rqi=EZfn1pHfrDEN4LfucfeyZlPykD
RT1ELEC-128-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable arrangement is not neat. Re-arrange properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616950&prj=626&rqi=7QjpMSSfMu67p2z3rPRy37yb7b
RT1ELEC-130-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Incorrect cable tagging. Should be: from 1MDSB_C_1 to 1DB_C_DATA HALL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616946&prj=626&rqi=RbagTrbW1Y087wNg9XjuBS85YI
RT1ELEC-128-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Missing cable tagging for L2, N, and G | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616948&prj=626&rqi=r8s0AROPscJIZCYZoxHSXXmT1e
RT1ELEC-55-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616826&prj=626&rqi=JS8KFRHz9ZTVzGRL3B8dNSKM8r
RT1ELEC-128-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Remove temporary marker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616952&prj=626&rqi=7xhW79vOeqffxdoo5L5vBl2WOs
RT1ELEC-55-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Minor dents & scratches require touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616829&prj=626&rqi=sOWZFrE3Vtm1gVtJNgWk5bU6hQ
RT1ELEC-55-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Provide temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616838&prj=626&rqi=94p4h7ZDNzV9E8U3BRhwAAX3ou
RT1ELEC-129-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable tagging not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616954&prj=626&rqi=uBQXsgZ0yiiljWkJeCDM8upHUV
RT1ELEC-55-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Deep cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616832&prj=626&rqi=bSweR4nia8bzi7wbYXDvXwMlxP
RT1ELEC-55-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Please provide correct GA & SLD drawings for 1STSSB_C_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616834&prj=626&rqi=g9loVsOo7sWlQT56HPTVrGIGK8
RT1ELEC-55-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Panel tagging not as per design (should be 1STSSB_C_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616828&prj=626&rqi=jRKfKKckOLhD5r0uZJ8O1vOUPV
RT1ELEC-130-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Improper termination, conductor still exposed. Please rectify cable vinyl | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616943&prj=626&rqi=oqneymVNbvZzrDf9phplFRpPPa
RT1ELEC-129-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Missing bonding jumper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616953&prj=626&rqi=w5THwkpLrpgJ5CbSAQFfKMNSoE
RT1ELEC-130-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable containment is not properly aligned/levelled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616944&prj=626&rqi=T4HNh8lhxn8cMdEED5y0vimTAc
RT1ELEC-55-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Ensure all ACB & HMI are properly protected from construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616836&prj=626&rqi=EezIXMMlswK5g0AENobyJEMWCK
RT1ELEC-130-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable insulation (vinyl) is torn. Please replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616945&prj=626&rqi=aSwHm2Vm3k6ieVrUtFwy7Ziq0x
RT1ELEC-55-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Control cables appear not connected, please verify and confirm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616830&prj=626&rqi=JaZdH1hFSjXByg9efKrex8p1Po
RT1ELEC-128-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable tagging incorrect and no phase identification (L1, L2, L3). Revise to: from 1MDSB_C_1 to 1DB_C_CRITICAL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616951&prj=626&rqi=GW9jyNpwcdibL1Uz8OVQzQJC94
RT1ELEC-55-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Busbar joint bolts not yet torqued and torque-marked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616831&prj=626&rqi=ygokzM7q4iUVpmdYMz60c2ulQS
RT1ELEC-55-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Vertiv emblem on panel door is loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616835&prj=626&rqi=Thln5gl0QSXuiP9yBDYsFxogKG
RT1ELEC-128-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Glanding cap at cable gland not properly installed; incomplete coverage observed. Reinstall to ensure proper sealing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616949&prj=626&rqi=tHw8aqw6Egq0THwidiFTxgpULX
RT1MECH-115-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616790&prj=626&rqi=GtUctPKvCpEqDhZ9Kj5Sz4fmWs
RT1MECH-115-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | please remove unused material / object, and also need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616791&prj=626&rqi=GVj4g8jau8a8kja8DCUAWaFQRK
RT1ELEC-35-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Approved layout drawings not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616796&prj=626&rqi=ErLrTjJW01U8jJfYd6nI5ALjOX
RT1ELEC-35-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Panel tagging not as per design (should be 1LIBATTSYS_C_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616800&prj=626&rqi=9BKeq0uQgbdlRf96P3qObeiJBg
RT1ELEC-36-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616807&prj=626&rqi=BbUfEcMljb7BeoqZfS99JVURk3
RT1ELEC-35-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616801&prj=626&rqi=Y7T6eMXD7sSHClvh7R0UokfOao
RT1ELEC-36-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | General cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616811&prj=626&rqi=HXtFIEAnwzt6LpDifX0d3BsYhF
RT1ELEC-35-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | General cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616803&prj=626&rqi=afUxuC33cAesIzbhN4DA77VJn9
RT1MECH-115-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | minor scratch has found | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616788&prj=626&rqi=5lLU1ktu2PpKy6HBZ7wXnDmhbn
RT1ELEC-36-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Approved layout drawings not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616805&prj=626&rqi=2Q20hVd7lvHiQLhr9HPvYi0l7r
RT1ELEC-35-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Provide temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616802&prj=626&rqi=zIHMDyugAYZ8YNeCAJ5acxHoBP
RT1ELEC-35-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Anchor bolt thread minimum 3 threads exposed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616799&prj=626&rqi=l1qSeSexfEfhjmaKgzCyXGFSz0
RT1ELEC-36-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Panel tagging not as per design (should be 1LIBATTSYS_C_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616809&prj=626&rqi=ukWv8ZoMUwRW4D9V9CgDZjmFdg
RT1ELEC-36-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Provide temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616810&prj=626&rqi=xCsN6hPpRvwXsKMZv1FxZsUgI9
RT1ELEC-171-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | There is a discrepancy between the drawing and the actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616671&prj=626&rqi=TLkj3hYq5QRJDWG6K46kb569mb
RT1ELEC-171-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616670&prj=626&rqi=GbXIwgextxuXMZh5TjQ6OB0ojl
RT1ELEC-170-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616665&prj=626&rqi=SbWCH7Y2jmNSpS18f0vYddjgQP
RT1ELEC-171-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | Please provide temporary cover to protect from construction damage, dust and debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616673&prj=626&rqi=LXM19IvOsfwlX69WuitjNhD7C9
RT1ELEC-170-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Approved Technical Submittals / Material approval / Specs not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616664&prj=626&rqi=AmvFShRYw3x564qDw8UKSVtKbu
RT1ELEC-170-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Please provide temporary cover to protect from construction damage, dust and debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616669&prj=626&rqi=FFGwsNOXNLW55ikwzfzVtBDFOF
RT1ELEC-170-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616668&prj=626&rqi=vdgob0LhbC1bm9MCnTdEaOzKEz
RT1ELEC-171-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616672&prj=626&rqi=tSbM5qFXKImyxbAhvqqafGa85b
RT1ELEC-170-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Cable tube marker is faded. Need replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616666&prj=626&rqi=pIbjLEinkuiGhGWCOVVMhqJ7qb
RT1ELEC-170-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | There is a discrepancy between the drawing and the actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616667&prj=626&rqi=bpRPIug47wNwa8BI4O2u9M62i2
RT1ELEC-173-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616475&prj=626&rqi=1X1AytLAuIwSnz08am5rlaNp63
RT1ELEC-172-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Cable tube marker is faded. Please replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616479&prj=626&rqi=pdNoEKM9g1rtE4beYZyhlkFcKI
RT1ELEC-128-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | There is a discrepancy between the drawing and the actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616410&prj=626&rqi=LUOXJB06NwIoXke2CcOxHmBl3Y
RT1ELEC-128-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Equipment need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616413&prj=626&rqi=gGPr7rdAK2KyB1x4qcr4zjHhYS
RT1ELEC-128-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Please confirm torque value applied to panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616414&prj=626&rqi=nBDm60fw0XbTZ3s2bqxGVcFHtu
RT1ELEC-128-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (1MDSB_C_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616409&prj=626&rqi=qunIGRG6bg1rrqEqqbTnzLi9nq
RT1ELEC-128-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Please upload correct document for 1DB_C_CRITICAL. This documents for 1DB_D_CRITICAL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616340&prj=626&rqi=JzJr9d5wYCkeqyrs04wKnbj8Ia
RT1ELEC-172-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616481&prj=626&rqi=4UEqJzg9RtbzsIig4Xaljdk2pO
RT1ELEC-128-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_C_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616411&prj=626&rqi=sqgwmJHTLgJiqPWPWHNjc3qIbC
RT1ELEC-128-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breaker, similar to breakers Q1-1 to Q1-3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616412&prj=626&rqi=aIurlGbzM4vz4YCxOzEr1eyuyc
RT1ELEC-172-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616480&prj=626&rqi=cmlEPMlFtZUvW0b2FHRiyd0AM0
RT1ELEC-130-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (1MDSB_C_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616422&prj=626&rqi=MM4zjHQ0XlsmjxlI2lP6wFyAgX
RT1ELEC-130-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Panel body is dirty. Need to clean | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616419&prj=626&rqi=0C6wNHOFONELeQ2bQ0tC4OQXL0
RT1ELEC-172-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Missing phase separator / barriers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616482&prj=626&rqi=UMfAkt7Z5jL2BDBqwR6fjx5Mqj
RT1ELEC-177-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616511&prj=626&rqi=reZnKuMGgPDyHMXr51LhQDVVur
RT1ELEC-177-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | Approved Technical Submittals documents not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616507&prj=626&rqi=kVHVMRnlxhQ0PBr66ySPHIV6qP
RT1ELEC-175-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616522&prj=626&rqi=KBLtRK9pUXeH7mmCcVyxe3IRiU
YT1ELEC-4-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2B MV Cable RMU_F to MLTX_F) Tan delta values on phase S increase significantly, indicating possible insulation degradation. Please clarify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616528&prj=626&rqi=jZ1bLiEuuf2c3TCsSAvvsiJYoB
RT1ELEC-175-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Please upload following documents: 1. Approved technical submittals documents 2. Factory test data documents 3. GA & Schematic drawing 4. RFIT documents 5. MoS CxL2B documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616518&prj=626&rqi=u3GiVTOCYlttXB1r678NwPllhC
RT1ELEC-175-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616523&prj=626&rqi=0gSOXorzqBxKWzVaQ6SKUELFSZ
RT1ELEC-177-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616509&prj=626&rqi=4QBnyOLl5OWgcVU9OyCVmSvdrj
RT1ELEC-177-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | Cable vinyl material (neutral) is inconsistent with others. Standardize to match | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616510&prj=626&rqi=slsZrW3IshSMbn79Gee4jtOY5U
RT1ELEC-177-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | TOU F positioning is not shown in the latest approved layout drawing (only TOU A). Revise drawing and include dimensions (mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616508&prj=626&rqi=G3sQ0TIVS6WyugtO1XrGtsY4OT
RT1ELEC-175-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Phase separator / barrier is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616520&prj=626&rqi=sBaBpG6Z4bi5roq18PsmzLvQKg
RT1ELEC-130-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_C_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616424&prj=626&rqi=WSbR0PWAO6spUEsasVXWRdZWW9
RT1ELEC-130-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | There is a discrepancy between the drawing and the actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616415&prj=626&rqi=gOUipfyN9SvonuivEDXJkBxPiZ
RT1ELEC-130-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Please upload correct document for 1DB_C_DATA HALL. This documents for 1DB_D_CRITICAL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616342&prj=626&rqi=3HXRt59o2GrTdnHFLpvrBjUeVc
RT1ELEC-130-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels (feeder) on the acrylic cover above the breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616417&prj=626&rqi=Z96Qkwp6ntbuHLktlpenB5iPMy
RT1ELEC-130-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Please confirm torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616423&prj=626&rqi=PIZe5xnIFbWoeAdtt6zSA9koXF
RT1ELEC-173-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Paint stains on panel surface. Need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616477&prj=626&rqi=ElAnGDP3JxS1PITXe3BXjDgHFI
RT1ELEC-173-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Approved Technical Submittals documents not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616474&prj=626&rqi=jkghgVRVeFemCVMy5WxLtf1nq9
RT1ELEC-173-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Please provide temporary cover to protect form construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616478&prj=626&rqi=AYH9wlZSQdjqEgMBs6UVq3R1um
RT1ELEC-133-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (1MDSB_F_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616487&prj=626&rqi=UuRmc2YYmIwr6hsPrPjJQZVFC4
RT1ELEC-173-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616484&prj=626&rqi=OIQgjesMh0f8IOLYAUVwP9BhGN
RT1ELEC-173-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Cable termination is not properly done. Copper conductor is exposed. Please rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616476&prj=626&rqi=V3wx76eHAkaeDY7VdjHNf3r0VQ
RT1ELEC-175-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | TOU F positioning is not shown in the latest approved layout drawing (only TOU A). Revise drawing and include dimensions (mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616519&prj=626&rqi=EFkNVXHHi7daqveEldYKIqz3HN
RT1ELEC-133-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616490&prj=626&rqi=QNPwJggS5zp24WVxeY5PLs3oDd
RT1ELEC-129-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please upload correct document for 1DB_C_EWALL. This documents for 1DB_D_CRITICAL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616341&prj=626&rqi=k1SzERaJGkkwEfWy6w9gR48hFr
RT1ELEC-133-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Incorrect document uploaded. This for 1DB_D_CRITICAL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616493&prj=626&rqi=pB0DFz1BMy4UV5NKmMzpzksjjj
RT1ELEC-129-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (1MDSB_C_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616399&prj=626&rqi=p3lYWx06Vp6g3uLTV8neB0iYrv
RT1ELEC-133-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_F_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616471&prj=626&rqi=wjUW9oZH8rH6WfERnlizyesu3P
RT1ELEC-133-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Cable tube marker is faded. Need replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616495&prj=626&rqi=LVRXyD3nao0uabibaM2Kc3lafA
RT1ELEC-129-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_C_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616407&prj=626&rqi=W2xAIQznWJmMVUWDIukzeV35ph
RT1ELEC-129-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breaker, similar to breakers Q1-1 to Q1-4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616401&prj=626&rqi=CJA6NJJhzsQNQPvXAUhYzhI1My
RT1ELEC-129-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | There is a discrepancy between drawing and actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616406&prj=626&rqi=p6AKLLoGdfAimoN7RXn96EMzUH
RT1ELEC-133-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels (feeder) on the acrylic cover above the breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616489&prj=626&rqi=Urdc9T7C3s5cYUT8UreVrX4qxY
RT1ELEC-133-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | There is a discrepancy between the drawing and the actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616486&prj=626&rqi=CD40VR4q3IUwZH4OZQNV3hNn04
RT1ELEC-129-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616403&prj=626&rqi=Dgk0hjeZ35MvliLmVLqtv63jUD
RT1ELEC-129-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please remove any temporary marker markings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616404&prj=626&rqi=xNNIlEheP5nFpcvVZfnt0j8tgW
RT1ELEC-124-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | Please update the drawing to reflect actual unit positioning based on the RFIT inspection results | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616253&prj=626&rqi=OkO3Okwae6QqJfGX5hZgjctDp9
RT1ELEC-123-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breakers, similar to breakers Q1-1 to Q1-4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616247&prj=626&rqi=zrOkfWvbmZDtC1FIZhOi3p4qus
RT1ELEC-123-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Remove temporary marker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616246&prj=626&rqi=btJqsyzSABTcjB7zF0BAlDxLV0
RT1ELEC-124-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breakers, similar to breakers Q1-1 to Q1-5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616252&prj=626&rqi=JblKHKoiavYDYyUVo4EQ2WgQdy
RT1ELEC-124-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | Cable marker is unclear/faded. Please replace with a proper label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616250&prj=626&rqi=fawye1zVbL6IAEbq1m0O0QQN8B
RT1ELEC-124-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | Please clean the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616251&prj=626&rqi=s7qsj3mEJpxITimDswA31w95RS
RT1ELEC-122-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breakers, similar to breakers Q1-1 to Q1-5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616243&prj=626&rqi=cVyAGZ5Z2HssC52IexwPmWgdmR
RT1ELEC-122-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | Please update drawing based on RFIT report for positioning unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616238&prj=626&rqi=L739Nj4ugboaHY91OPP3FgcHOz
RT1ELEC-122-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | Please correct the incoming (source) label in accordance with the approved drawing/design (1MDSB_B_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616240&prj=626&rqi=iqvgAMvQLximBUtp7kGJbWSdGG
RT1ELEC-123-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Please confirm the torque value for the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616245&prj=626&rqi=DVLBwDicRi4DAPdPOWXQ5dMKuR
RT1ELEC-123-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Please correct the incoming (source) label in accordance with the approved drawing/design (1MDSB_B_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616244&prj=626&rqi=QHdXpmQfYiJ6JoTA14b3oZ699Q
RT1ELEC-123-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Please update the drawing to reflect the actual unit positioning based on the RFIT inspection results. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616248&prj=626&rqi=oiS3q0QQSjfpyOpIZ4lqdcupOm
RT1ELEC-124-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | Please correct the incoming (source) label in accordance with the approved drawing/design (1MDSB_B_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616249&prj=626&rqi=aTCXE7iMf9GISYDRYqZAtrq0S6
RT1ELEC-53-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Please upload Installation and Start-up Manual is documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615854&prj=626&rqi=xxt3QwwV0YLqAzTD1UdHef2epr
RT1ELEC-53-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Please ensure all ACBs are properly protected to prevent construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615860&prj=626&rqi=51ioUSo1DLURFqlNDX61Xwt2c8
RT1SEC-9-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Security | equipment | 1ACS_level_4_General | ACU _ Access Control |  |  | Installation does not comply with approved drawing and is positioned too close to the manual call point (MMR B Level 4) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616223&prj=626&rqi=8Vw7hsB4OyEmLaUJzUzTkMHP3k
RT1ELEC-53-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | MoS CxL2A document is still empty and has not been uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615857&prj=626&rqi=xPodItJtwMsu21VQWvnveNRaPK
RT1ELEC-53-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Torque wrench calibration certificate does not match the tool used during inspection. Please upload the correct and valid calibration certificate for the actual torque wrench used | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615856&prj=626&rqi=hcksy1Occlc3gtnpZ7LKb53b4i
RT1ELEC-53-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Anchor bolts shall have minimum 3 exposed threads | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615861&prj=626&rqi=lsDVjKoACh3GOuF17swsxaHbdr
RT1ELEC-53-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Minor dents/stains on panel surface observed, need touchup | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615858&prj=626&rqi=8Vmqi1x69ffWrVp1Iz4MzD5M6X
RT1ELEC-53-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Factory Test Data document not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615852&prj=626&rqi=M5h64xIdOicWuVP9w4fy9KWDqG
RT1SEC-12-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Security | equipment | 1ACS_level_7_General | ACU _ Access Control |  |  | Please upload following documents: 1. Approved technical documents 2. Installation Startup manual documents 3. Inspection checklist 4. Approved shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616228&prj=626&rqi=Kbth3g4zLVH3UlkCGpDZOEd3JJ
YT1ELEC-3-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L2B | Torque required | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Busbar connections between batteries have not been properly torqued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616232&prj=626&rqi=p2FSew9T689MrMFAZDWonupnac
RT1SEC-10-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Security | equipment | 1ACS_level_5_General | ACU _ Access Control |  |  | Please upload following documents: 1. Approved technical documents 2. Installation Startup manual documents 3. Inspection checklist 4. Approved shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616224&prj=626&rqi=RhxOfw2cv7vva9vPOa63WKXmB1
YT1ELEC-3-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Grounding cable is not connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616233&prj=626&rqi=sD7OpwW3snZzG4KXq0JGU0C5R7
RT1SEC-10-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Security | equipment | 1ACS_level_5_General | ACU _ Access Control |  |  | Tx room level 5 is installed with a single reader device instead of a double reader as per approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616227&prj=626&rqi=8sFkIQZN283gDFWUl1Gmmdvbp9
RT1ELEC-53-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Please confirm busbar join not yet connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616235&prj=626&rqi=l2sPWsq09mVl1erHcVOUHc74BM
YT1ELEC-3-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Please apply cable vinyl for proper insulation and finishing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616234&prj=626&rqi=saOzH0TByHK2mRFQLzbx7yFySX
RT1ELEC-26-001 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-03-16 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | UPS Mech D2 rear anchor bolt not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615772&prj=626&rqi=V9rY8JX0cxUEJUlA4leHW2zFsf
RT1ELEC-2-017 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) The equipment needs FOD | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615750&prj=626&rqi=gpFnxMRxk1VJaivzKvZSwyQZUc
YT1ELEC-4-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Please confirm the BTU incoming breaker rating. As per approved MoS it is 15A, while the actual installed breaker is 20A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616231&prj=626&rqi=l88WK71iZuHBaSWezm7dPKwis0
YT1ELEC-2-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Please confirm the BTU incoming breaker rating. As per approved MoS: 15A, actual installed breaker is 20A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616230&prj=626&rqi=EonKnMQv8lfQgSAUI7EBDpFBKD
RT1ELEC-56-001 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-03-16 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | STTSB rear back frame anchor bolt not installed. Front panel anchor bolt also not complete | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615755&prj=626&rqi=EGN3mAJ9d0xPfauQJ3q6cE5V32
RT1ELEC-24-001 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-03-16 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | UPS Mech C2 rear anchor bolt not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615771&prj=626&rqi=Rh0lnedNhhP6WPORVXiqdlc6hl
YT1ELEC-4-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Busbar connection each battery not yet torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615698&prj=626&rqi=lAhBX1zQlNB9AF0iwhqUR7AjB7
YT1ELEC-4-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Grounding cable not yet connected to main earth bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615695&prj=626&rqi=Ygv6JqhbRD9xCDZRhm6RA4SRgf
RT1ELEC-2-016 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Minor dent & scratches observed, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615704&prj=626&rqi=aoY9mNBVT8mbKd15kCP8dKpca4
RT1ELEC-2-015 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Grounding cable not yet connected to main earth bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615703&prj=626&rqi=Oynx1y2GXyLX9Rk4QSgYIVEEdU
RT1ELEC-4-025 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable) MV cable grounding braid not properly installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615672&prj=626&rqi=3EmGupVy6guGzpm9taSElujUXK
RT1ELEC-11-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | (Issue CxL2A MV Cable) MV cable grounding braid not properly installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615671&prj=626&rqi=7MXhTOKDqpXVMWJb9ct71eYyGi
RT1ELEC-1-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Latest GA & schematic drawings not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615402&prj=626&rqi=gz22W8MjLhexs9uxeiUGMwYkAF
RT1ELEC-1-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | HV cable design not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615393&prj=626&rqi=JdlRbntxCEz67Qnh6EL9edQHi8
RT1ELEC-1-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Bolts found rusty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615406&prj=626&rqi=0AWli2BYzABTmkmqy5cA8Bf2xO
RT1ELEC-1-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | MV LV Network Discrimination Study documents not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615391&prj=626&rqi=iznTl22lhF0n14vu8GDrQASX24
RT1ELEC-1-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Dust & debris found inside the equipment need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615398&prj=626&rqi=z5VHNX7a31T1AIAlfRyKoDSJ4K
RT1ELEC-1-009 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Relay protection unit is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615399&prj=626&rqi=xOTrcpFy3KGlRq0vXMFdYLTDui
RT1ELEC-1-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Multicore cable schedule not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615392&prj=626&rqi=sJsPHUgFZsNMPc7DxDPVN9nhQW
RT1ELEC-1-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Please upload RFIT report document for positioning unit RMU not MV cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615397&prj=626&rqi=FkEEcpZVsfTvrn16JGqUv3USKN
RT1ELEC-1-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Factory test protocol calibration certificates not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615389&prj=626&rqi=cJ7jrkjRH2Pn9i1D8wHnAjgQf8
RT1ELEC-1-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | L2B Static Testing Method statement not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615395&prj=626&rqi=LjkKpnIf7okC5o6q6EOmQ2E8Bn
RT1ELEC-1-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Switchgear Installation and Operation manual documents not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615390&prj=626&rqi=c7PbGQ4LeJcZfig3k5XctG6v7v
RT1ELEC-1-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Some components have only one label on the mounting/body, and terminals are not labeled. Each component should have two labels (on the mounting and on the component body) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615403&prj=626&rqi=C8henLpnV981e5vBWLXUk4OnPJ
RT1ELEC-1-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Sticker found damaged and shall be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615405&prj=626&rqi=3ltv14quzBLeaTvf0na7SccH0F
RT1ELEC-1-015 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Equipment positioning different from latest approved drawing (please refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615407&prj=626&rqi=mpNhDYrGNu0Yg2NZYRW83zeXUB
RT1ELEC-8-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Tap changer opening is not covered. Please provide a proper cover for the opening to prevent dust ingress and accidental contact | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615387&prj=626&rqi=CP6sou5q1o2pS8Ycdx5gq493mD
RT1ELEC-8-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Equipment positioning different from latest approved drawing (please refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615388&prj=626&rqi=FqJTeyfswFN2CPHil3SraR6Oax
RT1ELEC-8-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Fan cables are not properly dressed. Poor cable arrangement may cause damage or disconnection during maintenance activities. Please tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615386&prj=626&rqi=1CVzBgHVquWAgzAzzGwZsgAqlN
RT1ELEC-8-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Door scratches, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615385&prj=626&rqi=VEw579gGequ5NnHqAx3YeQK9mI
YT1ELEC-3-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Invalid Testing Tools due to expired calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615443&prj=626&rqi=e2QpWuWlqXZD1eVtOj9EO7ZtPo
YT1ELEC-3-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Some of test not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615442&prj=626&rqi=JO20YtoB2ml3wR91qfY7rBwt4s
YT1ELEC-2-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Some of test not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615439&prj=626&rqi=XfKhe2Lpv7GyfPzYRRYVQ2AXeh
YT1ELEC-2-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Invalid Testing Tools due to expired calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615441&prj=626&rqi=l7yJQWAupQnhwtUaxD8NL0HbwL
RT1ELEC-125-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Neutral termination bolts found loose, please tighten | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615207&prj=626&rqi=qfcJabgHEqSmMDyMKicihwF0Yx
RT1ELEC-32-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | Dust & debris found inside the panel, cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615241&prj=626&rqi=RmqSPZzpTvzDr5HRGeUGfAosoD
RT1ELEC-125-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Add temporary cover to prevent construction damage, dust, and debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615211&prj=626&rqi=teWLSuhIizOcs5AJ9DsK5vvr5v
RT1ELEC-125-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Dust and debris found inside panel, cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615213&prj=626&rqi=SYp8EbhSdygyOIq3pSeIqdVyVt
RT1ELEC-125-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Equipment positioning not aligned with the latest approved shop drawing (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615204&prj=626&rqi=vOycapGzTdCMwLCnpLGWfe43pC
RT1ELEC-31-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Anchor bolts must have at least 3 threads | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615236&prj=626&rqi=GHzcZnrEGWJUjCgTbsMxggrNPG
RT1ELEC-31-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Unused anchor holes found, please seal/cover all unused holes | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615237&prj=626&rqi=PORm1DbY3JcDcQnrf5GsMkANKt
RT1ELEC-126-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Neutral termination bolts found loose, please tighten | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615217&prj=626&rqi=Krnd6s7H8cxRMluoUlQuDMKGCs
RT1ELEC-126-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Please upload material approval/specs documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615215&prj=626&rqi=cq1fpR9xsov5HhMZFZwUcGEme2
RT1ELEC-32-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | GC to upload latest approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615238&prj=626&rqi=ef1vhXGPizYgzm3KEfccYOKqEH
RT1ELEC-32-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | Anchor bolts found loose during torque check. Please check all anchor bolts, re-torque, and apply torque marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615240&prj=626&rqi=NzKx2iHcyjBqLVz8LeRvH7OHTv
RT1ELEC-125-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Please rectify cable tube installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615210&prj=626&rqi=0rXRSg0kJOLN3lyIjQKPZFHJ13
RT1ELEC-32-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | Installation checklist from Vendor completed (signed off) not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615242&prj=626&rqi=0oo28vsT6uhhd413rFZU7mD9YW
RT1ELEC-31-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | GC to upload latest approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615225&prj=626&rqi=GuOX0YUReoO2KwiPy0vP61fHQV
RT1ELEC-126-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615221&prj=626&rqi=H7Q9iAMKWlzvduReaXQQN5XgBm
RT1ELEC-31-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Dust & debris found inside the panel, cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615235&prj=626&rqi=Fu4L1Q5XylpXDyNV8DJTwbPePp
RT1ELEC-125-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Confirm cable gland hole quantity and size as per approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615208&prj=626&rqi=SpbEOGeKM66KplmYD6PVKvx2Xw
RT1ELEC-126-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Gland plate bolts not properly tightened | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615220&prj=626&rqi=ctIvvPW61SOz4KiUUG8zeGx4Cm
RT1ELEC-31-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Anchor bolts still loose during torque check. Please check all anchor bolts, re-torque, and apply torque marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615234&prj=626&rqi=LD6EVPWRk4hiaknKj1WoYJmNdf
RT1ELEC-31-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Equipment labelling/tagging still temporary. Permanent labels/tags shall be installed as per the approved labelling scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615233&prj=626&rqi=wWcHvktcprntZi76q9K6xMeFbj
RT1ELEC-126-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Factory Test Data/ Factory QA/QC document not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615214&prj=626&rqi=eXm4azeAic0eNT6Gc3w0la88kK
RT1ELEC-125-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Provide protection for power meter | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615212&prj=626&rqi=8bjw9R2h4ycPNmuu8KRj1LFB9F
RT1ELEC-125-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Factory Test Data/ Factory QA/QC document not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615201&prj=626&rqi=2KS9q1OHgncqSet03ZPruldg4V
RT1ELEC-32-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | Equipment labelling/tagging still temporary. Permanent labels/tags shall be installed as per the approved labelling scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615239&prj=626&rqi=z1y53tCUcQEWMPfcj97yO74mR2
RT1ELEC-31-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Equipment positioning not aligned with the latest approved shop drawing (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615232&prj=626&rqi=AB8JD8guGIxXM3hpEVu1RnpUq4
RT1ELEC-126-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Dust and debris found inside panel, cleaning required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615219&prj=626&rqi=dCL7b0ttIsOxdctMOfFr3siqlk
RT1ELEC-125-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Acrylic bolt missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615209&prj=626&rqi=Xh37nxlfFbGgWdDJF6BP9TAlu5
RT1ELEC-126-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Confirm cable gland hole quantity and size as per approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615218&prj=626&rqi=Wv9e3mA2U0B8kCXZQ5b8T83pkw
RT1ELEC-126-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Equipment positioning not aligned with the latest approved shop drawing (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615216&prj=626&rqi=CUWZSnsjhSr7KkQBeJXBPCrCFr
GI-010 | JK01-2 | APAC | Closed | P2 Medium DCOS | dickyhermawan@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Issues SFAT DCOS 24 February 2026 â€“ Day 2 as per the Issue List in the Attached Picture for the issues open. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615099&prj=626&rqi=ILxfrYFlliUMpeYaoeBCjB0stc
GI-009 | JK01-2 | APAC | Closed | P2 Medium DCOS | dickyhermawan@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Issues SFAT DCOS 23 February 2026 â€“ Day 1 as per the Issue List in the Attached Picture for the issues open. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615097&prj=626&rqi=SNFsQu4sPUtmG7tVtyMN0sFS6J
GI-011 | JK01-2 | APAC | Closed | P2 Medium DCOS | dickyhermawan@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Issues SFAT DCOS 25 February â€“ Day 3 as per the Issue List in the Attached Picture for remaining open issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615100&prj=626&rqi=XtIEvAuOy2KHCherBCMunvSNok
RT1ELEC-14-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A DCOS UTP Cable) - Cable installation on GEN_C still not completed (labelling & terminated) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615058&prj=626&rqi=Z2isEdtWZQHLdDjp3PhwfzNR0v
RT1ELEC-148-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_2 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MSB_B to UDP_B_2) Busduct installation is not level. Please refer to the waterpass photo and the elevation measurements differ at each point as shown in the photos | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615094&prj=626&rqi=w0TNEhYjrr4ReqEVMVVsBzTmXK
RT1ELEC-13-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A DCOS UTP Cable) - Cable installation on GEN_D still not completed (labelling & terminated) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615062&prj=626&rqi=fT0t1iCFaNdSCb4sfiWPMq6IU6
YT1ELEC-5-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Auxiliary supply not yet connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615437&prj=626&rqi=p9QavNFXjusK1iPPC32sN2f2uU
YT1ELEC-5-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Point-to-point verification for control/signal cable cannot be performed as the cable installation is not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615436&prj=626&rqi=PDswgIJEdRIHEI9jOdzQD2aUMG
YT1ELEC-5-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Simulated trip from thermal relay to VCB cannot be performed as the control cable installation is not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615435&prj=626&rqi=NCRVyGlMtUQdgMHbPc7xUulmXT
RT1ELEC-4-021 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Cable lug connections may not be properly torqued? Please verify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614759&prj=626&rqi=2sNWx16dgmt7AQ88upwbSmWGl0
RT1ELEC-4-020 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Busbar connection between batteries not be properly torqued? Please verify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614758&prj=626&rqi=Wn0kwIgBdq5uWfoLDMBhmKlepD
RT1ELEC-4-022 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Battery stopper still not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614760&prj=626&rqi=FFGkPmyE8t55om94fRoZlSy6Xs
RT1ELEC-9-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Remove binding wire from cable containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614755&prj=626&rqi=7i6SuDx3D1ua4AWzBKH3RA05ZF
RT1ELEC-4-024 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Discrepancy between drawing and actual equipment position, refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614762&prj=626&rqi=FPJ8s4DWvFw8TYdFXdkj3WNcEU
RT1ELEC-9-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Clean construction debris on cable containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614754&prj=626&rqi=rOQszDppjukKg1dfZI63N9RDKl
RT1ELEC-9-015 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Incomplete firestop at all wall openings/penetrations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614757&prj=626&rqi=Cfx7w6XSLck2IWEwY4zbmplcV5
RT1ELEC-10-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Incomplete firestopping at all wall openings/penetrations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614751&prj=626&rqi=6rQU5K9q9dzz8mPA3OiZ78R8PC
RT1ELEC-10-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Install bonding jumper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614752&prj=626&rqi=EOYAnvAyHOooibtL35UKoOXtTm
RT1ELEC-10-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Standardize all bonding jumper colors to silver | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614750&prj=626&rqi=LokHJrSdaOeLuqvkUaB3wkApYA
RT1ELEC-9-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Temporary labels shall be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614756&prj=626&rqi=HbDgDmL3UoUkjG9mzuUDHJX2BF
RT1ELEC-4-023 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Cable over-bending observed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614761&prj=626&rqi=XZRwmarphSrgajAVNs39X3x7Z7
RT1ELEC-19-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Please upload Discrimination/ Co-ordination Study documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614663&prj=626&rqi=5ISY1YM29tV4IgMtrqZ43Vuv0s
RT1ELEC-10-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | (Issue CxL2A â€“ MV Cable) Grounding braid is not properly installed (joint observed) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614691&prj=626&rqi=kNJSSc6TiixNVlq900XMexl2Y9
RT1ELEC-19-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Please ensure the HMI display & all ACBS is properly protected to prevent construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614667&prj=626&rqi=i06LAr5hU7WbXkMuS6CQtO0cVM
RT1ELEC-19-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Please upload on site (Internal) Torque connection sheet documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614662&prj=626&rqi=bZChm79GBndVbxdbnNi23J0BN9
RT1ELEC-19-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Based on the RFIT inspection document, there is a discrepancy between the drawing and the actual equipment positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614665&prj=626&rqi=KqJW8pBdjNtaZssInFtIdO4oxu
RT1ELEC-19-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Minor dents need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614668&prj=626&rqi=Tu4uDrz6t2lhGLa3CTChvLRTwj
RT1ELEC-19-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | There is a discrepancy between the panel drawing and the panel label. The drawing indicates â€œ1CHWSTR_F_05_CH_1â€, while the panel label shows â€œ800A TPN ISOLATOR FOR AIR COOLER CHILLER.â€ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614666&prj=626&rqi=2fgM2of17GAKq4WHf8JUsADqD8
RT1ELEC-19-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | GC to upload torque wrench calibration certificates for anchor bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614664&prj=626&rqi=tGdlDO59JabnFyH0q93z6nZawB
RT1MECH-17-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_F_74 | EF - Exhaust Fan |  |  | The equipment name tag shall be fabricated from the same material as the name tag used on the other equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614603&prj=626&rqi=cEoddpH41CceSQn20CCyvklIHY
RT1MECH-16-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | The equipment name tag shall be fabricated from the same material as the name tag used on the other equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614604&prj=626&rqi=qpQN7cBRFrHBwr1ywDSlboysp7
RT1MECH-18-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | Please provide approve shop drawing of the equipment and floor layout also | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483516&prj=626&rqi=tjry9NI6IurkBlbfl23Ik1vVAc
RT1MECH-19-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | The distance between the equipment and the wall does not comply with the approved shop drawing (120 & 390 in drawing, while actual distance is 305 & 665) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483525&prj=626&rqi=LuWxSiBtlGw1U4LBYZOuCfZdU9
RT1MECH-19-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | Please provide approved method statement for this equipment and also method statement for pressure testing/ vacuum testing (if applicable) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483527&prj=626&rqi=mskn2bQnUEFOMg0gC5vY2zEMXu
RT1MECH-18-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | Please provided approved method statement for this equipment and also method statement for pressure testing/ vacuum testing (if applicable) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483524&prj=626&rqi=ShrHLIdB9iMsz6Jt8jHcXbHkrE
RT1MECH-18-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | Visual inspection observes defect minor scratch on VRFOD body and nameplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483521&prj=626&rqi=RHKFlY1G4KqSSL7FfQ5b2P8ujE
RT1MECH-19-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | Please provide approve shop drawing of the equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483526&prj=626&rqi=vJWeZtyDslp0mt77R1LcnydbIS
RT1ELEC-9-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Please upload CxL2B MoS document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483411&prj=626&rqi=S42mqh2puiETRmITbvW9GxVPWr
RT1ELEC-9-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Temporary labels shall be replaced with permanent labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483416&prj=626&rqi=NVB1pgVymSLXsrQ66yUlV106Wn
RT1ELEC-9-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Please upload cable schedule documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483410&prj=626&rqi=rNbx0rotoj9fUrEVpKROwN6Y7D
RT1ELEC-9-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Dust and debris found inside the equipment. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483417&prj=626&rqi=vdoIxt7lxuQlM9S8ZyuX5Rci96
RT1ELEC-9-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Please upload Factory Test calibration certificates | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483408&prj=626&rqi=sdxESbJJnmHrqFL828FZKRNKmX
RT1ELEC-9-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Why is the nameplate tagged as â€œMLTX_Bâ€? Please clarify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483419&prj=626&rqi=64DXowxVHuzXmflc73bBU19kWy
RT1ELEC-9-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Tap changer opening is not covered. Please provide a proper cover for the opening to prevent dust ingress and accidental contact | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483413&prj=626&rqi=gTtBV3HDLoQujuWyL8cCZHZuAo
RT1ELEC-9-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Minor dents and scratches were observed on the transformer body and enclosure. Touch-up is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483412&prj=626&rqi=dleCwQDDFHlqu17EGS8Ii7zMpw
RT1MECH-55-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_C_09 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221120&prj=626&rqi=2D5cvdVbD2J1cuZKPtpcnlBStJ
RT1MECH-14-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_D_53 | EF - Exhaust Fan |  |  | The equipment nametag shall be made from the same material as the other equipment installed on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221139&prj=626&rqi=JdNtX2zZNm1177dfO2wKAvaA1y
RT1MECH-11-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_C_54 | EF - Exhaust Fan |  |  | The equipment nametag shall be made from the same material as the other equipment installed on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221137&prj=626&rqi=Mxjn9kS3pC1yDYyvCrj7488R8f
YT1MECH-31-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | During the penetrant test witness conducted on 13 February 2026, approximately 20% of the total number of weld seam were found to be not acceptable. Rectification works were carried out, followed by a re-test; however, the results were still not acceptable. Consequently, another re-test was conducted on 25 February 2026, and the results were found to be acceptable. All test results have also been verified by NDT Level II personnel, pak Wiwid Dwihartanto from KIK. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221132&prj=626&rqi=JtBLKipghghk3fEMl1CT2zwQZr
RT1MECH-55-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_C_09 | CA - Cool Array |  |  | Dust and debris were observed on the equipment and shall be properly cleaned. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221121&prj=626&rqi=LD1q1H3h98HIr3VUW4TcDuLNuQ
RT1MECH-13-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | The equipment nametag shall be made from the same material as the other equipment installed on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221138&prj=626&rqi=SLrhMXVOIAg8jZ8GMvE3JqCQEy
RT1MECH-10-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_C_53 | EF - Exhaust Fan |  |  | The equipment nametag shall be made from the same material as the other equipment installed on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221136&prj=626&rqi=n5hUg5O58EyfCqWuVrI8z7eX7u
RT1ELEC-149-009 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MSB_D to UDP_D_2) Busduct above 1UDP_D_2 is not level, adjustment is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212894&prj=626&rqi=aqjzZ7ndeqlE10Z9iZR5yXnvea
RT1ELEC-147-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_16 | CP - Control Panel |  |  | Some bolts are rusty and need to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199925&prj=626&rqi=1TvFtH1WsSweDD4StCodb5U6ci
RT1ELEC-147-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS | Controls | equipment | 1RPP_1_GW_16 | CP - Control Panel |  |  | Cable gland washer is not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199924&prj=626&rqi=bibCrKq8DOWkRer1F1tIPBkmia
RT1ELEC-149-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload approved latest shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212870&prj=626&rqi=2hSxBm1ULNB53iqHuc5r7sLdVD
RT1ELEC-149-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload equipment delivery note / material incoming inspection document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212878&prj=626&rqi=vdbBmkW99TU1QtbRkV8y1NEMJL
RT1ELEC-150-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_D to MSB_D) Provide temporary protection to prevent construction damage, dust, and debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212886&prj=626&rqi=o1OtuLiA3Qb2Ij7SkjEz9C15mp
RT1ELEC-150-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload O&M documents of busduct | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212874&prj=626&rqi=kKXvfYYhIGT5kFXQcPC07x4Mg5
RT1ELEC-149-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_D to MSB_D) Sleeve and firestop at wall penetration are not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212892&prj=626&rqi=apf0F3P0JfZ5NVlGc8LIliMS8S
RT1ELEC-149-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_C to MSB_C) Elevation discrepancy (refer attached photo): Drawing: 4200 mm AFFL, actual: 4351 mm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212889&prj=626&rqi=dovnavcSkvytXVv7IROtH502Uj
RT1ELEC-149-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload torque wrench calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212869&prj=626&rqi=FWd1USU9Et2vlPpB1Ql6DZdp7M
RT1ELEC-147-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_16 | CP - Control Panel |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199923&prj=626&rqi=QNaQyIg3EhXN978WyEykpI2rpg
RT1ELEC-150-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload equipment delivery note / material incoming inspection document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212876&prj=626&rqi=3AakkaStw4F3RpmzHNWyONl6J5
RT1ELEC-150-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload calibration certificate for torque wrench | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212872&prj=626&rqi=aN01EVxurLbFoT8y2SnkXsb1eJ
RT1ELEC-150-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_D to MSB_D) Busduct installation at Tx Room does not comply with the latest approved drawing. Drawing shows straight routing, actual installation differs (refer to attached photo). Please clarify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212885&prj=626&rqi=ZLYj0NrKRxm515tvaCcBbOBCcs
RT1DCOS-9-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | Based on panel drawing, power supply is tagged as â€œPS 1,â€ but the actual label inside the panel is â€œPS-A.â€ Please update accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212853&prj=626&rqi=YqIB9Bx7RKxaS0XRxYs289Y0od
RT1ELEC-149-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_D to MSB_D) Unistrut support is misaligned/not straight, rectify accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212893&prj=626&rqi=dO2JPrav3zRkB4UA2SrzfgRhIt
RT1DCOS-9-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | Inside panel is dusty and dirty, cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212855&prj=626&rqi=pL3G3tCr6DvpVae19iY4aKMMHU
RT1ELEC-144-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_13 | CP - Control Panel |  |  | Dust & debris found inside the panel, need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199927&prj=626&rqi=qKaDXEWe4ync0LQgsA65lraf56
RT1DCOS-9-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | Please upload factory test data documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212857&prj=626&rqi=1VShisGFRbZ2l6413Z0s8hlE1Y
RT1DCOS-9-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | Please upload MoS CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212852&prj=626&rqi=Jb9Gv7J8iyLiIO0pCJT2otmacs
RT1ELEC-144-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_13 | CP - Control Panel |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199926&prj=626&rqi=cWD2Kgl1lrURTYwL7Xyahx1JKT
RT1DCOS-9-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212854&prj=626&rqi=fxDOdSdNwuWWt8cwfNVAzeDGbR
RT1ELEC-149-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_D to MSB_D) Elevation discrepancy (refer attached photo): Drawing: 4500mm AFFL, actual: 4444mm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212891&prj=626&rqi=0pV3Dp9eVtrQwNNFIH8dvXpkCE
RT1ELEC-150-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload approved latest shop drawings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212873&prj=626&rqi=Hn9eaLBe9Ij85LxxerDeLiINCb
RT1ELEC-149-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload O&M documents of busduct | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212875&prj=626&rqi=Yh6wnmXprYZJKbvBTpXvIiWDbV
RT1ELEC-145-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_14 | CP - Control Panel |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199928&prj=626&rqi=Swf7oTjt0UHh5GmP4KkDHX3ZCX
RT1ELEC-145-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_14 | CP - Control Panel |  |  | Dust & debris found inside the panel, need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199930&prj=626&rqi=ERbvWcOybwnu4XfujT3dyKzjNk
RT1DCOS-10-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Please upload MoS CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212860&prj=626&rqi=2CAXTllaKQnIo6SO3prBbvolhf
RT1DCOS-10-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Based on the panel drawing, the power supply is tagged as â€œPS 1,â€ but the actual label inside the panel is â€œPS-A.â€ Please update accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212865&prj=626&rqi=uYTeW7sPvcD4sLvmc7ywYYki4x
RT1DCOS-10-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Please upload factory test data documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212859&prj=626&rqi=A7ouHqA0haXJ8xSLa6MPpGjsyi
RT1DCOS-10-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212864&prj=626&rqi=ihe6hlvvh71VV1rDbEydsn7jFE
RT1DCOS-10-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Minor dents on the panel body need to be touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212862&prj=626&rqi=ZneMdIwkdD4pcRznSLxyRf9jPv
RT1DCOS-10-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Please install temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212861&prj=626&rqi=2x6SqS5GYGagieywPHYwHy5TQb
RT1DCOS-10-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Anchor bolts have not been torqued and marked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212863&prj=626&rqi=aBVQjyZKmNGDGbvKhQKMnQdVPe
RT1ELEC-2-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue DCOS Cable UTP) - Please align the conduit to ensure it is straight and properly aligned (location RMU_D Lv5) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212866&prj=626&rqi=IPVQQ7bqyVEDBfxL6HLrAfblCq
RT1ELEC-146-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS | Controls | equipment | 1RPP_1_GW_15 | CP - Control Panel |  |  | Cable gland washer is not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199921&prj=626&rqi=r0nA47JlVndyQ3KCBllDkWrj48
RT1ELEC-146-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_15 | CP - Control Panel |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199920&prj=626&rqi=ckd9PdYDHlmvNC9mVCq7LGRUTU
RT1MECH-13-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | During the inspection of LCP panels D_52 and D_53, there were dirt and dust inside the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199763&prj=626&rqi=ZRvszdWKNFyfqovhC3NBzmKCkx
RT1MECH-13-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | During the inspection of LCP Panel D_52 & D_53, loose bolt was found inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199808&prj=626&rqi=CnQXwucL7SuoPqZwrT8ShPmOUD
RT1MECH-16-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | During the inspection of LCP panels F_73 and F_74, the bolts and nuts located at the upper left side of the panel failed the torque test, not even failed, the anchor bolt is keep moving when it get tighten. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199759&prj=626&rqi=le0HdpTPjbbk47aLIknSnKINDD
RT1MECH-13-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | During the inspection of LCP panels D_52 and D_53, the nut at the upper left side of the panel failed the torque test, the nut is keep moving when it get tighten. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199807&prj=626&rqi=DufbDC4CW6mqYPMBCcagHEclM2
RT1MECH-16-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | During the inspection of LCP panels F_73 and F_74, A cable lug was found disconnected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199760&prj=626&rqi=i9rdj4wT0irXZE3lozjk5SsXa1
RT1MECH-7-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_B_31 | EF - Exhaust Fan |  |  | During inpection of LCP Panel B_31 & B_32, loose bolt and disconnected cable lug was found inside the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199809&prj=626&rqi=LLXjXUHsKgeUzulq5xeUYi0i1d
RT1MECH-16-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | During the inspection of LCP panels F_73 and F_74, there were dirt, dust, and unused materials inside the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199762&prj=626&rqi=gcrnFzPlM7TtUbvUKOwMO8B8bB
YT1MECH-57-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-22 04:00:00.000 +0400 | General Contractor | L2B | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | During the hydrostatic test of the CHW pipe in the cool spine area at 10-11 Feb 26, a pressure drop of 0.6 bar was observed over a 24-hour period, exceeding the 0.5 bar acceptance criteria. Consequently, a re-hydrotest was conducted on the CHW pipe the next day, and the result for the second test is within the acceptance criteria. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199744&prj=626&rqi=3G0b8mdpzHkLbBeKvPHP6bpiU3
RT1ELEC-3-023 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) Cable skirt installation not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199696&prj=626&rqi=eMEHAEKCK37zqitnmgANzhLr2y
RT1MECH-29-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Findings of damage, scratches, and dents were observed at several locations on the equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199653&prj=626&rqi=yir6bRS4f4gYViGOtLrFNfUB4q
RT1ELEC-4-016 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) Sleeve and firestop at wall penetrations have not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199698&prj=626&rqi=b8vRyQFbumEGBvsdwBPdB0YkB9
RT1MECH-30-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Findings of scratches were observed at several locations on the equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199654&prj=626&rqi=tpZ07Y1r9s1lkwxcHyTgVsPJaY
RT1ELEC-4-018 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) MV cable grounding braid looks not properly installed, with too many joints observed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199700&prj=626&rqi=zq9zWf9EHO7cNc88rIYOPgHiko
RT1ELEC-3-022 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) Grounding braid has not been connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199695&prj=626&rqi=VafjGW3w7sihpIEWclQirJPhFQ
RT1ELEC-4-017 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) Bonding jumpers at several cable ladder joints have not been installed. Please re-check all cable ladder joint connections | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199699&prj=626&rqi=YKlmYS6BssnjwwhU4RDnxf58cf
RT1ELEC-4-019 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) Cable containment alignment is not straight as per approved drawing (at Level 6) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199701&prj=626&rqi=EnA2StROzBeEyVVhozskx5BGAk
RT1MECH-28-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-16 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199250&prj=626&rqi=T3W5SYZsFeY0m9aupjM1gqTcXG
RT1ELEC-33-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | Please upload battery cabinet (inc circuit breaker) Factory Data document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199196&prj=626&rqi=Y14BLKmC59jm7rfFJ9su9uqLXz
RT1ELEC-34-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_2 | LIBATT - UPS Battery |  |  | Please upload battery busbar join connection report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199204&prj=626&rqi=z4HhkY089BATfe6bkXC3bPgtLX
RT1ELEC-34-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_2 | LIBATT - UPS Battery |  |  | Please upload battery cabinet (inc circuit breaker) factory data document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199202&prj=626&rqi=e4DzwxGxSvsJsoKcVx4B5lqZGf
RT1ELEC-143-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_06 | CP - Control Panel |  |  | There is dust and debris inside the panel. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199211&prj=626&rqi=EZlwTQWo3Z0VgLRcmafAwshb3p
RT1ELEC-33-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | Please upload battery busbar join connection report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199198&prj=626&rqi=2c9qzZIXpIC0bS5yLpgPBAs7F1
RT1ELEC-142-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS | Controls | equipment | 1RPP_1_GW_05 | CP - Control Panel |  |  | All unused holes must be properly covered to keep the enclosure fully closed and protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199207&prj=626&rqi=4hRL9ty6TK1xvaEScAH5eZzoKp
RT1ELEC-143-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS | Controls | equipment | 1RPP_1_GW_06 | CP - Control Panel |  |  | All unused holes must be properly covered to keep the enclosure fully closed and protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199210&prj=626&rqi=zNyPUlgIMxtkwtqAOQhFOeW6de
RT1ELEC-33-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | Equipment labeling/tagging is still using temporary. Permanent labels/tags shall be installed in accordance with the approved labeling scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199200&prj=626&rqi=ofaPUUBvZO3jtBtF2yFIvOx2b4
RT1ELEC-34-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_2 | LIBATT - UPS Battery |  |  | Equipment labelling/tagging is still using temporary. Permanent labels/tags shall be installed in accordance with the approved labeling scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199205&prj=626&rqi=vuecjWeLisYkGEzNbOiJyQTNwu
RT1ELEC-142-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_05 | CP - Control Panel |  |  | There is dust and debris inside the panel. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199209&prj=626&rqi=DckefBmNanT01I1UejzWObeuV8
RT1ELEC-33-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | GC to upload the latest approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199197&prj=626&rqi=wJAM31Z7KyUfGBVyH7quSDGrkJ
RT1ELEC-34-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_2 | LIBATT - UPS Battery |  |  | GC to upload the latest approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199203&prj=626&rqi=eVjdm1dGf6zm2m7Ej6vcnzdvFl
RT1ELEC-4-015 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Relay protection unit is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198914&prj=626&rqi=v8cx62aYeNbsV2lYJ6NHHFlqzO
RT1ELEC-4-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Permanent equipment tagging/nameplate not yet install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198913&prj=626&rqi=ZaXr8yg0POL6Wcq3mHVmt8I7t0
RT1ELEC-4-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Gaps observed between cubicles, need to rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198907&prj=626&rqi=Nqy2wTfSXUn9Pk8lBOFOCDZy5H
RT1ELEC-4-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Verification of the circuit breaker serial number could not be carried out. The MCE vendor is required to provide clear photographs of the circuit breaker serial number for verification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198912&prj=626&rqi=0zV5k5tk3vLg1pRHt5MCbBuUPR
RT1ELEC-4-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Drawings are not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198911&prj=626&rqi=gESggAJQ0TQFi84s4BZYdowVfF
RT1ELEC-4-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Scratches on the door body, touch-up repair is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198908&prj=626&rqi=Lt4cTuxSdVmGsXpRdKBJmJG8W8
RT1ELEC-4-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please upload cable schedule documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198902&prj=626&rqi=6Q6izzgKE2Yb22PWPBLwvpIdTq
RT1ELEC-4-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Terminal blocks require sticker/labeling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198909&prj=626&rqi=xmw1OKpgzoPKHKie7zFbHPk2ia
RT1ELEC-57-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Equipment positioning does not comply with the latest approved drawing: - Right side to wall: drawing 1425 mm, actual 1440 mm - Rear side to wall: drawing 483 mm, actual 575 mm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198989&prj=626&rqi=NJju1Eat8UT0847OMzTdVXZmZn
RT1ELEC-4-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Panel is not level (tilted) refer to the attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198904&prj=626&rqi=zXxQUQl0Ll9mr40OPb2v0n1DCy
RT1ELEC-57-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Dust and dirt observed inside the panel, cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198996&prj=626&rqi=qj788OtTNJeIn2k6mxnKSYyBSa
RT1ELEC-4-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please upload HV cable design documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198903&prj=626&rqi=iZUc0LYvIXS2taCMwumNu0xF6h
RT1ELEC-57-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Please upload Installation and Start-up Manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198988&prj=626&rqi=ejgLlF51Upiqm0Cgr3T7PIK1zQ
RT1ELEC-57-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Need to install temporary cover to protect equipment from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198991&prj=626&rqi=F9x1bbUSQkY9X2A2nocCbb5QGq
RT1ELEC-4-011 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Anchor bolt torque could not be verified during inspection due to excessive bolt length, torque wrench head could not be applied | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198910&prj=626&rqi=XzmOGx5JbW8rRT6YMh3N5LiOKp
RT1ELEC-57-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Control cables appear not connected, please verify and confirm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198998&prj=626&rqi=Rta4LfkTGfFVzM1oXk3aWdJVEx
RT1ELEC-4-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Equipment is dusty and requires cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198906&prj=626&rqi=hYjAf85O3Ar5GzuO2Aye9s7ZVg
RT1ELEC-57-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Drawing not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198994&prj=626&rqi=qCzmQjq4MQCxNP2KP3OAIim1qA
RT1ELEC-57-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Busbar joint bolts have not been torqued & torque-marked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198997&prj=626&rqi=Th4f8GjEQGtGzcK6WBPE6rzUBq
RT1ELEC-57-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Please upload calibration certificates tools | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198984&prj=626&rqi=qbnQ2N84xN2004h2kJ3r4Quudv
RT1ELEC-57-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Minor dents, need touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198990&prj=626&rqi=mlMYJdWO7JFofDYtpFdSoPbtXV
RT1ELEC-10-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Cleaning is required, excessive dust observed on the transformer, and cable tie and plastic debris found inside the enclosure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198893&prj=626&rqi=7aMNlVvv1sDphGuMVyqmdPFuAd
RT1ELEC-10-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Some components have only one label on the mounting or body, and terminal labels are missing. Each component shall have two labels (on the mounting and on the component body). Terminal labeling is mandatory | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198886&prj=626&rqi=sq9eG4Uf5AsnW1dFfWNG40UFND
RT1ELEC-10-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Control cables appear not connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198891&prj=626&rqi=2v1NYk6KLMPplyM3kgkxgbCEqa
RT1ELEC-4-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please upload MV Discrimination Study | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198901&prj=626&rqi=PwIpxDYCRKV90DnN4Z8eO3eBPD
RT1MECH-31-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Visual inspection observes defect minor scratch on chiller body and nameplate unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198884&prj=626&rqi=WHF04TnL60EHAWIwyto2roB6nu
RT1ELEC-10-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Fan cables are not properly dressed. Poor cable arrangement may cause damage or disconnection during maintenance activities. Please tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198889&prj=626&rqi=EcruUKbLmbdzU0gGdhNmMBnmiR
RT1ELEC-4-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please upload Installation and Operation manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198900&prj=626&rqi=t8TZ99VRV1eOL6Nb70lnXIpfaj
RT1ELEC-10-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Bolts were found loose during torque check, clarify the required torque value and re-torque with proper torque marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198892&prj=626&rqi=HyXu3nY73SxVgihFAIhBnXWoEe
RT1ELEC-10-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Minor dents observed, touch-up repair is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198890&prj=626&rqi=4LsmfBhcaGtLI5xMk3D9T1XsWN
RT1ELEC-4-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please upload factory test protocol calibration certificates | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198899&prj=626&rqi=B1bCyNJRP922ei7cEQOmC3B0VS
RT1ELEC-10-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Please upload cable schedule documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198863&prj=626&rqi=LNhHy1Bpp7Cp1DzuHwxxLNiIXE
RT1ELEC-10-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Please upload cable schedule & L2B MoS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198894&prj=626&rqi=xaGi80zEc8eafX5sWdXComI7US
RT1ELEC-10-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Need to provide "danger" sticker/label on the transformer body | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198866&prj=626&rqi=DzZb567DVeGaP6DnfBhcK3YJcg
RT1MECH-52-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_C_05 | CA - Cool Array |  |  | The unit support is misaligned. Rectify the alignment and remove any unused bolts if not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198668&prj=626&rqi=Q6Hey2pzAhB5O4UsJi4u35Mdxz
YT1MECH-23-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_42 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198677&prj=626&rqi=RJpwCn5NpIUrCEpLWykPFPh139
YT1MECH-26-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198679&prj=626&rqi=SOzWGSxnu5j0m4xKDzgj8ETAbW
RT1ELEC-17-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Anchor bolts were found loose during testing, re-torque and apply torque marking to all anchor bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198623&prj=626&rqi=yyO2L4mAvka24F2tM6FOPTQnmp
YT1MECH-27-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198678&prj=626&rqi=i9vHI3ENmuhof0lBWDBK3UuoIg
RT1ELEC-17-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Equipment cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198625&prj=626&rqi=VzIckvED0GiWD6NCE1Jama2ckQ
RT1ELEC-17-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Remove marker pen markings on the busbar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198624&prj=626&rqi=CDbouWw8m1OiGL1p2cyAmIDzUB
YT1MECH-24-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_B_41 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198675&prj=626&rqi=t03WvjUZWO1iPM9riUfwkAZkqB
YT1MECH-22-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198674&prj=626&rqi=kS0nV25SaDAhXApIdMtwC5imyC
RT1ELEC-17-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Provide protection to the ACB to prevent construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198622&prj=626&rqi=qPDWhD7XS6Q4cvDkLXcCuHJxr8
RT1ELEC-17-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Minor dents on the panel body shall be repaired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198620&prj=626&rqi=Vfmqoc3ZM6xsXLoGqNpBHEEtgH
RT1ELEC-17-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Please upload on site (Internal) torque connection sheet document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198619&prj=626&rqi=PbWGDVGm3uIRlBeDa1A1dP3Hqh
RT1MECH-52-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CA_C_05 | CA - Cool Array |  |  | Please upload approved method statement for flushing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198667&prj=626&rqi=2L5WXfCJ6ZwwMDVkMi0kySUNjD
YT1MECH-25-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198680&prj=626&rqi=IoIEarsT6AHETEsjUhQ37qc1Xh
RT1ELEC-17-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Temporary labels shall be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198621&prj=626&rqi=C4QESLSngkmwUe1Azj1JnLW4KS
RT1MECH-114-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Fan cables shall be properly dressed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198331&prj=626&rqi=svpGVZp50it8mrkZ6aQTgKXRnS
RT1MECH-114-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Damaged insulation at the chilled water outlet shall be repaired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198335&prj=626&rqi=5MqmygReAGL5jjRPc1mHzQG7u0
RT1MECH-114-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Left-side access door cannot be fully opened due to obstruction by the STSSB panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198330&prj=626&rqi=QPqsk9f8COSIKLDSV1JYz8kGhs
RT1MECH-114-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Air openings are left open. Temporary covers shall be provided to prevent dust and foreign object ingress | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198326&prj=626&rqi=WYi5dpt7hrwuLxhsZ5fg9dwmG5
RT1MECH-114-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Internal equipment is dirty with excessive dust, cleaning is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198329&prj=626&rqi=JuMn5p8jgxXI7P6dXap6TPAKww
RT1MECH-114-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Body-to-baseframe connection bolts are missing and must be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198334&prj=626&rqi=3Ij6ISHo32s7021liLOBqjEE0U
RT1MECH-114-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Stains on the equipment body shall be cleaned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198327&prj=626&rqi=68gDXVQPwAknnNhynVERbXHey3
RT1MECH-29-001 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198298&prj=626&rqi=VnscJnd7s7P7o1KGhdLt2W3q2C
RT1ELEC-18-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Equipment positioning does not comply with the latest approved drawing (photo attached): - Left side to wall: drawing 1598 mm, actual 1629 mm - Rear to wall: drawing 244 mm, actual 235 mm - Front clearance to 1STSSB_D_2: drawing 1478 mm, actual 1580 mm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198309&prj=626&rqi=zfMbC8zENbXFbg1WyybvZ9n4N4
RT1ELEC-18-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Phase separator / barrier between phases is missing and must be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198314&prj=626&rqi=amex04ZLjKqFtG4I0aFcbulQus
RT1MECH-32-001 | JK01-2 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-02-03 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Buffer Tank _C Jacket insulation broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198295&prj=626&rqi=qBA8iMn5HLMfUPw5heGbS53wX4
RT1MECH-30-001 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198299&prj=626&rqi=oXETpaLfLxHmardUs9MsLevzfl
RT1MECH-134-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1LCP_FPUMP_A2 | FT - Fuel Tanks |  |  | The device tagging label inside panel is different from the approved drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198293&prj=626&rqi=YZ2gjyNP6IHwdvPvfCVEeRIBvL
RT1MECH-135-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Fuel | equipment | 1LCP_FPUMP_B2 | FT - Fuel Tanks |  |  | LCP_FPUMP_B2 Panel Installation not level | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198291&prj=626&rqi=iMWZFbx43JtL9u57ZtP0NIzlKY
RT1MECH-31-001 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198300&prj=626&rqi=h9IT9DwbkRjoykBGqoW0kcYzv3
RT1MECH-135-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1LCP_FPUMP_B2 | FT - Fuel Tanks |  |  | The device tagging label inside panel is different from the approved drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198292&prj=626&rqi=5ai8TEaafxXaVmOdxgTCJrvBuq
RT1ELEC-18-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Fuse labels shall be replaced with new labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198311&prj=626&rqi=ZmxUfq0DvgYvggAE7utFg9kmvD
RT1ELEC-18-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Temporary labels shall be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198310&prj=626&rqi=i4kSF9aIq6jUcsaxdRwt56LRVb
RT1MECH-28-001 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | paint broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198297&prj=626&rqi=UMSw9fUvGQb5HnX5RhsD5VAEil
RT1ELEC-18-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Equipment is dirty with dust and foreign materials. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198312&prj=626&rqi=x0F76PbHpmRiEeS06XLok78dQx
RT1ELEC-18-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Marker markings on the busbar shall be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198313&prj=626&rqi=uKNzGr3y6SaZQQqZ7Pq1y7Hmxx
RT1ELEC-2-013 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | BTU panel HMI display loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198175&prj=626&rqi=bNLaLx2iC43D2Dpx5uqSpuWCTu
RT1ELEC-3-018 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | 1BTU_C all battery connection not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198163&prj=626&rqi=dUEWBc8ahc2yBK0GcRqIeP3CFj
RT1ELEC-3-021 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Design correction needed | Design | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | BTU battery panel need to add battery stopper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198167&prj=626&rqi=ZcipA9xjLVYJzYlTavxPxxLQ45
RT1ELEC-18-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Please upload calibration certificates for factory test | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198126&prj=626&rqi=abMkR9zogQMasBx90MuoxeFDtu
YT1MECH-6-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-02 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | (Issue from CxL2A) - Please provide permanent equipment labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198171&prj=626&rqi=NFtJIB7QUknYdtbcRnjV8z9tvr
RT1ELEC-9-003 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | the door cannot be closed properly. scratches on the door frame | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198162&prj=626&rqi=aVJj6AT1lqV04n9Ni3bTFpdEC2
RT1ELEC-9-002 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Missing door hinge | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198161&prj=626&rqi=Kb6U9bZeyMyI9KnRHuAXaZLYXR
RT1ELEC-10-001 | JK01-2 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Maintenance doors facing wall, need to relocate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198159&prj=626&rqi=fZ7YlAJk8jKgzFS4wZAXVPC7Yx
RT1ELEC-9-001 | JK01-2 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Maintenance doors facing wall, need to relocate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198160&prj=626&rqi=tMDgYa0J8kX9n1bUZrhCjx2wX0
YT1ELEC-2-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue from CxL2A) - Permanent equipment labels were not installed. Equipment tagging with the correct language and approved colour scheme is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198170&prj=626&rqi=FkChjNcqr5AUzOgXxMZNehS1XS
RT1ELEC-2-012 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | BTU battery connection not complete. need add battery stopper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198174&prj=626&rqi=ARJW78tRIhS0JEkWxg0gPsxtcY
RT1ELEC-3-020 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Design correction needed | Design | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | BTU panels are at risk of water splashes from the louvers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198165&prj=626&rqi=3kIIqHMjSN1bdfxuyD3HofRHqx
RT1ELEC-3-019 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | BTU_C HMI display loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198164&prj=626&rqi=TWBZ547JnPL4DOjH01LmyeZn8U
RT1ELEC-2-011 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Design correction needed | Design | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | BTU panels are at risk of water splashes from the louvers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198173&prj=626&rqi=IrQK83XSymQHfe8hczohpqw9Eh
YT1ELEC-3-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue from CxL2A) - Permanent equipment labels/tagging have not been installed (Main Tagging Equipment) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198172&prj=626&rqi=LAXWfYP75HcMBrUObk3bL9CXGY
RT1ELEC-11-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Need to provide "danger" sticker/label on the transformer body. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198105&prj=626&rqi=ZtwSUJ79PKcYe9VBFeVjqNupLh
RT1ELEC-11-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Fan cables are not properly dressed. Poor cable arrangement may cause damage or disconnection during maintenance activities. Please tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198106&prj=626&rqi=RbWToeFGH5a2m6ZRl2zPlcOslg
RT1ELEC-11-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Need to be cleaning & touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198103&prj=626&rqi=Q9IATQqWNazai1PN6KzdLtiDkc
RT1ELEC-11-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Side access door installation MLTX enclosure (for maintenance access) differs with the approved drawing. GC/MCE shall clarify. Incorrect installation or missing access door will result in no proper maintenance access. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198101&prj=626&rqi=96RkGPVXwQWEJVUwmCeGqFUcAQ
GI-008 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | MLTX_F - Incorrect Enclosure Maintenance Door Direction | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198084&prj=626&rqi=gmX2ZiHF46I1A2Q9BzC83UNwuM
RT1ELEC-11-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Vibrations pads has not been torque-tightened and torque marking is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198102&prj=626&rqi=rjfZjlhaFkWIOYsatMTx9souST
RT1ELEC-11-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Please upload following document: 1. Approved factory test calibration certificates 2. CxL2B Method Statement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198086&prj=626&rqi=m4QGNSxBa9MKmPB4IuzLfo6sdG
RT1ELEC-11-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Scratches and dents are observed on the equipment. Touch-up work is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198107&prj=626&rqi=4X50cqgMMMuIb0VmO7kToA5fQc
RT1ELEC-11-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Please upload cable schedule documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198111&prj=626&rqi=wCeMm9zE3D7pz6RGNxhSdcpJPE
RT1ELEC-11-010 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Anchor bolt size does not comply with approved LS specification (required M12, installed M16) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198109&prj=626&rqi=C0LgpeYAzhym7RQg0qReRKOcE5
RT1ELEC-11-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Permanent equipment tagging is not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198108&prj=626&rqi=CYuJXh22XMHF2JP3YLnzUkZaAT
RT1ELEC-11-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Some components have only one label on the mounting or body, and terminal labels are missing. Each component shall have two labels (on the mounting and on the component body). Terminal labeling is mandatory | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198104&prj=626&rqi=EiVjYkYACLnKWGa83OrePJjfwW
RT1ELEC-3-017 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-28 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Sleeve and firestop at wall opening/penetration not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197874&prj=626&rqi=slLLU2YkeEJckGEY0mfwPwcEHM
YT1MECH-111-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_2.01 (Existing) | PAV - Pre-Action Valve |  |  | Seismic bracing not yet installed (drawing not yet approved) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197847&prj=626&rqi=pMsdbog0V1m1GGnBReczB0Tv1W
YT1MECH-111-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_2.01 (Existing) | PAV - Pre-Action Valve |  |  | At cool spine area level 2, sprinkler pipe BOP elevation differs from the latest approved drawing: 5300 mm (drawing) vs 5100 mm (actual) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197848&prj=626&rqi=EV4yqYuJTtbBTkev3CDbA7Euo1
RT1ELEC-3-016 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-28 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Bonding jumper on cable ladder not installed, please re-check all jointing cable ladder | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197869&prj=626&rqi=Kp0kZX0yv7iUMaFcGJNzoGWo7C
GI-004 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-01-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Design correction needed | Design | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | BTU panels are potentially exposed to water splashes from the louvers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197642&prj=626&rqi=DrU92Ft60e2ROeK7nmAFFbIArF
GI-003 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-01-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Battery cable termination not proper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197637&prj=626&rqi=l7RITrBiA7HKZaFgO1k0tcMFip
GI-005 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-01-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | BTU panel position is not the same as in shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197643&prj=626&rqi=kUXx3TlMS7of7Rrxf5eHgfAw0t
GI-002 | JK01-2 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-01-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | RMU_F MV2 missing PQM | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197636&prj=626&rqi=NTaV63swiq1YAGAQhHhb4Ljaxo
RT1MECH-118-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Equipment is dirty with dust and foreign objects. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197311&prj=626&rqi=CjEb07PySyFJwcWTSkwMevzrX4
RT1MECH-119-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | Please cut cable ties and tidy up the cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197317&prj=626&rqi=ShYv7s2fiKClKIBcB12t4fzkpB
RT1SEC-3-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Security | equipment | 1CCTV_level_4_General | CCTV - Closed Circuit Television |  |  | Why is the uploaded inspection report for CCTV Level 7? This checklist is for Level 4. Please replace it with the correct report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197299&prj=626&rqi=jNOvUGmao0KHqBf0REWr6TIGlT
RT1MECH-119-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | Equipment is dirty with dust and foreign objects. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197315&prj=626&rqi=5hK76FzJLEokrP7KpaTzydIF0N
RT1MECH-119-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | Equipment labels/tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197318&prj=626&rqi=4CzimxI93a10WyDSbzpBDKCBx3
RT1MECH-118-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Equipment labels/tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197309&prj=626&rqi=RzO5CG0a9DOQJeBNlkEmIUvQhQ
RT1SEC-3-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Security | equipment | 1CCTV_level_4_General | CCTV - Closed Circuit Television |  |  | Please upload calibration certificates | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197298&prj=626&rqi=EBStMxnOitiwGB5gLVjBJ8atXe
RT1SEC-4-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Security | equipment | 1CCTV_level_5_General | CCTV - Closed Circuit Television |  |  | Please upload calibration certificates | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197300&prj=626&rqi=It1sJk4QMEAFMWa4B3QSLHrIo3
RT1MECH-118-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Physical dents identified on the equipment body | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197304&prj=626&rqi=W2vCugSaEz0OPqEmACr1320NOa
RT1MECH-118-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Please cut and tidy up the cable ties | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197310&prj=626&rqi=LetqCI9Yq9UlGuCUhStxacXR22
RT1MECH-118-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Please install the proper covers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197307&prj=626&rqi=G3U6EWuXGKg90TLJSrlbVtYBVc
RT1MECH-118-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197301&prj=626&rqi=WOE7IOJC3RNjcxKGLIRLToQyBk
RT1MECH-119-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197314&prj=626&rqi=cZ2OeYIxmtW3e27HeIxv4O5MFH
RT1MECH-107-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Nameplate / equipment tag is not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197168&prj=626&rqi=5aZrsK9ho44QFYuo80J2Pppe6H
RT1MECH-111-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Please upload General Arrangement and schematics drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197173&prj=626&rqi=f6cXWxbeDH7p6f7ZxPkJoQN5X0
RT1MECH-106-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197151&prj=626&rqi=ErqSyzcWCWuwEcardCgkHaHGVR
RT1MECH-111-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Equipment position does not match the latest approved drawing. Rear: 290mm in drawing (actual 300 mm), side: 190 mm in drawing (actual 100 mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197180&prj=626&rqi=rrOUHu98aeUeoFmh1IgzX7bt1F
RT1MECH-107-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Please upload General Arrangement and schematics drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197164&prj=626&rqi=uNBa34F6IvGtLW5IzKsZPJPizk
RT1MECH-106-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Please upload General Arrangement and schematics drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197150&prj=626&rqi=CWnxxYC1uZn5LBP1ZglFXePaHQ
RT1MECH-111-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Equipment needs a temporary cover to protect it from dust and foreign objects | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197187&prj=626&rqi=7elLRycRfnm7cNFB8NmVEbHqgz
RT1MECH-106-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Control cables are messy and need to be properly arranged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197160&prj=626&rqi=wLh8od8Wi0UzZEhUy6nOTHQ37M
RT1MECH-106-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Equipment is very dirty with dust and foreign objects. Cleaning (FOD) is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197155&prj=626&rqi=e7pgtZixzBHF0ud8deGjrKv595
RT1MECH-107-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197165&prj=626&rqi=9EdURcjJj45a291tb3Z0JP4LF6
RT1MECH-111-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Anchor bolt markings are unclear and require re-marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197182&prj=626&rqi=npOB4n9ujIJqePG1zCrdMdsfQ6
RT1MECH-111-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Control cables are messy and need to be properly arranged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197184&prj=626&rqi=ps8MA3njt4BskiT7YulD9b9VDu
RT1MECH-107-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | FAT report serial number does not match the serial number of the installed unit (FAT Doc: 001156011000007928 / Installed: 001156011000007967) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197166&prj=626&rqi=yMpN1VcTaUaltSFhvZEdq42awi
RT1MECH-106-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | FAT report serial number does not match the serial number of the installed unit (FAT Doc: 001156011000007967 / Installed: 001156011000007928) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197147&prj=626&rqi=L5z6Qa8xEa6zcXfl8wP2nAqCmK
RT1MECH-106-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Internal chilled water outlet insulation is damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197159&prj=626&rqi=iFJBAv708YFfAlfpTOF3Y9T1ND
RT1MECH-106-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Chilled water inlet and outlet pipes are open and need to be covered to prevent foreign objects from entering | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197161&prj=626&rqi=sPosCHGAMogU5DpANPo3adgyUz
RT1MECH-107-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Equipment is very dirty with dust and foreign objects. Cleaning (FOD) is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197170&prj=626&rqi=QuSjBsxiuEdLez8zWRVVOiWw1A
RT1MECH-106-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Equipment needs a temporary cover to protect it from dust and foreign objects | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197162&prj=626&rqi=llMTh551ElhHTWFLWSiyAJfFCR
RT1MECH-107-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Cable arrangement is not neat and needs tidying up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197167&prj=626&rqi=3jPf46iyhLNuGTY6iiCVED1Sqb
RT1MECH-111-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Equipment is very dirty with dust and foreign objects. Cleaning (FOD) is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197181&prj=626&rqi=ZaRX1eGFU2LCDlvLH99Hgy5BRG
RT1MECH-107-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Internal chilled water outlet insulation is damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197169&prj=626&rqi=V5S749djUZOIAhiR2E1g845Ogk
RT1MECH-111-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Chilled water inlet and outlet pipes are open and need to be covered to prevent foreign objects from entering | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197183&prj=626&rqi=gk6mPx2HHje3cNwYF6UN3Ly0fu
RT1MECH-111-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Nameplate / equipment tag is not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197186&prj=626&rqi=VtxhWzULwurN8x2TetXNQw6jOl
RT1MECH-107-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Update the layout drawing for 1CRAH_C_22 based on the actual site condition. Ref JK1-2-M130-02-IFC-DWG - MECHANICAL EQUIPMENT PLAN L2 - FITOUT | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197171&prj=626&rqi=pbzIexZDU0snkOw28g2rD2HrXm
RT1MECH-111-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197174&prj=626&rqi=WczeQGHbsajspPaoU6lteXHT7j
RT1MECH-106-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | nameplate / equipment tag is not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197157&prj=626&rqi=fUAcymQ04LTjVigXNoCU8A2GId
RT1MECH-110-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Permanent equipment labels / tagging have not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196967&prj=626&rqi=XgRjdwek54sfzVtaKFUvgQYVcL
RT1MECH-110-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Air openings are still open and must be covered with a temporary protective cover to prevent dust and foreign objects from entering the equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196964&prj=626&rqi=pT2ztRtSOsukyEbTMCK6bJECIR
RT1MECH-110-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196962&prj=626&rqi=9WgPjwokimX64AQlltvlmAG2Yo
RT1MECH-110-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Connection loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197010&prj=626&rqi=rB8MyKcY0yhr0i7tr133BWTpEo
RT1MECH-110-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Significant dust and debris were found inside the equipment. Please perform FOD cleaning. Refer to the attached photos | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196966&prj=626&rqi=1lWNyavl5lWc3mkxyakrzZ6wgy
RT1MECH-110-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Disposable filter found damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196971&prj=626&rqi=JXODQ4XTz5IJndBQsMEljPV0F4
RT1MECH-110-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Dents / scratches were observed on the equipment body and doors during inspection. Please refer to the attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196965&prj=626&rqi=Shccx2EoaFHS0QrKaDjCtGzspb
GI-006 | JK01-2 | APAC | Closed | P2 Medium DCOS | dickyhermawan@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Issues SFAT DCOS 13 Jan 2026 â€“ Day 1 as per the Issue List in the Attached Picture. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197979&prj=626&rqi=ZxXSZoD9eGsrson1NsthmTM2tV
RT1MECH-110-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Equipment positioning does not comply with the latest approved drawing. The required clearance from the wall is 715 mm as per drawing (actual 820 mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196970&prj=626&rqi=Kn7rXf2tGGYJpynfyC8jXZyxk3
RT1MECH-110-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Please re-mark all anchor bolts and body-to-baseframe bolts, as the existing markings are not visible or have not been applied | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196968&prj=626&rqi=8lSJ98rVlpO8Hm8ExNtLjMPkZJ
RT1ELEC-16-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Defects, scratches, and dents were found on the panel body and door during visual inspection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196734&prj=626&rqi=6q8Zm5eQd8TP60MrRjJhmYtgJl
RT1ELEC-3-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Construction is incomplete. Cable termination has not been done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196727&prj=626&rqi=GNyDHcSRMQoDox1tsCM1XnHwot
RT1MECH-6-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | Number of spring mountings installed does not match the approved drawing (actual: 2, drawing: 4) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196766&prj=626&rqi=TDymMoXQqT8VtkphzsE0u1w7OB
RT1ELEC-16-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Loose cable found disconnected from the terminal | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196736&prj=626&rqi=Zht2PjiPfJ0lHABYEJudDbJfbB
RT1MECH-6-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | Please upload Approved Engineering Sequences of Operation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196756&prj=626&rqi=niakeJltfHQpJzEHJbe4jLJEik
RT1MECH-6-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | Please provide permanent equipment labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196757&prj=626&rqi=EwcHY6NBUzHx5JOLxWptcZ13JH
RT1MECH-6-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | Please upload Technical Submittals documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196755&prj=626&rqi=U6EQi275Fl23dmxo39OhFkL2jj
RT1ELEC-3-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | The earth switch has no status indication. Status indication needs to be provided, and an attention/similar label should be installed above the inspection window | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196729&prj=626&rqi=2YAMlGhnnSyJ8ptVOrxiB3s7Bn
RT1ELEC-16-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Several ACBs are not provided with protection, which may lead to scratches or damage during construction. Please provide proper protection for the ACBs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196738&prj=626&rqi=UDUkApk2AQmRlfsgExMzQRwhKN
RT1ELEC-16-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Please upload document related to inspection/checklist from Vendor completed (signed off) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196742&prj=626&rqi=fAyc0hsjnsY3eSlvG13q00uAEi
RT1ELEC-3-015 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Cable arrangement in the cable duct is too crowded, so it cannot fit the cables properly. Please tidy up and reorganize the cables | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196754&prj=626&rqi=qPShbycJvfOU4t0D3sdL66ruC6
RT1ELEC-3-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | No drawing pocket and latest approved drawings were not found inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196725&prj=626&rqi=4yTeq3Bh61OJhxBgw3rpzygMFe
RT1ELEC-3-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Verification of the circuit breaker serial number could not be carried out due to obstruction by MV cables under ongoing construction. The MCE vendor is required to provide clear photographs of the circuit breaker serial number for verification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196731&prj=626&rqi=WPDVeDigcLl8bLkMc9QVfNwd5K
RT1ELEC-16-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Please upload on-site torque wrench calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196741&prj=626&rqi=Cs9xaFLCT7nvfsEz6NOXHEbUSd
RT1ELEC-3-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Some components have only one label on the mounting/body, and the terminals are not labeled. Each component should have two labels (on the mounting and on the component body). Terminal labels are required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196728&prj=626&rqi=u9FpjjKjbuSJx2JJmYJl60snEl
RT1ELEC-16-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Several phase stickers/labels were observed missing or detached. Replacement is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196735&prj=626&rqi=ZwAJvpx11HIuoGNVYr4vZPOSDL
RT1ELEC-3-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Component/Equipment Failure | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Cable insulation is not properly covering | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196730&prj=626&rqi=tdA6q20ltFygLZVOryCaeKcHQd
RT1ELEC-3-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Permanent equipment labels/tagging have not been installed (Main Tagging Equipment) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196726&prj=626&rqi=mXaQuUa93Vrb3X3ZlxRQX9uWqP
RT1ELEC-3-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Please provide a temporary cover to avoid debris or foreign objects entering the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196732&prj=626&rqi=BkRNPDQoTqmJD8H5ORH0rIFA9l
RT1ELEC-16-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Cable marker/labels are faded and unreadable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196737&prj=626&rqi=nyfncSUZ74TYQecFpLphVny1N9
RT1ELEC-16-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Equipment found dusty and dirty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196739&prj=626&rqi=BAbX1AIG2BI8gY3ycOGmgAs82r
RT1ELEC-16-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Panel position does not match the latest approved drawing. Rear: 235mm in drawing (actual 250mm, side: 1450 mm in drawing vs (actual 1410 mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196733&prj=626&rqi=Tgtm9IS5aZFvndlrqn4clo9gYm
RT1ELEC-16-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Please upload on site (Internal) Torque connection sheet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196740&prj=626&rqi=Ta7h7ddHCKKtKlvJcJEbVKQl2i
RT1ELEC-3-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Please upload HV cable design documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196691&prj=626&rqi=2jJjRyA4Z7aMlVE7AJV2EVxxwS
RT1ELEC-3-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Panel position does not match the latest approved drawing. Rear: 100 mm in drawing (actual 115 mm, side: 100 mm in drawing (actual 210 mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196694&prj=626&rqi=CP86UqpEflXmdyjMx9dirAy9oz
RT1ELEC-3-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Please upload cable schedule documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196690&prj=626&rqi=OSSUjPoJDgXQ9RpNSEJBurFJiq
RT1ELEC-3-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Door has scratches caused by interference with the panel body | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196695&prj=626&rqi=IQwNETimNFNDxUIj5MaFkLyDmV
RT1ELEC-3-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Visual inspection found defects, scratches, and dents on the panel body/door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196697&prj=626&rqi=veDRn0kHd9Fnt426y9lSCaPsTB
RT1ELEC-3-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Panel is not properly leveled during installation, panel found not level (tilted) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196692&prj=626&rqi=XDWOUAlDKu2pUZghyq3m0UZovd
RT1MECH-25-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | FCU positioning does not comply with the latest approved drawings. For BOU, the drawing indicates 3500 mm (actual 3450 mm), and the wall-to-unit is specified as 450 mm (actual 550 mm). Alignment with the approved drawings is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196545&prj=626&rqi=boh8cZlWVtidCB2EWBzAwfTgaz
RT1MECH-46-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CA_D_06 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196548&prj=626&rqi=JWeJo4lQGixDUl0oDKQLbLmksU
RT1MECH-49-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CA_D_11 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196551&prj=626&rqi=aJXcxmjJRoOnvIWWGSZgKb4wWH
RT1MECH-43-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Torque verification of the unit anchor bolts at the corner positions could not be carried out due to limited access, as the torque wrench could not be properly applied. Confirmation of anchor bolt torque compliance with the specified criteria is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196539&prj=626&rqi=lE10EW9D4y6YiobbssgIfWeCR6
RT1MECH-47-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CA_D_07 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196549&prj=626&rqi=DslW1TmYF8DdN9q5VU5J0zkX9d
RT1MECH-44-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CA_D_03 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196546&prj=626&rqi=ApqbpU7ftrKN6qS6YbDMh1GxN0
RT1MECH-45-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CA_D_05 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196547&prj=626&rqi=AiT0eVIam6ulNFQow2r71CBZuF
RT1MECH-48-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CA_D_09 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196550&prj=626&rqi=R68ypf45XxQ5NZRIB9AqmZVSBu
RT1ELEC-2-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Please upload HV cable design is document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196448&prj=626&rqi=HsQj2MnjRqGZJUTEp9p3ikA7Tc
RT1MECH-25-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | equipment tagging not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196470&prj=626&rqi=cwpMkGPsGE7RgslppGB9mrTWsa
RT1MECH-116-003 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | Internal panel need to FoD and cleaning inside the CRAH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196452&prj=626&rqi=hSOZDxGNrhC5QGzRJcG4R3bonG
RT1MECH-116-002 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | Air opening not sealed yet to prevent debriss | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196451&prj=626&rqi=OEznbYs2m2QW3dEmzN64ELhYUf
RT1ELEC-2-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Permanent equipment labels were not installed. Equipment tagging with the correct language and approved colour scheme is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196473&prj=626&rqi=ANhbPpJBGwCYDE946tYjc9by6n
RT1MECH-45-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_05 | CA - Cool Array |  |  | Equipment tagging ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196428&prj=626&rqi=gE27ACURD7WReNAssAT5Z3nscS
RT1MECH-117-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_62 | CRAH - Computer room air handler |  |  | Equipment ID tagging not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196456&prj=626&rqi=zTMMJSNTSzEgzAjCYNlveeQbiL
RT1MECH-25-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | Missing document upload: - MoS - Material approval - QA QC report factory - Drawing installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196469&prj=626&rqi=hlRtqTnsE95XmO59dHLpAAw27u
RT1MECH-44-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_03 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196424&prj=626&rqi=CvPxGmI3zXzr0tvG2dmMV0L2FY
RT1MECH-43-003 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | bolt torque under 3 threats behind the nuts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196422&prj=626&rqi=xUv4MbqJM3MDZ64pbIoxfUbyHR
RT1MECH-26-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | Equipment tagging ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196466&prj=626&rqi=yGt2dJ5owB0EWn4ySokq6IClOi
RT1ELEC-2-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Surface scratches, stains, and paint marks were observed on the panel door and enclosure body. Rectification is required to meet project quality requirements | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196462&prj=626&rqi=fgH6KAnh2xwF4hSAOVXAKWpXLS
RT1MECH-43-004 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Sensor cable needs to tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196423&prj=626&rqi=LZ3fz23KPnOakETqO9C6OLHxrk
RT1MECH-45-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_05 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196427&prj=626&rqi=sQwTgdsGy3KJBlV8HXCzzhnA20
RT1ELEC-2-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Exposed copper conductor observed at control cable termination. Ferrule is missing or incorrectly crimped. Re-termination with correct ferrule required to ensure no bare copper is visible | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196476&prj=626&rqi=jDxOr06gagMNPq4KLt0EjKo7Gk
RT1MECH-49-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_11 | CA - Cool Array |  |  | Tagging equipment ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196438&prj=626&rqi=n4qsR0p9K9SVRjmEPH1rnhh8sP
RT1MECH-27-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | Equipment tagging ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196459&prj=626&rqi=3EtkxU0XKcCqh4GcnMbIaLbtRm
RT1ELEC-2-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | The switchgear tool board was not secured to the wall and was found placed on the floor. Proper installation and securing to the wall are required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196467&prj=626&rqi=pLIlRoNuXpB7u67xTVeOcdAu7Z
RT1ELEC-2-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Gland plates are not installed on the RMU panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196449&prj=626&rqi=OB2gR9LbHt9hOONLLovt6IBsbd
RT1MECH-47-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_07 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196432&prj=626&rqi=XktMW84uyzJJmQTbQl1vi7oy95
RT1MECH-47-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_07 | CA - Cool Array |  |  | Equipment tagging not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196433&prj=626&rqi=DRy4AGbOL3CMfrM13YpyKTICYK
RT1ELEC-2-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Latest GA and schematic drawings were not available within the panel. Drawings to be provided and installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196464&prj=626&rqi=5m3Ch0hh6cxffYcgK9y7wsTHQ9
RT1MECH-27-003 | JK01-2 | APAC | Closed | P1 High CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | Positioning FCU have discrepancy between drawing and the actual onsite. Please refer to drawing attached, GC need to provide the clarification. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196461&prj=626&rqi=iBxQ66iA4XARqM06WJ22Q2coaL
RT1MECH-44-003 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_03 | CA - Cool Array |  |  | Bolt torque under 3 threads under the nuts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196426&prj=626&rqi=VSxk8sFvJtsfAVeEKBsWq2fego
RT1MECH-26-003 | JK01-2 | APAC | Closed | P1 High CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | Positioning FCU have discrepancy between drawing and the actual onsite. Please refer to drawing attached, GC need to provide the clarification. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196468&prj=626&rqi=daInxGRqJKGqxgT5KAPmp8fwmu
RT1MECH-117-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_62 | CRAH - Computer room air handler |  |  | Air opening not sealed yet onsite to prevent debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196455&prj=626&rqi=xWfpvHnCcS2mEBtoJKwrHLuCIj
RT1ELEC-2-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Please attach CxL2B testing methode | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196447&prj=626&rqi=PLyxvqOm3oIhjAHNvJGYK83AuY
RT1MECH-48-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_09 | CA - Cool Array |  |  | Equipment tagging ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196435&prj=626&rqi=ecWxVK3lI5Ryi8IZLPPPqYiv0y
RT1MECH-46-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_06 | CA - Cool Array |  |  | Equipment ID tagging not yet installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196431&prj=626&rqi=492pYvKrHYMiXi9yhz9K7piHmB
RT1MECH-44-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_03 | CA - Cool Array |  |  | Equipment tagging ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196425&prj=626&rqi=Kb9wLEtPlqg3IFpZSV5hDQGcti
RT1ELEC-2-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | The equipment was found in a dirty condition. Please provide temporary cover to protect from debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196472&prj=626&rqi=EuhXqBx7UZXzudCxW3WCz4WbSb
RT1MECH-43-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Tagging ID equipment not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196421&prj=626&rqi=LZpphKvHFfjtMcDWsWjZo3zIfW
RT1MECH-48-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_09 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196434&prj=626&rqi=nPNPfllJ3WEu9IzTuyBfR7veFJ
RT1MECH-45-003 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_05 | CA - Cool Array |  |  | Cable sensors need to FoD, tidy up and suggest adding spiral cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196429&prj=626&rqi=V5WJhh2ZmHzVd36nMNvPdH5mYa
RT1MECH-116-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | Tagging equipment ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196450&prj=626&rqi=aKf3KezPJy1DbvtOVApS3e1Miv
RT1MECH-27-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | Missing document upload: - MoS - Material approval - QA QC report factory - Drawing installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196458&prj=626&rqi=aTcIZh0qJXCF8Lx4j2oyHStfhq
RT1ELEC-2-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Verification of the circuit breaker serial number could not be carried out due to obstruction by MV cables under ongoing construction. The MCE vendor is required to provide clear photographs of the circuit breaker serial number for verification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196475&prj=626&rqi=Qkaj4Gi6LQISyC4lpZA4MD6gVm
RT1MECH-26-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | Missing document upload: - MoS - Material approval - QA QC report factory - Drawing installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196465&prj=626&rqi=aWGZFv9rIvMEehnlPGLOMmm1hm
RT1MECH-43-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196420&prj=626&rqi=ht7DQGNG0HY6U9q3XquZXkNbFn
RT1MECH-46-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_06 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196430&prj=626&rqi=eQMrK4BOi4PTej4cdYqmNjAEPd
RT1MECH-117-003 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_62 | CRAH - Computer room air handler |  |  | Need to FoD and cleaning inside the CRAH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196457&prj=626&rqi=N6XEukzOl5JvNu2CqxAlqBmken
RT1MECH-49-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_11 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196437&prj=626&rqi=c2UVaDgK1wImoA5uXUGcL07CUn
RT1MECH-48-003 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_09 | CA - Cool Array |  |  | Installation for 1CA_D_09 is not level. Please refer photo attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196436&prj=626&rqi=YJ0mLhOmt6YA04QXIQWtwtcGBB
RT1MECH-60-002 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196335&prj=626&rqi=vHcV8rgWxtwpck2cDHrxGtmrA5
RT1MECH-57-002 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196332&prj=626&rqi=o9LFespFtDIBziQmnJntAnE4oe
RT1MECH-62-002 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196337&prj=626&rqi=zgSCusWGVezUpV4AzODi2Aph24
RT1MECH-58-002 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196333&prj=626&rqi=2nigKx3CfGLxjcHmRlOnaQB5UD
RT1MECH-61-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196329&prj=626&rqi=6E54WhuimEAGF6tW7O2JFpdHdm
RT1MECH-59-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196327&prj=626&rqi=ymYX9oxpVWaxsawR2suBQOYeSU
RT1MECH-59-002 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196334&prj=626&rqi=VqErXL4DGw6yoVO4xdaif3x2XM
RT1MECH-57-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196325&prj=626&rqi=MiKNPAYX5Lm5M5O0ZuOmNZx4If
RT1MECH-58-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196326&prj=626&rqi=RwxRz3rTitPLNqjOB0OlXrGuJX
RT1MECH-62-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196330&prj=626&rqi=6CTGhgErPunHAXRYXCySUFsD5O
RT1MECH-60-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196328&prj=626&rqi=XvyIny9ucnXVzhjsqxthicDm62
RT1MECH-61-002 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196336&prj=626&rqi=iApnf83ZMvsIRVoPbixQwspSEi
RT1MECH-63-002 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_11 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196338&prj=626&rqi=caynsdTK2ynSyrkmr4KapvEtqq
RT1MECH-63-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_11 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196331&prj=626&rqi=cTgw0JZUrP5ovBozxgHVBSngw6
RT1MECH-621-001 | KL02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | MCP-1EF-M1-09 | MCP - Mech Control Panel |  |  | MCP-1EF-M1-09 Labeling Incorrect | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631733&prj=647&rqi=Y1NkDXSGQ1WP0xd4rP4NO4QV85
RT1MECH-620-001 | KL02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | MCP-1EF-M1-08 | MCP - Mech Control Panel |  |  | MCP-1EF-M1-08 Labeling incorrect | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631732&prj=647&rqi=iBqfFkdSJFtHUHr7WGcSHlxoqv
RT1MECH-618-001 | KL02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-07-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_09 | EF - Exhaust Fan |  |  | 1EF_M1_09 The equipment tag does not attach as per approved naming convention | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627972&prj=647&rqi=abdp1izC2Tv9Nfm7Rv0BjJ1DuY
GI-044 | KL02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-07-05 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_08 | EF - Exhaust Fan |  |  | 1EF_M1_08 The equipment tag does not attach as per approved naming convention | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627973&prj=647&rqi=pYGPcLOyTq6Y5wAgM7UaRR2MMh
GI-040 | KL02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | [FWT] Fuel PLC Bench - Fuel return valve open status should be to the lower fuel level Fbulk, but the return valve maintains to bulk tank 2; status remain until the following Fbulk detect high high level, following return valve faulty and fire mode; | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626840&prj=647&rqi=Qc8D7RCA4VMC5j5IonQ5QlkKhK
GI-038 | KL02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | [6 empty] | [FWT] Fuel PLC bench - No password protection & user selection for setpoint page and ATG setpoint modification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626838&prj=647&rqi=ZWbHSI6ICmqDf4epaauKmJdt4j
GI-041 | KL02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | [6 empty] | [FWT] Fuel PLC Bench - SOO mention the bulk tank 1 is lead signal is pump 2, lag signal is pump 2 and lead is pump 1; reversely bulk tank 2 is lead signal is pump 1, lag signal is pump 1 and lead is pump 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626841&prj=647&rqi=GPLHaYpphj70ERcDaxO6KLZ1hL
GI-039 | KL02-1/2 | APAC | Open | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Incomplete Connections | Commissioning | [6 empty] | [FWT] Fuel PLC Bench - Modulating valve trigger failed to close after failed to open trigger | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626839&prj=647&rqi=XT8Lr3Gx15AraEQInjQZbEJLhJ
RT1MECH-766-001 | KL02-1/2 | APAC | Open | P2 Medium CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning | Fuel | equipment | 1FP_A_LCP_1 | FCP - Fuel Control Panel |  |  | [FWT] Fuel PLC Bench -Setpoint of the voltage relay as default -Pump overload setting as default | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626654&prj=647&rqi=r7ARXZog3U7GgCOkeUaVwJV72J
GI-036 | KL02-1/2 | APAC | Open | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning | [6 empty] | [FWT] Fuel PLC Bench - To standardize the equipment labelling at the HMI page, with approval naming convention | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626655&prj=647&rqi=TyuEX3uBSniEwcZrUbukWeI8Op
RT1MECH-766-002 | KL02-1/2 | APAC | Open | P2 Medium CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not complete | Commissioning | Fuel | equipment | 1FP_A_LCP_1 | FCP - Fuel Control Panel |  |  | [FWT} Fuel PLC bench -Fiber optic media converter is not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626652&prj=647&rqi=qcw9XpBQDYteGGdmudaCp7bDLN
RT1MECH-772-001 | KL02-1/2 | APAC | Open | P2 Medium CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Incomplete Connections | Commissioning | Fuel | equipment | 1FP_HMI_1 | FCP - Fuel Control Panel |  |  | [FWT] Fuel PLC Bench - HMI setpoint is not sync between HMI 1 and HMI 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626656&prj=647&rqi=TxShh5uxrhh78ritmOjroMg9OM
GI-034 | KL02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | [6 empty] | [FWT] Fuel PLC bench -1FP_M1_2, 1FP_M1_3, 1FP_HMI_1 and 1FP_HMI_2 tagging is block by the outer door panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626653&prj=647&rqi=6q7pp1aDLUfWYFXm8z8BhZvg3i
GI-032 | KL02-1/2 | APAC | Open | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation not issued/ Required | Commissioning | [6 empty] | [FWT] Fuel PLC Bench -Terminal block quantity and tagging different with approval construction drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626648&prj=647&rqi=dnkOEIMrKMwhXrT3Hpr4lXDkUT
GI-028 | KL02-1/2 | APAC | Closed | P2 Medium CX | geoffreytan@commtechasia.com | 2026-05-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1LBSB_1 | LBSB - Loadbank Switchboard |  |  | [FWT] Bolt connections, bolt threads come out less than 3 threads above the nuts. To comply with Equinix Commissioning Playbook 6. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623425&prj=647&rqi=MUKundQmNLoib62jM6sGmw7mYb
GI-029 | KL02-1/2 | APAC | Open | P3 Low CX | geoffreytan@commtechasia.com | 2026-05-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | [FWT] 1RPP_XX_01_XX 1. Name label of equipment missing 2. Spare Breaker label missing 3. MCMS Card label, too add identifier labels to the MCMS cards | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623428&prj=647&rqi=VQCOrK5MVxWYwsmGERFpTHvoOA
GI-030 | KL02-1/2 | APAC | Open | P3 Low CX | geoffreytan@commtechasia.com | 2026-05-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | [FWT] 1RPP_XX_01_XX - Update the wiring drawing of the MCMS module, to indicate network cable position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623429&prj=647&rqi=w3ttWPRELZm46Iwn5lx92PHH3T
GI-011 | KL02-1/2 | APAC | Open | P3 Low CX | geoffreytan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning | [6 empty] | (FWT) VSD Panel incoming breaker setting for LSIG to be provided by JCI. Equipment S/N: 50612A68708365 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616932&prj=647&rqi=bulpeeFxbJTy8nfLtWKd3DZZnz
GI-009 | KL02-1/2 | APAC | Open | P3 Low CX | geoffreytan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | (FWT) To install missing labelling for cables within control panel. Equipment S/N: 50612A68708365 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616930&prj=647&rqi=PgyIwGakJtk8O2xUO0EV9JyPtC
GI-010 | KL02-1/2 | APAC | Closed | P3 Low CX | geoffreytan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Cleaning | Commissioning | [6 empty] | (FWT) Surface Rust to be cleaned off Equipment S/N: 50612A68708365 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616931&prj=647&rqi=c1CfHBWvUR23RAIif6erNLIC0c
GI-007 | KL02-1/2 | APAC | Open | P3 Low CX | geoffreytan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | (FWT) To install cover for emergency-stop button at chiller control panel. Equipment S/N: 50612A68708365 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616927&prj=647&rqi=8P0IJleUFmKLyzdTFa1hSB04Gc
GI-008 | KL02-1/2 | APAC | Closed | P3 Low CX | geoffreytan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | (FWT) Chiller tagging nameplate to be installed. Equipment S/N: 50612A68708365 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616929&prj=647&rqi=TpoxKYz2aBlBmKm1HPSR2PB12d
GI-006 | KL02-1/2 | APAC | Open | P3 Low CX | fazandrayusfiandika@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS | [6 empty] | (FWT) DCOS test was conducted based on the pending signed off SICD by the DCOS SI. Observed changes and additions to DCOS point mapping as follows: - Output Breaker 1 Status (CB3A): Modbus address changed from 607 â†’ 609. - Output Breaker 1 Status (CB3B): Point to be removed. - Equipment Over Temperature Warning: To be added (address range 686â€“702). - SCR 1 Shorted: To be added (address range 839â€“847). - SCR 2 Shorted: To be added (address range 873â€“881). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197981&prj=647&rqi=ro9rCucigqvbiHJZIlCF6zZmiv
GT1MECH-11-001 | LD06 | N-EMEA | Open | P3 Low CX | andrew.sharp@implexcritical.com | 2026-08-06 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | TCS/SFN - 01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | Confirm (if applicable) any EoR/EQX approved as-built drawings have been uploaded to Equinix document control platform. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632614&prj=675&rqi=FdePtVd24h9KXl8pfbGgby1c6F
YT1MECH-6-001 | LD06 | N-EMEA | Ready for Verification | P3 Low CX | andrew.sharp@implexcritical.com | 2026-08-06 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | TCS/SFN - 01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | Confirm TSC/SFN pipework has been flushed in accordance with the Equinix TCS/SFN Cleaning and Flushing Requirements and all documentation including test equipment calibration certificates are uploaded, reviewed and CxA approved on the Equinix document platform | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632577&prj=675&rqi=gWV1y4tOBu50k64D2TRAulJBN2
RT1MECH-6-002 | LD06 | N-EMEA | Closed | P3 Low CX | andrew.sharp@implexcritical.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | TCS/SFN - 01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | It is recommended that protective caps/covers are fitted to the stems of the PICVs to protect against any potential damage. This comment is applicable to all the TCS/SFN PICVs and the Primary CHW PICVs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628520&prj=675&rqi=D22dGnQKTvktJZYNgYM2fmFocg
RT1MECH-6-001 | LD06 | N-EMEA | Closed | P3 Low CX | andrew.sharp@implexcritical.com | 2026-06-18 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | TCS/SFN - 01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | Confirm the EoR/EQX approved DCOS points list has been uploaded to Equinix document control platform. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626206&prj=675&rqi=TSSkqu7sVNABfNMFZIuYRk6Ggg
GI-017 | LD07.2-P1 | N-EMEA | Closed | P1 High CX | eosman@global-cxm.com | 2026-04-29 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | [6 empty] | UPS-13 Module 4 keeps dropping load during 4 hour heat run. Testing cancelled. Schneider and Socomec investigating | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620004&prj=617&rqi=7zqbtQySkwX1jzIZWdq0FRQqwx
GI-015 | LD07.2-P1 | N-EMEA | Closed | P3 Low CX | eosman@global-cxm.com | 2026-04-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning | [6 empty] | LV-13 Micrologic Damaged to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618350&prj=617&rqi=u0AqDfwYHkTJn3pS6bdSNxt7ek
GI-014 | LD07.2-P1 | N-EMEA | Closed | P3 Low CX | eosman@global-cxm.com | 2026-03-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning | [6 empty] | PPR's for LD7.2 P2 - Armstrong FAT not including DCOS works carried out due to limitations of equipment being available. To be captured as on site witnessing when available | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616257&prj=617&rqi=4PwQIvm7IbkECzcoHvwfexIzyo
GI-012 | LD07.2-P1 | N-EMEA | Closed | P2 Medium CX | eosman@global-cxm.com | 2026-02-19 04:00:00.000 +0400 | Equinix Commissioning Manager |  | Component/Equipment Failure | Commissioning | [6 empty] | PT100 Sensor on TX-16-D Failed, 6x Replacements have been ordered, Request to replace all PT100 as a preventative measure from Equinix | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199662&prj=617&rqi=c1KMQSjYlIj70x81g1YdLNFyso
RT1ELEC-1-001 | LD07.2-P2 | N-EMEA | Open | P3 Low CX | eosman@global-cxm.com | 2026-08-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Incomplete Connections | Commissioning | Electrical â€“ MV | equipment | GEN-8-01 | GENM - Generator |  |  | LV/ELC Cable entrance box has been left detached and inside the unit to allow steel works to be erected with out hindrance (LOR) to fix in place when they complete their steel gantries. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633013&prj=687&rqi=o0NF5FqZp5sACwTndQBZdkyH0b
GI-004 | LD07.2-P2 | N-EMEA | Closed | P3 Low CX | jhancill@global-cxm.com | 2026-07-28 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning | [6 empty] | All chillers waiting on shrouding to be installed in front of L1-L3 cables inside panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631146&prj=687&rqi=yAirJd7U1xGvkQQPNE5Cfr8vFl
GI-003 | LD07.2-P2 | N-EMEA | Open | P3 Low CX | jhancill@global-cxm.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning |  | equipment type |  |  |  |  | All new AACC's missing asset ID's | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624337&prj=687&rqi=7fEOvl206lSV6bee9qQKCNblWK
GI-002 | LD07.2-P2 | N-EMEA | Closed | P3 Low CX | eosman@global-cxm.com | 2026-05-28 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning | [6 empty] | PPR's for LD7.2 P2 - Armstrong FAT not including DCOS works carried out due to limitations of equipment being available. To be captured as on site witnessing when available | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623352&prj=687&rqi=WMGOUPtOx7EfyJxko0e8xky4LD
GI-148 | LD09-P2 | N-EMEA | Closed | P3 Low DCOS | Alen.Francis@eu.equinix.com | 2026-01-29 04:00:00.000 +0400 | Facility Manager |  | DCOS General Issue | DCOS | [6 empty] | GDC Item outstanding in DCIM LD9.PG2.RMU_M_RMU_L2_BSM: measure_active_power SUDB-2 Utility Incomer Power factor GSB3 Gen Incomer Frequency GSB4 Gen Incomer Frequency GSB5 Gen Incomer Active Power GSB5 Gen Incomer Frequency GSB6 Gen Incomer Frequency Issue: These Points cannot be proven at the moment as there is no load on the MV equipment. Can this be proven once load is availble | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197885&prj=308&rqi=7DZ9Jf5lVBwJ1LNIZnKo3wPL27
GI-149 | LD09-P2 | N-EMEA | Closed | P2 Medium DCOS | Alen.Francis@eu.equinix.com | 2026-01-29 04:00:00.000 +0400 | Facility Manager |  | DCOS Comms Issue/ Fault | Commissioning | [6 empty] | GDC Requires the folowing Items to be clear of Alarms so they are Resilient. These Items are customer impacting. LD9.PG2_CRAC_12A_01 LD9.PG2_CRAC_12A_02 LD9.PG2_CRAC_12B_01 LD9.PG2_CRAC_12B_02 LD9.PG2_CRAC_12C_01 LD9.PG2_CRAC_12C_02 LD9.PG2_CRAC_12D_01 LD9.PG2_CRAC_12D_02 LD9.PG2_CS_2_3 LD9.PG2_CTA_2_3 LD9.PG2_CTB_2_3 LD9.PG2_UPA_12M | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197891&prj=308&rqi=hoIHz9h5KjIfvxuhJYpcijcqug
YT1ELEC-677-001 | LD14-1 | N-EMEA | Open | P3 Low CX | jknight@global-cxm.com | 2026-09-01 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1HEAT_R1_411 | AH - Air Heater |  |  | Earth on heater frame comes off TX earth bar. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636284&prj=646&rqi=KKYgaWW5z9RK5galQEouXPyx5X
GI-069 | LD14-1 | N-EMEA | Closed | P2 Medium CX | jknight@global-cxm.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1EB_PUR1_1 | ERTH - Earthing |  |  | Single link earth bar fitted. Earth bar does not match drawing or spec and main earths are doubled up on one stud. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635550&prj=646&rqi=NVyPIITe8tuBgoq1cDPu8SgvvQ
GI-068 | LD14-1 | N-EMEA | Open | P3 Low CX | jknight@global-cxm.com | 2026-08-19 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1EBPPR-M1_8 | ERTH - Earthing |  |  | Two studs on the earth bar have snapped off inside the nut. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634375&prj=646&rqi=as2pFp7CVGT0qr8xNFTGrN5KAz
RT1FD-104-001 | LD14-1 | N-EMEA | Open | P3 Low CX | abadat@global-cxm.com | 2026-08-06 04:00:00.000 +0400 | VER - Vertiv | L2A | Labelling | Commissioning | Fire Detection | equipment | LD14_FAP_06_01 | FP - Fire Panel |  |  | No identifying label attached. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632710&prj=646&rqi=ieBNTvz9lecMrjzy9SL6w6IUOx
RT1FD-104-002 | LD14-1 | N-EMEA | Open | P3 Low CX | abadat@global-cxm.com | 2026-08-06 04:00:00.000 +0400 | VER - Vertiv | L2A | Installation not correct | Commissioning | Fire Detection | equipment | LD14_FAP_06_01 | FP - Fire Panel |  |  | The FAP door cannot be opened and closed properly. The interfaces below are installed too close to the FAP. There should be a spacer in between the interfaces and the FAP in order to allow the door to open/close as intended. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632711&prj=646&rqi=IXli30iKDrVbVXHaVPfrSl6BYU
YT1ELEC-718-001 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-07-16 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1EBLV_M1 | ERTH - Earthing |  |  | Cable References to be Confirmed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629822&prj=646&rqi=geQ3N6thEU4HzEJTpaSyIxE7Aa
GI-053 | LD14-1 | N-EMEA | Open | P3 Low CX | jknight@global-cxm.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | Electrical â€“ MV | equipment | 1MVTB_R1_HMI | HMI - HMI Panel |  |  | Cable ID missing from earth. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628602&prj=646&rqi=DtmYC8J79f4QQSBKJFNIJcMT6f
RT1ELEC-731-001 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-07-02 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1EBPPR-M1_8 | ERTH - Earthing |  |  | asset ID not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627716&prj=646&rqi=NkUhOKorDMTNCtm4mLZXkb0HSl
RT1ELEC-730-001 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-07-02 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1EBPPR-M1_7 | ERTH - Earthing |  |  | asset ID not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627715&prj=646&rqi=SiFsf3d3IQ8WNaaXDECbqo95VQ
RT1ELEC-729-001 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-07-02 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1EBPPR-M1_6 | ERTH - Earthing |  |  | asset ID not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627710&prj=646&rqi=nVM4gIa8M8KhyEwx8Bal92XIX6
RT1ELEC-682-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-07-01 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1HEAT_R1_411 | AH - Air Heater |  |  | Permanent labels not attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627575&prj=646&rqi=yXj2yApKZ0anJUD1jeEgJZGXFJ
GI-040 | LD14-1 | N-EMEA | Closed | P2 Medium CX | ganderson@global-cxm.com | 2026-06-17 04:00:00.000 +0400 | General Contractor |  | Installation Damage | Commissioning | [6 empty] | Critical MeWall - UPS Switch Room M1 - water ingress took place in switch room M1 due to the removal of the Roxtec blocks. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625666&prj=646&rqi=b48S9Q1X93RrtWy2yTQ4paRp9P
RT1MECH-688-001 | LD14-1 | N-EMEA | Open | P3 Low CX | gharbottle@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1WT_M1R1_FLT_04 | WT - Water treatment |  |  | Missing permanent asset label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624836&prj=646&rqi=Qxm34KAu5zsU91t6SY5oDIPZxT
RT1MECH-687-001 | LD14-1 | N-EMEA | Open | P3 Low CX | gharbottle@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1WT_M1R1_FLT_03 | WT - Water treatment |  |  | Missing permanent asset label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624835&prj=646&rqi=wnCKIYgQeiAei4n5nphwuHdjK5
GI-032 | LD14-1 | N-EMEA | Open | P3 Low CX | jknight@global-cxm.com | 2026-05-14 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MEB_A | ERTH - Earthing |  |  | Asset labels missing for earth bar. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621958&prj=646&rqi=dhxbBe7RwNRlw06zXbnkO8b4MG
RT1MECH-593-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-05-04 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_410 | DXID - FCU/DX Indoor Unit |  | FXHQ100AVEB8 | No asset identification label present on installed FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620374&prj=646&rqi=YQAozuRde4zQJU59JErzPhtn8F
RT1MECH-586-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-05-04 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_312 | DXID - FCU/DX Indoor Unit |  | FXHQ100AVEB8 | No asset identification label present on installed FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620375&prj=646&rqi=qbQb478eBROuWQ4PXa68HfYvaD
RT1ELEC-75-002 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-04-30 04:00:00.000 +0400 | SCH - Schneider Electric | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1MVTB_R1_HMI | HMI - HMI Panel |  |  | Two identification labels missing within HMI panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620113&prj=646&rqi=gbeb1kJE1WfNED8KJ0R4UlTOFH
RT1ELEC-75-001 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-04-30 04:00:00.000 +0400 | SCH - Schneider Electric | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1MVTB_R1_HMI | HMI - HMI Panel |  |  | Damaged keys for the HMI selector | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620112&prj=646&rqi=9aKtrptpmNucGgmFmlZFMpTKyO
RT1ELEC-79-001 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-04-30 04:00:00.000 +0400 | SCH - Schneider Electric | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1MVTB_C_HMI | HMI - HMI Panel |  |  | HMI selector key set (supplied as a pair) includes one bent key. The second key remains in good condition | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620096&prj=646&rqi=9B3se4PmVI5ewjRBWuevFbAcgv
RT1ELEC-76-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-30 04:00:00.000 +0400 | SCH - Schneider Electric | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1MVTB_M1_HMI | HMI - HMI Panel |  |  | Key snapped within generator selector switch barrel on HMI | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620114&prj=646&rqi=k13MleOUWa0S1eb28jLSiONBbq
RT1MECH-672-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_411 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617970&prj=646&rqi=KTaq5SV7j7kFr6ydzRsSZLXtUT
RT1MECH-307-001 | LD14-1 | N-EMEA | Closed | P2 Medium CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Installation Damage | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_410 | DXID - FCU/DX Indoor Unit |  | FXHQ100AVEB8 | During RT inspection, FCU casing damage was noted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618070&prj=646&rqi=5NNW8gJxv0fzMX7g9UKxmUpj81
RT1MECH-663-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_206 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618037&prj=646&rqi=r7kZBpaSZvp9EYdPshcGSNZNUb
RT1MECH-661-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_212 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618051&prj=646&rqi=AC7NEtO50DPfVEaT9iP7yUihDi
RT1MECH-307-002 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_410 | DXID - FCU/DX Indoor Unit |  | FXHQ100AVEB8 | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618073&prj=646&rqi=raSb6ljQpD12jn4lFnqkWkxblU
RT1MECH-660-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_A_211 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618050&prj=646&rqi=bUime1BoahW1FqRgu68TzgFDBv
RT1MECH-655-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_M1_111 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618054&prj=646&rqi=qMOogIukdqgCkUC38tBvZWnZa6
RT1MECH-673-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_A_412 | DXID - FCU/DX Indoor Unit |  |  | Install correct asset ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617976&prj=646&rqi=vrTbGuJGfZr3t3mrenZY1FBmQf
RT1MECH-662-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_A_205 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618036&prj=646&rqi=qSY1gvjzpJEn0cq62Zh8ZLr6fW
RT1MECH-654-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_M1R1_110 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617567&prj=646&rqi=Go23VtxgEi7Uf0GskvbrCUiuq5
RT1MECH-650-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_M1_011 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617565&prj=646&rqi=SW2KZ5uNF6SVFV3uW54QyToO7Y
RT1MECH-649-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_M1R1_010 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617568&prj=646&rqi=NGGeo66XsMTwVRPGo92MBo3yTK
RT1MECH-656-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_112 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617563&prj=646&rqi=6yMAmS3osqN0ruSuA0ndlycXAe
RT1MECH-664-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-07 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_A_310 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617493&prj=646&rqi=SLp4MQfxaCnuSimyTORlTvYMNk
RT1MECH-665-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-07 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_311 | DXID - FCU/DX Indoor Unit |  |  | No asset Id on fcu | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617509&prj=646&rqi=Sx3mvf2FrbF8f3XxQXnUEtSPOu
RT1MECH-653-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-27 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_014 | DXID - FCU/DX Indoor Unit |  |  | FCU installed without permanent equipment/asset identification label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616710&prj=646&rqi=bBgWjcxsSZT6QEOyGDxymYhCnq
RT1MECH-658-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-27 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_114 | DXID - FCU/DX Indoor Unit |  |  | FCU installed without permanent equipment/asset identification label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616708&prj=646&rqi=24x4awVH7SPbfXd2AqqVkWncaS
RT1MECH-651-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-27 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_012 | DXID - FCU/DX Indoor Unit |  |  | FCU installed without permanent equipment/asset identification label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616711&prj=646&rqi=wvYKwUcwFkDGQFP9I5aRiX3EXx
RT1MECH-671-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_306 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615948&prj=646&rqi=6K1Ka5TAFB5bVjapiCZ0L6FxRl
RT1MECH-670-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_305 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615942&prj=646&rqi=kXAUzL7lOM8p7UTAVUft3M4PG0
RT1MECH-669-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_A_304 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615947&prj=646&rqi=Lgz9ClW2I790rwfKp3FwnhNUtK
RT1MECH-668-001 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_M1R1_303 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615949&prj=646&rqi=KPABi8HJEOa9qwvkZl1P0jluzk
RT1MECH-667-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_R1_302 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615952&prj=646&rqi=5ZojhufFaV0nBHB87p0N6jHGOV
RT1MECH-675-001 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-03-16 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_B_402 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615810&prj=646&rqi=Hx8vrpvXAtHGimtMPcTD2xPcxU
RT1MECH-676-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-16 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_403 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615816&prj=646&rqi=LxOciumH2vfHIjawcmVbshvU2d
RT1MECH-674-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-16 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_R1_401 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615800&prj=646&rqi=snsVFxYpHNDbwdaFwLfW06DPxD
GI-030 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General FWT/FAT Issue | Level 1 FWT | [6 empty] | BAC Cooling Tower - It was noted during the FAT that there was slight misalignment of the plates used for locking/securing of the access doors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198795&prj=646&rqi=VXuzn3JxvaZbJaucFtkN1oogyK
GI-031 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General FWT/FAT Issue | Level 1 FWT | [6 empty] | BAC Cooling Tower - During the visual inspection of the unit at the FAT it was noted that there is a slight weep between two mating surfaces of the basin module and the lower chamber wall. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198796&prj=646&rqi=f5YVdXBef91idRtc0YbWbPWL2z
GI-027 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General FWT/FAT Issue | Level 1 FWT | [6 empty] | BAC Cooling Tower - during the FAT inspection it was found that there is sharp edging on the stainless steel profile strips on the external corners of the unit that require dressing or chamfering. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198780&prj=646&rqi=lpMbBgVFsAHt76w8XK29XS79AZ
GI-029 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General FWT/FAT Issue | Level 1 FWT | [6 empty] | BAC Cooling Tower - during the FAT it was noted that the internal wire mesh to support the internal insulation of the upper chamber is not fitted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198784&prj=646&rqi=5LXxSaXeyrTmDEgtWKr4ZUCvzg
GI-026 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General FWT/FAT Issue | Level 1 FWT | [6 empty] | During the BAC FAT for the cooling tower it was noted that earthing points/lugs were not fitted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198768&prj=646&rqi=bALxnVufKulq2NFKS32RBhJXwD
GI-019 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-02 04:00:00.000 +0400 | REH - Rehlko Gens |  | Missing Components | Commissioning | [6 empty] | Generators - Selective Catalytic Reducers: The SCR units were delivered to site without protective covers fitted to the exhaust outlet flanges. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198198&prj=646&rqi=sDlOUusWP2eD1z7dIvbWcItHW2
GI-018 | LD14-1 | N-EMEA | Closed | P2 Medium CX | ganderson@global-cxm.com | 2026-01-26 04:00:00.000 +0400 | VER - Vertiv Electrical |  | General FWT/FAT Issue | Level 1 FWT | [6 empty] | Critical MeWall E-house - Transformer has been supplied without anti-vibration pads. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197574&prj=646&rqi=P6A3mFoBbzP88LGz2TEkZ8jDnj
GI-017 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-01-22 04:00:00.000 +0400 | SCH - Schneider Electric |  | General FWT/FAT Issue | Level 1 FWT | [6 empty] | SUDB E-house B - protective conduit to be fitted to DX unit external condensers' piping/cabling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197514&prj=646&rqi=urf2j9GbiumChS3ssZkVgU6Htr
GI-016 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-01-22 04:00:00.000 +0400 | SCH - Schneider Electric |  | General FWT/FAT Issue | Level 1 FWT | [6 empty] | SUDB E-house A - protective conduit to be fitted to DX unit external condensers' piping/cabling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197513&prj=646&rqi=DEWN2UWhVcV8uZy43Ex3k3FLA9
RT1MECH-320-001 | LD14.2 | N-EMEA | Closed | P3 Low CX | gharbottle@global-cxm.com | 2026-06-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_M1_16 | VRF - Variable Refrigerant Flow System |  |  | Missing permanent asset label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625066&prj=686&rqi=kvr2igrwGg7QdFQwsASXkUA567
RT1MECH-319-001 | LD14.2 | N-EMEA | Closed | P3 Low CX | gharbottle@global-cxm.com | 2026-06-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_R1_15 | VRF - Variable Refrigerant Flow System |  |  | Missing permanent asst label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625064&prj=686&rqi=zWcOSRR1o0SYCJSbkZ1OEmWF3N
RT1MECH-321-001 | LD14.2 | N-EMEA | Closed | P3 Low CX | gharbottle@global-cxm.com | 2026-06-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_M2_17 | VRF - Variable Refrigerant Flow System |  |  | Missing permanent asset label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625068&prj=686&rqi=4f8rgmxKKK1NBehuO1aAShc4YA
GI-053 | LS02-1 | S-EMEA | Closed | P3 Low DCOS | Alen.Francis@eu.equinix.com | 2026-01-29 04:00:00.000 +0400 | Equinix Ops |  | Design correction needed | Design | [6 empty] | GDC Requires the following to be actioned. Due to Low Load in the building and multiple assets in a alarm local Ops needed to open up alarm bands to stop the large amount of alarms coming through to the EOC Please when load is availble can they be put back to the commissioned settings as per smartsheet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197892&prj=455&rqi=EcLqqEf0yekoQAhRvl1lgCizKs
YT1ELEC-191-002 | LS02-2 | S-EMEA | Open | P3 Low CX | radek.kmak.ext@bureauveritas.com | 2026-09-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1SUDB_01 Feeder Q2 (Feeder to RMU_E) | SUDB - Secondary Utility Distribution Board |  |  | Poor containment installation, bent containment, missing and damaged covers. Missing firestopping | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638070&prj=674&rqi=1YIKvHrTHgv9HSGtmQSLDKcYGE
YT1ELEC-191-001 | LS02-2 | S-EMEA | Open | P3 Low CX | radek.kmak.ext@bureauveritas.com | 2026-09-14 04:00:00.000 +0400 | SCH - Schneider Electric | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1SUDB_01 Feeder Q2 (Feeder to RMU_E) | SUDB - Secondary Utility Distribution Board |  |  | Verify permanent equipment labels affixed, contract specific label colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637946&prj=674&rqi=Fo3m3QIaxaLmklpTvY7Yve9ia1
GT1ELEC-123-002 | LS02-2 | S-EMEA | Open | P3 Low CX | radek.kmak.ext@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1SUDB_02 Feeder Q4 (Bypass from SUDB_01) | SUDB - Secondary Utility Distribution Board |  |  | Confirm Live test results (SAT) uploaded to Asite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636720&prj=674&rqi=ugvq243Z4jlqDvCISMQiXBGHBM
GI-011 | LS02-2 | S-EMEA | Closed | P2 Medium CX | gabriel.matiasarnal@bureauveritas.com | 2026-08-05 04:00:00.000 +0400 | General Contractor |  | General Design Issue | Design | [6 empty] | As per Site Specification for Earthing, LS021-QUA-XX-XX-RP-E-ERTH-8001-Earthing. "Separate protective earth networks shall be provided for low voltage and medium voltage of metallic enclosures of electrical panels and equipment" and "Protective grounding system, consisting of the grounding lines and the corresponding grounding electrodes that directly connect to ground the conductive parts of the installation elements not normally subjected to electrical voltage, but which could be put under voltage by faults or accidental contacts, in order to protect people against contacts with dangerous voltages." Under that definition the Metal Frame holding the chiller should have a grounding connected to the BTP Roof 2 and the cable schedule doesnt reflect this. Please confirm if Chiller Metal Frame needs a Grounding Bound | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632270&prj=674&rqi=o7sp7AgLFA5iTf0jGAY6F1Vt1J
GI-010 | LS02-2 | S-EMEA | Closed | P2 Medium CX | gabriel.matiasarnal@bureauveritas.com | 2026-08-05 04:00:00.000 +0400 | General Contractor |  | General Design Issue | Design |  | equipment type |  |  |  |  | As per Site Specification for Earthing, LS021-QUA-XX-XX-RP-E-ERTH-8001-Earthing. "Separate protective earth networks shall be provided for low voltage and medium voltage of metallic enclosures of electrical panels and equipment" and "Protective grounding system, consisting of the grounding lines and the corresponding grounding electrodes that directly connect to ground the conductive parts of the installation elements not normally subjected to electrical voltage, but which could be put under voltage by faults or accidental contacts, in order to protect people against contacts with dangerous voltages." Under that definition the Container Housing the Generator should have a grounding connected to the BTP Gen and the cable schedule doesnt reflect this. Please confirm if Generator Container needs a Grounding Bound | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632247&prj=674&rqi=gJDneUP9418F3urYwy2BYnnIyB
GI-009 | LS02-2 | S-EMEA | Closed | P2 Medium CX | lars.dietrich@bureauveritas.com | 2026-07-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | No Drip-Trays under ACC on the Roof. there are no drip trays installed underneath ACC`s. Trane uses POE oil in DX cycle and Glycol N in FC cycle. Both are prohibited to enter rainwater drains or sewer. Please provide the plan to prevent the Glycol and POE oil to enter rainwater drain in event of leak. Even oil separator in rainwater drain ,might still allow the POE to enter and pollute nearby river as POE is made of Acid and Alcohol. Getting in touch with water, it splits up in itÂ´s origin substances and might not be captured by oil separator. Please explain how to prevent substances used in ACC to enter rainwater drainage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630867&prj=674&rqi=IkFA5ihaNtBRFH0TpPklfQbjWW
GI-008 | LS02-2 | S-EMEA | Closed | P2 Medium CX | lars.dietrich@bureauveritas.com | 2026-07-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Position of Fuel-Kill-Valve. The blow fuse is located in the Air-Intake right next to the FDAY of the Generator Container. See drawings attached. In event of fire, which occurs usually at the Motor these fuses will not trigger as permanently cooled by the Inlet Air. Please review design and explain how the system should operate in event of fire. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630861&prj=674&rqi=HyeFdfqq8EwHlkVpNuqD5QkumK
GI-007 | LS02-2 | S-EMEA | Open | P3 Low CX | gabriel.matiasarnal@bureauveritas.com | 2026-07-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation not issued/ Required | Commissioning | [6 empty] | LVSB C1/D1/E1 Aux Switchboard generator Technical submitall and drawings not matching installation Your installation and O&M manual (LS021-STE-GT-B1-OM-E-GENL-7063-Switchboard Panel â€“ SWAUX01 O&M Manual-AB01-Phase 2) has only one socket X1.1 However on TN and Drawings on doc holder it has two more sockets, please remove it from TN and reupload new version on ASITE, place correct drawings on panels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630555&prj=674&rqi=YfHIliep5ZHfgoT1HAkKfnriOl
GI-006 | LS02-2 | S-EMEA | Closed | P2 Medium CX | gabriel.matiasarnal@bureauveritas.com | 2026-07-17 04:00:00.000 +0400 | SOC - Socomec |  | Missing Components | Commissioning | [6 empty] | Internal Busbar connection missing a washer Confirm if bolt and nut wont be affected by vibration when loaded without a washer installed or if STS busbars need extra washers to be installed (Torque mark on the other side, missing the double torque mark but a different issue was created for it) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629881&prj=674&rqi=dV5OP4xDKAVXUJZZQfhbfQuEck
GI-005 | LS02-2 | S-EMEA | Closed | P2 Medium CX | gabriel.matiasarnal@bureauveritas.com | 2026-07-17 04:00:00.000 +0400 | SOC - Socomec |  | Torque required | Commissioning | [6 empty] | On STS Q30 Connection without washer and less than one thread out If its a design constraint because of space please confirm that installation is ok | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629880&prj=674&rqi=Lj1cC7d9gv6YthsWigSUyeCbSA
GI-004 | LS02-2 | S-EMEA | Closed | P3 Low CX | gabriel.matiasarnal@bureauveritas.com | 2026-07-16 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | [6 empty] | Following RPPs missing permanent labels and arc flash label: 1RPP_CR_1_6 1RPP_CR_2_3 1RPP_CR_2_6 1RPP_DR_1_1 1RPP_DR_1_2 1RPP_DR_1_4 1RPP_DR_1_5 1RPP_DR_1_8 1RPP_DR_2_1 1RPP_DR_2_2 1RPP_DR_2_4 1RPP_DR_2_5 1RPP_DR_2_8 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629609&prj=674&rqi=1OHrFbJhIpTFwcSKkkaa66JdlU
GI-002 | LS02-2 | S-EMEA | Open | P3 Low CX | gabriel.matiasarnal@bureauveritas.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | Generators missing docs on holder | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628546&prj=674&rqi=Af8HaaTRBK8ZiY1E5rablsuDrD
RT1ELEC-176-002 | LS02-2 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LVSB_C_2 | LVSB - Low Voltage Switchboard |  |  | loose earthing cable termination Carry out full visual inspection of panel and confirm no defects, scratches, dents, abnormalities | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627322&prj=674&rqi=RAVoUqb1pCpDw2xvEihgFiKuqe
RT1ELEC-142-001 | LS02-2 | S-EMEA | Closed | P2 Medium CX | ismail.kose@bureauveritas.com | 2026-06-25 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1SUDB_02 Feeder Q4 (Bypass from SUDB_01) | SUDB - Secondary Utility Distribution Board |  |  | SUDB_02/Q2: Visual copper spots at ct control cable. BX13 - 9 Earth cable csh200 -S2pe Carry out full visual inspection of switchboard and confirm no defects, scratches, dents, abnormalities | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626906&prj=674&rqi=F7QFb7P2vexaXnDWSePqqhEoob
RT1ELEC-142-003 | LS02-2 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-25 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Torque required | Commissioning | Electrical â€“ MV | equipment | 1SUDB_02 Feeder Q4 (Bypass from SUDB_01) | SUDB - Secondary Utility Distribution Board |  |  | qa4 earth termination missing torque marks. Broken torque marked. Tightness of bolted electrical connections by calibrated torque-wrench method in accordance with manufacturerâ€™s published data. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626908&prj=674&rqi=p6yu37HbVFZLjbE5gGo06kx4Jp
GT1ELEC-123-001 | LS02-2 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-25 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ MV | equipment | 1SUDB_02 Feeder Q4 (Bypass from SUDB_01) | SUDB - Secondary Utility Distribution Board |  |  | Live circuits not having right colour. grey instead of white. Please check upstream to downstream. Refer to attached screen shots. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626880&prj=674&rqi=9wJkeuQbDPhsblBZVlh3xlw6vn
RT1ELEC-142-002 | LS02-2 | S-EMEA | Open | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-25 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1SUDB_02 Feeder Q4 (Bypass from SUDB_01) | SUDB - Secondary Utility Distribution Board |  |  | Multiple dents and scratches Confirm SUDB delivery visual Inspection/checklist is complete with defects noted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626907&prj=674&rqi=PF5TgM4tgyYAJfHEERxhLpZEce
RT1ELEC-178-002 | LS02-2 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LVSB_C_4 | LVSB - Low Voltage Switchboard |  |  | Verify Installation of equipment is complete in final location and as per Manufacturers Spec. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624971&prj=674&rqi=PVkuiHkY0XY3ZMbrekuWgAHE2Z
RT1ELEC-186-002 | LS02-2 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1LVSB_R_11 | LVSB - Low Voltage Switchboard |  |  | door hinges support/locking mechanism broken Carry out full visual inspection of panel and confirm no defects, scratches, dents, abnormalities | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624973&prj=674&rqi=4WaCoXf3LNF3ErIzvKcCKvPNBp
RT1ELEC-178-003 | LS02-2 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LVSB_C_4 | LVSB - Low Voltage Switchboard |  |  | main power supply should be torque marked after being torqued with a certified torque wrench. source: Verify Internal bolted electrical connections tightened by calibrated torque-wrench method in accordance with manufacturerâ€™s published data. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624972&prj=674&rqi=nn8dDvz9Ut3jIOJl64TgYWitdk
GI-001 | LS02-2 | S-EMEA | Closed | P2 Medium CX | serdar.tuccaroglu@bureauveritas.com | 2026-05-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation not issued/ Required | Commissioning | [6 empty] | 75 L2A checklists have been scheduled to be completed by 22/05/2026 while only 41 are signed off, 24 are awaiting documentation and 5 are in progress: Actual vs Planned L2A Commissioning Ratio is 55%. GC Project Cx schedule is not accurate and not aligned with the FG timeline monitor. GC 2WLA is not accurate and not aligned with the FG timeline monitor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622956&prj=674&rqi=eYF9TfbxonQMHxM6FvGQXp2Dw0
RT1ELEC-186-001 | LS02-2 | S-EMEA | Closed | P3 Low CX | andrew.mercer@bureauveritas.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LVSB_R_11 | LVSB - Low Voltage Switchboard |  |  | Technical submittal is provided only in Portuguese. As per Playbook 6.1 Section 1.2.1.1., all commissioning documentation through Cx levels 0 to 6 is mandatory to be written in English, local language can supplement the English language documents based on region specific requirements. Where a discrepancy between English and local language arises in a document, the English language form takes precedence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622474&prj=674&rqi=2YZx1g75mqaug01QV96zmqP4mP
RT1ELEC-178-001 | LS02-2 | S-EMEA | Closed | P3 Low CX | andrew.mercer@bureauveritas.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LVSB_C_4 | LVSB - Low Voltage Switchboard |  |  | Technical submittal is provided only in Portuguese. As per Playbook 6.1 Section 1.2.1.1., all commissioning documentation through Cx levels 0 to 6 is mandatory to be written in English, local language can supplement the English language documents based on region specific requirements. Where a discrepancy between English and local language arises in a document, the English language form takes precedence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622475&prj=674&rqi=wtfAQJSKHReZnrJWdSDNguYZmX
RT1ELEC-176-001 | LS02-2 | S-EMEA | Closed | P3 Low CX | andrew.mercer@bureauveritas.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LVSB_C_2 | LVSB - Low Voltage Switchboard |  |  | Technical submittal is provided only in Portuguese. As per Playbook 6.1 Section 1.2.1.1., all commissioning documentation through Cx levels 0 to 6 is mandatory to be written in English, local language can supplement the English language documents based on region specific requirements. Where a discrepancy between English and local language arises in a document, the English language form takes precedence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622418&prj=674&rqi=5oWJ3Ipf6mcpS7B4tLxAOe1I4S
RT1ELEC-177-001 | LS02-2 | S-EMEA | Closed | P3 Low CX | andrew.mercer@bureauveritas.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LVSB_C_3 | LVSB - Low Voltage Switchboard |  |  | Technical submittal is provided only in Portuguese. As per Playbook 6.1 Section 1.2.1.1., all commissioning documentation through Cx levels 0 to 6 is mandatory to be written in English, local language can supplement the English language documents based on region specific requirements. Where a discrepancy between English and local language arises in a document, the English language form takes precedence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622462&prj=674&rqi=umKwqmDwg6IAjG6ihN6vm1qNYw
RT1ELEC-179-001 | LS02-2 | S-EMEA | Closed | P3 Low CX | andrew.mercer@bureauveritas.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LVSB_C_5 | LVSB - Low Voltage Switchboard |  |  | Technical submittal is provided only in Portuguese. As per Playbook 6.1 Section 1.2.1.1., all commissioning documentation through Cx levels 0 to 6 is mandatory to be written in English, local language can supplement the English language documents based on region specific requirements. Where a discrepancy between English and local language arises in a document, the English language form takes precedence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622467&prj=674&rqi=1X0Ke5kx4vriYsWLHm6aiP3UFb
RT1MECH-57-002 | MA05-P1 | N-EMEA | Closed | P3 Low CX | nrae@global-cxm.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1-CH-E-1 | ACC - Chiller â€“ Air Cooled |  |  | Verify Anti-Vibration mounts are correctly fitted and adjusted Anti vibe mounts still to be installed in 4 locations. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624441&prj=645&rqi=9hPSxv5VkGobfBdc7J8fwSCOHz
RT1MECH-57-003 | MA05-P1 | N-EMEA | Closed | P3 Low CX | nrae@global-cxm.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1-CH-E-1 | ACC - Chiller â€“ Air Cooled |  |  | Permanent equipment labels to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624453&prj=645&rqi=dvZF1OgrlKEHbwDtMJD8fWHFkW
RT1MECH-58-001 | MA05-P1 | N-EMEA | Closed | P3 Low CX | nrae@global-cxm.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1-CH-G-1 | ACC - Chiller â€“ Air Cooled |  |  | Anti vibe mounts are not installed correctly. Vendor has supplied the wrong anti vibe mounts. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624467&prj=645&rqi=QSA0UEX6Cd43MW7QdwFaqDB8Ma
RT1MECH-57-001 | MA05-P1 | N-EMEA | Closed | P3 Low CX | nrae@global-cxm.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1-CH-E-1 | ACC - Chiller â€“ Air Cooled |  |  | Carry out visual inspection of Equipment and confirm no defects, scratches, dents and any other damage. Bent fins on the chiller coil, minor damage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624406&prj=645&rqi=nS0y9vygUqskDEfHK0TAcJuCZq
WREPORT-23-001 | MA05-P1 | N-EMEA | Closed | P2 Medium CX | tkhan@global-cxm.com | 2026-04-15 04:00:00.000 +0400 | Equinix Ops | DELIVERABLES | Design correction needed | Design | Multi-Discipline | system | Weekly Report |  |  |  | Approval time for new CR to change the timer values of MSB-T11 and Chiller's restart time was around 5 weeks | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619503&prj=645&rqi=mWw1nzQM9B62WKkAqazYr2odm0 | https://equinix.facilitygrid.co.uk/x/project/645/system/13103
RT1ELEC-36-001 | MA05-P1 | N-EMEA | Closed | P3 Low CX | asaville@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1-MSB-E | MSB - Main Input Switchboard |  |  | Permanent labelling to be installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615820&prj=645&rqi=PjBypI0np9z53m1V1cNM6Kwskn
GI-2677 | MB03-1 | APAC | Closed | P3 Low CX | KunalKavathankar@commtechasia.com | 2026-02-06 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Alarm maintenance mode and alarm shelve duration not demonstrated Asset tab datasheet and weblink was not demonstrated Applicable for all assets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198685&prj=227&rqi=HE0MbsxhDvnN5YObb9eD9N2xNU
GI-2676 | MB03-1 | APAC | Closed | P3 Low CX | sganeshmahadik@ap.equinix.com | 2026-02-02 04:00:00.000 +0400 | Facility Manager |  | DCIM Maximo Issue | DCIM | [6 empty] | Maximos not available to integrate with DCIM, BCM and Battery Monitoring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198095&prj=227&rqi=BZfEZ6F7DbQVs4EYb1eMkFEm5t
GT1MECH-175-003 | MD05-1 | S-EMEA | Open | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-08-05 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | An alarm has been triggered on fire pump No. 2 due to a low engine coolant temperature. The pumpâ€™s temperature sensor is not measuring correctly and will need to be replaced. This does not affect the pumpâ€™s functionality. Once the issue has been resolved, the supervisory alarm associated with that pump should be activated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632284&prj=396&rqi=tsCVpYXxjYVYb1WFpyFXAlKvqL
GI-102 | MD05-1 | S-EMEA | Closed | P2 Medium CX | arkaitz.santos@eu.equinix.com | 2026-08-04 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning | [6 empty] | Vesda fault alarm active sine August 1st. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632134&prj=396&rqi=RzYsKeFfUJ3hqofkODBaBvZmgI
DCOSL5-1-003 | MD05-1 | S-EMEA | Closed | P3 Low CX | arkaitz.santos@eu.equinix.com | 2026-07-14 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Controls | system | DCOS |  |  |  | PV_1 and PV_2 communication lost every few minutes and during night time. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629180&prj=396&rqi=EqVtafRv5fayNvcaZtJ4H4PgE5 | https://equinix.facilitygrid.co.uk/x/project/396/system/14475
DCOSL5-1-002 | MD05-1 | S-EMEA | Closed | P2 Medium DCOS | arkaitz.santos@eu.equinix.com | 2026-07-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Template Issue | DCOS | Controls | system | DCOS |  |  |  | Need to clean the around 50 assets with warnings at DCOS IDE. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629124&prj=396&rqi=6Ui6iYDqZWgsdCIlsyxu1r36w8 | https://equinix.facilitygrid.co.uk/x/project/396/system/14475
DCOSL5-1-001 | MD05-1 | S-EMEA | Closed | P2 Medium DCOS | arkaitz.santos@eu.equinix.com | 2026-07-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | Clear the around 13000 alarms generated each day at DCOS Aveva system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628600&prj=396&rqi=bXAcKag6kpQoYvIQqIq4rdqR6i | https://equinix.facilitygrid.co.uk/x/project/396/system/14475
GI-100 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-07-08 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Rotor lock alarms are being generated intermittently on low load running 2 happened over the weekend of 03/07-05/07 on WCC A & B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628296&prj=396&rqi=Zn04OIgX44jwgLiR0ADDGG9EF2
GI-096 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | WCC A & R are failing to restart automatically during transfer to gens in IST | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627300&prj=396&rqi=YCxnQwK9saRvaxnzlnXCjnfBeG
GT1MECH-310-001 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-06-26 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Fuel | equipment | 1FPCP_B_01 | FPCP (Fuel Pump Control Panel) |  |  | During the IST tests conducted today, it was verified that the fuel system loses redundancy in pump system B during transitions from facility to the generator set. An alarm appears on the Fuel Distribution Loop 2 controller for B, and the pumps B go into alarm. System in A is available and working. The system must be reset from the control panel at fuel pump B. The fuel system has operated correctly during all tests, but redundancy for system B is lost until it is manually reset from the INPRO PLC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627148&prj=396&rqi=GIvKE2KrdxZOuITQeAd0lZcjWn
GI-095 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-06-26 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | During IST during Test 3 hall SLAs we're breached for 10 minutes due to slow restart of WCCs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627075&prj=396&rqi=RbF1T29p55N61QbQAETptPogSO
GI-094 | MD05-1 | S-EMEA | Closed | P3 Low DCOS | liam.piervulivo@hdrinc.com | 2026-06-24 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Configuration | DCOS |  | equipment type |  |  |  |  | WCC compressor suction/ discharge pressures do not make sense Revise MODBUS addresses with vendor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626686&prj=396&rqi=cmSJkccGv3PHWww6rhowQe8Stn
GI-092 | MD05-1 | S-EMEA | Closed | Outstanding Paperwork/Documentation | liam.piervulivo@hdrinc.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS General Issue | DCOS | [6 empty] | SOO testing docs outstadning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626673&prj=396&rqi=zk1mvhOX39LlX1QlXHk91WqReT
GI-090 | MD05-1 | S-EMEA | Closed | P3 Low CX | liam.piervulivo@hdrinc.com | 2026-06-15 04:00:00.000 +0400 | Equinix Commissioning Manager |  | Installation Not Correct | Commissioning | [6 empty] | WCC B & R loading to be repeated with glycol in primary circuit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625278&prj=396&rqi=oKIQA8jngC6h8jHLYKewPwB4tk
SOR-17-001 | MD05-1 | S-EMEA | Closed | P3 Low CX | jason.beachill@hdrinc.com | 2026-06-15 04:00:00.000 +0400 | DCOS - Equinix |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Equipo Ref DCOS Ref Facility Grid Bomba 1Âº DAC 1CHWSTR_X_X_CWP_1 1CHWSTR_X_CWP_02 Bomba 1Âº Condensor 1CHWSTR_X_X_CWP_2 1CHWSTR_X_CWP_01 Bomba 2Âº Instalacion 1CHWSTR_X_X_CHWP_1 1CHWSTR_X_CWP_03 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625290&prj=396&rqi=RTHem8QVOUtvzzCmoLDk0yrXMC
FPT-410-001 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | HVAC | system | CHW System |  |  |  | CWST A TT-13 is reading a degree higher than logical, this temp did not drop to TT-08 value when buffer tank is in recharge mode Instrument calibration needs to be checked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625299&prj=396&rqi=4YnrRbA0eYAEaBSF0Kout2qgiF | https://equinix.facilitygrid.co.uk/x/project/396/system/13433
GI-089 | MD05-1 | S-EMEA | Closed | P2 Medium DCOS | liam.piervulivo@hdrinc.com | 2026-06-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Loss of DAC run status lost when outlet temps increased past 38 deg C Run status lost due to deviation from SP, as raising SP to 25 deg C resulted in return of run status | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624787&prj=396&rqi=Cjb1irPl1sy3xKXWBZgqXaX3LP
GI-087 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-06-09 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning | [6 empty] | DAC supply temps are very oscillatory when SP is above OAT, particularly when difference is more than 10 deg C | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624384&prj=396&rqi=w6JvppvHstfsl5wjOYUnE4BsUb
GI-085 | MD05-1 | S-EMEA | Open | P3 Low CX | liam.piervulivo@hdrinc.com | 2026-06-09 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | DAC sending fault signals for less than a second when on and running, this are not considered real failures | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624381&prj=396&rqi=Ss7vVSe80ThhpcXGOV8btJu8sU
FPT-397-001 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-06-09 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Correct | Commissioning | Fuel | equipment | 1FPCP_A_01 | FPCP (Fuel Pump Control Panel) |  |  | During the fire valve simulation in GEN R , it was found that the lever could not be lowered fully as it interfered with a manual valve, and the system was unable to shut off the fuel supply. The pipework must be modified to prevent any contact. This applies to generators A, B and R. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624483&prj=396&rqi=NZ3Gt0eDy3cHTLP9dTBmftEew8
GI-086 | MD05-1 | S-EMEA | Closed | Outstanding Paperwork/Documentation | liam.piervulivo@hdrinc.com | 2026-06-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Design Correction Needed | Design | [6 empty] | SOO not inline with onsite programming as changes have been made SOO needs top be uploaded and approved | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624382&prj=396&rqi=s51xwKYuQ1pIPlldSF2vfLS2vT
GT1MECH-309-001 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Fuel | equipment | 1FPCP_A_01 | FPCP (Fuel Pump Control Panel) |  |  | The differential pressure switch on the fuel filter is not working properly. Inpro will supply a replacement, and its correct operation must be checked. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623633&prj=396&rqi=mWw5wgMOvPvaPUeQBBrUukABBR
GT1MECH-309-002 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | Fuel | equipment | 1FPCP_A_01 | FPCP (Fuel Pump Control Panel) |  |  | Minor changes have been made to the wiring in the two PLC panels in both Room A and Room B. The diagrams must be updated, and the new cables installed in both the panels and the diagrams must be identified. Furthermore, it must be checked that there are no discrepancies between the panels and the diagrams. Check relay K17 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623637&prj=396&rqi=2dmAPb9Gb8qe9hXn1LwJ6jBcwj
GI-080 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-05-07 04:00:00.000 +0400 | VER - Vertiv Electrical |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Cool array HOTSPOT functionality not working in DH 1.3 or DH 1.4, to be checked prior to L4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620663&prj=396&rqi=URRA0YvGdVGW6aUbCMMSB1BeSQ
GI-078 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-05-06 04:00:00.000 +0400 | ARM -Armstrong |  | General Design issue | Design |  | equipment type |  |  |  |  | Flow switches to be set up with pump min speed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620513&prj=396&rqi=586jKsNzdd26Eo8M1XRga85FGu
GI-079 | MD05-1 | S-EMEA | Closed | P1 High CX | liam.piervulivo@hdrinc.com | 2026-05-06 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | design flow rates are not being achieved on condenser or primary circuits, affecting WCC, DAC and heat exchanger performance Potentially linked to foaming or gas entrained witnessed in water samples | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620515&prj=396&rqi=HVk0hfLzjC5c5jOFNEbW2qw25W
GI-077 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-05-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | Confirmation on what signal type & range is required for PICV valves feedback (V or mA, 0-10V, 2-10V, 4-20mA, 0-20mA) In PPR 1,2 & 3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620511&prj=396&rqi=sFJBzKAYw6zdB032M9Q6oU9jM7
GI-064 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-04-27 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Temperature control of condenser water inlet is not fine enough and causing issues with WCChttps://equinix.facilitygrid.co.uk/inquire/?action=eiss&trf=1&PID=619505&prj=396# | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619505&prj=396&rqi=ucXFVuiP6csP08t45DIaOSw2Yi
GI-063 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-04-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Primary/ condenser loop flowrates cannot be consistently read and appear lowerthan design when read at orifice plate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619504&prj=396&rqi=nTceeoGsUppLmKxAAkkX8xOCa3
GT1MECH-175-002 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-04-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | The water liquid cooling system for the fire pumps discharges directly onto the exterior of the building, creating small pools of water. We request that the discharge point be situated near a drainage point. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617019&prj=396&rqi=jqDvaKV4dC08s69hIxng9hKPSK
GT1MECH-175-001 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-04-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | During the internal test of the the pumps verifying the curve and consumption was noted that the jockey pump starts at 8 bar and stops at 8,5 bar with a delay more or less of 2 seconds. As a result of the delay, the pressure in the pipe rises to 13 bar. Please verify the way to improve the settings in order to avoid high pressure in the piping system during the jockey functionality. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617008&prj=396&rqi=dpy961hhqsOhv9pkPHVAqpZA0P
GI-061 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-03-18 04:00:00.000 +0400 | ARM -Armstrong |  | Design Correction Needed | Design |  | equipment type |  |  |  |  | DPT 01&02 range is too high and causing issues with measurement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615971&prj=396&rqi=juTdTr0di6I0xOst952wGushIl
GI-060 | MD05-1 | S-EMEA | Closed | P3 Low CX | luis.newman@hdrinc.com | 2026-03-09 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning | [6 empty] | Blanking panels in Ewall B are not properly fixed down and with a small amount of airflow from the CRAHs the panel is being pushed back and swaying back and forward | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615115&prj=396&rqi=wfxgf3L0llOHZoOBdV1l1JeVM4
GI-058 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-03-04 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Condenser flow status point monitored by DCOS is looking at a lack of alarm for condenser flow, this is generating a flow status when everything is off (chillers & pumps) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614682&prj=396&rqi=JGDRcg1Ne2i72Pw4jS6dYatt54
GI-059 | MD05-1 | S-EMEA | Closed | P2 Medium DCOS | liam.piervulivo@hdrinc.com | 2026-03-04 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Design Correction Needed | Design |  | equipment type |  |  |  |  | Ready to run point not used in sequencer logic as per CHW SOO sFAT | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614683&prj=396&rqi=qvUeGvULNNobos8yxTuCIvKfx4
GI-057 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-03-04 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Ready to run signal logic sent to DCOS logic needs to be changed so that chiller is always either in fault or ready to run. One is the inverse of the other | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614681&prj=396&rqi=fudF8rjDdUJCMpjRiSnrMm7qOH
YT1MECH-327-001 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-02-19 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning | Fuel | equipment | 1FPCP_A_01 | FPCP (Fuel Pump Control Panel) |  |  | Inside the pump rooms, the cable containment system needs to be repaired. The DP copper piping also needs to be repaired, and outside, the valves and pipes need to be painted and checked. At a minimum, the valves, flanges and pipes need to be repainted, cleaned and oxidation to be repaired. To be fixed the cable installed in the bulk tanks (improve the fixation, cables with the correct radios, and to be cleaned). This applies to FPCP_A01, FPCP_B01, and Fuel Pumps in A and B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199527&prj=396&rqi=KC0x7zJyqDsyAVYTQGc9diX3zr
YT1MECH-189-004 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-02-18 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | In one of the pump fuel tanks It is observed a leak in the tank. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199458&prj=396&rqi=UD7elw9wCEZOVMVnPRZzJsh5M7
GI-054 | MD05-1 | S-EMEA | Closed | P2 Medium CX | luis.newman@hdrinc.com | 2026-02-11 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning | [6 empty] | Water detected in Ewall B, in front of MDSB_B1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199028&prj=396&rqi=F1vLnk4DtQY3h1QEiwIEQBcDZi
GI-051 | MD05-1 | S-EMEA | Closed | P3 Low CX | liam.piervulivo@hdrinc.com | 2026-02-09 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning |  | equipment type |  |  |  |  | Lagging and cladding to be replaced where it's been removed to install DAC temp sesnors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198787&prj=396&rqi=gnGlAoN9WWZs7z6V8uyJCwePy3
GI-053 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-02-09 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | PPR/ PCR control valves are not actuating correctly as per DCOS signal. Suspect loose 4-20mA connection instead actuator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198789&prj=396&rqi=O1d1XUpsdwmjdiRejnQVy6oOCo
YT1MECH-189-003 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-01-30 04:00:00.000 +0400 | General Contractor - Commissioning |  | Incomplete Connections | Commissioning | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | To be verified the leaks in the refrigerant pipe of the pumps | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198005&prj=396&rqi=VJ89VcgTGxpx7FmQx0BACop4fj
GI-050 | MD05-1 | S-EMEA | Closed | P2 Medium DCOS | liam.piervulivo@hdrinc.com | 2026-01-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Installation Not Complete | DCOS |  | equipment type |  |  |  |  | Hard wired cable to control DAC SP not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198017&prj=396&rqi=ozTx3OmEoJATCcQx2Cf1RrMixZ
YT1MECH-189-002 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-01-29 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | To be include a water protection in the ventilation pipe out of the fire pump room | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197861&prj=396&rqi=715j4FXi1wxfReBZhX4u6xYRhX
YT1MECH-189-001 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-01-28 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | To be repaired the protection element from the pump 1SP_B_01. Also pending to be connected the bonding-earthing cables in 2 pipes | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197782&prj=396&rqi=jFFoqi6ZsMgFSEwICzkciJj5JV
GI-049 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-01-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Indoor Fan Coil units in battery rooms and NER rooms are not working in heating mode This is causing these rooms to be outside the acceptable temperature range | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196963&prj=396&rqi=AGre0azV4kIw71pfSUGvWDU9p6
GI-275 | MI01-3 | AMER | Closed | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-07-15 04:00:00.000 +0400 | General Contractor |  | Documentation Not issued/ Required | Commissioning | [6 empty] | Panel Drawings missing in BCM enclosure - west COLO | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629431&prj=500&rqi=uQnbREGycjDe5sKhOPf20PnPHW
GI-274 | MI01-3 | AMER | Open | P2 Medium DCOS | sdetardo@equinix.com | 2026-07-15 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | please see Sensor 1 for CRAH 5_25 is in alarm at 81.4 degrees. This sensor does not appear in the floor layout of the colo. Please review all CRAH sensors on the graphics and that alarming is feeding through | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629426&prj=500&rqi=Pl5c4S3yUr9jHkFRyWqMvcqXt1
GI-132 | MI01-EOL | AMER | Open | P3 Low CX | sdetardo@equinix.com | 2026-08-26 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [6 empty] | Installation incomplete - hose for Fire System Nitrogen device - see photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635390&prj=611&rqi=tqb0wVbt2IQUAhpoiZ7P8h7gnM
GI-131 | MI01-EOL | AMER | Open | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-08-24 04:00:00.000 +0400 | Controls Contractor |  | Documentation not issued/Required | Commissioning | [6 empty] | Equinix TES/Controls has not received the IP Address or Password list for the delivered equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634931&prj=611&rqi=9CxLjGgFOjcoJQ3QEKpKVqYQl8
GI-130 | MI01-EOL | AMER | Open | P2 Medium CX | sdetardo@equinix.com | 2026-08-20 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design | [6 empty] | Generator breakers do not have kirk keys. In the event voltage is present from the mobile temp gen - it is possible to backfeed the fixed generator. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634383&prj=611&rqi=nmkGd1bQKXC0cCGEQOl782XEgs
GI-129 | MI01-EOL | AMER | Open | P2 Medium CX | sdetardo@equinix.com | 2026-08-18 04:00:00.000 +0400 | Design Professional |  | Installation not complete | Commissioning | [6 empty] | Mobile Generator / Rollup Tap Box remote start is inoperable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634134&prj=611&rqi=5KNp2yB92gfaRrg1tjNH9Y7WPb
GI-127 | MI01-EOL | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-07-17 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | update graphics to show new sources of chillers and pumps | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629890&prj=611&rqi=IqcO04ppeNsTBnTeyFBmaSthtH
GI-118 | MI01-EOL | AMER | Closed | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | PLC inside daytank controller not labelled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629788&prj=611&rqi=wYZrGr58inm0z79qMVb9S4VsJG
GI-124 | MI01-EOL | AMER | Closed | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | fuel controller - uplink is labelled with the name of the panel, not the upstream switch + port. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629795&prj=611&rqi=IrZuAThnhcC8rV6vfRxqtZSwdX
GI-119 | MI01-EOL | AMER | Closed | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Ethernet to both MSB K + MSB L PLC's not labeled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629789&prj=611&rqi=lkxpxS4Sn4ZGlJv6zPyIiftaGm
GI-120 | MI01-EOL | AMER | Closed | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | TGW and associated ethernet inside day tank controller not labeled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629790&prj=611&rqi=Sti5jkXSm1FNFLMQcHSzESWBwH
GI-123 | MI01-EOL | AMER | Open | P2 Medium CX | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Commissioning Issue | Commissioning | [6 empty] | loose cabling, open raceway, and ethernets using couplers - not home runs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629794&prj=611&rqi=tSAwdfEFSvmlRF7Ewgz0LBEBNu
GI-121 | MI01-EOL | AMER | Closed | P2 Medium CX | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Inside K Block HMI - ethernet cable too long, not labeled, and pulling weight on the Power Connection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629791&prj=611&rqi=nh2BC0gD9Vd2IJAOrWLQ7qMI9l
GI-122 | MI01-EOL | AMER | Closed | P1 High CX | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Commissioning Issue | Commissioning | [6 empty] | Free hanging wires with ends using tape inside the MSB K | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629792&prj=611&rqi=3MB6nWtB5K07ZSgy0VctzOKubR
GI-117 | MI01-EOL | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-07-14 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | When navigating - Floor Layout - > Electrical Room -> 2nd Floor -> West Electrical Room There are items in data loss, and a large daytank in the wrong place. See attached screenshot | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629233&prj=611&rqi=VBPtQWVQKpJ7kyEzjq8Dsraf6O
GI-116 | MI01-EOL | AMER | Closed | P3 Low CX | lily.perrette@veolia.com | 2026-07-09 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | MV-3 relay getting com alarm, and PHS can't bing it, PHS has been able to bing it but stop communicating , can see PQM, | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628598&prj=611&rqi=8BJz3oOnm83fEWbyW5EzUVruFU
GI-114 | MI01-EOL | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-07-08 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Duplicate entries for MSB PQMs exist in SmartView. Please review all SmartView assets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628441&prj=611&rqi=QAQgQA28W7TfJxMhCSzs2ooO43
GI-115 | MI01-EOL | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-07-08 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [6 empty] | Maintenance mode is not syncing between Aveva assets and SmartView assets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628442&prj=611&rqi=OTeuRSm9PulXDtXHbdb5gh302d
GI-113 | MI01-EOL | AMER | Closed | P1 High CX | sdetardo@equinix.com | 2026-07-08 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | [6 empty] | MSB Main Switchgear compartment has high noise and is vibrating the enclosure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628439&prj=611&rqi=dEBTUHJVKQxD6mgry6S2hTC159
GI-111 | MI01-EOL | AMER | Open | P2 Medium CX | sdetardo@equinix.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment failure | Commissioning | [6 empty] | All battery strings have certain batteries in WARNING and 1 now Critical. K1: 2 Warning K2: 1 Critical ; 6 Warning L1: 11 Warning L2: 6 Warning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627592&prj=611&rqi=Q0TjGnI5eg64FWFmScTE9L2Ojv
GI-112 | MI01-EOL | AMER | Closed | P1 High CX | sdetardo@equinix.com | 2026-07-01 04:00:00.000 +0400 | VER - Vertiv |  | Commissioning Issue | Commissioning | [6 empty] | On K2 UPS HMI - The IOB Breaker is labeled MIB. All other UPS's are correct | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627594&prj=611&rqi=zapp3N0c0nDcZBdqAPH7P7lhtY
GI-106 | MI01-EOL | AMER | Closed | P2 Medium CX | sdetardo@equinix.com | 2026-06-18 04:00:00.000 +0400 | Controls Contractor |  | Labelling | Commissioning | [6 empty] | CAT6's are not labeled inside Control Panel CP-2W-01, in addition PLC does not have an IP address or identifying NAME | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625896&prj=611&rqi=xch8JiSeX2qAcOXQmQFkr50Jog
GI-105 | MI01-EOL | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-06-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [6 empty] | Controls cabinet "CP-2W-01" is missing schematics inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625895&prj=611&rqi=f3lRVYxs6F1JnyAPD5l9dUA0Tb
GI-108 | MI01-EOL | AMER | Closed | P2 Medium CX | sdetardo@equinix.com | 2026-06-18 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | [6 empty] | Permanent Labels on breakers on SCC-R are missing for feeds down to 2nd floor UDP R's | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625904&prj=611&rqi=mUhZqwwwbGvhahb6HrjE8m8f21
GI-107 | MI01-EOL | AMER | Closed | P2 Medium CX | sdetardo@equinix.com | 2026-06-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [6 empty] | WING Wireless extender is not permanently installed in any type of enclosure. Device is exposed to high heat and conditions of engine room. Wires are hanging . Unit appears to be still in "testing phase" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625897&prj=611&rqi=3NfhUeH1V43mBIV1zAogkDLUaJ
GI-109 | MI01-EOL | AMER | Closed | P1 High CX | sdetardo@equinix.com | 2026-06-18 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | UPS Faceplate has Battery Remaining Time in "Seconds" -- value given "22" - is actually minutes - see screenshot | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625911&prj=611&rqi=K6ToqLvYQOiBm18hzN5XQZJYKI
GI-103 | MI01-EOL | AMER | Closed | P1 High CX | sdetardo@equinix.com | 2026-06-17 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment failure | Commissioning | [6 empty] | 3 of 4 crahs in the electrical room did not restart after a utility hit. The units were stuck in "Remote OFF" Power cycle of the 480v switch reset the hmi and the units restarted. It was addl discovered that the internal UPS is not holding on these 2 units as the controls should have stayed on when the 480v was killed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625738&prj=611&rqi=tZnW0hBTpEJDedYW7KR4ihiaXv
GI-104 | MI01-EOL | AMER | Closed | P2 Medium CX | sdetardo@equinix.com | 2026-06-17 04:00:00.000 +0400 | Electrical Contractor |  | Component/Equipment failure | Commissioning | [6 empty] | Perimeter Receptacles along the exterior colo wall (ex outside colo 255) have no power (northwest side) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625763&prj=611&rqi=LvUI4jfMiK8hkUqEUopSgJmthE
GI-101 | MI01-EOL | AMER | Closed | P3 Low CX | dustin.haugh@veolia.com | 2026-06-12 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning | [6 empty] | Generator D glycol leak from union pictured | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625096&prj=611&rqi=ZmNul6rd5P8zReQfnvSL2EHTLy
GI-099 | MI01-EOL | AMER | Closed | P1 High DCOS | sdetardo@equinix.com | 2026-06-11 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [6 empty] | PUE calc and popup do not take into account new blocks K + L | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625041&prj=611&rqi=xhGybbh8ZwU7SGoUozOsry0qrk
GI-097 | MI01-EOL | AMER | Closed | P3 Low CX | klemmens@equinix.com | 2026-06-10 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | BTUs connects to the network directly and then bringing in the point for general alarm via OPC. BUT screen disables when that is implemented. Please have this issue fixed with SE. We need to see the display. Assigned to Veolia for redirection of issue by DM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624789&prj=611&rqi=QUDBErBexnpLhR1DEPcDHi4MU4
GI-096 | MI01-EOL | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-06-09 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | We are missing a Power Overview screen that covers the K + L electrical equipment -SD 6/11 - reviewed screen - MSB-K and STS KR2 are listed twice, please review | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624582&prj=611&rqi=yCDJ4JAGQ78R7PgV3IDURr0PBM
GI-095 | MI01-EOL | AMER | Closed | P3 Low DCOS | sdetardo@equinix.com | 2026-06-08 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | On floor layout view for 2nd floor SE - the cage on/off button does not turn off cage backgrounds from background. Addl - cage layout has heavier line width and does not match other floor quadrants | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624342&prj=611&rqi=Mag5KAMiLg3K65lnrWHXkWqP2q
GI-091 | MI01-EOL | AMER | Closed | P2 Medium DCOS | samet.ozdemir@veolia.com | 2026-06-05 04:00:00.000 +0400 | Owner's Representative |  | Design correction needed | Design | [6 empty] | Installed ASCO solenoid valves on the fuel oil day tanks are not in compliance with the Equinix EBCS-1 standard in that the valve does not have limit switches or aux contacts providing positional feedback. The solenoid valves are also fail close valves because they need 24V to open. Conversations were held with Equinix project team on potentially replacing these valves. Equinix to provide direction. See attached photos for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624177&prj=611&rqi=qsabA8vGrWC6TNgIbD7l5cWZOi
GI-087 | MI01-EOL | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-06-05 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not complete | Commissioning | [6 empty] | Provide buckets for all chain valves in the generator and electrical rooms where needed. see attached photos and reference photo of bucket. Also relocate valve tags to the bottom of the chains for visibility. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624148&prj=611&rqi=ZHdGdl48zwuGPN3GlawVDRMrQo
GI-086 | MI01-EOL | AMER | Closed | P3 Low DCOS | samet.ozdemir@veolia.com | 2026-06-05 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment failure | Commissioning | [6 empty] | Leak detection was added in the generator room but cannot be tested due to single use ropes being installed. PHS to provide new rope since current one was wetted or supply new reusable rope if avalible. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624145&prj=611&rqi=CrpRmNkS6YQPQqyIxCQlo9eW6w
GI-084 | MI01-EOL | AMER | Closed | P3 Low DCOS | samet.ozdemir@veolia.com | 2026-06-05 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Ensure equipment on the electrical floor layout matches the same locations as the drawings. See attached snippet for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624140&prj=611&rqi=XFBWDIgRh0bQqpG33mXBY51CIu
GI-083 | MI01-EOL | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-04 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | [6 empty] | 2UDP L1: orange wire labeled Phase A&B not landed on breaker PDU 21-25 /2E10. Unsure of leadâ€™s purpose, but it is dead ended inside the cabinet.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624134&prj=611&rqi=mXAAKDCdl8uT0tnc94jTgknZHY
GI-062 | MI01-EOL | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-03 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation Damage | Commissioning | [6 empty] | UDP-L-2 doors are misaligned preventing closure. Some doors are bent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623791&prj=611&rqi=jVTceyeGIcT9jdJuXN5CwPbC24
GI-063 | MI01-EOL | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-03 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | UDP-All equipment panel grounds not installed in various cabinets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623798&prj=611&rqi=mVlHMeuuAXJRNCdhbowx02gkZK
GI-061 | MI01-EOL | AMER | Closed | P3 Low DCOS | samet.ozdemir@veolia.com | 2026-06-03 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Objects on the BMS floor layout need to match the equipment location in the field. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623788&prj=611&rqi=0QgGhsDPKK6eAqAr98rG8IgfxK
GI-049 | MI01-EOL | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Incorrect Settings | Commissioning |  | equipment type |  |  |  |  | (Vertiv CRAHs) L4 CHWV fails closed instead of failing last/open. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623337&prj=611&rqi=kRxeQu2Qgpvo2sxMQnxSwEEfnt
GI-052 | MI01-EOL | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-05-28 04:00:00.000 +0400 | CMM - Cummins |  | Component/Equipment failure | Commissioning |  | equipment type |  |  |  |  | (All Glycol Pumps) L4 Pump overloads consistently trip when set to 11A. After review of pump amps rating, overloads have been set to 16A. To be retested and verified | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623401&prj=611&rqi=bwrvczYOMpB2n9xzd02hO0k4uw
GT1ELEC-2-001 | MI01-EOL | AMER | Closed | P3 Low CX | darren.thurber@veolia.com | 2026-05-27 04:00:00.000 +0400 | SCH - Schneider MV | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 2BTU-1 | BTU - Battery Tripping unit |  | SCH - Schneider | BTU - Verify metering is accurate. Provide points list for metering and alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623228&prj=611&rqi=N3oRmaD3w4UvcgXWhGiRxo6JHP
GI-039 | MI01-EOL | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-05-15 04:00:00.000 +0400 | CMM - Cummins |  | Design not as specified | Design |  | equipment type |  |  |  |  | (BOTH Gen Glycol Pump Skids) L4 When pump skid is called on, the selector will randomize between pump 1 and 2 to equalize lifetime wear. If a running pump fails, the other pump will be called on as a backup. Per Equinix design, this behavior needs to be modified such that pump 1 is the default, and only if it fails will pump 2 turn on. Cummins was directed from pump skid vendor to modify the wiring to the pump selector to conform to Equinix's SOO. The new wiring will default to pump 1, but will not call another pump on when pump 1 fails. Original wiring was left as is, Cummins is awaiting further direction from the vendor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621996&prj=611&rqi=PQIoS4VimkvVh5NNZOgtNFLkOm
GI-041 | MI01-EOL | AMER | Closed | P1 High DCOS | alec.dughi@veolia.com | 2026-05-15 04:00:00.000 +0400 | General Contractor |  | Component/Equipment failure | Commissioning |  | equipment type |  |  |  |  | (BOTH Gen Day Tanks) L4 Float level sensors give slightly inconsistent values between each other and between different trials. When float sensor is physically moved to top/bottom extremes of travel, signal received varies, and is not exactly 4-20mA (more like ~5 - 18mA) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622001&prj=611&rqi=VP2SBGX46KqQhKCbakRf0lgU60
GI-038 | MI01-EOL | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-05-14 04:00:00.000 +0400 | General Contractor |  | Component/Equipment failure | Commissioning |  | equipment type |  |  |  |  | (Gen fuel pump system) L4 Fuel is back-siphoning from each day tank to belly tank on the first floor. The fuel is suspected to be leaking through the solenoid valves FCV-01 and FCV-02, through lag pump piping and pressure relief valve, back into the belly tank. The pressure relief valves at the pumps were tightened from 0psi to ~80psi. This slowed down the siphoning issue but it still persists. Next step is to add check valves to the supply lines to prevent this backflow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621914&prj=611&rqi=KSXq0Ar4nN78ee8YzKziv7on8i
GI-037 | MI01-EOL | AMER | Closed | P3 Low DCOS | samet.ozdemir@veolia.com | 2026-05-11 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | The command / status of the day tank solenoid valves in the Aveva graphic did not match the faceplate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621127&prj=611&rqi=o3V3RUzDAOCyJNSsKv356OUyTr
GI-036 | MI01-EOL | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-05-08 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [6 empty] | B phase power feeder serving the day tank PLC was found to be loose. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621017&prj=611&rqi=jQrS8cehIWf0SS8eowCoUvCUCq
GI-034 | MI01-EOL | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | Provide permanent labels for all energized mechanical equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621015&prj=611&rqi=YWjnOLOQmNROnk4DTAe2U88U9b
GI-030 | MI01-EOL | AMER | Closed | P3 Low DCOS | alec.dughi@veolia.com | 2026-05-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | (DAY TANKS) L4 Day tank names are switched in BMS. "02240T00_2FDAYK_RAS_LT" should read "02240T00_2FDAYL_RAS_LT" and vice versa. No asset to link to, leaving as a general DCOS issue #fuel pump system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620566&prj=611&rqi=RNkdtZTd6rKIjXacdXAWrm8C3q
GI-031 | MI01-EOL | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-05-06 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | When the fuel oil pumps were in operation the pump CTs indicated the pump was not running. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620570&prj=611&rqi=RMQJz9kh6J08QXYKWJii9eBg5x
GI-029 | MI01-EOL | AMER | Closed | P2 Medium CX | samet.ozdemir@veolia.com | 2026-05-06 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 2nd floor day tank fuel oil pumps were found to be spinning the wrong way. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620565&prj=611&rqi=fwCZo4tKJqHDTX4fJSNK8T9rSM
GI-028 | MI01-EOL | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-04-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | Battery cabinet L-1 is missing jumper between battery cells.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620089&prj=611&rqi=cMUNL2m21svzKmvq2iREcjmdYE
GI-027 | MI01-EOL | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-04-23 04:00:00.000 +0400 | VER - Vertiv |  | Installation Damage | Commissioning | [6 empty] | UPS K1 broken connector.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619219&prj=611&rqi=4KHXd34RDaYtFrOGLcsaQIr8vn
GI-025 | MI01-EOL | AMER | Closed | P1 High CX | chase.negich@veolia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment failure | Commissioning | [6 empty] | Kirk key R32 broken off in RMU K.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618855&prj=611&rqi=mjrnW8bu9hYre50gnMQGAHN7ww
GI-022 | MI01-EOL | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-09 04:00:00.000 +0400 | Mechanical Contractor |  | Documentation not issued/Required | Commissioning | [6 empty] | Provide pressure test results for chilled water piping | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617665&prj=611&rqi=IVNrNrHaTbIpHWmU9pRzXLTREe
GI-023 | MI01-EOL | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-09 04:00:00.000 +0400 | Mechanical Contractor |  | Documentation not issued/Required | Commissioning | [6 empty] | Provide pressure test results for generator coolant piping (glycol loop) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617675&prj=611&rqi=1YPyUFUUxEcKQiSSCtFb7UjxN7
GI-019 | MI01-EOL | AMER | Closed | P3 Low CX | francis.callan@veolia.com | 2026-03-25 04:00:00.000 +0400 | Mechanical Contractor |  | Installation Damage | Commissioning | [6 empty] | Duct work inside battery room K has been damaged such that it causes safety concerns with the support able to fall. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616449&prj=611&rqi=nGu2lw58Pg2wWTcSBsCC97TgOx
GI-010 | MI01-EOL | AMER | Closed | P2 Medium CX | klemmens@equinix.com | 2026-02-26 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Missing Components | Commissioning | [6 empty] | CW181 should come with 40-50ft Leak detection rope per the standard MCE. Please confirm this will be delivered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352242&prj=611&rqi=5XSDLpCRPzCVT0tnwVahHPOP20
GI-004 | MI01-EOL | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-02-18 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation Damage | Commissioning | [6 empty] | Mismatched hardware on Schneider 400A breakers There are 3 different bolts that were used across these breakers stamped O1RL, SKS, and UH. All these bolts have different lengths. This might be causing some of the issues with stripping the threads. The common hardware configurations I noted are as follows: O1RL bolts are the most common and have 2 square washers and a Belleville washer. SKS bolts are longer and have 2 square washers, a Belleville washer, and a lock washer. UH bolts only have 1 square washer and a Belleville washer The Schneider documentation I found calls out M10 x 25 bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199485&prj=611&rqi=C38kmyEULj6LZQqeP5dpZSBIJf
GI-001 | MI01-EOL | AMER | Closed | P1 High CX | lily.perrette@veolia.com | 2026-01-26 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Component/Equipment failure | Commissioning | [6 empty] | MSB Sections not lining up - Electrician have run into issues with bus work with connecting sections, bus work is not lining up. We verified the sections are lined up in order and with correct MSB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197597&prj=611&rqi=Xto1vr1rqP1ViydEWTDfBKSQby
GI-006 | ML05-P1 | S-EMEA | Closed | P3 Low CX | stefb@straightlineconsulting.co.uk | 2026-05-08 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1-UDP-C-1 | UDP - UPS Output Switchboard |  |  | ELECTRICAL LV; Whilst investigating an excessive issue on the MLTX in this power string for an unrelated Issue, it was observed that excessive heat was detected on the Load Bank ACB Cubicle of the UDP. Whilst, at time of writing, this Asset is L4 Blue Tag Signed-Off, it may need to be taken back to a previous status, and defective parts replaced/ retested. The excessive heat has led to distortion of the internal PVC arc-flash separation. Clamps of the fixed part of the ACB appear to be not all identical and, during the load tests undertaken after reclosing the ACB and external panels, temperatures exceeding 80Â° were detected on breaker metallic parts. Also refer to attached EoR email. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620964&prj=619&rqi=ViBb8sWZOZxCGggr7Jd95hRaga
GI-005 | ML05-P1 | S-EMEA | Closed | P1 High CX | stefb@straightlineconsulting.co.uk | 2026-05-07 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1-MSB-C-1 | MSB - Main Input Switchboard |  |  | ELECTRICAL; LV. This Issue was originally raised against the Tx, but further tests on 07/05/26 have revealed that the E & I LV Busbar from the TX to the MSB is causing the problem. Refer to attached documents. The buzzing noise is being caused by the installation, clamping and torquing of the busbar connections onto the Tx secondary side. Previously raised Issue wording; Following completion of the TX L4 Blue Tag, and during 4 hour load burns on the final MV Cables 1-CBL-MV-014 and 015 (test dates 27/04/26 & 28/04/26:, the Tx started to make a noticeable buzzing sound once under circa 80% load; 2.0 MW. Casing inspections and thermal scans have revealed no issues, but the noise continues, for most of the time, when the Tx is under load. Thermal scans revealed low temperatures of 30-45 Degrees Centigrade; temperatures of no concern. SGB have requested that acoustic scans be conducted. 08/05/2026; RESPONSE ADDED; This Issue cannot be Closed as, following tests on 07/05/2026, a new Issue can be raised for E & I Vertiv responsibility, with further detail added. 29/06/2026; RESPONSE ADDED; Testing carried out and witnessed on 26/06/2026 confirmed that origin of issue was discovered and rectified, observed for 2 hour load test at 2MW - no buzzing sound observed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620940&prj=619&rqi=dRPomMzWXiwEDANWfQDzj6zVIl
BT1ELEC-5-001 | ML05-P1 | S-EMEA | Closed | P2 Medium CX | garyf@straightlineconsulting.co.uk | 2026-04-16 04:00:00.000 +0400 | General Contractor - Commissioning | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1-UDP-C-2 | UDP - UPS Output Switchboard |  |  | Electrical Communication failure with CB C1 feed from 1-MSB-C-1, this is a loss of communication that has happened post-L3 DCOS screenshots and appears to be a failure of the IFE module or the communication module itself. Closed 06-05-2026 With attached Screenshots 23-1 & 23-2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618522&prj=619&rqi=LIdPyf00kJ5N1e1iPU8ekvRtGv
BT1ELEC-5-002 | ML05-P1 | S-EMEA | Closed | P3 Low CX | garyf@straightlineconsulting.co.uk | 2026-03-25 04:00:00.000 +0400 | General Contractor - Commissioning | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1-UDP-C-2 | UDP - UPS Output Switchboard |  |  | ELECTRICAL 26/03/2026 Whilst completing DCOS screenshots for 1-UPS-C-2 Blue Tag, it was noted that the following CB's are not reporting correct data from the trip unit â€¢ 1-UDP-C-2 - LOADBANK CB (see attached image) â€¢ 1-UDP-C-2 SUPPLY FROM 1-UPS-C-2 CB (see attached image) 27/03/2026 On review of SE DCOS response to this issue, it has been reassigned to E+I for corrective works. 30/06/2026 Schneider / E+I engineer attended site to make correction to power sign wave direction settings using EcoStructure software on 1-UDP-C-2 - LOADBANK CB - works complete on this breaker, report and screenshots attached in responses. Breaker 1-UDP-C-2 SUPPLY FROM 1-UPS-C-2 CB - issue still not resolved, breaker not communicating with software. E+I to issue report and recommendations (replace breaker / replace module) 07/07/2026 issue with breaker 1-UDP-C-2 SUPPLY FROM 1-UPS-C-2 CB has been identified by Vertiv. Replacement Micrologic module recommended and scheduled for installation with verification of correct data being reported. Clear close-out scope of works identified and arranged. Issue priority to be down graded to P3 Low, issue will be closed following the remedial works and associated CX report. 17/07/2026 Schneider / E+I engineer attended site to replace breaker micrologic module (NSX630N 5.3E Micrologic) and confirm connectivity to communications, make correction to power sign wave direction settings using EcoStructure software on 1-UDP-C-2 - SUPPLY FROM 1-UPS-C-2 CB - works complete on this breaker, report and screenshots attached in responses / documents. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616499&prj=619&rqi=2ShdmHOjdk9c8f6I6AR0yvyq40
BT1ELEC-1-001 | ML05-P1 | S-EMEA | Closed | P1 High CX | garyf@straightlineconsulting.co.uk | 2026-03-18 04:00:00.000 +0400 | General Contractor - Commissioning | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1-UPS-C-1 | UPS - Uninterrupted Power Supply |  |  | Electrical Date: 19/03/2026 Whilst completing the blue tag testing of 1-MSB-C-1, test 2 of the E+I test script requires a mains failure from RMU-C. 1-MSB-C-1 PLC then completes a transfer from Utilities supply to Generator supply (test completed at 2MW via building Load Bank). Once supplied by 1-GEN-C-1, the UPS exhibited voltage fluctuations (see attached images), which caused the rectifier to shut down and the UPS to reject the load. This test was repeated at a reduced load, and the same occurrence was observed; see the attached images of the Voltage relay in MSB-C-1, indicating both over- and under-voltage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616019&prj=619&rqi=yPHDltk4QegEcDBwfdBkfFZull
GI-004 | ML05-P1 | S-EMEA | Closed | P3 Low CX | stefb@straightlineconsulting.co.uk | 2026-02-05 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1-RMU-C | RMU - Ring Main Unit |  |  | ELECTRICAL; When replacing the Microswitch components in Loop 2 cubicle, a small fixing screw was not fitted as it was not to hand. Refer to attached, marked photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198683&prj=619&rqi=zRQu9Mba0JmL5L5M4eLzKjNXbW
GI-002 | ML05-P1 | S-EMEA | Closed | P1 High CX | stefb@straightlineconsulting.co.uk | 2026-01-19 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1-RMU-C | RMU - Ring Main Unit |  |  | ELECTRICAL; On Tx Feeder Cubicle 3, the mechanical mechanism which operates the microswitch broke during operation, and requires urgent replacement. At present, with the circuit breaker Closed, the microswitch is sending an Open signal. With this being a major safety Issue, the RMU has been shut down and isolated. Temporary remedial works are to remove the corresponding component from Cubicle 2 and fit into Cubicle 3, whilst awaiting new replacement parts. This is to be undertaken ASAP. The defective component is to be removed and sent to SE MV R&D Department for urgent analysis and RCA. 10/02/2026; Updated RCA now attached, so this issue can now be Closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197149&prj=619&rqi=6iXxMN1KHeN5DpAuqfrCgHlDJV
YT1MECH-27-001 | ML05-P1 | S-EMEA | Closed | P3 Low CX | stefb@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1-CRAH-C-18 | CRAH - Computer Room Air Handler (CHW) |  |  | Mechanical; During the 5 bar pressure test on 13/01/2026, a very slight weep was discovered on one of the welded joints. Note that this pipework was installed some years ago in Phase 1. 15/01/2026; Pressure test re-conducted, witnessed and passed. Issue Closed. Refer to Observation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196854&prj=619&rqi=Cxr5FldWWfFJb5dH00jDhOBGTN
GI-001 | ML05-P1 | S-EMEA | Closed | P3 Low CX | garyf@straightlineconsulting.co.uk | 2026-01-08 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1-UPS-C-1 | UPS - Uninterrupted Power Supply |  |  | There are a number of paint work defects identified on 1-UPS-C-1, see attached images as examples that were identified 16/101/2025 The paint work defects will be addressed by VERTIV once the L4 Blue Tag commissioning has been completed and this issue will be closed. 26/01/2026; Repairs inspected and Accepted; Issue Closed. Very Well Done. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196631&prj=619&rqi=TafkRTcuhTJfJzu23N2puSaqVg
WGR-1-002 | ML05-P1 | S-EMEA | Closed | P3 Low CX | garyf@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | DELIVERABLES | Commissioning Issue | Commissioning | Multi-Discipline | equipment | Room 114 - UPS Room | Room Readiness |  |  | ELECTRICAL; MV & LV Schematics have not been positioned within the switchroom | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196493&prj=619&rqi=ELjE9LkACF9LInK18PcLV2YQYt
WGR-1-001 | ML05-P1 | S-EMEA | Closed | P2 Medium CX | garyf@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | DELIVERABLES | Commissioning Issue | Commissioning | Multi-Discipline | equipment | Room 114 - UPS Room | Room Readiness |  |  | Fire stopping of 1 No. Earth Cable leaving the UPS switch room to go to the Battery Room. 12/02/2026; Accepted and Closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196490&prj=619&rqi=szgA8YmAZzqQAgxav8y1smKehW
WGR-1-003 | ML05-P1 | S-EMEA | Closed | P3 Low CX | garyf@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | DELIVERABLES | Commissioning Issue | Commissioning | Multi-Discipline | equipment | Room 114 - UPS Room | Room Readiness |  |  | Fire stopping of 1 No. Earth cable leaving the UPS switch room (underneath raised access flooring to the right of the earth bar) is to be completed. 12/02/2026; Accepted and Closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196552&prj=619&rqi=fj1xo3ODy6Gddop1mPVkctliA4
YT1ELEC-32-002 | ML05-P1 | S-EMEA | Closed | P2 Medium CX | stefb@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1-MSB-C-1 | MSB - Main Input Switchboard |  |  | ELECTRICAL; There is an earth connection that has not been terminated underneath the MLTX, which is connected to the MSB earth bar. Vertiv/ E & I to address and Close ASAP. This Issue was originally raised against the MLTX L2B Yellow Tag (issue #11), but as Issues cannot be transferred to other Asset's once raised, we could only Close it, and create this new Issue on the MSB, 12-01-2026 UPDATE; Earth cable removed, so Issue can now be Closed. Refer to photos attached to Response. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196559&prj=619&rqi=zCt8YqrstVpSI9WrBnfDag4ZLv
DCIML4-2-001 | MT01-3 | AMER | Closed | P3 Low CX | Jonathan.Calotes@jll.com | 2026-08-31 04:00:00.000 +0400 | DCOS - Equinix | L4 | Commissioning Issue | Commissioning | Integrated Automation | system | DCIM |  |  |  | EQX working on Modbus license for MT1-03 for JLL access | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636135&prj=622&rqi=b6cUYVZFrgawnPOhVzeXlOBfv3 | https://equinix.facilitygrid.co.uk/x/project/622/system/12546
GI-003 | MT01-3 | AMER | Closed | P3 Low CX | piotr.sosniak@jll.com | 2026-08-24 04:00:00.000 +0400 | Mechanical Contractor |  | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | system | Chilled Water |  |  |  | Provide TAB Plan for chilled water and air systems. Include Flow meter calibration, pump curves, DP initial settings, DP final settings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634932&prj=622&rqi=j6bMShtfjOMvk8wAsPJdBne76a | https://equinix.facilitygrid.co.uk/x/project/622/system/14872
GI-002 | MT01-3 | AMER | Closed | P2 Medium CX | Nathan.fu@jll.com | 2026-07-15 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not complete | Commissioning | [6 empty] | The chilled water pump vibration was still observed during the test on July 15, 2026, even with the new VFD settings implemented. The field testing team believes the vibration appears to be from the fluid flow in and out of the pump rather than from the pump motor. The Smardt team has reported this issue to Armstrong and Kolostat, and both parties will follow up and investigate accordingly. Updated to July 17, 2026 (JLL): Armstrong technician is suspecting an issue with the coupling between the motor and pump shafts. He's requesting replacements and should be back on site to install them., Smardt will work with Armstrong next week to plan this. Smardt is hoping to get them to address this issue first thing when the site is operational again in a couple of weeks. From their experience with Armstrong, replacing the coupling is fairly quick | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629423&prj=622&rqi=V8KK1GfEHCRUdJTdJ3vHhtKwGL
GI-001 | MT01-3 | AMER | Closed | Outstanding Paperwork/Documentation | amirreza.barekatain@jll.com | 2026-06-29 04:00:00.000 +0400 | Electrical Contractor |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | - Missing certificate of calibration of phase rotation >> OK | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627289&prj=622&rqi=2acU34IP5gGF3PJI6gOOFgXG9S
DCIML2B-1-001 | MT01-3 | AMER | Closed | P3 Low CX | roozer.samuvel@jll.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2B | DCOS Design Issue | DCOS | Integrated Automation | system | DCIM |  |  |  | During the SFAT brief, it was identified that the alarm banner around the chiller graphics is missing from the BMS manager interface. This may be due to the site operating on older Aveva standards that do not include this alarm banner functionality as part of the standard configuration. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626571&prj=622&rqi=BDGiTTq8UF1RYtotGHlTdrGunE | https://equinix.facilitygrid.co.uk/x/project/622/system/12546
RT1ELEC-44-002 | MT01-3 | AMER | Closed | P3 Low CX | amirreza.barekatain@jll.com | 2026-02-08 04:00:00.000 +0400 | Engineer | L2A | Design correction needed | Design |  | equipment type |  |  |  |  | missing some cable specifications on cable schedule E720. BA1-C56 -- E602.6; PDUA1-1-1 BA1-C57 -- E602.6; PDUA1-1-1 BA1-C68 -- E602.6; PDUA1-1-3 BA1-C84 -- E602.6; PDUA1-2-1 BA1-C89 -- E602.6; PDUA1-2-2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198758&prj=622&rqi=7Iwr3pxc98pzyuiqdS6TpCxC8v
GI-106 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Insulation to be installed on incoming portable water connection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637127&prj=643&rqi=v8EuojNDmp8is9RYm5637YR0sD
GI-078 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Modbus module on all VFD to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637094&prj=643&rqi=OKKRVv3PdP79oOvxFQA5EMvo23
GI-079 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ All fuses in chiller and electrical panels to have a small key installed on the inside door explaining their size and purpose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637095&prj=643&rqi=NMsUpoBQv0BRQFEXJPYQ4DHHwm
GI-080 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ PCRSBâ€‘Fâ€‘1 primary injection results missing for chiller supply breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637096&prj=643&rqi=KYAFsYACsQYNGoZd5fgqb1mo7u
GI-081 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ PCRSBâ€‘Fâ€‘1 aux and section D3 missing on schematic | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637097&prj=643&rqi=bz0btF39ULKSowjyFIjTMmJDNy
GI-082 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Tags missing for valves | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637098&prj=643&rqi=RysfyUbzM8q8Z7vs3vV3MKfBvS
GI-083 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Tags missing for equipment (please reference latest approved P&ID) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637099&prj=643&rqi=gqEOzDIju2z7IEdwX1su7u5klE
GI-084 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Tags missing for instrumentation (please reference latest approved P&ID) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637100&prj=643&rqi=5c9OV9s0R6VTLSfGE7I6NU228P
GI-085 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ The approved size of the external Uniâ€‘Strut supporting the AC unit is longer than the specified dimensions; an asâ€‘built diagram must be sent to Mercury Design to verify there are no clashes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637101&prj=643&rqi=XvNP0fTTFkZ4keyuEGL3zVy4n0
GI-086 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ PPU dimensions must be laserâ€‘verified and Hamzah must supply evidence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637102&prj=643&rqi=3PGX7Gkgt3wnsGTmTcIQWdxOEm
GI-087 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Nozzleâ€¯4 external flanges are 30â€¯mm higher than the 3090 actual dimensions; Armstrongâ€™s asâ€‘built drawing must be sent to the MER team. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637103&prj=643&rqi=FhUY5i5ImgbtRLHMShfPqgxHta
GI-072 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller â€“ cannot verify fuses F3, F4â€¯&â€¯F6, F7â€¯&â€¯F1 as no sizes on schematic | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637084&prj=643&rqi=tAdxX6rWNn5v2Gr8kG17w4mjHX
GI-073 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ No way to secondary injection settings on breakers on both switchboards and chiller (this can be verified at L2B onsite) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637085&prj=643&rqi=X1t7D22UY0ScxNqgQe9XO60J65
GI-088 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Nozzleâ€¯1 andâ€¯2 flanges show 500â€¯mm but actual measurement is 550â€¯mm; Armstrongâ€™s asâ€‘built documentation must be sent to Mercury Design. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637104&prj=643&rqi=lEg3koTu6Xph3fG1Pw8JL2Dszs
GI-090 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation Damage | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Both vessel lagging must be repaired. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637108&prj=643&rqi=U1Pjiz4UwV6K2LV5SaGzjTlffY
GI-091 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ All NDT and test reports for the chillerâ€™s refrigerant system must be sent by Aermec. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637109&prj=643&rqi=w0UdW28AM4h24ALy8xPfTk1wxV
GI-074 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller â€“ temperature sensors have been packed with silicone | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637089&prj=643&rqi=eL1mzVQBiXU2yMyAmvERcUuwa7
GI-089 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Nozzleâ€¯3 andâ€¯4 flanges show 750â€¯mm but actual measurement is 761â€¯mm; Armstrongâ€™s asâ€‘built documentation must be sent to Mercury Design. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637107&prj=643&rqi=gzwHUC6d7Fo3VDRq7zgkhcMOne
GI-075 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller â€“ cable management under chiller and to compressors needs tidying up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637090&prj=643&rqi=KPB2QheoTphETCZLt5HO9AJPrI
GI-092 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller lifting eyes must be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637110&prj=643&rqi=JtWpWPsCO04qq6n0f267bjuRJT
GI-076 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller â€“ cable stuffing glands not tight (under chiller and compressors) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637091&prj=643&rqi=eNp2bC5lTZNJ1MmJ3eHbj1ByUG
GI-077 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Schematics to be installed on wall (P&ID, both switchboards) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637092&prj=643&rqi=oaL5mOdXAURkmOskWtivCEkUIf
GI-093 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Technical data sheet for bellows must be sent and reviewed against installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637111&prj=643&rqi=Bi3FvOb7UCKchVgxNEA8fYccIM
GI-094 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Torque required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Torque reports and any calibration certificates for all flanges, bellows, etc., must be supplied. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637113&prj=643&rqi=r3bfnQg0xXpmeOrlWbIz3acIsY
GI-095 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Labelling | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Both HVAC fans must be labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637114&prj=643&rqi=JgQCjPMd3HH4x2t1lGxQ8R52r5
GI-096 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Confirmation regarding the proper operation of the check valve is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637115&prj=643&rqi=rxWkag1gDBOaF780ljnfNddtM5
GI-097 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Leak detection was not installed at the time of FWT. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637117&prj=643&rqi=HoGMa1pZfdgaYXC4kel7nki7RA
GI-098 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ The floor is not painted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637119&prj=643&rqi=iWcI0hqqZkCnhi4frayXd5Vr0O
GI-099 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation Damage | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Plinth painting is damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637120&prj=643&rqi=wWjjYh5UhnmpG5SaCIofWPINcg
GI-100 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ A drip tray must be installed below the portable valve and above the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637121&prj=643&rqi=qXrDA2Gwf53CVtpCufvk5K1FPF
GI-101 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Valves after the sockets must be installed for each 3/3 flow meter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637122&prj=643&rqi=N23UpnGZ5GD7kZ1uOgKbC3SV1s
GI-102 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ The pneumatic test report must be accompanied by a markedâ€‘up schematic clearly indicating the tested sections. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637123&prj=643&rqi=apVBxgIKm8uVEZ19w4TYStxa05
GI-108 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Condensate pipework to be completed prior to shipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637129&prj=643&rqi=j1paLhpCT8VsC8kYdMFDTW7hTM
GI-109 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 :Chiller - pipe insulation to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637130&prj=643&rqi=e45fE2oSoGufdZITopA2VuGpHJ
GI-107 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Pipework to be capped prior to shipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637128&prj=643&rqi=oIuxuCgv8tLv52QGWaYCfWdUJ2
GI-110 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Cleaning | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 : Chiller and all container requires a final clean prior to shipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637133&prj=643&rqi=1xCuyf67PGa0NafXBHDfEwB8P6
GI-103 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Support clamps for the two vertical copper discharge lines from the safety valves are required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637124&prj=643&rqi=v0YIune2bv0ecisImzWzp3kqLR
GI-104 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ The chillerâ€™s cable runs are leaning against copper pipe; ensure these are correctly secured and not touching any pipework. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637125&prj=643&rqi=x30wHpOmA4cuCFB8kpbRX7Vyrc
GI-105 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Verification throughout FWT P&ID was an old revision â€“ please reâ€‘upload the latest revision for review | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637126&prj=643&rqi=V7N4aw9tpaH7Xw9v3ZC7GVsacs
GI-111 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Labelling | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 Tags and labels missing for pipework (glycol) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637134&prj=643&rqi=hhd4mWzVORU4oOQnur14U2Vc4y
GI-112 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Labelling | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Tags and labels missing for pipework (flow direction) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637135&prj=643&rqi=elkMCSmEAiXTr4prysHJ4nz2o0
GI-060 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Cable bone tags missing from 1PCRSB_F_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637069&prj=643&rqi=3NKjLduFwOogqUWtVQ8ugsZMbL
GI-069 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ 1DCOSâ€‘RIOâ€‘05 no torque markings on the frame bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637080&prj=643&rqi=1bFtZ4DLLZXXtSvt4zkUTDqXg5
GI-068 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ No entry for DCOS cable in UPCRSBâ€‘Fâ€‘10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637079&prj=643&rqi=CjV2rOvBkELjQWlIw06wOMD9sS
GI-065 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Paint damage on heatâ€‘exchanger frame | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637076&prj=643&rqi=J3D7bt8KOtagSgnHqDfdEFOBAS
GI-064 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Gland plates to be earthed on pump isolators | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637075&prj=643&rqi=4RnxX1AncUrdEe51GSdf55j8b1
GI-062 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Earth bar to be colourâ€‘coded Green and Yellow | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637071&prj=643&rqi=EPJ7EOqhucryYZvX7qIs56YAH7
GI-061 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ 1PCRSB_F_1 400â€¯V labels to be changed to 415â€¯V | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637070&prj=643&rqi=LGYe1eqGfSGUsQXm2eTnDRb3ou
GI-067 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ No Roxtec transit frame installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637078&prj=643&rqi=CnMtaPOp1FoIy6Sar6T9XLMPf0
GI-071 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ External louvre not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637082&prj=643&rqi=UzTqUFLDyUqlR3TsRS2VpJbUVq
GI-058 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Pump isolators â€“ 400â€¯V labels to be changed to 415â€¯V | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637067&prj=643&rqi=d0wHqbMJa2EhQkZGjgyivZt9tY
GI-063 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Earth straps to be installed on all flanges | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637072&prj=643&rqi=BF3sAr3OTAW2QZcmmGT5kx9Ee1
GI-059 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Grommet trip protection missing from tray work | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637068&prj=643&rqi=jZyn8KrjiITWwr7yguBfMEgKJV
GI-057 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Pump isolators â€“ missing internal shrouds to ensure IP2X protection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637062&prj=643&rqi=guf0TfzLJ2Ias4vFMggKTWvW2U
GI-070 | MU04-3 | N-EMEA | Open | P1 High CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller â€“ incoming cable not connected to earth | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637081&prj=643&rqi=z3b99U5NPHMNaOYLlV13RGP0yG
GI-066 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | AER - Aermec |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ UPCRSBâ€‘Fâ€‘10 metal tieâ€‘wraps inside panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637077&prj=643&rqi=2B8ZjBkvc6fjAAhNNSDbn6iVy6
GI-051 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation Damage | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller insulation was damaged in small amount of areas. Can you please rectify? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636882&prj=643&rqi=39QPlY0ajibIASp65ZIVbag9t4
GI-050 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Dosing pots have pipework installed at high level, running above electrical equipment. Can you please review this and provide solution to protect any electrical equipment from potential exposure of liquid from these pipes? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636881&prj=643&rqi=vYssBNnYNWdwlWpWyH1oSS6HHa
GI-047 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ There was a slight misalignment of bellows, manufacturerâ€™s confirmation to prove install is sound | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636873&prj=643&rqi=6yje7Vq5dLXkYthAqg5pVOngng
GI-045 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Flow meters have not arrived and it is the clientâ€™s concern that these will cause issue at flushing stage, for example, rather than installed before sending it to the project. Flow meter pockets are left at 90Â° horizontal for these to be installed. Please check with manufacturer if this is acceptable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636869&prj=643&rqi=2PZdmtPFveDaOfz7jh4wq3DzOO
GI-046 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ There is a requirement in script to prove that when multiple and identical assets are being used, it is important to prove that these are not from the same manufacturing batch. Please provide evidence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636871&prj=643&rqi=SLhGA1gKOYXToGBH6bVSNQK38K
GI-055 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ There are HEX bolts yet to be protected by foam | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636892&prj=643&rqi=P9afrS6KSeXkPLTiohn48flU8i
GI-053 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ There are still some opening to be cut into the structure/wall of plantroom. Please complete and provide evidence of works and include QA cleanliness checks following completion | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636889&prj=643&rqi=b63NMgVk2tphMQxXxvP2FU20pV
GI-042 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“Covers to be fitted on studded rod hangers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636864&prj=643&rqi=ICBjPjen0aaHKeDegBYChp1uy4
GI-049 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ There is bund installed within area protecting electrical equipment from any liquid exposure during leak incident. Bund area also prevents any leak from plantroom. Please confirm how this is tested or ensured that bund area will hold water following floor being drilled to mount plantroom equipment and all welding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636878&prj=643&rqi=dUI2tteUT82zr3WqfLljniBq8n
GI-052 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Condenser side of chiller has no bellows fitted at point of connection with pipework. Confirmation is required that this is correct | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636883&prj=643&rqi=u3ibFiLg44tcgDx1JVwq6XOMqo
GI-044 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Labelling | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ General: Equipment labels are to be installed, while matching PIDs: Missing Trafolyte labels of Pumps Missiing traffolyte labels for VFD Missing labels on Pump Isolator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636868&prj=643&rqi=tYJg1QCVjNXJ6X2zFRAPoaWKyS
GI-054 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Buffer vessel and other piece of equipment requires to be bolted down. Confirmation will be required that equipment located within bonded area had correct procedure applied ensuring water bund was not compromised. Expansion tank - Not fixed to floor Buffer vessel - Not fixed to floor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636890&prj=643&rqi=g7v58HJ8B4mK6B8oXwhgWI1LQE
GI-056 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller has a number of small water valves with no end plugs. Please install to prevent any accidental leak in future | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636893&prj=643&rqi=dAHYNpXMHPfG2BQS1XM4G73Mae
GI-043 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Tags and labels missing for pipework (water) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636865&prj=643&rqi=wxfZLdBs6uCFrpKDolNBvcPBDj
GI-048 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Dosing pots are missing end caps/plugs at the bottom valve used to discharge liquid from pot itself | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636876&prj=643&rqi=vsvP7QMBc9QWM6PFi02O4bdxIV
GI-038 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Points list to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636830&prj=643&rqi=EmIrpqxBWsZfys8CSAMhMy7JOU
GI-041 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Update PID with correct model number of HEX | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636836&prj=643&rqi=WSaKmcvO3sJH5dEqAPrCHBIPLG
GI-040 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Incomplete Connections | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Water discharge pipes from Pressure relief valves are to be mounted securely | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636832&prj=643&rqi=LKgwtqHwaH47iRMgQxdZ0HGfby
GI-039 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | General Design Issue | Design | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ MU043â€‘RHKâ€‘XXâ€‘XXâ€‘SPâ€‘Mâ€‘XXXXâ€‘7110 â€“ CHW Buffer tank specify that buffer tank shall have inspection hatch. Buffer tank within PPCR has no inspection hatch. Can you please clarify if this was agreed? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636831&prj=643&rqi=aEkCrTpkFZdACDiHQoEhhdi8NN
GI-037 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Number of test packs were provide, and some were yet to be provided. Test Packs are to be compiled and complete where required. Calibration certs to be included | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636829&prj=643&rqi=Ljp5y3bnjdJm34PVJnalfHRdzI
GI-036 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Cleaning | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ General Cleaning shall be carried out following completion of all installation. Swarf, debris, dust shall be removed from plantrooms, any panels and equipment prior shipment. This is particularly important prior to any energisation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636827&prj=643&rqi=X5XGae7Rz7DexnEc8YBHpsnfua
GI-035 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Ensure any missing panel dimension drawings, wiring diagrams are provided within panels or attached to equipment before leaving factory. Ensure all panels have a documentation holder aa well. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636826&prj=643&rqi=ORVxh1fW5M8oukIC92XfN9IzcP
GI-034 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ MU043â€‘RHKâ€‘XXâ€‘XXâ€‘SPâ€‘Mâ€‘XXXXâ€‘7002 â€“ Pipework insulation states in pointâ€¯5 of additional comments that: All internal pipework that is indicated as â€œnot insulatedâ€ shall still be insulated inside the building after penetrating the outer wall over a length of minimumâ€¯2â€¯m to avoid cold bridges and condensation. Currently there is no insulation applied and it was understood that no insulation will be installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636825&prj=643&rqi=SXLMNrUWbRadVkS0maEvjP2STG
GI-033 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Please review isolator switch panels. When isolator is used to deâ€‘energize equipment, opening the panel door poses a risk as incoming power is still live, while there is no physical restriction to touch live terminals/cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636820&prj=643&rqi=ACblKkRcstVa7B5JCFOwkQszEV
GI-032 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Minor installation works are ongoing, and some of the kit is yet to be bolted down; ensure the bund area remains waterproof | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636819&prj=643&rqi=a1yZJDgQfQdzhKvqANDA6jbeb4
GI-031 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCR FAT module 6 : The Unistrat channels have sharp edges that lack protective covering. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636809&prj=643&rqi=EljygxQAIPxRX4xguSAbsYe8mo
GI-021 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT: Trip hazards are not marked throughout the pump room, creating a risk of falls. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635558&prj=643&rqi=H47YGZeDuOIU8AnQutVAPCXzFq
GI-020 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT: The WCC PRV pipework contains an unfilled hole. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635557&prj=643&rqi=VKWkXFpC70IaWVfc1juxDtJQb9
GI-002 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | The PPR system has no earth bonding on the main structure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635290&prj=643&rqi=n8SHXW8nJzauy2SZKfMxVGHwf9
GI-017 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPR-FWT : The exhaust fan has not been installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635553&prj=643&rqi=azjjoOKcv1Vo4KGvScWHetCIsS
GI-018 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Cleaning | Commissioning | [6 empty] | PPR-FWT : The waterâ€‘cooled chiller is extremely dirty. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635554&prj=643&rqi=9WR48qyNJoAnizD47z7iwux4aN
GI-013 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR- FWT : Sheet metal on base not secure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635548&prj=643&rqi=VxsaSloqg4OXqs8mSOmktYNAkO
GI-019 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT : The DX unit installation is incomplete because the cable tray requires a notch cut out and the pipework lacks sufficient lagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635556&prj=643&rqi=hdFIjnIozMBvddeG32mNcfyADu
GI-012 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR -FWT : Pump glands are loose and incoming cables lack proper labeling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635541&prj=643&rqi=TAgPuQD27vgmH9ROnWHLxaDURC
GI-030 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT: Cable terminated incorrectly, no torque marks, no bonding on frames. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635577&prj=643&rqi=ohU167V0TO4hdslFQUbiNWFQYV
GI-029 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT: DCOS cables require termination into WCC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635576&prj=643&rqi=hRXgn5btoByrXjZMKLEujuFM1h
GI-003 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | During the FWT of the PPR systemâ€™s, it was observed that the DCOS panel is fitted with a UK socket, which fails to meet EU electrical standards. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635293&prj=643&rqi=uFXmy2OVcnlUoKSjCI6VeBOovz
GI-016 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT : The WCC lifting anchors are no longer required and must be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635552&prj=643&rqi=IuOLUzYeCMd5pd1f3ituQuMHno
GI-014 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT :The expansion vessel is not secured to the system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635549&prj=643&rqi=4DmG3lRJKEU1Rosr31FpBLLDOf
GI-008 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPR-FWT : Valves lack clutch clips, preventing proper mechanical engagement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635336&prj=643&rqi=Mt4xBGPC1CxeWEhSXcwVuZnvYK
GI-005 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Torque required | Commissioning | [6 empty] | PPR-FWT : The DCOS panel lacks torqueâ€‘marking on its earth connection, making it difficult to verify that the earth bond is tightened to the required specification. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635327&prj=643&rqi=bnVQtCxrKn1rJqckbw9xOpKhPW
GI-028 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT : Mains cable on VFDs not secure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635575&prj=643&rqi=S8QCRfmcetzAJYJGstquAcbHvB
GI-007 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPR-FWT : The primary pump isolator is poorly installed: the cables are incorrectly terminated, lacks torque marks, and the door is not earthed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635330&prj=643&rqi=xk3LDXWKGqUhbkrL6jfDHOffZm
GI-027 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT : Compressor glands loose on WCC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635574&prj=643&rqi=OdHLsTuLLBoILaeUERqP0mROVh
GI-026 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPR-FWT : Secondary pump isolator - very poor install cable needs re-terminated, no torque marks, no door earthing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635573&prj=643&rqi=nRYZHKUcohm9B4Q5TnESU9Vgj7
GI-025 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPR-FWT: The pump room lacks a declaration of conformity plate, and no conformity paperwork has been provided for any assets within the area. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635565&prj=643&rqi=gvlKhlHDvio2tLtHwy4fFrcgP8
GI-024 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPR-FWT : No documentation has been provided for the refrigerant circuit, including pressureâ€‘test, evacuation, and charge records. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635563&prj=643&rqi=Qrg0N9C5k5BBPnAgkPfAyOSr03
GI-006 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Cleaning | Commissioning | [6 empty] | PPR-FWT : All assets are very untidy and require a deep clean, including the panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635328&prj=643&rqi=q62QCexkmOP21El5HjteAatR7H
GI-009 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Labelling | Commissioning | [6 empty] | PPR-FWT : The system lacks traffic labels and flowâ€‘direction markings, making it impossible to identify correct flow paths or routing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635340&prj=643&rqi=aEAqjvDFUhZMgsHqffsJSr3Yte
GI-010 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Incomplete Connections | Commissioning | [6 empty] | PPR- FWT : The distribution panelâ€™s stuffing gland opening is left unsealed, exposing the interior to potential contaminants. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635347&prj=643&rqi=e5ek9wJyf2BWAmBSeo6tKMfYJZ
GI-023 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPE-FWT : The condensate pipe lacks sufficient structural support, risking sagging or misalignment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635560&prj=643&rqi=o3cS6QMppEy8XhWqrGXHt245ho
GI-004 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | DCOS General Issue | DCOS | [6 empty] | The PPR systemâ€™s DCOS panel has inadequate trunking and cable management, leading to cluttered, hardâ€‘toâ€‘inspect cabling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635326&prj=643&rqi=gweLUK1gUZmAntFzzKGISlUy93
GI-015 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT : The chiller cables are not properly terminated, leaving an open connection point. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635551&prj=643&rqi=np4qXzadnW4Ct2pCBgsyfghKFt
GI-011 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR- FWT : Chiller panel cables need to be fixed and labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635538&prj=643&rqi=HNp14fjFSI7Azx6WpGvKFezmmB
GI-022 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT : The required external opening was not constructed within the room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635559&prj=643&rqi=MTnY4zThp8JJS6IhYr9DpbFjue
GI-001 | MU04-3 | N-EMEA | Ready for Verification | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-04-28 04:00:00.000 +0400 | AER - Aermec |  | Design not as specified | Design | [6 empty] | Dry Air Coolers and Waterâ€‘Cooled Chillers have been selected by the vendor for seaâ€‘level operation. MU4.3â€™s site elevation is over 500â€¯m, and the vendor expects at least a 3â€¯% performance degradation per DAC due to the reduced ambient air density. DACs will also be used to cool the condensers of WCCs, but the impact of the higher site elevation on WCCsâ€™ cooling capacities is currently unknown. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619831&prj=643&rqi=0KhA2BV0aGWVe6inzbOEnfmBcc
GI-455 | NY03-2 | AMER | Ready for Verification | P3 Low CX | Christopher.Federico@veolia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor - BMS |  | Component/Equipment Failure | Commissioning |  | system | CHW System |  |  |  | CHWSTR-ALL: Recharge valve "failed to start" nuisance alarm occurred when thermal storage remained in recharge mode but valve commend was zero because actual was close enough to setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635767&prj=560&rqi=iJYuXwl907ZHPwTbEd5zxwkzro | https://equinix.facilitygrid.co.uk/x/project/560/system/11494
GI-453 | NY03-2 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | UOM to be added by SI. Image attached. To be updated for all the similar asset type points | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634511&prj=560&rqi=aoLeKdR63zrzuorRZHob89HRNf
GI-445 | NY03-2 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Tags not performed once. To be corrected by SI | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634372&prj=560&rqi=q3FgJNhHI4ElyWNKHYeL2L0dBZ
GI-451 | NY03-2 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | State_text to be added to missing int points by SI. file already provided also in another INC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634504&prj=560&rqi=ZEySp1dkx24ClbtaxH0FIJGNS4
GI-452 | NY03-2 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Design Issue | DCOS | [6 empty] | Alarm Configuration to be updated by SI in graphics for all CRAHs. Screenshot attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634505&prj=560&rqi=1BppGicR23ZMQAMfdcYD0LzYiS
GI-444 | NY03-2 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | Maximo Asset Number updated under Maximo Asset ID for below assets. Maximo Asset ID should be kept blank in DCOS. NY3.011050T00_1CRAH_H_07 NY3.011050T00_1CRAH_H_09 NY3.011050T00_1CRAH_H_10 NY3.022060T00_1CRAH_G_19 NY3.022060T00_1CRAH_G_20 NY3.022060T00_1CRAH_G_21 NY3.022060T00_1CRAH_G_23 NY3.022060T00_1CRAH_G_24 NY3.022060T00_1CRAH_H_13 NY3.022060T00_1CRAH_H_15 NY3.022060T00_1CRAH_H_16 NY3.022060T00_1CRAH_H_18 NY3.01040000_1PDU_E_01_01 NY3.01040000_1PDU_E_01_02 NY3.01040000_1PDU_E_01_03 NY3.01040000_1PDU_E_01_04 NY3.01040000_1PDU_E_02_01 NY3.01040000_1PDU_E_02_02 NY3.01040000_1PDU_E_02_03 NY3.01040000_1PDU_E_02_04 Check thr files for more issues associated, wrong assigment, shifted ones, etc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634367&prj=560&rqi=F6ODLHPdub08CWQIgUx8AUJM5g
GI-447 | NY03-2 | AMER | Closed | P3 Low DCOS | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | Negative and/or Non-standard values found in few points. SI to Check and correct the values. Sample images attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634391&prj=560&rqi=87liUx1OJacRMGr9aJ8QTHPmpp
GI-448 | NY03-2 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Template Issue | DCOS | [6 empty] | Assets missing in DCIM. Please use the correct template and add into DCIM. Screenshot attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634396&prj=560&rqi=q9zezqcoiN5HFYsUS3j5aNyRtT
GI-450 | NY03-2 | AMER | Closed | P3 Low DCOS | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | Non-standard Display Point name needs to be renamed by SI. Iâ€™ve attached screenshots with comments for non-standard points from one asset of each asset type. Please use the Standard Points List to rename all applicable assets accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634487&prj=560&rqi=MEVOE8cLuPGv3w0wz2nolXgHgI
GI-446 | NY03-2 | AMER | Closed | P3 Low DCOS | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Design Issue | DCOS | [6 empty] | Misspellings of Display Name to be changed by SI. All Heat Trace, Transformer and PID. Sample Image attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634374&prj=560&rqi=INtbkhNss0eYHyrLXFjsCc8yfq
GI-449 | NY03-2 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Design Issue | DCOS | [6 empty] | Wrong Naming Format of the asset. 022203T00_1GEN_G_DATA. Attribute should not be in Asset name. Numbers overlapping the box in graphics. Screenshot attached. Wrong Maximo Asset Number assigned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634436&prj=560&rqi=U42wcQzbiEM24UhbcZf6epBrUT
GI-443 | NY03-2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-08-14 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Design Issue | DCOS | [6 empty] | MSB alarms incorrect naming and attributes. - the name can not include the "alarms" word -the asset type is switchboard, not generic template -the attrs are not the required ones | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633739&prj=560&rqi=yyb0Sq5SxxywKCrTHXBD7Elqq9
GI-442 | NY03-2 | AMER | Open | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-08-14 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | Aalogmonitor errors and warning clean up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633738&prj=560&rqi=HquhkjUFHb4PRC1ASOu7rpJJKR
GI-441 | NY03-2 | AMER | Ready for Verification | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-08-14 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | Topserver errors and warning clean up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633737&prj=560&rqi=auxGvrkz9XkM2VYS7QhGuJeyw5
GI-440 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - RMU - The BARD unit template shows two units with a lead/lag setup but the actual controller only has one of two units connected. Recommend discussing with Equinix to update template to show just a single unit with no lead/lag. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630006&prj=560&rqi=IF6O2Pb5qPCU8qwMKBrraVP54y
GI-433 | NY03-2 | AMER | Closed | P3 Low DCOS | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - MSB - "TVSS Alarm" comes in on transfers to/from generator due to power loss on TVSS. Discuss with Equinix a time delay to override nuisance alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629999&prj=560&rqi=JDsxA0PovGCe0o9rIKt6nVjGaP
GI-425 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - Generator Faceplate - The acknowledge buttons disappeared from the Faceplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629991&prj=560&rqi=x0UhcDKoZbnbnQ2NDfxRfyvmgV
GI-436 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - On the UDP Block Single Lines - Show the feeds from the primary UDP to the tethered UDP with a hyperlink to the appropriate UDP page) (ie. UDP-F1 needs to show a new feed to UDP-J1-1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630002&prj=560&rqi=GgIMyj7LZl4q0aS6vaqn1p5qYX
GI-430 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - UPS - "Bypass Not Available" is only coming in on UPS-F1/G1 and not on UPS-F2/G2. Need to confirm if this is an equipment or BMS issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629996&prj=560&rqi=N42i1WphGTiVfGGUNRN6yazStS
GI-432 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - UPS - PHS indicated that battery runtime provides an out of range value when UPS is not on battery so they mask the value as zero. Discuss with Equinix if there are ok with showing "0" when UPS is not on battery. May rather show as "unknown" or blank. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629998&prj=560&rqi=7GbKOOtWvfRNWUtktng8zvbCQW
GI-439 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - Chiller - The timer for the recharge valve to open stopped at 234 seconds on the graphics though it appeared to run in the background and valve opened after the approximate 300 seconds. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630005&prj=560&rqi=NkBxvZ2crfHKzVL1TpxHKoOERG
GI-427 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - Generator - "Fuel Hours" show alarm and 0 when generator is running. Should show an actual value with no alarm. Also discuss with Equinix if there are ok with showing "0" when generator is not running. May rather show as "unknown" or blank. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629993&prj=560&rqi=bjt1W9Q4F4YVXbenq0ZaYVwtB7
GI-424 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - Certain alarms (ie. generator & UPS) are not coming into the alarm banner. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629990&prj=560&rqi=JF5RvlLYcCAsKJVt3TFLqloxTn
GI-434 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - PUE kW/RT - The calculation is incorrectly using input kW divided by runtime hours should be kW/Ton. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630000&prj=560&rqi=CFzOP2XTXSzndz1Ift5C2YVMQo
GI-429 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - UPS - "Bypass Not Available" is showing as a Priority 4. I was under the impression that Priority 4 is only for Communications alarm. Confirm with Equinix. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629995&prj=560&rqi=pn0AEeMCqSrcjNrSmedIpfCQ2b
GI-437 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - On the LBSB Single Lines - Change all the UDP X to UDPR X for the boxes shown on the R spine (between "Block R1" and "LBSB") | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630003&prj=560&rqi=q7pyDvuuPGR9GsEpVGsXJe5kyN
GI-431 | NY03-2 | AMER | Closed | P3 Low DCOS | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - UPS - "Bypass Not Available" and "Inverter/Bypass Out of Sync" and "Warning" intermittently come in on transfers to/from generator. Discuss with Equinix a time delay to override nuisance alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629997&prj=560&rqi=lnZzWpadUVMljj0aWYqE7UduL7
GI-435 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - PUE kW/RT Total - The calculation is incorrectly adding the kW/RT of each Chiller. Should do a total kW/total Ton calculation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630001&prj=560&rqi=BWhhW5crZPf1r4HUluMb1WfKlJ
GI-426 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - Generator - Confirm the difference in the alarm registers for "Battery Charger AC Fail Alarm" and "Battery Charger Fault". As far as I can tell, we only have one alarm wired from the battery charger, so I am not sure what the second alarm would be. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629992&prj=560&rqi=DwAvI4XY56tAFfAzS8HPPc5mv0
GI-428 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - Generator - When generator is running, the "Summary" reads "Stopped, Auto, Alarm". Not sure why it would show "Stopped". | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629994&prj=560&rqi=Nt4ajvbSrvgGv2YkgMh6rQdPsD
GI-423 | NY03-2 | AMER | Closed | P1 High CX | steve.mulakkal@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning | [6 empty] | During Electrical Pre-IST, the UDPR-G1 Main breaker was opened to simulate an 180 degree Out of phase transfer on the G1 STSs. However, when the UDPR-G1 main breaker was opened the following occured. - STS-G1-1, G1-2, and G1-3 transferred from S2 to S1 (Expected Response) - STS-J1-2-1 and J1-2-2 transferred from S2 to S1 (Expected Response) - STS-E1-1, E1-2, E1-3, E1-4 serving customer load transferred from S1 to S2 (Unexpected Response). - UPS -E1 registered a "INV Volt Abnormal-TR" alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629239&prj=560&rqi=kQobPyZQJzFL7jme6qOdmmyK3M
GI-422 | NY03-2 | AMER | Closed | P3 Low DCOS | jreitz@equinix.com | 2026-07-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCIM Platform issue | DCIM | [6 empty] | Yesterday we looked into and opened a ticket for Topserver at the NY3 site to address an issue with Quick Client. We did some initial investigation to better understand the problem and quickly realized that Quick Client is not connecting to Topserver. We captured a few relevant screenshots of the error, along with UAExpert successfully establishing a connection. The ticket opened with Software Toolbox (CASE Number #46222848275) describes the issue and includes the screenshots. It took a bit of time to gather the required information and work through their bot. It referenced a couple of knowledge base articles which were helpful but did not address this issue, and then connected us with John, a Technical Application Consultant. John walked us through a few additional steps to gather more information, including screenshots of configuration settings and, this morning, a basic set of logs. As he explained, Quick Client connects to Topserver using OPC-DA, while UAExpert uses OPC-UA, which explains the difference in results between the two tools. His next step in troubleshooting is to investigate a potential COM/DCOM permissions issue, despite everything running under the local system account. OPC-DA is enabled, and the configuration appears to be correct. Weâ€™ve submitted the log files and asked what indicators might point to the failure, as well as where we can find resources to review the logs on my own. We will keep you updated as we learn more. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627718&prj=560&rqi=IsG0tJ6IPiJXggF9NSMptXatVF
GI-419 | NY03-2 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor |  | General Design issue | Design |  | equipment type |  |  |  |  | Generator Fuel Supplier pipe pressure - RFI#30 - pressure issue with the generator fuel supply line inside the generator enclosures specifically between the check valve and the high level solenoid valve. When the solenoid is engaged due to a tank high level alarm (set to 90% of usable fuel) the heat of the solenoid transfers to this section of pipe and builds pressure. Under this condition this section of pipe in generator C experienced a leak when the pipe pressure surpassed the pressure gauge rating. The tank high level alarms do not automatically clear when the conditions are met (ie the tank fuel level drops below the high level) and will require an operator to manually clear at the fuel supplier panel HMI. At this point and to alleviate the current issue, if a generator fuel tank enters high level alarm the operators can transfer fuel into a lower level tank to exit the high condition and clear the alarm at the fuel panel; however this would require constant monitoring of the fuel system if fuel levels are maintained close to 90%. Outside air conditions and generator runs will also affect the tank fuel temperature and may cause fuel levels to increase or decrease. In the case mentioned above for generator C, the high level alarm and solenoid were active for long enough to build temperature/pressure in this line and break the pressure gauge. One potential solution would be installation of a pressure relief line from the fuel supply line to the fuel polishing return line, as this is open to the tank; similar pressure relief lines have been installed on the NY5 generator fuel supplier/polisher lines. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626566&prj=560&rqi=F0jw3LDNrZBlwqouA2pl0Ghwx1
GI-418 | NY03-2 | AMER | Ready for Verification | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - Asset Mapping | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626402&prj=560&rqi=ZAW6uPE5eRcdrax3zM5EE3gx2w | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-415 | NY03-2 | AMER | Ready for Verification | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - DCOS Accuracy | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626399&prj=560&rqi=lIpHKLPugtudrJ1INWz4rHobqc | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-417 | NY03-2 | AMER | Ready for Verification | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - DCIM Quality | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626401&prj=560&rqi=w2yxGVp4RyVhx4zQvUkVQo1sMF | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-416 | NY03-2 | AMER | Ready for Verification | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - DCIM Config | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626400&prj=560&rqi=D8ypTDoXPbDcZLCHbGmPevnZfw | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-414 | NY03-2 | AMER | Closed | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - DCOS Quality | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626398&prj=560&rqi=PMOkVwLzjJy3ACGSnul0ebupeV | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-413 | NY03-2 | AMER | Ready for Verification | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - DCOS Config | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626397&prj=560&rqi=loixv1J0V7NjsmL6e6dUojBscB | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-411 | NY03-2 | AMER | Closed | P3 Low CX | kyle.vogt@veolia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Transformer 1 Over Temperature and Transformer 2 Over Temperature Alarms are present locally but are not present on BMS for F and G PDUs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625142&prj=560&rqi=i2YPUUk1slxCE3QTzRr5brY2JV
GI-409 | NY03-2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Installation Not Complete | DCOS | [6 empty] | DCOS-DCIM Validation NOT COMPLETED Check the attached files for reference, but the Validator tool is the real source of truth: https://onboarding.dcim.corp.equinix.com/ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624915&prj=560&rqi=NszlsDebHhUReVQdJRtiTse6Of
GI-410 | NY03-2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | All Electrical Skid CRAH's: The Electrical Skid Graphic at Skid F and Skid G always displays all CRAH's to have an M, indicating manual mode, whether or not the CRAH is actually in Manual Mode or not. The M on the graphic should appear only when the CRAHs are in Manual Mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624950&prj=560&rqi=WbQZc9w4JOJV6XZtnH57Sc05pU
GI-408 | NY03-2 | AMER | Closed | P2 Medium DCOS | manuel.gomez@eu.equinix.com | 2026-06-09 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS General Issue | DCOS | [6 empty] | DCOS - DCIM Onboarding validation is not completed. Attached are the reports for evidence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624482&prj=560&rqi=KC2fSoImv6HdEYrPK2uY3TbmP2
GI-404 | NY03-2 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - BMS |  | Component/Equipment Failure | Commissioning | [6 empty] | PDU-H1-2-2 - Initially this PDU was not communicating to the BMS. Upon troubleshooting, PHS discovered a bad ethernet cable between the PDU and the IBX network switch. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623986&prj=560&rqi=R4uQotHTVP6DmgM6fBogVK5FLS
GI-405 | NY03-2 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-06-04 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Component/Equipment Failure | Commissioning | [6 empty] | PDU H1-2-1 Breaker 1 - Breaker is not communicating to the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623987&prj=560&rqi=VwTDVmnUWd5Dsqfhzc1elI8ej1
GI-406 | NY03-2 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-06-04 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Component/Equipment Failure | Commissioning | [6 empty] | PDU H1-2-1 Breaker 2 - Breaker is incorrectly displaying a voltage of 375V when all other breakers are reading 405V. Hanley to investigate and rectify the issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623988&prj=560&rqi=iBBHg02A9G1qKz92i1rNPyas8l
GI-403 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - Electrical |  | Incomplete Connections | Commissioning |  | equipment type |  |  |  |  | PDU-H1-2-1 Breaker #6: While load banking the PDU, the A-phase pigtail connected to the load bank on CB6 reached 350 degrees F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623734&prj=560&rqi=VuslzlIIWfYxnawbg4B6TILQau
GI-402 | NY03-2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-01 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | DCOS - DCIM Validation not completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623552&prj=560&rqi=lMLHY2hyxKKSRUMSwKnTdSGPtZ
GI-399 | NY03-2 | AMER | Closed | P3 Low CX | steve.mulakkal@veolia.com | 2026-05-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Component/Equipment Failure | Commissioning | [6 empty] | UDP-G2 (Spare Breaker): Lockout tab is stuck and can not be pulled out to LOTO breaker. Issue was originally discovered on STS-G2-2 breaker. and lockout out tab was replaced with part from spare breaker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623225&prj=560&rqi=wQf4zoROMmL4l3TKrZRtOhLJwf
GI-393 | NY03-2 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS | Controls | system | DCOS |  |  |  | CWWT-A-01-CP-1 / Makeup Water Overview - Not communicating to BMS; MCE to check | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622681&prj=560&rqi=VicSIyKtQa8BB35vjRKoYy8lDN | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-394 | NY03-2 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-05-21 04:00:00.000 +0400 | Design Professional |  | DCOS Design Issue | DCOS | Controls | system | DCOS |  |  |  | MUW-PMP-1 & 2 / Makeup Water Overview - Flow switch proves flow without the pump operating, head pressure from storage tanks is high enough to make up Cooling towers without starting pump - Pump in alarm on BMS currently sending "fail to stop" even though pump is not running. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622682&prj=560&rqi=nBq7d3jgzDEKhSh1lz8sDMuxk3 | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-392 | NY03-2 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCIM |  |  |  | De-icing Manager - Fan Direction control timer analog input boxes - can not be edited from the faceplate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622680&prj=560&rqi=p8rJGoWum95Ai7Nzegwv2gnSAt | https://equinix.facilitygrid.co.uk/x/project/560/system/11779
GI-396 | NY03-2 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | MSB-"X" Alarms Symbol / Block E Graphic / Block C and D overviews include a "MSB-X Alarms" symbol and corresponding faceplate, but this is not included on Block E at this time. Does this need to be included on the Block E overview page? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622684&prj=560&rqi=ISOC3Hv9rdDPNqdcRp0ztvncfI | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-388 | NY03-2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-05-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Incomplete Connections | Commissioning |  | equipment type |  |  |  |  | WSHP F1, F2, G1, G2: Tripping the smoke detector does shut down the unit. MPS needs to update their wiring, so that a trip of the smoke detector is latching and remains in alarm until it is reset. Using the test button, the unit alarms until you remove your finger from the test button, and the alarm instantly clears. Similar issue we had with WSHP's E1 and E2 in the past. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622496&prj=560&rqi=540FTkVtikvi2T7I7fC2kSjVKO
GI-391 | NY03-2 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | Data Hall First Floor Area B East Graphic - Graphic needs to be updated by removing the half hot aisle closest to CRAH-F-1. See attached screenshots based on latest design documents. This may cause confusion since there is no CRAH hot aisle temperature sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622519&prj=560&rqi=AqgfqsUrkUByIAsBvyNX8wZftJ
GI-384 | NY03-2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-05-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | Electrical Skid CRAH's: Supply air Hi and Supply air Lo setpoints are unable to write to on the BMS and do not display the correct values on the BMS. Correction: We are now able to write the BMS, however the unit itself does not take the setpoint value. There is no correlation between BMS setpoint input and actual unit HMI setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621227&prj=560&rqi=16HMHy4WSObWZb59gl0tIVt8jM
GI-382 | NY03-2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-05-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | Electrical Skid Delta CRAH's: Cannot write a supply temperature setpoint to each E-CRAH. The BMS also does not display the correct Supply Temperature setpoint value. Correction: We are now able to write the BMS, however the unit itself does not take the setpoint value. There is no correlation between BMS setpoint input and actual unit HMI setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621225&prj=560&rqi=EjagDmj6kV3OjEhgwcMkPt1Ldy
GI-383 | NY03-2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-05-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | Electrical Skid CRAH's: Cannot place units into manual mode from BMS. Changing the unit int manual mode from the HMI also does not correctly update to "Manual Mode ON" on the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621226&prj=560&rqi=Xn0S7RpmlRerlm4kTJqRZ6j1Tq
GI-377 | NY03-2 | AMER | Closed | P3 Low CX | kyle.vogt@veolia.com | 2026-05-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Not Complete | Commissioning |  | equipment type |  |  |  |  | 1PDU_J1_2_1: ground cable lug damaged and disconnected from ground | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620823&prj=560&rqi=cwTtnFZfqiQKFue37jrSGyZc51
GI-370 | NY03-2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | Data Hall CRAH's: Total CFM value is reading ~4500 CFM when all fans are powered off. When failing one fan, the current total CFM value would remain. In most cases, it appears that the HMI is presenting the average CFM output of each running fan and multiplying it by 4, even if only 2 fans are running. However, when failing all the fans from the breaker on a running unit, the total CFM indicator still reads 4500 CFM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620310&prj=560&rqi=Rxze9T5hCC2JBJlxxC33YsQab1
GI-369 | NY03-2 | AMER | Open | P3 Low CX | Christopher.Federico@veolia.com | 2026-05-01 04:00:00.000 +0400 | Equinix Project Manager |  | Installation Damage | Commissioning | [6 empty] | STS-JX-X: STS damaged during transport. Makes opening and closing unit very difficult. Delta to provide a quote for repair. (unit designation TBD) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620118&prj=560&rqi=2Otooq7kMsTcQAf41DKgszowYQ
GI-367 | NY03-2 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor - Mechanical |  | General Design issue | Design |  | equipment type |  |  |  |  | Fuel Supplier/ Fuel Polisher - Upon MSB transfer to generator or Utility power, the respective pnuemercator is power cycled and sends alarms to the fuel supplier - critical low, low, full, high, and critical high alarms. These alarms are nuisance and require operator manual reset at the fuel panel. ISP has added a 30 second time delay to avoid these nuisance alarms on power transfers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619770&prj=560&rqi=c68OGQEwuaLcnyMCmZdknWOIlH
GI-365 | NY03-2 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-04-24 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | Phase 2 - BMS "Electrical One Line overview" page need to be updated for Blocks E, F, G, H to properly display the UPS to IOB breaker line animation. See attached images for discrepancies to match Blocks R1, A, B, C and D. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619348&prj=560&rqi=7ZnwpswmlxXVuovyCCQQ7jI0Bg
GI-395 | NY03-2 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-03-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | Controls | system | DCOS |  |  |  | PDU-C-1-1 / Electrical One-Lines / Faceplate and graphic are different between phase 1 and phase 2 equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622683&prj=560&rqi=7jnWXgPcJXgcifWGRqX9cQru99 | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-340 | NY03-2 | AMER | Closed | P2 Medium CX | steve.mulakkal@veolia.com | 2026-03-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | Phase 2B - All PDUs - Lexan covers for PDU bus protection is missing on majority of Phase 2B PDUs. Hanley to provide and install all missing Lexcan covers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615868&prj=560&rqi=uOMBYRTu40o6YOzxmAvGExNSLh
GI-335 | NY03-2 | AMER | Closed | P2 Medium CX | nicholas.leber@veolia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Phase-2A - Chiller Manager - After completion of IST, the "number of chillers required" analog input box would not accept a changed value from OM11 BMS screen. The signal would send from OM11 and start the next in line chiller skid, however the chiller would shortly stage down as the manual input did not hold; rather it reverted back to the original value. Through troubleshooting, determined that OI01 and OM01 were overwriting this point. This issue was previously resolved prior to IST during the points mapping transfer effort reverification. This issue is now resolved, PHS removed the input from OI01 to OI11, such that the manual input to this "number of chillers required" is resolved again. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615344&prj=560&rqi=jrmZzBUvWzNfSOKe0AF7rUkWnt
GI-333 | NY03-2 | AMER | Closed | P2 Medium CX | Christopher.Federico@veolia.com | 2026-03-05 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Phase-2B - PDU-J1-1-1: Breaker 01A, B-Phase on the breaker is testing 1200+ micro ohms while A and C phases are testing at <350 m ohms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614840&prj=560&rqi=t7wpDskNEd7P7wWjziI5kZlUrx
GI-397 | NY03-2 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-03-04 04:00:00.000 +0400 | General Contractor |  | DCOS Comms Issue/Fault | DCOS | Controls | system | DCOS |  |  |  | 00027T00_City Water_PMP - Aveva Floor Layout - Popup Faceplate - Failure to communicate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622688&prj=560&rqi=ZxmWNfmemti0bqWA5DjJAN3TgG | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-329 | NY03-2 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-02-13 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | MAU-B2 - Unit was still addressed by both the new and old OI Aveva systems causing conflicting control signals - which may have resulted in the damper actuators dysfunctionality and condensate build up in the unit. This was previously caught on MAU-A1 - mode control was not constantly fluctuating. This issue should now be closed, as PHS confirmed the old OI is no longer writing to MAU-B2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199219&prj=560&rqi=Dds1PCHjOn3xSdoUaGCsgJ2tSR
GI-324 | NY03-2 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-01-28 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | PHASE-2A - Generators C & D - Fuel system page displays a leak alarm for both of these generator tanks, although there are no alarms at either generators or Pneumercators. Need to confirm if correct modbus point is used for this alarm and/or if point needs to be inverted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197784&prj=560&rqi=zngHqXKiDLGbgh76TdEwG7c9Qb
GI-279 | NY05-P2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-17 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | DCOS-DCIM Validation did not pass. Attached the doc as evidence and linked it below to the online tool. https://onboarding.dcim.corp.equinix.com/dataflow | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625659&prj=527&rqi=BXdJ0LQ9TA96vsNVBfKFjMeJ5o
GI-269 | NY05-P2 | AMER | Closed | P3 Low DCOS | jreitz@equinix.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | Shows an alarm on sensor 2 when the value is within the acceptable range. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624326&prj=527&rqi=niwTkEdrBYYbg6xPATadI7uU2W | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-261 | NY05-P2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Installation Not Complete | DCOS | Controls | system | DCOS |  |  |  | Missing PUE link on the home page, and the script is not using the latest standard either. Assign to PHS team, they are not currently on the list to assign | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623747&prj=527&rqi=6pQFoYaQ1ZQ07BtevbN2hnMwFb | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-263 | NY05-P2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | Controls | system | DCOS |  |  |  | Links from different objects are not going to the proper page, eg Gens | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623749&prj=527&rqi=po56AWufN8PwkvY2zxo4hst2r0 | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-264 | NY05-P2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Design Issue | DCOS | Controls | system | DCOS |  |  |  | These two alarms from the GENs must be suppressed if the GEN is not running : Frequency not within limits Voltage not within limits | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623750&prj=527&rqi=y6wcCvAkTWJvWjstEpVurh6LeB | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-262 | NY05-P2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | We can not export the logs for topserver neither the project as the system have a poor performance and its crashing due to the huge amount of errors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623748&prj=527&rqi=KVW9YVW9MCpiAwIooavmxnFV46 | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-260 | NY05-P2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | Controls | system | DCOS |  |  |  | Graphics not aligned as per stds. Numbers over lines. check screenshoot | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623740&prj=527&rqi=UA8BvszXAEWnwHed3xV5lIP0ey | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-278 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-05-26 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | Generetor Breaker Open and MSB switch not in AUTO are both stuck in initializing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624335&prj=527&rqi=gZ4b8ZLFYr1I2wuwASDqmJGL2Q | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-277 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | When trying to control the electric room RTUs if you click on the unit it opens a faceplate with no actual controls other than to put the alarms in maintenance mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624334&prj=527&rqi=JOiZ35xbnkLzFWIJZ4Bmtsqo5I | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-276 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-05-08 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | TL:DR The system does not react to massive water use in an effective way. Recently on hot low humidity days we have been having a major issue with draw down on the MUW tanks. The system is not balancing correctly. City water pressure is varying wildly. The system needs to maintain a bare minimum psi of 22+ in order to replenish the tanks and lift to the roof. However maintaining that pressure requires significant valve manipulation. On 5/6 we burned through ~60k gal of water in the tanks before 11am. LC_PRIMUW_03 and LC_PRIMUW2_03 were open to >65% but the recirc valve PC_PRIMUW_04 was also open about 30% and the city supply valves were open to LC_MUWT1_03 ~13% and LC_MUWT2_03 ~30%. PSI was very lowon the city side of MUWT1_03 <20, but pretty high on MUWT2_03 >35. Tank levels were down to <163K per tank and dropping quickly. The Stilling basins had also dropped to below 12" By closing the recirc PC_PRIMUW_04, opening city feed MUWT2_03 to 100%, and setting city feed MUWT1_03 to 18% we were able to drive all PSI to >20 and start to reverse the draining of the tanks. My ask here is why the system was not modualting the valves to slow or reverse the tank loss? If those tanks had continued to drop at that rate and the conditions existed for more than a day we would have been in serious risk of running out of water. Is there any logic in the system to look at the tank depletion rate and open the city valves as far as they can be while still maintaining lift pressure? Once T2 was open to 100% and started reversing the water loss we opended the bypass valve which in turn slowed and then stopped water loss in T1 even though we could only open MUWT1_03 to ~18%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624333&prj=527&rqi=oMbx64WV9may0vb7eNLLp2bERK | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-275 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-05-07 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | the history service is not running on OM11 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624332&prj=527&rqi=MndyaNaQeHjaeC2GpFHKxfyKeB
GI-258 | NY05-P2 | AMER | Closed | P2 Medium CX | moutaz.abdelhamid@veolia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | BATT-E2 | UPS Battery |  |  | The end-of-life (EOL) was 21+ minutes, exceeding the expected 19 minutes. However, battery 13 of string 6 dropped 1V between minute 19 and minute 21. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618765&prj=527&rqi=M1CuIcG4KRRfLL68XqYAHCisBX
GI-274 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-19 04:00:00.000 +0400 | Equinix Commissioning Manager |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | If you move the mouse off of a face plate, while attempting to change the value in any numerical text box contained therein, it will result in the disappearance of the "AnalogUserInputAnimation". The value can still be edited but only by using the keyboard while avoiding moving the mouse. The issue also occurs when attempting to edit values in boxes on the main BMS screen, such as in the Liquid Cooling Skids page, but it seems to be more forgiving. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624331&prj=527&rqi=lfEW2KJS1Xkbmif5wTA2ms2pOp | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-273 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-18 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | If one tries to change the command of LC_MUWT1/T2_03 in manual, the window where you can adjust the value disappears as you scroll over it | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624330&prj=527&rqi=LNdXdRakeyVH51m0X62oIHmiKJ | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-272 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-17 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | Loss of comms on both STSs. The Loss is constant on 3 intermittent on 4. The screens on both STSs are functioning properly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624329&prj=527&rqi=ERhiGjDar8qiaSSvZHggt5n5z7 | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-266 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | Setpoint of 190,000gal with a deviation of 10gal for hi and lo alarm. Deviation should be a percentage not a unit measure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624323&prj=527&rqi=ZovPd6lKSCboZ7tIWoVN96AbfD
GI-271 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | Meter disable checkboxes are backwards | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624328&prj=527&rqi=oTfMN7k7beWeRQUebirdQaYrzI | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-268 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | Shows a chem treatment alarm with no other information what does this reference? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624325&prj=527&rqi=RLQSUGt7r6LUocLmhOFn7DtRcW | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-270 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | MSB header doesnt show what the values listed represent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624327&prj=527&rqi=vbRvhFu1bUxlVkNJzgcHS0rBcs | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-267 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | Setpoint of 190,000gal with a deviation of 10gal for hi and lo alarm. Deviation should be a percentage not a unit measure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624324&prj=527&rqi=EY0zeXtHGTKmt9KpnHdLRWTlJ6
GI-265 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-15 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | Cooling Tower Stilling Chamber Level Setpoint is not adjustable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624322&prj=527&rqi=4HI6dLF9Udq09xdKAqoVxQ0shs | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
FPT-45-001 | NY05-P2 | AMER | Closed | P1 High CX | moutaz.abdelhamid@veolia.com | 2026-04-14 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | UPS H Mech does not appear to have an MBB mapped or available. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618154&prj=527&rqi=SgJZGpCkiPMtSP6Gennm3fv5ic
FPT-45-002 | NY05-P2 | AMER | Closed | P2 Medium CX | moutaz.abdelhamid@veolia.com | 2026-04-14 04:00:00.000 +0400 | Owner | L4 | DCOS Comms Issue/Fault | DCOS | Electrical â€“ LV | system | H Block |  |  |  | UHD-H1 & UHD-H2 - MIB and MBB breakers are not reading voltage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618157&prj=527&rqi=UtVAt8ju2upzWg2a1JnRzLscgz | https://equinix.facilitygrid.co.uk/x/project/527/system/14170
GI-254 | NY05-P2 | AMER | Closed | P1 High CX | moutaz.abdelhamid@veolia.com | 2026-04-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | UPS-E system design has been revised from six (6) VRLA battery cabinets to five (5). Confirm whether the existing single set of 4/0 cablesâ€”originally sized for six cabinetsâ€”remains adequate for the system with five cabinets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617227&prj=527&rqi=RXJz6VZ1nPmhuST7fDNIPvrmZG
GI-252 | NY05-P2 | AMER | Closed | P2 Medium CX | moutaz.abdelhamid@veolia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | Electrical â€“ LV | system | E Block |  |  |  | Arc Flash stickers currently installed are temporary. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616718&prj=527&rqi=NIEQRss6CoH9FeLdb9TQHLITsg | https://equinix.facilitygrid.co.uk/x/project/527/system/11048
GI-245 | NY05-P2 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | Electrical â€“ LV | equipment | BATT-E1 | UPS Battery |  |  | Missing Labels for all strings on battery cabinet E1 Battery E1-1 Battery E1-2 Battery E1-3 Battery E1-4 Battery E1-5 Battery E1-6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616441&prj=527&rqi=katZpRIuzw0A40qqzySxncpx7l
GI-246 | NY05-P2 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | Electrical â€“ LV | equipment | BATT-E2 | UPS Battery |  |  | Missing Labels for all strings on battery cabinet E2 Battery E2-1 Battery E2-2 Battery E2-3 Battery E2-4 Battery E2-5 Battery E2-6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616442&prj=527&rqi=XPv3BuVV97UrCr0m0KUyb4Hvbo
GI-248 | NY05-P2 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | Electrical â€“ LV | equipment | BATT-H2 | UPS Battery |  |  | Missing Labels for all strings on battery cabinet H2 Battery H2-1 Battery H2-2 Battery H2-3 Battery H2-4 Battery H2-5 Battery H2-6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616444&prj=527&rqi=1LTO9LtUv5sopAzVBESgnliFme
GI-240 | NY05-P2 | AMER | Closed | P1 High CX | moutaz.abdelhamid@veolia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | MSB and UHD MTZ Schneider breakers all lost BMS communication. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616431&prj=527&rqi=xved7jifpbsw88GaE55rsu3nWV
GI-247 | NY05-P2 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | Electrical â€“ LV | equipment | BATT-H1 | UPS Battery |  |  | Missing Labels for all strings on battery cabinet H1 Battery H1-1 Battery H1-2 Battery H1-3 Battery H1-4 Battery H1-5 Battery H1-6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616443&prj=527&rqi=XYJbS6dHEn7GHPs8yo1ZPF3117
GI-249 | NY05-P2 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | Electrical â€“ LV | equipment | BATT-MECH1 | UPS Battery |  |  | Missing Labels for all strings on battery cabinet Mech UPS1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616445&prj=527&rqi=k0GDQ6YU3FBlj0Xx490XEadHvH
GI-250 | NY05-P2 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | Electrical â€“ LV | equipment | BATT-MECH2 | UPS Battery |  |  | Missing Labels for all strings on battery cabinet Mech UPS2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616446&prj=527&rqi=XQwqvATLYrUShHRvEfa3MbiYos
GI-239 | NY05-P2 | AMER | Closed | P1 High CX | moutaz.abdelhamid@veolia.com | 2026-03-24 04:00:00.000 +0400 | Mechanical Contractor |  | Design Correction Needed | Design |  | equipment type |  |  |  |  | The Generator tanks were not manufactured with an internal drop-down line for the polisher return. A possible option of rerouting the 2â€ line into the 4â€ opening then extending into tank. Foley to review and confirm. See attached markup showing current site install and possible alternative. Also attached are the submittals from P1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616323&prj=527&rqi=oKyKBjVy4dkXZZLQfGGQsUkspb
GI-233 | NY05-P2 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Provide labelling to all ports for Generators E&H. See attached Image of generator E as example. Labelling format to match exisiting generators. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615731&prj=527&rqi=pkDtVJIgV7jtF4p5w8on60fXyz
GI-237 | NY05-P2 | AMER | Closed | P1 High CX | moutaz.abdelhamid@veolia.com | 2026-03-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | The fuel water separator system has an NTP thread nipple connection instead of a STOR thread, which is causing the leak. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615738&prj=527&rqi=aANFMTcu1LrAFLO2XBlcCxrZZP
GI-236 | NY05-P2 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-16 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | The approved ECMP 4.0 controller is currently installed; however, its firmware version differs from the version specified in the approved Modbus point list. I am reaching out to Angel Gray to confirm the latest controller-approved firmware version. The current installation runs FW 4.13, which Foley believes is the most recent version available. I will let you know as soon as I hear back from Angel. All the points from the attached approved list proved functional except for LowCoolantLevelAlarm. The register used was 400354.6 instead of 400351.7. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615734&prj=527&rqi=DjTFn3shIqJ5lIh9oq2PjBjqXF
GI-238 | NY05-P2 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Generator fuel oil back pressure relief pipe is high off the ground causing a trip hazard. Similar pipe on other Gens are are labelled and painted bright color to prevent tripping. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615739&prj=527&rqi=40OQweOQoGZFo7diuh2qBj6uM9
GI-232 | NY05-P2 | AMER | Closed | P2 Medium CX | moutaz.abdelhamid@veolia.com | 2026-03-12 04:00:00.000 +0400 | Engineer |  | Documentation Not issued/ Required | Commissioning |  | equipment type |  |  |  |  | UHD E1/E2 MTZ breakers maintaince mode settings not specified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615478&prj=527&rqi=WW7x1UTeX5F8R8y4dJsctIvcDV
GI-226 | NY05-P2 | AMER | Closed | Outstanding Paperwork/Documentation | moutaz.abdelhamid@veolia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Documentation Not issued/ Required | Commissioning | [6 empty] | GC to provide required documentation for project closeout, this includes Torque sheets, balancing reports, Meggering reports...etc. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615134&prj=527&rqi=gFgqYYyOj2UhPY2KF8j77lezDW
GI-227 | NY05-P2 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-09 04:00:00.000 +0400 | Engineer |  | Documentation Not issued/ Required | Commissioning | Electrical â€“ LV | system | E Block |  |  |  | E-509 review comments - Arup to incorporate comments (Attached) as part of NY5-P2 As-built record drawings for both Capacity and Liquid cooling E509E and E509H drawings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615135&prj=527&rqi=k3ZE3ZXnsw9qPjAjmnug8Rst5l | https://equinix.facilitygrid.co.uk/x/project/527/system/11048
GI-225 | NY05-P2 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | The UHD-E1 and UHD-E2 key interlock SOO placards are has incorrect statment to return loadbank K21 key to SCC, which is incorrect and required to be updated as called out in Veolia submittal review comments for NY5-P3. AMG will need to reprint and replace the placards on the previously installed UHD-E1 and UHD-E2 units to ensure consistency. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614812&prj=527&rqi=Gr7Hfb4MqY45EVFPQNbx9GvM7y
GI-224 | NY05-P2 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | The MSB-E and MSB-H key interlock SOO placards are inconsistent with the placards provided by Eaton. Veolia identified this discrepancy during the NY5-P3 scope review; however, AMG will need to reprint and replace the placards on the previously installed MSB-E and MSB-H units to ensure consistency. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614810&prj=527&rqi=TNTpFbklkl1JCBoyHxs8To4yux
GI-009 | NY10-EW | AMER | Closed | P3 Low CX | jimmy.mendoza-farfan@veolia.com | 2026-07-06 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not complete | Commissioning | [6 empty] | P-trap is not installed on the condensate drain line as per contract drawing M501 detail 4. TYP for both units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628100&prj=696&rqi=YlRO6OYyJTTx7HqWJ8HGzq0hsZ
GI-010 | NY10-EW | AMER | Open | P3 Low CX | jimmy.mendoza-farfan@veolia.com | 2026-07-06 04:00:00.000 +0400 | Mechanical Contractor |  | Installation Damage | Commissioning | [6 empty] | Upper top left lip of cabinet is bent. Door can be opened somewhat easily, but closing the door is difficult. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628101&prj=696&rqi=1wkefzue7nRM1ghzYUNhHt1GL4
GI-008 | NY10-EW | AMER | Closed | P2 Medium DCOS | jimmy.mendoza-farfan@veolia.com | 2026-07-06 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not complete | Commissioning | [6 empty] | RTU power exhaust power and control wiring has not been pulled/terminated inside of the unit. Power exhaust was shipped loose and field installed. TYP for both RTUs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628099&prj=696&rqi=cYJ9TuStAVGH5JhXlfexXIt17q
GI-003 | NY10-EW | AMER | Open | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | PNL_H8A panel schedule shows a 15A breaker for heater box but submittal shows 20A. DLB confimed that the most current submittal is 15A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624561&prj=696&rqi=yVlZRhEQE14SpsGZq4cVgYpl7D
GI-001 | NY10-EW | AMER | Open | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | system | Electrical - LV |  |  |  | Temporary Arc flash stickers are currently installed on site equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624346&prj=696&rqi=ary7gGfkGkidJJ7KeNh0f5cTwU | https://equinix.facilitygrid.co.uk/x/project/696/system/14658
GI-002 | NY10-EW | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-06-08 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | [6 empty] | Breaker feeding PNL_H8A within the exisiting HMD-8 panel require a permenant Phenolic label. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624350&prj=696&rqi=zQkAgrPg3HSInEJHtV3ZKSp1IO
GI-202 | NY11-5 | AMER | Closed | P3 Low DCOS | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | Installation Not Complete | Commissioning | [6 empty] | RPP BCM's - Some of the NY11-5 RPP's were being moved by Site Ops. Need to be informed when construction is complete. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623658&prj=552&rqi=lMHvBofsd56DA6xC7k3eJNoXlv
GI-200 | NY11-5 | AMER | Closed | P3 Low CX | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | Electrical Contractor |  | DCOS General Issue | DCOS | [6 empty] | Thermal Monitoring - Need to confirm procedure and test thermal monitoring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623656&prj=552&rqi=ZZkxHT8lbcelTAA8ToC6lkHIpE
GI-199 | NY11-5 | AMER | Closed | P3 Low CX | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Configuration | DCOS | [6 empty] | Chillers - Need to setup time sync server capabilities. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623655&prj=552&rqi=Bqu0f6CNOtuVNluWWYly5OrGnq
GI-201 | NY11-5 | AMER | Closed | P3 Low DCOS | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | Configuration | DCOS | [6 empty] | Need to complete BMS Aveva License Transfer - Rovisys is in talks with Equinix controls to complete. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623657&prj=552&rqi=Ys8ardLSc5M3ftg3Z8x1SyzCtS
GI-196 | NY11-5 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-03-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS Single Line - Need to verify the single line graphic is correct after the tethers have been removed/Changed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614925&prj=552&rqi=35DT7B2DRlMf00RpLMVwRqhkxE
GI-195 | NY11-5 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-03-04 04:00:00.000 +0400 | Design Professional |  | Design Correction Needed | Design | [6 empty] | CHWP-ALL - The breaker tripped when the VFD was used in Bypass. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614746&prj=552&rqi=h8BuXTy6y9sootYMve6xz2f0V8
GI-185 | NY11-5 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-02-07 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | MSB-B SPD Alarm: The unit appears to not to be in alarm. But the alarm is active, and the unit is working correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198735&prj=552&rqi=52vyB5dP1FV3cpX1OyDzuOjkNH
GI-184 | NY11-5 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-02-07 04:00:00.000 +0400 | Controls Contractor |  | DCOS Template Issue | DCOS | [6 empty] | ALL UPSs for NY11-4 and NY11-5: Need to have the Alarm limti set to the correct values on KW, KVA and output current. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198734&prj=552&rqi=SY6Hd8j0ijSVrJXsu6uDlD3Se1
GI-050 | NY11-P1 | AMER | Work Completed | P3 Low CX | dustin.haugh@veolia.com | 2026-09-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | Cubical 07A door need adjustment for opening and shutting. The top 5 hinges on cubical 8 collide with the door preventing normal operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638190&prj=660&rqi=GINYhDh5vN0YCkvh3ebMuhvxDh
GI-048 | NY11-P1 | AMER | Open | P2 Medium CX | dustin.haugh@veolia.com | 2026-09-15 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | Low voltage control wires ran with 480v loads. Blue wires in attached pictures should enter cabinet in provided low voltage knockout at top of control cabinet.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638160&prj=660&rqi=aqQxXhXgFy8LRWOKLEr0T8oLBM
GI-049 | NY11-P1 | AMER | Open | P2 Medium CX | dustin.haugh@veolia.com | 2026-09-15 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MDSB_C_1 | MDSB - Mechanical Distribution Switchboard |  |  | Control wires enter and run with 480v load wires. Wires need routed in factory looms to prevent EMF issues. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638189&prj=660&rqi=hN3D6t0RDNAtV4kbQ06XxKA3xH
GI-046 | NY11-P1 | AMER | Closed | P2 Medium CX | Christopher.Federico@veolia.com | 2026-09-10 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MDSB_C_1 | MDSB - Mechanical Distribution Switchboard |  |  | MDSB-C-1: Top breaker has incorrect lug size. correct lugs need to be ordered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637609&prj=660&rqi=qK1ZeOJ98a39LlTuMeJo7JVST4
GI-045 | NY11-P1 | AMER | Open | P3 Low CX | Christopher.Federico@veolia.com | 2026-09-09 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1PNL_C_H1_2 | DB - Distribution Boards |  |  | PNL-C-H1-2: Two set screws on line side of breaker are stripped. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637528&prj=660&rqi=yicZ40Cf012WBg6x0QHHomgKYq
YT1ELEC-50-004 | NY11-P1 | AMER | Open | P3 Low CX | edward.woodruff@veolia.com | 2026-09-01 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | UMDSB-C: Breaker Q3 (MBB) only has one Aux NO/NC contact. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636371&prj=660&rqi=g5Ma6bONLgsGGf78S0IMGnkIdU
YT1ELEC-45-005 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-09-01 04:00:00.000 +0400 |  | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: The Mimic lines on the swbd are incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636375&prj=660&rqi=DMbld1wbpIxKKlEl32frd8sdYA
GI-044 | NY11-P1 | AMER | Closed | P3 Low CX | jimmy.mendoza-farfan@veolia.com | 2026-08-28 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | CHW recharge line for ACC7 has the wrong Series 70 Bray valve model installed. Note the different part number for the Series 70 Brays. The DA Bray model is only supports ON/OFF control. The G0 Bray model has modulating control. ACC7 has a DA Bray valve installed on the recharge line that needs to be swapped out with the extra G0 Bray valve installed on the ACC8 discharge line. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635986&prj=660&rqi=EDSsaZgElgQ1ouKZ29rznxCe4c
GI-043 | NY11-P1 | AMER | Closed | P2 Medium CX | jimmy.mendoza-farfan@veolia.com | 2026-08-28 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Check valves need to be rotated in the correct orientation. Currently the check valve is oriented to prevent backflow into the return line. Check valve should be installed to prevent backflow into the chilled water supply line. Typ for both chiller skid piping. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635983&prj=660&rqi=MlARaIlD2Jgavmp1KXaWtCSNoQ
RT1ELEC-57-002 | NY11-P1 | AMER | Open | P3 Low CX | dustin.haugh@veolia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L2A | General Design Issue | Design | Controls | equipment | REMOTE HMI | HMI - HMI Panel |  |  | No drip pan below AC condensate drain connection. Drip pan above AC unit not tied into the drain.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635631&prj=660&rqi=fBhrMSVhizR4EShWgQK6eFEIOT
GI-042 | NY11-P1 | AMER | Closed | P2 Medium CX | dustin.haugh@veolia.com | 2026-08-24 04:00:00.000 +0400 | TRN - Trane |  | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Control wiring to chiller sensor damaged. Right cabinet on back of chiller, top middle area. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635063&prj=660&rqi=11dHW5rxgAmbC5wvNld8pVyi05
YT1ELEC-50-003 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | UMDSB-C3: The polarity appears to be reversed on the PQM CTs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630733&prj=660&rqi=1KgpCIrTXW1sufb91pkeyP8QxB
YT1ELEC-45-004 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: All CT polarity's appear to be reversed on all PQMs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630734&prj=660&rqi=mr7oHmxmeEumAesMskBPyT1d3f
GI-039 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-23 04:00:00.000 +0400 | VER - Vertiv |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | IT AND MECHANICAL UPS Batteries: the cabinets are missing the barrier and spacing required by fm global for lithium batteries and cabinets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630725&prj=660&rqi=AjAIM0EXfW57649QQEP8GU7P4v
YT1ELEC-45-003 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | 1MSB-C: The high contact resistance found on Camlock section 8 and 9 from LBB (both) to the Phase A camlock. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629837&prj=660&rqi=vYs6zN7HJxULuZZEgyxcOWJLfj
YT1ELEC-50-001 | NY11-P1 | AMER | Closed | P2 Medium CX | edward.woodruff@veolia.com | 2026-07-14 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | 1UMDSB-C: Breaker Q1 has failed NETA testing due to contact resistance. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629168&prj=660&rqi=juqe2ylSfxbylqgndp3r8tjPO7
YT1ELEC-50-002 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-14 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | 1UMDSB-C: Breaker Q7 has failed NETA testing due to contact resistance. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629169&prj=660&rqi=1PlEUy0vlC4Syyso2Qvg6kvgw5
GI-038 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-13 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | 1UMDSB-C: The as built breakers sizes do not match the submittel sizes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629036&prj=660&rqi=9ghRUBNuXogYrTNhckuUYMA76H
GI-037 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-13 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MDSB_C_1 | MDSB - Mechanical Distribution Switchboard |  |  | MDSB-C: The as built breakers sizes don't match the submittel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629035&prj=660&rqi=XjiECnFzPQiXzWnYfBxzE9yWKq
GI-029 | NY11-P1 | AMER | Open | P3 Low CX | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | CMM - Cummins |  | Design correction needed | Design | [6 empty] | GEN-C - As observed on other jobs, the battery charger failure is now an alarm that appears instantaneously on a power failure and creates a nuisance alarm. In the past, we believe we had a 30 second time delay to override momentary power blips to the battery charger before an alarm was initiated at the generator. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623651&prj=660&rqi=7bPh69UjxVO5oBtzP533lJOlap
GI-028 | NY11-P1 | AMER | Closed | P3 Low CX | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | HAP - Hitachi Energy |  | Documentation not issued/ Required | Commissioning | [6 empty] | MLTX-C - The submittal did not include the proper primary side cabinet and associated accessories. Components were installed in field. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623649&prj=660&rqi=EUWbtP6kLmDzUrGYQAWkR0gIni
YT1ELEC-45-002 | NY11-P1 | AMER | Closed | P3 Low CX | ralph.ciardulli@veolia.com | 2026-05-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C - Section 4 Load Bank Breaker - Factory connections for vertical bus were disconnected for the installation of a bus duct flange. While reinstalling the Phase B left side (when viewed from front) vertical bus into the insulator, the bolt was torqued to 51 ft-lbs and clicked well before the connection was fully torqued down. The washer the spacer was still spinning. The volt was backed out and the same issue repeated. Upon further investigation, it appears that the insulator is spinning as the bolt in the back does not move. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623234&prj=660&rqi=CDSG0QaSJUlXNuuc1V1uKcc6Yf
YT1ELEC-45-001 | NY11-P1 | AMER | Ready for Verification | P3 Low CX | edward.woodruff@veolia.com | 2026-05-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB B: IOB1 K7 key assembly is not in the breaker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622527&prj=660&rqi=v4YHyKpaI6uOY5RnUQ4IqkpfBh
GI-026 | NY11-P1 | AMER | Closed | P3 Low CX | jimmy.mendoza-farfan@veolia.com | 2026-05-14 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | Bottom section of SWGR needs to be fixed. Refer to photo attached. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621916&prj=660&rqi=nXza1kI4umXJ3oCtBbHzeQq5iW
RT1ELEC-57-001 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-05-08 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning | Controls | equipment | REMOTE HMI | HMI - HMI Panel |  |  | MSB-C HMI: Above KS1 the placard should read " Auto Auto/Man Man". all on the same plane. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621005&prj=660&rqi=IuNLemLaCBhr3jahapzPl0U7lq
GI-016 | NY11-P1 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Ground wiring is not terminated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618148&prj=660&rqi=VnJF1ZjuHnfOsJAenwY6tPggfr
GI-022 | NY11-P1 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1-ACC-C-8 | ACC - Chiller - Air Cooled |  |  | Several control wires failed wire tug test | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618177&prj=660&rqi=YGvIt8Zxdzkxm49wdaxwCrLZ7S
GI-023 | NY11-P1 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1-ACC-C-8 | ACC - Chiller - Air Cooled |  |  | Control wiring located on the left side of the control panel enclosure needs to have wires reorganized. Typical for both chillers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618178&prj=660&rqi=IpkDXJxr6Q6x8LmZfXGBWNkTnc
GI-018 | NY11-P1 | AMER | Open | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [6 empty] | Provide protective enclosure for transformers inside the 480V cabinet similar to the lugs. Typical for both chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618150&prj=660&rqi=CQhcEJktzBe99GUk2Uz6lwqwFI
GI-017 | NY11-P1 | AMER | Ready for Verification | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Missing Components | Commissioning | [6 empty] | Fan guard is missing inside the 480V cabinet. Typ for both chillers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618149&prj=660&rqi=QjIC28O5aM7VcGvQse2mmYWB2e
GI-015 | NY11-P1 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Several control wires failed a tug test. See photos for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618147&prj=660&rqi=iZyWr4kehjn2TdIP3QmY0Pzxmb
GI-019 | NY11-P1 | AMER | Ready for Verification | P2 Medium CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Missing Components | Commissioning | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Chiller came equipped with 2 position bray valve for freeze protection. Per equinix EBCS-3 control valve should be fully modulating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618169&prj=660&rqi=MsltkLYZjanCYfJGJ6NncEFlcQ
GI-021 | NY11-P1 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Missing Components | Commissioning | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Provide additional neoprene pads (4 total, 2 per chiller) for chillers. See photos for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618172&prj=660&rqi=QJxOsjLrGuezO3qvoxg1QBKjOR
GI-020 | NY11-P1 | AMER | Closed | P2 Medium CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Missing Components | Commissioning | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Onicon provided with the chiller skid does not match the approved submittal. Flow meter provided is FT-3000 series (FT-3206). Model number on the approved submittal notes FT-3400. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618171&prj=660&rqi=htHMSHqdmKXqp4QDiUw88Pwozg
GI-009 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-03-09 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: the Cam loc section of the MSB-B Kirk key does not match existing K2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615142&prj=660&rqi=ndDTIM3SP12s0l67rhSCaXJ8q1
GI-008 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-03-09 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: the LBB K2 Kirk key does not match existing K2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615125&prj=660&rqi=TuS2bzAAIR4LV37LKYVfWfX9qp
GI-007 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-03-06 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C- the main CTs are not ridgedly supported on the main bus | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614899&prj=660&rqi=2qlUH8HGFYA1cQ9gLcl9rQ7X6S
RT1ELEC-46-002 | NY11-P1 | AMER | Closed | P2 Medium CX | Christopher.Federico@veolia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | UDP-C1: Needs phase transition piece to properly terminate busway into the gear. Different phasing between manufacturers was not taken into account. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483376&prj=660&rqi=RgPAAZHgzB0LloKPlIOX1KbO57
RT1ELEC-46-001 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-02-25 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: MSB skirt pieces were damaged and dented during shipping. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221109&prj=660&rqi=neCufRrGjIluOAuOLgfXPmzwJ7
GI-005 | NY11-P1 | AMER | Closed | P2 Medium CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design correction needed | Design | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: Design of the glastic barrier behind the section 03A incoming cable entry prevents clean installation of the 13th cable that will be landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199691&prj=660&rqi=VZAKeT90vkSJKrPcKQi70BAq6K
GI-002 | NY11-P1 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C HMI: Labels on HMI are all blank. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199688&prj=660&rqi=hnTa87kus5fFBsFTPrEybxVFPF
GI-004 | NY11-P1 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: All voltage indicator lights on the board are white instead of amber. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199690&prj=660&rqi=zFNFKXHhig6I03DG1UBxUNCitj
GI-006 | NY11-P1 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: Circuit breaker slots for UPS LBBs in sections 08B and 09B currently have a metal plate over the cutout intended for the breaker when instead it should have a bubble-type enclosure installed on the front in order to lock up the breaker when in use. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199692&prj=660&rqi=jlDDkYVRYurVBthqM4hkjcIcMm
GI-003 | NY11-P1 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C HMI: Unnecessary K5 switch is installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199689&prj=660&rqi=2aMw0CVziPffkmqkD0e5qWIjZi
GI-001 | NY11-P1 | AMER | Closed | P2 Medium CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C HMI: Key switches do not release in all positions like they should. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199687&prj=660&rqi=ne9FMgqRtDUwVVJn3cy6fTEEAM
GI-050 | OS03-4 | APAC | Closed | P3 Low CX | milanshrestha@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | FAT Mechanical OS3-P1 CRAH/AHU Regarding the performance test, the actual average value is 173.4kW. Please explain why it is 173.4kW. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352251&prj=519&rqi=MCkEsQrPnb2ku8d0v9QyZGaS20
GI-051 | OS03-4 | APAC | Closed | P3 Low CX | milanshrestha@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT Bus Duct Test Script (Page 14) Kinden said that the Bus Duct Temperature sensor path was changed (indicated by arrow and cross mark below). Please make the correction when submitting the Test Result. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352252&prj=519&rqi=dSNYV3V23Z9OIEcBjBBz5X0tVZ
GI-052 | OS03-4 | APAC | Closed | P3 Low CX | milanshrestha@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT Electrical During the "System Star-up and Check" on Bus Duct Temperature Sensor, temperature was displayed as "zero" on the GX20(BMS) for BD29 to BD32 (highlighted in red color in figure) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352253&prj=519&rqi=ynGFUSU2cl3S86u8VhOMIYAoD9
GI-049 | OS03-4 | APAC | Closed | P2 Medium CX | milanshrestha@commtechasia.com | 2026-01-27 04:00:00.000 +0400 | Commissioning Authority |  | General Contractor [GC] | Commissioning | [6 empty] | SAT OS3-P1 Primary UPS no. 5 (12F) : Mitsubishi Electrical - UPS - 2400kVA - 24-7MP4093 EF - Cx4 During the UPS functional performance test (load test), a fan temperature abnormality alarm occurred. This issue caused the UPS thermal load test to be terminated. Cause: The required blanking panel (divider plate) was not installed between the UPS module panel and the bypass panel. This blanking panel prevents the inflow of hot air from the module panel to the bypass panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197649&prj=519&rqi=W7IpxayniX2VNARcaft92p2ScN
GI-082 | OS05x-1 | APAC | Ready for Verification | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-11-05 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | HLT : - Mechanical - (PAC) [Daikin - PAC - FVYCP560MA - Cx4] [HLT Issue No.1]_Mechanical_(DH 3-1-2) During the 100% load test, the RA of PAC No. 40 in UPS Room 3-1-2 recorded a temperature of 30.1Â°C. The temporary data logger also recorded a temperature of 32.3Â°C. At that time, four PAC units were in operation, and the SA setpoint was 23Â°C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622086&prj=521&rqi=wPGgW6YbYvnu3SbSHXqYt3EzMl
GI-131 | OS05x-1 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-09-07 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | SAT: - Electrical - (Diesel Engine Generator) [CAT / BEMAC - Diesel Engine Generator / DEG Panels - 4875kVA - C175 - 20 - Cx4] On the third day of the UPS No. 9 test, when the power supply switched from the mains to the generator, alarms were triggered on the Fuel Tank No. 1, No. 2 and No. 4 transfer pumps. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637041&prj=521&rqi=y8SI4vdwgBkPD0uWA7cSTI94yQ
GI-132 | OS05x-1 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | SAT : - Electrical - (UPS) [Mitsubishi - UPS - MELUPS 9800G - Cx4] During the 3rd day of the UPS No. 9 test, an overload test was conducted while the UPS was supplied by the generator. The test scenario required the UPS load to be increased to 110%. If the load remained at 110% for 10 minutes, the UPS was expected to transfer from inverter supply to internal bypass. The UPS successfully transferred to internal bypass as expected, and the operation was completed without any issues. However, when the load was subsequently reduced from 110% back to 100%, the UPS was expected to automatically transfer from internal bypass back to inverter supply. This transfer did not occur as expected, and the UPS remained on internal bypass. After the synchronization switch was turned off and the test was done, the UPS successfully transferred from internal bypass back to inverter supply without any issues. However, a failure alarm was triggered on the UPS during the transfer. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637042&prj=521&rqi=1tY0GuVLHCX3unHV28sheJDHi1
GI-123 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Electrical IST Day 2 Issue No.29] Building Elec IST Preparation: Since the power factor display on the BMS shows -100%, correct it to 100%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630070&prj=521&rqi=04ULGiKlJqy7lLC4XbqZGVnQl6
GI-122 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Electrical IST Day 2 Issue No.28] Building Elec IST Preparation: Before the start of the Building Elec IST Day 2, offline alarms were triggered in 2-3-DP-12-U4-2-1 and 1-3-DP-12-U5-2-1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630069&prj=521&rqi=5rqXZLRkIEXrmBbvOj8iolIGSd
GI-124 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Electrical IST Day 2 Issue No. 30] Building Elec IST Day2 Test No.8 After power was restored to Test-8 on Day 2 of the Building Elec IST, a minor fault for DEG No. 5 was reported on BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630071&prj=521&rqi=xjKFgF5MWGzax1nHH9yRT54iZV
GI-127 | OS05x-1 | APAC | Open | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Electrical IST Preparation Issue No.33] Not completed the mapping of additional points and the point-to-point check for the BMS display related to generator fuel systems. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630274&prj=521&rqi=l6N51od2r7fgYIyzREGlwLB0iT
GI-126 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Electrical IST Day 2 Preparation Issue No. 32] Regarding the BMS display for the fuel system, â€œLocalâ€ is shown in green and â€œRemoteâ€ in red, but it should be the other way around. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630214&prj=521&rqi=90llGiJG8V2PbGYF0f4pWorReM
GI-125 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | IST : - Electrical - (Diesel Engine Generator) [CAT / BEMAC - Diesel Engine Generator / DEG Panels - 4875kVA - C175 - 20 - Cx5] [Building Electrical IST Day 2 Issue No.31] Building Elec IST Day2 Test No.9 During the building power outage for Test-9 and the subsequent generator startup, major, middle and minor alarms were triggered on Generator No. 5, causing the equipment to shut down. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630072&prj=521&rqi=tVEn3a1rHZX2Lmsx6jOKqVK3nN
GI-118 | OS05x-1 | APAC | Ready for Verification | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-07-16 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | IST : - Mechanical - (PAC) [Daikin - PAC - FVYCP560MA - Cx5] [Building Mechanical IST Issue No.24 Day 2] High Return Air Temperature alarm generated by the PAC unit that was in standby in UPS Room 3-2-1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630063&prj=521&rqi=j5kaKbzdeWA49cbmb6VO6VZkcN
GI-120 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-16 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Mechanical IST Day 2 Issue No.26] L2 No. 2 Riser Return Flow Rate Discrepancy: - BMS Display: Constant 4,436 L/min - BMS Trend Data: Fluctuating between 4,435 - 4,456 L/min - On-Site Meter: 0 L/min - Onsite current output measured at control panel: 0 mA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630067&prj=521&rqi=yFkjEBiy33DOWEMaeccamkgek9
GI-121 | OS05x-1 | APAC | Open | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-16 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Mechanical IST Day 2 Issue No.27] Update the Sequence of Operation (SoO) for the heat source area to the latest version and send it to the relevant parties. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630068&prj=521&rqi=ue6HAiaO7yfpnfvWn6uv17U39c
GI-119 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-07-16 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | IST : - Mechanical - (PAC) [Daikin - PAC - FVYCP560MA - Cx5] [Building Mechanical IST Issue No.25 Day 2] High Temperature Alarm for UPS Room 3-2-1: High temperature alarm for UPS Room 3-2-1 was observed during the PLC failure tests. Upon inspection of the temporary data loggers: the max temperature around the modules was observed to be 34 and battery at 23.7â„ƒ (approx 12:30) Temporary data logger Max readings at approx. 16:45: - Module area: Max 36.9Â°C - Battery area: 25.9Â°C | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630066&prj=521&rqi=9jruMcHKFdkNjrwPhn6jwhSMHE
GI-114 | OS05x-1 | APAC | Open | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Mechanical IST Preparation Day 1] Supply Air Temperature Fluctuation During DH Load-Up -> During DH load-up, supply air high-temperature alarms were observed on the BMS for the Cool Array Units. Trend review indicated that the supply air temperature on the smaller coils (Top Left and Top Right) was fluctuating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630059&prj=521&rqi=PR7uAEChKHRIS4rhCgDk4ZO2Ok
GI-116 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Mechanical IST Preparation Day 1 Issue No. 22] IT Server Breaker Monitoring Clarification Required -> Clarification is required on why some breakers supplying power to IT servers are not monitored. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630061&prj=521&rqi=7DyQ7YPid1Ajc0U05VP8yHWoC4
GI-117 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Mechanical IST Issue No.23 Day 1] During the A-to-B changeover, high-temperature alarms were observed on Risers 1 and 3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630062&prj=521&rqi=nJn31U8yKDe99A4IVrBpyPvjEu
GI-115 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Mechanical IST Preparation Issue No.21 Day 1] DH Load Adjusted to 2,400 kW Condition -> At the beginning of IST Day 1, the DH load was below 2,400 kW. After consultation with the vendors, the DH load was adjusted to approximately 2,404 kW for both data halls. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630060&prj=521&rqi=rg9mXglUMrlTytSiJv8tgWHgUp
GI-113 | OS05x-1 | APAC | Ready for Verification | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | Mechanical IST Issue No.19 <Cool Array> DH 3-2-1 During the lunch break on the second day of IST, a communication error occurred in the BMS measurement display for 2-3-CRAH-12-2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628796&prj=521&rqi=hjDslrOOJ5MsDIZkg4cnFUxUqs
GI-112 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | Mechanical IST Issue No.18 <Chillers> DH 3-2-1 4-3-CH-12-8 & 4-3-CH-12-9, all compressors stooped due to low flow during test 12 [Simulate the failure of one Cool Array at a time in the Data Hall (fan stopped), record the temperature rise to above 35Â°C, and then restore the temperature to the SLA tolerance as soon as temperature rise to above 35Â°C] | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628795&prj=521&rqi=epnNCuGmQdo7omGiELPtopUbfX
GI-111 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | Mechanical IST Issue No.17 <PAC> DH 3-2-1 Mechanical UPS PAC (2-3-FCU-12-PAC29) exhibited abnormal noise during the pre-IST inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628794&prj=521&rqi=YJQq1f5nebxendRqDwgLI5gNNV
GI-110 | OS05x-1 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | IST : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx5] MECH IST Issue No.16 <Chiller> During the monthly inspection on 5 July, discolouration of the thermal labels was discovered on OS5x, PHF floor, units 4-3-MDSB-12-P402 and 4-3-MDSB-12-P411. (Discolouration at a maximum temperature of 80Â°C) It was also found that the circuit breakers for compressors on Chillers No. 2 and No. 11 had tripped due to overcurrent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628793&prj=521&rqi=NyuzKgxdyyIQ3XaEnyaFDXiv5X
GI-109 | OS05x-1 | APAC | Ready for Verification | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-07-02 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <Chiller No. 5 & 10> DH 3-2-1 During the 100% load test of Chiller No. 10, Chiller No. 5, which was under exclusion, unexpectedly went offline and then automatically returned to an online status shortly afterward. A major alarm was generated on the BMS when the chiller went offline. Once communication was restored and the chiller returned online, the major alarm was automatically cleared from the BMS. The event was transient, and no further abnormalities were observed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628792&prj=521&rqi=5WbuLcE4rpO6B8ueyHaAIlmg4q
GI-108 | OS05x-1 | APAC | Ready for Verification | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT: - Mechanical - (Cool Array) [Vertiv - Cool Array Unit - TW240 (5 coil) - Cx4] SAT L4 <FPT Issue No.22> Cool Array 3-2-1 During the ATS switching test (A â†’ B), all CRAHs went offline and then recovered. However, 2-3-CRAH-12-3, 2-3-CRAH-12-8, and 2-3-CRAH-12-9 tripped again (offline) before returning to normal operation. During the return switching (B â†’ A), 2-3-CRAH-12-1 went offline before restoring, while all other CRAHs transferred back to source A without interruption. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627200&prj=521&rqi=ap1RBTIAA6inPgzxeMkW8SFkXk
GI-103 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | IST : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx5] (DH - 3 - 2 - 2 Mech IST No.11, Day-2) During the Chiller Failure and Restoration Test, the chiller was restored successfully at the site and resumed normal operation locally. However, the chiller remained in an offline status on the BMS and did not return to its normal operating condition within the BMS interface. To restore proper communication and status indication on the BMS, Main breaker (é›»æºå…¥åˆ‡ã‚Š) was performed. Following the action, the chiller status was correctly reflected on the BMS, and normal operation was confirmed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626671&prj=521&rqi=ic4tpdUefdnesjxKhvZQpZ8DMZ
GI-102 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | IST : - Electrical - (STS) [Kokubu Electric - STS - 0304301 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0304401 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0304501 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0304601 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0304701 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0304801 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0303701 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0303801 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0303901 - 1150 kVA- Cx5] Mechanical IST Issue No.10, DH 3-2-2. During the site inspection, a high temperature(data logger) of approximately 32Â°C was observed in the STS room under 100% load conditions. A similar temperature trend was also confirmed in the BMS data for the HLT on 17 June. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626660&prj=521&rqi=L4hns7CkoinbV8OpPqCJgThhjX
GI-107 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design | [6 empty] | HLT/IST : - Mechanical - (Hot Aisle Capping) [Shinryo - HAC - N/A - - Cx4/Cx5] Lessons Learned (DH3-1-1) The SLA temperature exceeded 27Â°C during 100% HLT load. It is believed that a problem with the temporary HAC structure caused a short circuit of cold air, resulting in a rise in the cold aisle temperature. Since the upper limit specified in MSFT's SLA requirements is 35Â°C, the test continued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627199&prj=521&rqi=gU1qvhH9ycEnSfwaowwDJKa1o9
GI-106 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | Commissioning Authority |  | General Contractor [GC] | Commissioning | [6 empty] | IST : - Mechanical - (Sensor) [N/A - Sensor - N/A - Cx5] (DH 3-1-1, DH3-1-2) Lessons Learned Since the cold aisle sensor is installed on the ceiling, move it to the correct position below the ceiling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627198&prj=521&rqi=26QRxaYHcJEmPXQuHgR7CWuC6X
GI-101 | OS05x-1 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | HLT: - Mechanical - (Cool Array) [Vertiv - Cool Array Unit - TW240 (5 coil) - Cx4] HLT Issue No.9 HLT DH 3-2-2 During the step load test, Supply High Temperature Alarm was triggered on the BMS for several CRAY units at 25% and 50% load. Upon investigation, was observed in the SA temperature for several CRAY units at DH3-2-2. For the 5-coil CRAY units, two different coil sizes exist, and the hunting was observed only in the smaller coils. The SA temperature for the larger coils was stable. The hunting was observed only at low load conditions (up to 50%). The SA temperature became stable from 75% load onwards. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626659&prj=521&rqi=0cCmOHwlO7y8VXZltPgXtjSwId
GI-098 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Electrical - (UPS) [Mitsubishi - UPS - MELUPS 9800G - Cx4] SAT L4 [FPT Issue No.19] UPS No.4 DH -3-2-2 During the UPS-4 L4 line changeover test, a discrepancy was identified between the electrical current and power readings indicated by the UPS-4 metering system and the corresponding values supplied from the extra-high-voltage (EHV) source. The difference in measured values has been recorded and will be investigated further. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626651&prj=521&rqi=9E4H4CXnjkytOUbieUSKPBolOk
GI-096 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | SAT: - Mechanical - (Cool Array) [Vertiv - Cool Array Unit - TW240 (5 coil) - Cx4] SAT L4 <FPT Issue No.17> Cool Array 3-2-2_ The wall-mounted temperature sensor in DH3-2-2 indicated a temperature exceeding 35Â°C, reaching approximately 36.4Â°C, which is significantly higher than the expected operating range. Upon investigation, it was suspected that the cool air discharged from the Cool Array was unable to effectively reach the area where the wall-mounted sensor is installed. This condition is believed to have been caused by the replacement of the fan cover in accordance with Microsoft's specifications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624063&prj=521&rqi=81W86cR9UByWIRYoVl7E3Hagbg
GI-097 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT: - Mechanical - (N2 gas sensor) [Nohmi Bosai - N2 Gas Sensor - 4083 (LGF, DH 3-LG-2) - Cx4] [Nohmi Bosai - N2 Gas Sensor - 4205 (LGF, DH 3-1-2) - Cx4] SAT L4 <FPT Issue No.18> DH 3-2-2 (2F) An alarm was generated on the BMS screen from the Nâ‚‚ Gas Detection Sensor 5093 associated with DH3-2-2. Upon investigation, it was confirmed that the alarm was caused by a faulty detector as there were not any reason for the sensor to activate. The defective sensor was subsequently replaced, restoring normal operation. The faulty sensor has been sent to the manufacturerâ€™s factory for detailed failure analysis. The investigation is expected to take approximately one month, after which the root cause of the failure will be reported. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624066&prj=521&rqi=EbbCqPMQK43FOIcC3XFwsVwRaM
GI-093 | OS05x-1 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | IST: - Electrical - (Diesel Engine Generator) [CAT / BEMAC - Diesel Engine Generator / DEG Panels - 4875kVA / C175 - 20 - Cx5] <Mech & Elec IST Issue No.8> BMS (3-1-1) A â€œMajor Control Power Failureâ€ alarm was observed in the BMS during a power outage (generator power supply). This alarm was triggered by a momentary loss of power to the fuel pump panel during the outage. A UPS for the fuel pump panel is scheduled for installation in August to prevent recurrence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624055&prj=521&rqi=2lIlNJPmpCGV8QjjvYWWaSIq9u
GI-089 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-15 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | SAT : - Mechanical - (PAC) [Daikin - PAC - FVYCP560MA - Cx4] SAT L4 <FPT Issue No.11> DH - 3-1-1 (DH3-1-1) During testing of Cool Array and STS L4, the temperature in UPS Room 3-1-1 rose under 100% load. The wall-mounted sensor recorded 38.6Â°C, and the PAC intake near the UPS module rack recorded 44.4Â°C. This is believed to be caused by exhaust from the UPS module blowing toward the PAC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624048&prj=521&rqi=uoosgnsHuA7ZjPaVjxsrSGwoHn
GI-087 | OS05x-1 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | IST: - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx5] <Mech & Elec IST No.6> (Mech and Elec IST for DH 3-1-2) There are chillers on both the OS4x side and the OS2x side. When two units were operating on one side and a unit on the other side started up, chilled water (return) did not flow, causing the return temperature on the other side to rise. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622092&prj=521&rqi=kzM7CDEDwbcIy2uBmn99X9mMs9
GI-086 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | IST : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx5] <Mechanical and Electrical IST Issue No.5> (DH 3-1-2) It has been determined that the method for obtaining chiller status and the chiller skip logic do not comply with Equinix standards. ãƒ»Chiller status must be obtained via a hardwired connection from the chiller controller. ã€€Current situation: Chiller status is not obtained directly from the BMS; instead, a judgement is made based on the pump status. ãƒ»The chiller must be switched to the standby unit if it fails to meet both of the following conditions for a period of 5 minutes: >>Flow rate at the chiller flow meter is at or above the minimum required flow rate >>Chiller outlet temperature is 21.5Â°C (specification +1.5Â°C) or below | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622091&prj=521&rqi=3muoHhW1RKPQL5GA2nX9ucUssO
GI-085 | OS05x-1 | APAC | Ready for Verification | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | IST : - Mechanical - (PAC) [Daikin - PAC - FVYCP560MA - Cx5] <IST No.4>_Nikken_Shinryo_(DH 3-1-2) While the system was under 100% load, a high-temperature alarm (60Â°C) was triggered in the UPS DH 3-1-2 bus duct. It was believed that the cause was a rise in temperature in the UPS room. At that time, the temperature on the front of the UPS module panel was recorded at 32.7Â°C. 4 PACs were operating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622090&prj=521&rqi=xDX4mUVqwffQRKqU5KP1X757Vs
GI-084 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | <HLT/IST No.3>_JCI_(DH 3-1-2) On the BMS screen while the generator is supplying power, the power transmission line remains green, should be red. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622089&prj=521&rqi=mrddjYfb5xViOONBkpqAfrFTuC
GI-088 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | IST: - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx5] <Mechanical and Electrical IST issue No.7> (DH 3-1-2) If a power outage occurs while the chiller is operating in tank charging mode, there is a risk that high-temperature chilled water will continue to be supplied to the Cool Array until the chiller restarts, in order to maintain tank charging mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622093&prj=521&rqi=h7d6m8PECnhoJi39gm6tOA325p
GI-105 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Commissioning Authority |  | General Contractor [GC] | Commissioning | [6 empty] | (DH 3-1-1, DH3-1-2) Lessons Learned Incorrect Data Logger Installation Location/ ãƒ‡ãƒ¼ã‚¿ãƒ­ã‚¬ãƒ¼ã®è¨­ç½®å€‹æ‰€é–“é•ã„ The temperature data loggers supposed to be installed at the same location as SLA sensors are not equidistant. E.g. below pic, gap between two adjacent data logger locations is significantly different. Is this as per the Exhibit C section I shared before, or as per the OS4x SLA sensor locations. Please confirm that the data loggers are in same position as the SLA sensors. Pressure sensor locations are also different from aisle to aisle. Please confirm those as well. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627197&prj=521&rqi=YwjQJhgr0jOisi7enWcwbBUW5L
GI-104 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Commissioning Authority |  | General Contractor [GC] | Commissioning | [6 empty] | (DH 3-1-1, DH3-1-2) Lessons Learned Issues regarding the installation of Temporary HAC / ä»®è¨­ã‚­ãƒ£ãƒƒãƒ”ãƒ³ã‚°ã®æ§‹ç¯‰é–“é•ã„ â€¢ The HACs are opened from front and back of the aisles, causing a short circuit between cold and hot aisles. This is different from what a DH with permanent HAC would look like and seems to be giving higher temperature reading. â€¢ It seems that to avoid reading too high temperature at the coil, they have put vinyl sheet blocking the airflow. This is basically manipulating the results and needs to be fixed. â€¢ The HAC installation quality is not very good and it seems to be coming off from many locations. Is it purposefully opened? If not, please ask GC for a proper installation. â€¢ The HAC start (in the CRAY side of DH) seems to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627196&prj=521&rqi=5XTAL2VZ9MvV5OWxkvPXwMg22c
GI-083 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-11 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | HLT : - Mechanical - (Cool Array) [Vertiv - Cool Array Unit - TW240 (3 coil) - Cx4] <HLT No.2>_Nikken_Shinryo_DKSH_(DH 3-1-2) The Î”T setting for the Cool Array was changed from 12Â°C to 11Â°C, resulting in an increase in the design airflow rate for the Cool Array (66774CMH/unit >> 72000CMH/unit). During the L4 HLT, a temporary capping was installed and an airflow measurement was conducted at 100% load; the results showed that the airflow was insufficient relative to the total design airflow rate following the design change. At that time, the maximum fan speed for the Cool Array was set to 70%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622088&prj=521&rqi=SAFKoTgGUXYVCwibxXkJxxnSeL
GI-081 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.10> (Chiller) DH - 3 - 1 - 2 During Adjustment of flow rate fluctuation during chiller stage-up/down, minor alarm on Chiller No.6, compressor No. 2 was generated. Upon confirmation it was identified as Rotor Starting Torque Fault. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621055&prj=521&rqi=aDywYsnNbfnKsiwowjthO2vsK1
GI-077 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.6> (Mechanical) Chiller 3-1-2 Before Chiller No. 6 failure test, all compressors stopped due to low flow protection. It was continued the test after the alarm was reset, but the issue was not observed again. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620847&prj=521&rqi=Ycdlr11eAe1sPbgojb6pyEcRc8
GI-076 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.5> (Mechanical) Chiller DH 3-1-2 During Chiller failure test, 3 phase overcurrent alarm (Chiller No. 1Compressor No.1, 2 and 4) was generated when Chiller No. 1 started. Subsequent investigations revealed that approximately 200 seconds after the chiller started up (with a 120-second stage delay), the condenser fan speed dropped to 0%, causing the compressorâ€™s power consumption to rise and triggering a â€œ3-Phase Overcurrentâ€ alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620845&prj=521&rqi=tTWrQd9QYV5sbJl0ezi3qgjr0b
GI-080 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.9> [Chiller] (DH - 3 - 1 - 2) During Chiller failure test, a major alarm was generated on Chiller No.10, which was in operation.(temperature sensor fault) After resetting the alarm once, normal operations resumed. NTTF is currently investigating the cause. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620895&prj=521&rqi=NgHZbu8nZSIjGlG3gmFG3RyuRS
GI-078 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.7> (Chiller) (DH - 3 - 1 - 2) When the connector between the chiller controller for the Chiller No. 6 and the UPS battery was disconnected, no major fault alarm was triggered. After that, only the pump continued to operate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620893&prj=521&rqi=IQoh53HE0c0OoTdbRKNHGKoG3W
GI-079 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.8> [ Chiller] DH - 3 - 1 - 2 During Chiller failure test, 3 phase overcurrent alarm (Chiller No.9 Compressor No. 1) was generated when Chiller No. 9 started. Subsequent investigations revealed that approximately 200 seconds after the chiller started up (with a 120-second stage delay), the condenser fan speed dropped to 0%, causing the compressorâ€™s power consumption to rise and triggering a â€œ3-Phase Overcurrentâ€ alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620894&prj=521&rqi=39XyGuRjSUvngFX71BnTYbR9c4
GI-073 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-04-24 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.2> [Mechanical] <Chiller No.7> (3-1-2) During the pre-startup check for L4, a communication error was detected in condenser fan 10B (#20) of Chiller No. 7. This communication error did not occur during the L3 test. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619436&prj=521&rqi=qCT3SvABGqWwBkAAzbpkKUEWRo
GI-074 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.3> (Mechanical - L4) (3-1-2) Chiller No.8, System - 1 Chiller No.9, System - 2 Chiller No.12, System - 1 During the pre-startup check for L4, the refrigerant liquid level sensor reading was showing 0% on the chiller screen. This communication error did not occur during the L3 test. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619437&prj=521&rqi=uvQnfFecjQVWuRBjZAlxmDighY
GI-072 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | SAT : - Mechanical - (PAC) [Daikin - PAC Unit - FVYCP560MA - Cx4] During the L4 test of cool array , UPS Room 3-1-2 recorded a peak temperature of approximately 46.4Â°C at 100% load. It was confirmed that exhaust from the UPS module was blowing directly onto the temperature sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618787&prj=521&rqi=yiR1RJCYIL9v2ZaRac0UOfnBUr
GI-070 | OS05x-1 | APAC | Closed | P3 Low CX | takahirowatanabe@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | A scratch was found on the condenser of Chiller No. 4-3-CH-12-13. Please carry out the necessary corrective action. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618234&prj=521&rqi=jf0UNanEc8VExpXxP2u5D94TMV
GI-071 | OS05x-1 | APAC | Closed | P2 Medium CX | takahirowatanabe@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx3] Discoloration of servo labels inside the power distribution panel. ãƒ»The report revealed that the servo labels inside the panel had discolored (It is believed this occurred during the commissioning and adjustment phase) ãƒ»During the commissioning and adjustment phase of this project, when the CRAH was operated at 100% capacity, an incident occurred where the fans stopped (breaker tripped) for units equipped with AHF (LG, 1st floor). ãƒ»From April 8 to 10, we performed AHF readjustments on the 22 CRAH units in the north and south sections of the first floor. ã€€For the CRAH units in the south section of the first floor, we operated the CRAH at 100% capacity overnight with the AHF turned on, ã€€and upon measuring the temperature, confirmed it was approximately 45Â°C. (We will continue to perform these adjustment tasks.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618236&prj=521&rqi=wygYxt9CykbWKVYuQ61yXaeTyg
GI-066 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT <Generator> The generator panel Tag seal has not been signed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197428&prj=521&rqi=4KI0O5dOZxHlmSqdajMjAJTebx
GI-069 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT <General> There are lot of equipment which are not yet finished (example : cable installation) but the vender declared L2A completed on the Tag Tracker. (UPS, STS, etc) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197433&prj=521&rqi=SI3DSaUJHLAo7HvYjUxL3LBtG9
GI-065 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT <DEG Indoor Panel> The actual nameplate of the DEG (indoor) panels were different from the entries in the Tag Tracker, as confirmed by Kinden. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197427&prj=521&rqi=UACOzlaOo0QcJYOcz8QFp9nMT0
GI-068 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT <General> There were electrical equipment that are not included in the Tag tracker which was previously confirmed by Vendor. Such as Panel (LG-3-MDSB-12-PCP-1, LG-3-MDSB-12-PCP-2). We advice to Kinden again to verify the Tag Tracker if any equipment are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197430&prj=521&rqi=6F1fxJhgeAn1EmMQYTCK3dqLVu
GI-059 | OS4x-F1 | APAC | Closed | P3 Low CX | takahirowatanabe@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | Fire IST DH 2-2-2 During N2 exhaust fan (4-2-EF-12-N2-4) startup, local operation of MD1-N2-4 was confirmed, but display operation on the BMS could not be verified. Subsequently, it was confirmed that the point for the subject MD was not being acquired by the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483407&prj=512&rqi=orv2c3oqS72TzcFo2SgVXzRftS
GI-049 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 2.) <IST> <DH 2-2-1> <Mechanical> 2026/02/04_ IST Test 9 â€“ Simulated Failure and Recovery of One Representative Cool Array Unit (Coil Failure to N) (Confirmation of Operation without Redundancy): After the communication cables for the CRAY fan and valve were disconnected, the cables were reconnected as part of a recovery operation, but the BMS and the site did not return to normal operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199315&prj=512&rqi=2gZsdUGFsuXpkA8KQtilara5aJ
GI-046 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 10.) <HLT> <DH 2-2-2> <Mechanical> During the HLT and IST, the following unexpected alarms were raised: DH2-2-2 HLT 13:49 CH6 COMP4 Bearing Fault [During Test 5 (100% Load) ] 17:28 CH6 COMP4 Bearing Fault [During Test 6B (Cool array power supply switching test) ] DH2-2-1 IST CH6 COMP4 Bearing Fault [During Test 13 (Cool Array communication failure ) ] | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199310&prj=512&rqi=jrBL6koDcAsD6OwmhhJBtgrxit
GI-050 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 3.) <IST> <DH 2-2-1> <Mechanical> 2026/02/05_ During test No.13 in chiller No. 6, bearing fault alarm was generated. ã€Motor Single Phase Overcurrent Faultã€‘ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199316&prj=512&rqi=y6KiPThDCio2FOUltB2TFi93Wb
GI-043 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 7.) <HLT> <DH 2-2-2> <Mechanical> During the HLT, the following unexpected alarms were raised: DH2-2-2 HLT 12:50 CH5 COMP4 Inverter Temperature Fault [During Test 5 (100% Load) ] 16:44 CH5 COMP4 Inverter Temperature Fault [During Test 5 (100% Load) ] 17:27 CH5 COMP4 Inverter Temperature Fault [During Test 6B (Cool array power supply switching test) ] Although a manual reset temporarily restored the system, the same fault occured three times in the same compressor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199307&prj=512&rqi=RTW8UXNShqcOJl9MvfWFxDgm77
GI-038 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 2.) <HLT><DH 2-2-1> <MECHANICAL> 2026/02/03_ During HLT Test-4 (75% Load), an unexpected alarm was triggered due to a condenser fan communication error while chiller unit 10 was operating, and a minor alarm was reported by the central monitoring system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199301&prj=512&rqi=HJSwfpXaZHvqfbCGRXnl6p5Mj0
GI-042 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 6.) <HLT> <DH 2-2-1> <Ductwork> 2026/02/03_ After HLT Test-5 (100% load) test, the wall-mounted temperature sensor in UPS room 2-2-1 recorded 29Â°C. Check the design temperature and the recommended environment for the UPS unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199306&prj=512&rqi=klQ5QH0QHxa4VGrPsjPhBbT3Oj
GI-052 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 5.) <IST> <DH 2-2-1> <Mechanical> 2026/02/05_ In IST Test-14 (Chiller Failure), the chiller was simulated to fail by disconnecting the connector between the chiller controller and the UPS battery. The chiller was restored according to the procedure written in the script, but the unit on-site and display on the BMS did not return to normal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199318&prj=512&rqi=3YWuCzbSIKrrT7unXgg3bw5pZm
GI-045 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 9.) <HLT> <DH 2-2-2> <Mechanical> 2026/02/10_ DH2-2-2 HLT During the HLT, the following unexpected alarms were raised: 13:21 CH6 COMP1 Rotor Starting Torque Fault [During Test 5 (100% Load) ] 13:49 CH6 COMP1 Rotor Starting Torque Fault [During Test 5 (100% Load) ] Although a manual reset temporarily restored the system, the same fault occured twice in the same compressor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199309&prj=512&rqi=sQTLnSV9bn6LYcMrXiujbyIJDa
GI-041 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 5.) <HLT> <DH 2-2-1> <Mechanical> 2026/02/03_ During the HLT test, MSFT pointed out that the CRAY ATS enable/disable and selected priority might be required to be displayed on the BMS screen. The same are not displayed in T1. MSFT will confirm internally and revert back on this requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199305&prj=512&rqi=fwLcDtTb1qSRbtsaBUgp7FmepT
GI-037 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 1.) <HLT> <DH 2-2-1> <BMS> 2026/02/03_ The hot aisle containment was not drawn correctly in the BMS, so this needs to be corrected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199300&prj=512&rqi=LC6ojvYPRvkNibpXGHtj2jUKkM
GI-040 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 4.) <HLT> <DH2-2-1> <Mechanical> 2026/02/03_ HLT Test 6B â€“ Cool Array Power Supply Switching Test (Common UPS to AC UPS): In the test script, the ATS switching time to be changed from 25 minutes to 5 minutes in order to shorten the test time, but the CRAH-1 ATS switched after 25 minutes instead of 5 minutes | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199303&prj=512&rqi=vImFOO7mOQkYSTm0gcUvfebhD5
GI-053 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 6.) <IST> <DH 2-2-1> <Electrical> 2026/02/05_ In IST Test-18 (STS MCDT automatic switching), the control panel of the simulated load banks was connected under a DP panel that did not have a switching function, so if the target breaker on the UPS output panel was opened, the load banks would lose power and the device could have failed. Therefore, the UPS output breakers other than the one on the load banks control panel were opened and the test continued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199319&prj=512&rqi=9anOmIJtWdxKNiEoWySZ9eUfvd
GI-044 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 8.) <HLT> <DH 2-2-2> <Mechanical> 2026/02/10_ 13:29 CH5 COMP4 Motor Single Phase Overcurrent Fault [During Test 5 (100% Load) ] 15:37 CH5 COMP4 Motor Single Phase Overcurrent Fault [During Test 5 (100% Load) ] | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199308&prj=512&rqi=mqE2142aByx8j1ONMmE8DbXAJy
GI-039 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 3.) <HLT><DH2-2-1><Mechanical> 2026/02/03_ During the HLT and IST, the following unexpected alarms were raised: Although a manual reset temporarily restored the system, the same fault occured multiple times. DH2-2-1 HLT (Issue no. 39) During HLT Test 5 (100% step load test), a minor alarm (Motor Single Phase Overcurrent) was generated on Chiller No. 8. COMP3. DH2-2-2 HLT (Issue no. 44) 13:29 CH5 COMP4 Motor Single Phase Overcurrent Fault [During Test 5 (100% Load) ] 15:37 CH5 COMP4 Motor Single Phase Overcurrent Fault [During Test 5 (100% Load) ] DH2-2-1 IST (Issue no. 51) During test 12 minor alaram (Motor Single Phase Overcurrent Faul.) on chillor No. 7 COMP2 was generated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199302&prj=512&rqi=JBGeCMydcefUM1vPRKPujv6ixI
GI-047 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 11.) <HLT> <DH 2-2-2> <General> 2026/02/10_ There is hole found in the SLA sensor bracket. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199311&prj=512&rqi=XInbyeeyZvvF6yun0ZwwB9qstl
GI-048 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 1.) <IST> <DH 2-2-1> <Electrical> 2026/02/05_ During the simulation of failure of three modules on UPS No. 1, the specification states that the system should transfer to internal bypass after one minute. However, during the actual test, the power transferred to bypass immediately. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199312&prj=512&rqi=2wqX3ixlRItiqXQEJd6XhMezkK
GI-054 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 7.) <IST> <DH> <Fire> 2026/02/05_ As there were no changes to the automatic fire alarm system or gas fire extinguishing system in this project, the test script agreed upon in advance did not include a Fire IST. On the day of the IST, MSFT requested that the test be carried out, and it was adjusted the schedule. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199320&prj=512&rqi=HHdHBWEjXS5kyAMMUVlii6fjnN
GI-057 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 10.) <IST> <DH 2-2-2> <Electrical> 2026/02/13_ During IST Test-15 (utility power failure/ restore), An insulation caution alarm was triggered at 2-SS2-TRB1. Since the affected system is an air conditioning outdoor unit, the test continued while investigating the cause. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199324&prj=512&rqi=d5VgcwDARc7KIuNa7yeJSk5mg4
GI-051 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 4.) <IST> <DH 2-2-1> <Mechanical> 20206/02/05_ During test 12 minor alarm (Heat source unit alarm.) on chiller no. 7 was generated. ã€Motor Single Phase Overcurrent Faultã€‘ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199317&prj=512&rqi=9RKKpHaamQ43s7orLLCRyWD9YM
GI-056 | OS4x-F1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning | [6 empty] | IST : - Electrical - (Diesel Engine Generator) [CAT / BEMAC - Diesel Engine Generator / DEG Panels - 4875kVA / C175 - 20 - Cx5] 9.) <IST> <DH 2-2-2> <Electrical> 2026/02/13_ During Test-15 (A, B-line utility power failure), an alarm was triggered on the BMS after starting Generator No. 7. Power supply were performed without issue. ãƒ»Auxiliary equipment failure batch alarm ãƒ»Charger 2 failure alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199323&prj=512&rqi=G8TLP201WohtACvqLf6vsAIYBY
GI-055 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 8.) <IST> < DH 2-2-2> <Mechanical> 2026/02/12_ In Test-9 (Cool Array Coil Failure), after disconnecting Valve-5 of 2-2-CRAH-12-19, Valve-3 became offline. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199322&prj=512&rqi=5YKwyIPL7gsIqAC6xWnSg4uzfI
GI-058 | OS4x-F1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | General Contractor [GC] | Commissioning |  | equipment type |  |  |  |  | IST : - Electrical - (STS) [Kokubu Electric - STS - 0300101 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300201 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300301 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300401 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300501 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300601 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300701 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300801 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300901 - 1150 kVA- Cx5] 11.) <IST> <DH 2-2-2> <BMS> 2026/02/13_ During Test-19 (STS MCDT Switching), The signal wire used to transmit status information to the BMS was found to be disconnected. As a result, the â€œPower ONâ€ indication was not displayed in the operational section of the STS status screen on the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199325&prj=512&rqi=2lzGpEzCyj66Xbs1Zwf0sL1SsH
GI-036 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-26 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | <SAT Mechanical> Cool Array, OS4x-F1(T2) The vendor is required to provide the technical specifications for the Cool Array temperature sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197565&prj=512&rqi=661Hkk80v3Eo9oqtyVMiTZqwbX
GI-034 | OS4x-F1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-01-26 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | SAT : - Electrical - (UPS) [Mitsubishi - UPS - MELUPS 9800G - Cx4] <SAT, Electrical> DP Panel, OS4x-F1(T2) During the load test of the DP panel, the UPS triggered an overload alarm and switched to bypass operation. Since the test was conducted at 96% load (2300 kW), investigate the cause of the overload alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197562&prj=512&rqi=NsGflnFLQdZ4BtYKW87qasGcKc
GI-035 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-26 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | <SAT Mechanical> Water Leakage Sensor, OS4x-F1(T2) The water leak detector sensor in the PAC location was found with a loose cable. Verify that all sensor cables are properly secured before conducting the IST. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197564&prj=512&rqi=JaW9bNZjPAhV4tLgXipHhlGP3s
DCIML3-1-002 | PA10-P1 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS Template Issue | DCOS | Integrated Automation | system | DCIM |  |  |  | UPS Resiliency Calculation must be update to integrate UPSs of Block A Generator Resiliency Calculation must be update to integrate Gen Block A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614833&prj=613&rqi=7n5VU837Sab8CexhZRWcfWP1tE | https://equinix.facilitygrid.co.uk/x/project/613/system/12280
BT1DCOS-1-001 | PA10-P1 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCIM Cooling Zone Issue | DCIM | Integrated Automation | system | DCIM |  |  |  | Location Vector missing for Mech assets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614797&prj=613&rqi=5NqjEONSzm4mR74w6zxBrdfmaI | https://equinix.facilitygrid.co.uk/x/project/613/system/12280
DCIML2B-1-001 | PA10-P1 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS | L2B | DCIM Maximo Issue | DCIM | Integrated Automation | system | DCIM |  |  |  | Maximo ID asset missing for all PA10.P1 assets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614798&prj=613&rqi=7vlMYf22K8zf72c6LJKguGaabq | https://equinix.facilitygrid.co.uk/x/project/613/system/12280
DCIML3-1-001 | PA10-P1 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS Template Issue | DCOS | Integrated Automation | system | DCIM |  |  |  | List of assets cannot be upsert on DCIM, sync issue 1_GEN_A 1_GEN_A_DT 1_CWST_01_FCV03 1_MVTB_A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614807&prj=613&rqi=nCxFCjBA9anWcIKVd6Y2vEdlx3 | https://equinix.facilitygrid.co.uk/x/project/613/system/12280
DCIML4-2-001 | PA10-P1 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCIM Cooling Zone Issue | DCIM | Integrated Automation | system | DCIM |  |  |  | Zone informations (Location Vector) missing for all assets concerned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614809&prj=613&rqi=3NHvfwaAIXI7TesWQ3sWYskahk | https://equinix.facilitygrid.co.uk/x/project/613/system/12280
GI-010 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-02-26 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1-CRAH-M1-043 | CRAH - Computer Room Air Handler (CHW) |  |  | During L4 redundancy testing of the CRAH, The Kopex condensate drain pipe of the CRAH became loose as fans were rotating and became lodged. This caused an audible noise and CRAH was disabled to investigate and test was paused. After investigation was carried out by VERTIV representative, it was agreed the CRAH was not visually damaged and to continue the redundancy test to completion. Replacement of damaged pipe plus any further inspection may be required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352274&prj=613&rqi=Kool3AqCnxwz2nsUIbM8xL1wYX
GI-009 | PA10-P1 | N-EMEA | Closed | P2 Medium CX | paulm@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1-FCU-R1-01 | DXID - FCU/DX Indoor Unit |  |  | Asset name is incorrect. DCOS naming indicates 1-FCU-R1-30 Clarification is urgently required as RT, YT, Test reports and Facility Grid will require amending to the correct asset name. Formal proof of correct name required to close issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198245&prj=613&rqi=JS7I7An6Dui88qX94KBcfA9Sux
SOR-10-001 | PA10-P1 | N-EMEA | Closed | P2 Medium CX | andrewa@straightlineconsulting.co.uk | 2026-01-30 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Racking out system of the G2 Breaker is faulty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198014&prj=613&rqi=hMDIIdvK1jkd8S4MRKNkDTMHGw
GT1ELEC-2-001 | PA10-P1 | N-EMEA | Closed | P2 Medium DCOS | mirceag@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ MV | equipment | 1-MVTB-A | MVTB - Medium Voltage Transfer Board |  |  | 1-MVTB-A Point to graphic issue As shown in the attached screenshots, the status displayed does not match the graphical status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197719&prj=613&rqi=rkqq3cvSb0RrXoxdttae7YjDZB
SOR-6-002 | PA10-P1 | N-EMEA | Closed | P3 Low CX | mirceag@straightlineconsulting.co.uk | 2026-01-23 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | Electrical â€“ LV | equipment | 1-GEN-A | GENL - Generator (LV) |  |  | 1-GEN-A FUEL SYSTEM CONTROL PANEL CPA10c During the visit of the CPA10c control panel i found the new cables installed are not labelled and some existing cables but not connected to any terminal .(currently loose) , they should be at minimum isolated and terminated into WAGO | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197505&prj=613&rqi=OK12OpdCDDJsTPXRWHe68q1hH0
YT1ELEC-2-001 | PA10-P1 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-01-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1-MVTB-A | MVTB - Medium Voltage Transfer Board |  |  | Arc Flash Labels are not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197506&prj=613&rqi=EnGznRi1dBnbH0B4TNsisJWgTh
YT1ELEC-53-001 | PA10-P1 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-01-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1-MLTX-A | MLTX - Transformer (MV-LV) |  |  | Arc Flash Labels are not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197504&prj=613&rqi=k5noABOe6wukJEqRhTTpDI3U8g
RT1ELEC-22-002 | PA10-P1 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | CMM - Cummins | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1-DP-A-3 | DB - Distribution Boards |  |  | The label for Q7/10A the labels shows Q7/2A . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196767&prj=613&rqi=qCWmfbRKfewXOXELuPxEp4ViJq
RT1ELEC-22-001 | PA10-P1 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | CMM - Cummins | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1-DP-A-3 | DB - Distribution Boards |  |  | Permanent equipment labels affixed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196763&prj=613&rqi=huf7DBFI2FIdD4nNPqf9yh7OAz
YT1MECH-27-003 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Installation not complete | Commissioning | Direct Expansion â€“ DX | equipment | 1-CU-R1-30 | CU - Condensing unit |  |  | Drainage Lines are not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196710&prj=613&rqi=zXZ291hPQr6qInimlyoZsETzLW
YT1MECH-27-004 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Documentation not issued/ Required | Commissioning | Direct Expansion â€“ DX | equipment | 1-CU-R1-30 | CU - Condensing unit |  |  | Vendor L3 Start Up Method Statement not available on Project Portal | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196711&prj=613&rqi=1Ej3mnBLi0ftiBplKU3NQkTOBT
YT1MECH-26-001 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Documentation not issued/ Required | Commissioning | Direct Expansion â€“ DX | equipment | 1-FCU-R1-01 | DXID - FCU/DX Indoor Unit |  |  | Missing Installation and Start-up Manual for DX | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196708&prj=613&rqi=sppnLgcoQ3pENzlsrAj0FfoP2J
GI-008 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-08 04:00:00.000 +0400 | Electrical Engineer |  | Documentation not issued/ Required | Commissioning | [6 empty] | DX Sequence of operation - PA101-BYE-ZZ-ZZ-TS-M-ZZZZ-0053 Below EQX comments to be updated to SOO and new revision uploaded to ASITE. Part 6 - How are PPR/PCR room low temperatures managed? Part 7.1 - Temperature setpoint adjustment is via DCOS only. How are wall mounted thermostat adjustments restricted to users? Part 7.1 - Battery room conditions are quoted as 22*C +/- 2*C which implies heating-not described here. Clarify including how units are configured to ensure they do not fight each other Part 7.2 - What are major / minor faults? Part 8.1 - Temperature setpoint noted as 22*C-does not cover PCR/PPR rooms Part 8.1 - Does not detail how thermostat is locked against future user adjustment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196595&prj=613&rqi=A51OR6ZjbNEGEdwM7rdWIqPz5V
YT1MECH-31-001 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1-CWST-01-CWP-M1-03 | CWP - Condenser Water Pump |  |  | Correct source / destination cable required to indicate where equipment fed from. Issue applies to 6no. pumps in PPR room. Photo required of all labels to close issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196503&prj=613&rqi=50Vktk91bSJtj0Rnn9zWIntng3
YT1MECH-29-002 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1-CU-M1-30 | CU - Condensing unit |  |  | Power Source / Destination cable label missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196384&prj=613&rqi=G98KVMsvaO95isZJxshmzQ3TEs
YT1MECH-29-001 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Direct Expansion â€“ DX | equipment | 1-CU-M1-30 | CU - Condensing unit |  |  | No drainage lines are installed on unit for condensation. Unit installed inside electrical room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196382&prj=613&rqi=XVtioF9pcF6nGK4EmGGqGTMz4n
YT1MECH-27-002 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Direct Expansion â€“ DX | equipment | 1-CU-R1-30 | CU - Condensing unit |  |  | No drainage Lines are installed on unit for condensation. Unit installed inside electrical room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196383&prj=613&rqi=UmN3gIxxBTkYm6vmWQTU3NceWZ
GT1MECH-51-001 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-05 04:00:00.000 +0400 | Electrical Engineer | L3 | DCOS General Issue | DCOS | Mechanical â€“Air | equipment | 1-CRAH-M1-043 | CRAH - Computer Room Air Handler (CHW) |  |  | When simulating return air temperature / humidity sensor fail, the alarm appears on the CRAH HMI as normal. There is no indication on DCOS of sensor failure or appears in issue log. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196340&prj=613&rqi=W9MpATnKQCHxvvE2wzbbVeuvwN
GT1MECH-51-002 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-05 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1-CRAH-M1-043 | CRAH - Computer Room Air Handler (CHW) |  |  | When CHW inlet supply is isolated, high supply temperature alarm is raised at the DCOS but CRAH HMI shows no indication | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196347&prj=613&rqi=4jIkIsFqpjrrbaZlUVfwUXWAjf
GI-012 | PA10-P2 | N-EMEA | Closed | P2 Medium DCOS | andrewa@straightlineconsulting.co.uk | 2026-07-23 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning | [6 empty] | Temperarture sensor not installed on a section of the Redundant Busbar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630651&prj=661&rqi=pMVH52a4OAmz5bxy8fTF9ePdx2
GI-011 | PA10-P2 | N-EMEA | Closed | P3 Low CX | magatte.sene@eu.equinix.com | 2026-07-16 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | [6 empty] | The Transformer door cannot be opened from the inside. it's imperative to resolve the issue to ensure the safety of personnel working inside the transformer enclosure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629805&prj=661&rqi=zn9gw3dKOQRaubeeJnC6ZCj4NA
GI-008 | PA10-P2 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-06-29 04:00:00.000 +0400 | Electrical Engineer |  | General Design Issue | Design | [6 empty] | Concern has been raised regarding gaps in the false floor around some equipment in UPS. This may affect room cooling when carrying out redundancy testing of the CRAHS during full load testing of electrical equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627321&prj=661&rqi=UfGcTREDYocQc52pTG9ZGZo8bu
GI-005 | PA10-P2 | N-EMEA | Closed | P1 High DCOS | andrewa@straightlineconsulting.co.uk | 2026-05-06 04:00:00.000 +0400 | General Contractor - Electrical |  | DCOS Comms Issue/ Fault | DCOS | [6 empty] | IP Address and VLAN not configured like describe on the SE document DCOS IP Address Schedule. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620645&prj=661&rqi=TsMYKjQbT9jrSIqM5L0ntXxZgF
GI-003 | PA10-P2 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-04-22 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | There is an HMI operational issue on SUDB-2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619211&prj=661&rqi=pP7EQVlXoFjZH7wiD7RAOrKZci
YT1FD-4-002 | PA10-P2 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Fire Detection | equipment | 1-MSD-21 | MSFD - Motorised Smoke Fire Damper |  | VU12 | Cable labels not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619094&prj=661&rqi=Y7tVZ2nqcDTJGQllWvPRTSrbNU
GI-004 | PA10-P2 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-04-22 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | MV Scada issues on SUDB-2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619212&prj=661&rqi=jtKijrplPyxNXMwYfOS172KxJZ
YT1FD-4-001 | PA10-P2 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | 1-MSD-21 | MSFD - Motorised Smoke Fire Damper |  | VU12 | Static Cable Tests and Inspection Reports (power) documentation not available | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619093&prj=661&rqi=kmNOysxZZpbbISIpa1tZLeuDfx
GI-002 | PA10-P2 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-04-16 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | There is a issue with the Power factor on the MVTB-E. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618490&prj=661&rqi=1QbJpwbxQs3Ot9TAs6N6TFceHU
YT1FS-9-001 | PA10-P2 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Fire Suppression | equipment | 1-MFD-155 | FD - Fire Damper |  | CR60-1S VIM | Both cable labels not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617669&prj=661&rqi=T2fjClvv2vlJTVPKxEWgKrGn5V
YT1FS-6-001 | PA10-P2 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Fire Suppression | equipment | 1-MFD-39 | FD - Fire Damper |  | CR60-1S VIM | Both cable labels not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617668&prj=661&rqi=eSNOZeD7rDbgSssvT5H3wtUw6N
YT1FS-4-001 | PA10-P2 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Fire Suppression | equipment | 1-MFD-152 | FD - Fire Damper |  | CR60-1S VIM | Both cable labels missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617653&prj=661&rqi=RPKX8MRQBm3xhd16vgHIIxhSif
YT1FS-3-001 | PA10-P2 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Fire Suppression | equipment | 1-MFD-151 | FD - Fire Damper |  | CR60-1S VIM | Both cable labels not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617667&prj=661&rqi=zFKl9DU7EvzNCGHTxMbjRmKBl6
YT1ELEC-74-001 | PA10-P2 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-03-24 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Documentation not issued/ Required | Commissioning | HVAC | equipment | 1-HT-M2-01-1 | TRACE - Trace Heating |  | Eltrace | L3 Green Tag Cx method statement not available on Asite. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616345&prj=661&rqi=mKD06TFoRNUZqwALAUU4Ix9bhH
RT1ELEC-80-001 | PA10-P2 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-02-26 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1-UMDSB-M1-2-11 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | Permanent equipment labels affixed and are as per approved colour scheme. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483354&prj=661&rqi=pWIwcZBFPD52hShqtYUUB2ekzR
GI-664 | PA12x-1 | N-EMEA | Open | P3 Low DCOS | aarond@straightlineconsulting.co.uk | 2026-09-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Schneider is required to revise the schematics to show the Max Cool activation contact as Normally Open (NO), as specified in the approved SOO. The current schematics incorrectly show the contact as Normally Closed (NC). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637586&prj=263&rqi=JQrmeSVzqIfNtHooBJFvV5JVTd
GI-661 | PA12x-1 | N-EMEA | Closed | P3 Low DCOS | aarond@straightlineconsulting.co.uk | 2026-09-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS | [6 empty] | MOT - MECHANICAL - CRAYS The Enable Setpoint Shift function changes the supply temperature setpoint from 25Â°C to 24Â°C when the coil supply temperature remains 5Â°C above setpoint and the valve position is greater than 80% for more than 60 seconds. The setpoint shift is visible on the Vertiv controller but is not displayed on DCOS. DCOS/Vertiv to investigate and confirm that the active shifted setpoint is correctly communicated and displayed on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637433&prj=263&rqi=T4PzArGz3Hpu8i9zFbKjZg5dej
GI-662 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-09-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Mechanical - Max cool system - in event of loss of power to Max cool panel both supplies, SOO Max cool indicates it max cool should be operated but wiring of the panel & schematics do not. schneider to confirm to if max cool should operate under full power loss | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637431&prj=263&rqi=lSQCk4egtbJs7ndMP5GAvzWM25
GI-656 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-09-03 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Mechanical - Max cool sensors / DCOS gateway sensors - multiple TT sensors are mixed up & wrongly labelled between Max cool system & DCOS GW TT Sensors, All Data halls to be checked 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636671&prj=263&rqi=pmBfoCGU5mqFlHGcdL3mqQ4Hgl
GI-655 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | MOT â€“ CRAYs DH03 Prior to testing the fanwalls, it was observed that multiple sensors were not reporting to DCOS. This issue was first noted following completion of the permanent fanwall shielding rectification, which replaced the temporary fix. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636536&prj=263&rqi=2Dye69iLMPr5M5rrHGSC9Ggaqy
GI-622 | PA12x-1 | N-EMEA | Open | P3 Low CX | gabrielsokolowsky@sygna-emea.com | 2026-08-21 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Commissioning Issue | Commissioning | [6 empty] | 1MSB_R1-Q28 : The micrologic menu cannot be accessed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634590&prj=263&rqi=pa9HnUJGs9zECfxSYI0M1CBSvl
GI-623 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gabrielsokolowsky@sygna-emea.com | 2026-08-21 04:00:00.000 +0400 | General Contractor |  | Cleaning | Commissioning | [6 empty] | Pigeon nest on busbar, phase 1, third floor, above emergency stairs door, MeWall M3 corridor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634595&prj=263&rqi=nVqxO73an7wNang6eqLY660gl7
IST-23-003 | PA12x-1 | N-EMEA | Open | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | REH - Rehlko Gens | L5 | Installation Not Correct | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | IST 2 - Generator - Fire curtains on ground floor rooms B+C failed to close correctly. during IST activation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634211&prj=263&rqi=c2F3dO3NwsCAFX2mWa6nN3WDPZ
GI-621 | PA12x-1 | N-EMEA | Open | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | General Contractor - Electrical |  | DCOS Comms Issue/Fault | DCOS |  | equipment | IST Phase 1.2/1.3 - Test 3.0 Dead Bus Test on String F | integrated systems testing halls 3,4,5 and 6 |  |  | IST 2 - Mechanical - The leak detection alarm for Cable_3_02 was triggered during the test and appeared in the alarm log; however, it was not displayed on the graphics. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634232&prj=263&rqi=0p0IKNm07cbggHg6S0O9uRLtqy
GI-619 | PA12x-1 | N-EMEA | Open | P3 Low DCOS | jayb@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | REH - Rehlko Gens |  | Component/Equipment Failure | Commissioning | [6 empty] | IST 2 - GEN SCR F,B,M1 and M3 - Power line/ gen graphics showing live on DCOS intermittently even though gens not running. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634229&prj=263&rqi=VH10FX61qN9Wb83pRKQhUGKppR
GI-620 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | jayb@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning | [6 empty] | IST2 - GEN C showing comm alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634230&prj=263&rqi=OlVyswK1OONUnBDkjxf0rDm73G
IST-31-001 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | jayb@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | General Contractor - Commissioning | L5 | Installation Not Correct | Commissioning |  | equipment | IST Phase 1.2/1.3 - Test 7.0 Failure of Mechanical Block M2 and IT Block B | integrated systems testing halls 3,4,5 and 6 |  |  | IST 2 - MLTX B core temps showing high core temp on L3 when all other MLTX show higher core temp on L2, suspected incorrect sensor termination in MARS panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634221&prj=263&rqi=2Fvk8tHqNTADY8T1BAm3mTaHLD
IST-23-004 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | General Contractor - Commissioning | L5 | General Design issue | Design |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | IST 2 - Fire alarm - Thermal detectors in all Gen rooms to be replaced by Smoke detector. during IST 2x thermal detectors activated due to heat from Gen B+C. All thermal detectors are currently isolated via Graphic operating PC for SSI system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634213&prj=263&rqi=NaU52VwFXMXzDxTBFbHeaTpdYT
IST-24-014 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-08-17 04:00:00.000 +0400 | General Contractor - Commissioning | L5 | Documentation Not issued/ Required | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Block R2. All testing documentation to be submitted for Vesda and Smoke Detection ZDA213 ZDA205 ZDA207 ZDA212 ZDA090 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633938&prj=263&rqi=khGR8RMEYhNUJVFbBUG7sEePuE
GI-618 | PA12x-1 | N-EMEA | Open | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-17 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning |  | equipment type |  |  |  |  | Fire Alarm - SSI Graphic PC not yet tested for Phase 1 system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633936&prj=263&rqi=EiPpa3RHjKSTdg7L6MNmTmKLKa
GI-614 | PA12x-1 | N-EMEA | Closed | P3 Low DCOS | joshw@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | DCOS - HLT 2 Ras_04 deviation alarms - 6,7 13,15,16,17 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633775&prj=263&rqi=UxZ7yg0Ui8qvr7QAFbB0Fc7Y1h
GI-611 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | HLT 2 -Mechanical - AHU's Not working at correct temperature control & operation. Control of heating and cooling systems to be investigated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633770&prj=263&rqi=hvhsLg9jvtDar7obld3RpF1mlf
GI-613 | PA12x-1 | N-EMEA | Closed | P3 Low DCOS | joshw@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [6 empty] | Mechanical - HLT 2 - Ras_04 devation alarms - 6,7 13,15,16,17 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633774&prj=263&rqi=raelVvcr6pghgAD6TmTwSfBOJM
GI-612 | PA12x-1 | N-EMEA | Open | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | HLT 2 -Mechanical - All Cool Array panels wiring has been amended with poor install & needs correctly installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633773&prj=263&rqi=AY6by4EfnVqITXNggvc0AaDARI
GI-616 | PA12x-1 | N-EMEA | Open | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | General Contractor - Electrical |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Electrical - HLT 2 - AHF 02 & 03 - General warning on both units to be investigated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633781&prj=263&rqi=IIhSMlF7364vHyniyYihCD4052
GI-609 | PA12x-1 | N-EMEA | Closed | P3 Low DCOS | markb@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | LLT - During Fuel Control Panel Controller Failure - DCOS alarm to be changed to red critical alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633764&prj=263&rqi=HWVnkwAl5C8V4WaAhbazPvBAhb
GT1MECH-744-001 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-08-14 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Documentation Not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | Leak detection - TQ Panel ( Refrigerant) | LEAK - Chilled water system leak detection |  |  | Electrical - Missing live cable test results | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633617&prj=263&rqi=RjNzSARw6bcmknTxyDHGq8n9rH
YT1MECH-671-001 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-08-14 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Documentation Not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | Leak detection - TQ Panel ( Refrigerant) | LEAK - Chilled water system leak detection |  |  | Electrical - Missing Dead cable test results | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633618&prj=263&rqi=eIvH5uFJ3s5PFjaFI2tOWL0VJG
IST-24-013 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | jayb@straightlineconsulting.co.uk | 2026-08-14 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Complete | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | sounder Head has been removed from wall | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633616&prj=263&rqi=ZtepMLHG9YyRVQrl9Q2MB5C2Tr
IST-24-012 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-13 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Component/Equipment Failure | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - During HLT ZDA228 activated 2 times without any smoke present in the area. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633394&prj=263&rqi=npCJ7k85WZQdTry4tJhJGk45oA
GI-607 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gabrielsokolowsky@sygna-emea.com | 2026-08-10 04:00:00.000 +0400 | Customer Access |  | Commissioning Issue | Commissioning | [6 empty] | XX | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632883&prj=263&rqi=zIEnCYqZjXesIHVjJ8tp08Q7oa
IST-24-011 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-08 04:00:00.000 +0400 | General Contractor | L5 | Installation Damage | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Fire Door damage. Location: ground floor FoH entrace to phase 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632776&prj=263&rqi=xTLVSW2pbyCnU44HAh3O6xNBnp
IST-24-010 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-08 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Design Correction Needed | Design |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - A100/Securitas Security panel to be moved. the placement of this panel stops the door holder magnet to align. Door magnet holder cannot be extended as this would then stop clear Security access being granted to the Access control reader and panel. Location: Ground floor FoH entrance to Phase 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632775&prj=263&rqi=xv11r4XXCr6jA82oMxpNYXmqzq
IST-23-002 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-08 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Documentation Not issued/ Required | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Design documentation to be submitted to PPA and approved for Sign off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632774&prj=263&rqi=nT02Pmx0m8uJNILPPJy7bHdUHK
IST-24-009 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-06 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Correct | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Poor workmanship in Riser 1288 and 1289. images sent to Essais SSI whatsapp group | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632569&prj=263&rqi=msaBSv8pIUBzfrTCiG8t7hMEhc
OPR-1-001 | PA12x-1 | N-EMEA | Closed | Outstanding Paperwork/Documentation | gregb@straightlineconsulting.co.uk | 2026-08-06 04:00:00.000 +0400 | General Contractor - Commissioning |  | Design Correction Needed | Design | [6 empty] | Asset List - Missing assets from Phase 1 construction. Stairwell Smoke Vents Nitrogen System Sprinkler Control panel Life safety remote modules (various locations in riser cupboards) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632572&prj=263&rqi=ZgR338dHIEb8sCbjIdw84bHS1X
IST-24-007 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-05 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Labelling | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire alarm - Yellow Ex call points have some labelling errors some examples attached. all Yellow Callpoints to be checked with Photo of each call point and location | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632243&prj=263&rqi=IDZ2G6GkBo8v5bAgVdGV5bZ2aj
IST-24-008 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-05 04:00:00.000 +0400 | General Contractor - Electrical | L5 | General Design issue | Design |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm DCOS - Due to incomplete Phase 2 the trouble signal is constantly active due to Phase 2 Rack being incorporated with Genset rack. Equinix to confirm if DC OPs will accept this constant fault. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632254&prj=263&rqi=Zv0XnifYgbfzfDQD3GhpHWWi4J
GI-593 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-07-29 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Damage | Commissioning | [6 empty] | Mechanical - 1CU_M2R1_58 - condenser fan damage. to be replacedÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631220&prj=263&rqi=GvdUrtMDIyQHjCdT2AXzHnaSVH
GI-592 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gabrielsokolowsky@sygna-emea.com | 2026-07-28 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [6 empty] | Emergency floodlights are not well installed in MVTB rooms : the wall plugs in place seem to be a model for concrete/brick wall but not for a hollow wall. The statement has been done in block D but it would be probably the same in all MVTB rooms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631057&prj=263&rqi=nUVunVSTPaoDsIvZWrhbFnhwxk
GI-591 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gabrielsokolowsky@sygna-emea.com | 2026-07-24 04:00:00.000 +0400 | Commissioning Authority |  | General Design issue | Design | [6 empty] | NEUTRAL PROTECTION ON BREAKER 1) ALL CALCULATION NOTES ARE NOT YET FULLY VALIDATED 2) ACCORDING TO THESE NOTES, NEUTRAL PROTECTIONS ARE 4P4D ON A LARGE NUMBER OF CIRCUIT BREAKERS 3) FOR EXAMPLE ON BLOCK D, breakers 1COP_DR2_1-Q01 and 1COP_DR2_1-Q02 WERE FOUND WITH NEUTRAL PROTECTION OFF (4P3D) WHEREAS ON THE NOTE IT IS 4P4D | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630650&prj=263&rqi=kKJmgvBSM8ZlfkFlNyt88Yrf5B
GI-589 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gabrielsokolowsky@sygna-emea.com | 2026-07-24 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Component/Equipment Failure | Commissioning | [6 empty] | 1COP_ER2_1-Q07 The MTU buttons for accessing the menu are not working. It needs to be determined whether all or part of the circuit breaker needs to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630648&prj=263&rqi=Zx8Y91paZvhhx2OP8xPL18nvdD
GI-590 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gabrielsokolowsky@sygna-emea.com | 2026-07-24 04:00:00.000 +0400 | General Contractor - Electrical |  | Component/Equipment Failure | Commissioning | [6 empty] | 1MDSB_M1R1_3-Q13 During SCCS shift for LV breaker control settings, the authorised person was not able to open the chamber door to access the breaker. This breaker has not been yet checked. Control must be done on W31. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630649&prj=263&rqi=b2F57oo1m0ltZE90WXzGlUI9nl
GI-588 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gabrielsokolowsky@sygna-emea.com | 2026-07-24 04:00:00.000 +0400 | Equinix Project Manager |  | General Design issue | Design | [6 empty] | For LV SCCS (breaker discrimination study - settings control) : 1UDPR_R2-Q29 breaker is used for the needs of the construction site on phase 2. No control possible for the moment. To be deferred to a future verification session dedicated to phase 2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630647&prj=263&rqi=Cabf3mfChbaiPWhZEviwwgIOE0
GI-587 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gabrielsokolowsky@sygna-emea.com | 2026-07-24 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation Not issued/ Required | Commissioning | [6 empty] | No on-site acceptance specific documentation was found for the installation of the (16A TP+N) MCBs of the fan walls, installed on the cool array's BB. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630646&prj=263&rqi=Hw8IuqnXtSGzJI91MwyVpE3dvV
GI-573 | PA12x-1 | N-EMEA | Closed | P3 Low CX | garyd@straightlineconsulting.co.uk | 2026-07-22 04:00:00.000 +0400 | General Contractor - Electrical |  | Cleaning | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_02 | DCOS - HMI Panels |  | SCH - Schneider | mechanical asset need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630276&prj=263&rqi=er0c9CVTXs54zSwVqp3How5BUf
GI-539 | PA12x-1 | N-EMEA | Closed | P3 Low CX | garyd@straightlineconsulting.co.uk | 2026-07-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Correct | Commissioning | [6 empty] | mechanical earth cable stuck in cover 1EXFM_M1R1_02 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629908&prj=263&rqi=2LPzezvjZZq5WYFDxrbUU5Wb4V
GI-537 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-07-16 04:00:00.000 +0400 | REH - Rehlko Gens |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | MOT - Â TTK fuel leak detection system in the pump rooms is now fed from batteries. This change was implemented after IST. Actions required: 1. Provide the intervention report for this change. 2. Provide updated drawings reflecting the new power supply configuration. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629772&prj=263&rqi=fjCGnJfm2Imq1BZJdvNtRedYSM
GI-536 | PA12x-1 | N-EMEA | Closed | P1 High CX | daniel.loayza@eu.equinix.com | 2026-07-16 04:00:00.000 +0400 | SCH - Schneider DCOS |  | General Design issue | Design | [6 empty] | During full load testing of chillers, 3 chiller breakers tripped: MSB M2 - Q-06 - Chiller 1-1 Q-10 - Chiller 3-1 MSB R1 Q-09 - Chiller 1-1 Early indication from AERMEC is that chillers have not over-amped, and early trends from DCOS suggest the breakers in the MSB's did see an overly high current. This leads us to suspect a potential AHF issue or breaker issue that needs to be investigated. BYES need to deploy Danfoss to begin trend gathering and analysis and ITEC need to confirm their equipment is functioning correctly. AERMEC need to provide relevant trend data on those chillers for analysis by the group. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629713&prj=263&rqi=Qtu8miYZ0uy7NPuryVKGVtPZEv
IST-24-004 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-08 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Correct | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - DH1-6 Dampers do not open after fire signal is received. Belimo seems to operate correctly but the damper blades do not open 1SSIRCFD_NO_0159 1SSIRCFD_NO_0160 1SSIRCFD_NO_0161 1SSIRCFD_NO_0162 1SSIRCFD_NO_0163 1SSIRCFD_NO_0164 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628292&prj=263&rqi=5Aw69zXVryFO9498wDnvn9y6Nz
IST-24-006 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-08 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Complete | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - DCOS connection not completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628298&prj=263&rqi=ZBTKGD1BpQJmhimZ2R1J9FB77y
IST-24-005 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-08 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Correct | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Smoke extract dampers failed to operate correctly. Dampers didnt open activation and/or close on reset. 1SD_NC_0021 1SD_NC_0022 1SD_NC_0023 1SD_NC_0024 1SD_NC_0025 1SD_NC_0026 1SD_NC_0027 1SD_NC_0028 1SD_NC_0029 1SD_NC_0030 1SD_NC_0031 1SD_NC_0032 1SD_NC_0033 1SD_NC_0034 1SD_NC_0035 1SD_NC_0036 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628295&prj=263&rqi=XVSfSFgQML9vgH62VDhtyUNrW8
GT1FD-80-002 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-07-07 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Design not as Specified | Design | Fire Detection | equipment | SSI_RACK_1 | FACP - Fire Alarm Control Panel |  |  | Electrical - ZDA. PPA stated thresholds differ from the BYES Aspire design calculations. Should PPA values be adhered too in Design for smoke activation levels? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628249&prj=263&rqi=HEBLsjiQPwq379KJd4F66Fzvsd
GI-504 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-06 04:00:00.000 +0400 | General Contractor - Electrical |  | Cleaning | Commissioning |  | equipment type |  |  |  |  | Fire alarm - All DH1-6 require Vesda pipework to be cleaned. extremely dirty with Dust from construction works in all Halls | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628014&prj=263&rqi=yHANOvWgPpME3al28TpQ58Gug7
IST-24-003 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-07-05 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Documentation Not issued/ Required | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - All updated drawings/documentation to be submitted to PPA for approval prior to C&E testing. As built drawings, C&E Matrix to show agreed changes to allow Testing and checklist to be signed off against valid documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627945&prj=263&rqi=uTH296wEKBvV8VJRTPmGzOxAO6
IST-24-002 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-05 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Correct | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire alarm - Automatic fire compartment doors are not closing sufficiently to seal the barrier of compartment. Air balance could be the issue stopping doors fully closing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627942&prj=263&rqi=at7jWFQNp59Vpe3R2IrEmSMVji
GI-502 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-02 04:00:00.000 +0400 | General Contractor - Electrical |  | General Design issue | Design | Fire Detection | system | Fire Detection |  |  |  | ZDA - within all DH's 1-6 , in certain HAC's the smoke extraction ductwork and sprinkler pipework is obstructing the Vesda detection holes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627688&prj=263&rqi=0OnLtFp4eVtvy9VgXbjpJO7Vtd | https://equinix.facilitygrid.co.uk/x/project/263/system/14098
GI-610 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Labelling | Commissioning |  | equipment type |  |  |  |  | HLT â€“ Mechanical â€“ Vertiv White Space Sensor Naming Discrepancy The Vertiv White Space (Cold Aisle) sensor naming convention does not align with the naming used in DCOS. In the field, the cold aisle sensors are labelled as White Space 3 & 4, whereas DCOS identifies these same sensors as White Space 5 & 6 for all standard Cold Aisles (with the exception of the Extension Units). This discrepancy creates confusion when comparing field readings with DCOS data and during fault investigation. Vertiv is requested to confirm the correct sensor naming convention and ensure all White Space sensors are clearly labelled in the field to provide consistency between the physical installation and the DCOS interface for operations and maintenance personnel. Evidence: DCOS screenshots for DH05 and DH06 are attached, showing the Cold Aisle sensors identified as White Space 5 & 6, highlighting the discrepancy with the Vertiv field labelling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627523&prj=263&rqi=kygs7t3bsV9LqMY9dqDro7kKOp
GI-501 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | HLT â€“ Mechanical â€“ DCOS Temperature and Max Cooling Sensor Labelling The DCOS Temperature Sensors and Max Cooling Sensors throughout Data Halls A, B, C, D, E and F have not been labelled as previously agreed with BYES. The absence of clear identification is causing difficulties when validating sensors during commissioning and fault-finding activities. It will also present ongoing challenges for operations and maintenance personnel when identifying and verifying individual sensors in the future. All DCOS Temperature and Max Cooling sensors should be permanently labelled in accordance with the agreed naming convention to ensure clear identification and maintain consistency with the project documentation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627524&prj=263&rqi=LZDgCvnO3XctRjk7TA1kfyq3N4
GI-500 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Multiple drawing folders have detached and fallen inside the cooling corridors. The folders are not securely fixed and should be re-secured to prevent obstruction, damage, or a potential housekeeping/safety hazard. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627516&prj=263&rqi=Z4P6fxJ1BSnbDVMZGweGj6rYJk
GI-482 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | MOT - Loss of power to out of sequence SCP (2 chillers in standby). The two pumps of the affected string started and went to 40 Hz. The chillers of the affected string started, then different chillers began to lock on flow. The PCP then started other chillers, creating multiple failures on the cascade. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627378&prj=263&rqi=XYOQMsmOOmWR7t62uQ8CiGpMej
GI-489 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | MOT - Simulate Pressure Drop The alarm name on the BMS "Leak detection" does not match the "Pressurization unit in operation" status. The alarm was received on the BMS after a delay of 90 minutes plus expansion tanks dropping below 20% Ã¢â‚¬â€ this is a significant time delay to receive the alarm on the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627387&prj=263&rqi=CtjdW7j4wmtZGohQuI2ykQfRdt
GI-643 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR â€“ PDT sensors in DH04 and DH05 were reading 0.0 during testing. This requires further investigation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627312&prj=263&rqi=M7d22S85fkbL3LDPHoKYodW6Lh
GI-647 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ Mechanical â€“ 1MAU_M3R1_02 generated a SAT High Temperature Alarm (34.5Â°C) at 15:55. At the time of the alarm, DX Unit 1 was OFF and DX Unit 2 was ON. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627320&prj=263&rqi=BvoIh7jOfCQ6NMWAVNmWopNw3H
GI-491 | PA12x-1 | N-EMEA | Closed | P3 Low CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design |  | equipment type |  |  |  |  | MOT - Gas Leak Detection When the refrigerant leak detection system tripped all operating chillers, after restarting the chillers, PRV valves operated and a huge amount of water was observed in the pressurization unit room. The cooling loop PRV valves operating value tags are not in place and the valves are not sealed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627390&prj=263&rqi=YIdSRn7KTS3ABvmFgJA0f7bLBN
GI-652 | PA12x-1 | N-EMEA | Closed | P1 High CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Not Correct | Commissioning |  | equipment type | Data Hall Heat Load Test Phase 2 | Data Hall Heat Load Test Phase 2 |  |  | HLT - Cool Array sensors calibration discrepancies across all halls. HLT â€“ Mechanical â€“ Calibration discrepancy identified between 1CA_M1R1_20, 1CA_M1R1_18 and the Data Hall temperature readings, with deviations of 1.1Â°C and 1.4Â°C. Further investigation - All Vertiv sensors have calibration discrepancies, Sensors have been replaced, software downgrades/upgrades, Factory support on sensors and still issue remains across all halls with calibration discrepancies 3-4+ degrees out | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627337&prj=263&rqi=v1NEyBH4qgqgwlTYiYwjPF3Q6c
GI-645 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Damage | Commissioning | HVAC | equipment | Heat Load Test Hall E | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ Mechanical â€“ A fan fault was identified on 1CA_M1R1_36 (Fan 22) during testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627315&prj=263&rqi=kUSRtblkHgnqrXy5WpKqltthmJ
GI-488 | PA12x-1 | N-EMEA | Open | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning |  | equipment type |  |  |  |  | MOT - 1. There is no site schematic electrical drawing for the unit. 2. The valves and sensors on the unit labels are not matching the names shown on the local system HMI. 3. Updated operation manual and system settings need to be shared. 4. Flow meter for the water supply to the pressurization unit is not connected to the BMS (information shared by the vendor). 5. The PRV is not sealed and the bar value tag is not in place. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627386&prj=263&rqi=d5mbtoBbdGWCWD9RWjboOVQtj2
GI-653 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall E | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ Mechanical â€“ 1CA_M1R1_20 generated a Differential Pressure Alarm (DP1 Out of Range). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627338&prj=263&rqi=gbskYVUjGFpYG9h9vjdipBN8ua
GI-644 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Not Correct | Commissioning | HVAC | equipment | Heat Load Test Hall C | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CA_M1R1_41 - White space temperature sensor reading 29.1 (High High Alarm) when 100% Load is applied | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627314&prj=263&rqi=OtHCrivKBhHQ0wD3Wsvds6ftpU
GI-642 | PA12x-1 | N-EMEA | Closed | P3 Low DCOS | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | DCOS Comms Issue/Fault | DCOS | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CRAH_ER1_27 Had a communication alarm present during the heat load testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627310&prj=263&rqi=g1NGXlsSgxS24Ktf7oJm2K8vH6
GI-463 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | LLT - ,BMS monitoring was observed to be intermittently lost and restored. The vendor confirmed that this is a recurring issue. Schneider attempted to reboot the BMS server on-site; however, the reboot did not restore BMS monitoring. Schneider subsequently conducted an unplanned intervention during the night to restore the system. Actions required: 1. Provide the intervention report for the night activity. 2. Provide RCA for this recurring BMS monitoring loss. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627355&prj=263&rqi=w40MK86SyaBMMqHnBPWTDlM0ou
GI-462 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Cleaning | Commissioning |  | equipment type |  |  |  |  | HLT â€“ Mechanical â€“ The cleanliness of the cooling corridors requires review. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627339&prj=263&rqi=hAyYfGAFV0n84Vy93js4BKPMri
GI-470 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | Design Correction Needed | Design |  | equipment type |  |  |  |  | MOT - Testing at the Fuel Control panel for loss of external fuel pipe heaters. The heat tracing units are placed on site in proximity to MV cables, and some other units are installed behind GRMUs in non-accessible, high-risk safety areas. Maintainability and accessibility issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627364&prj=263&rqi=n6jRzI3PXWajefa9eR30RyE3YQ
GI-472 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | MOT - Testing at the generator control panel for daily tank levels No alarm received on the BMS when failing the analog level sensor on the daily tank. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627366&prj=263&rqi=OLOaxSQA6WcPlRW98kb5OSSteH
GI-483 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | MOT - Loss of flow transmitter FT01 - Evaporator FT on running chiller 1.1. Initial status: Running chillers: CH 1.1, CH 2.1, CH 2.2. Upon failing the FT sensor at CH 1.1: CH 1.2 in the cascade started and CH 1.1 locked at low flow. The bypass valve opened to maximum rapidly due to loss of FT reading. On String 1, with CH 1.2 running: Due to the bypass valve's fast opening reaction, reverse flow occurred from the supply side of the network to the return (dropping the loop pressure). CH 1.2 with pump at 100% could not push water into the supply side loop network. Due to the pressure loss caused by reverse flow, additional chillers started in the cascade. The system took excessive time until the bypass valve closed and the system began dropping the unnecessary chillers. More than -40 L/S reverse flow!!. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627379&prj=263&rqi=ixKTQgiCAmUrXwTkC0Be7h8Ipd
GI-481 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | MOT - Loss of power to running SCP (2 chillers running). The two pumps of the affected string went to 40 Hz. The chillers of the affected string kept running, then later locked on flow. The PCP started the next chillers in the cascade, resulting in multiple chiller failures on flow, while the two pumps kept recycling hot water from return to supply and overpressurizing the loop. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627377&prj=263&rqi=n6fC27mIk61gR5Qdt5yQGs9dqF
GI-492 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design |  | equipment type |  |  |  |  | MOT - FCV valves remain at last know when power loss / comm loss and potentially result in the other chiller on the same string going to low flow situation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627392&prj=263&rqi=GPVtHsJ0GhCgF48EQHbLzyQeDx
GI-471 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | MOT - Testing at the generator panel for loss of power to supply motorized valve in day tank. No alarms received on the BMS when power was cut to the valves. Pumps were shown as unavailable on the FCP panel HMI, which is incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627365&prj=263&rqi=NyBsUF9MqdLY5wys2zStcpGEU5
GI-478 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | General Design issue | Design |  | equipment type |  |  |  |  | MOT - Multiple strings have buffer tanks in bypass mode during steady-state operation. In case of a utility outage, the buffer tanks will not support the critical load (TT05: below 21.5Â°C). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627373&prj=263&rqi=ZNYsonFTn0Ke0X4BK0qbUzdrXm
GI-640 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR_1_2 â€“ Evaporator Low Alarm received at 16:14. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627307&prj=263&rqi=rDS5eFEVcvEnaNb13e9hMvkFnp
GI-490 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning |  | equipment type |  |  |  |  | MOT - 1. There is no wire labeling on the unit. 2. A bad wire connection (exposed wire) was found. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627388&prj=263&rqi=sOczh3Etx6oqNszBGNczbyNo1h
GI-493 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | MOT - Chiller flow switch sensitivity target approx 28 L/s which is noted as below AERMEC setting | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627394&prj=263&rqi=qUtIIW5Y12uEIWCIpZTaxUBC1a
GI-646 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR_2_1â€“ Evaporator Low Alarm received at 13:00 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627317&prj=263&rqi=gYKHd6wOfeajuc5fIPqBAwzs8m
GI-648 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR â€“ Chiller M2R1_2_CH_1 tripped, generating a Chiller Fault alarm at 15:48pm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627330&prj=263&rqi=hby60AEz60172cQtpFTvpp0dtw
GI-496 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | MOT - DPT Riser 3 should also be tested for filtering or scaling behavior. A value jump is noted, but the exact numerical values should be confirmed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627396&prj=263&rqi=sCJQDAU2kR2SQ4cYnpp4Zdtz25
GI-499 | PA12x-1 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1CHWSTR_M3R1_6_ELC_1 | CP - Control Panel |  |  | Mechanical - found blown fuses during tests today. That requires further investigation as it has happened previously. RCA to be provided for each blown fuse. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627472&prj=263&rqi=2OkNiohdsD8wD7NbEgJk8AZkx3
GI-649 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR â€“ Chiller M2R1_3_CH_2 tripped, generating a Chiller Fault alarm at 15:48pm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627334&prj=263&rqi=0UYaVKR2EeQ3n25Ut0NNQLel7k
GI-477 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design |  | equipment type |  |  |  |  | MOT - All 8 SCPs are located in the same fire zone. A loss of all 8 SCPs will start all associated chillers and pumps at 40 Hz. Risks identified: 1. Risk of over pressurizing the loop. 2. Strings that are out of sequence will start and overload the electrical line-ups. 3. Proof that the cooling plant will be able to manage full load without SCPs is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627372&prj=263&rqi=f1i7Kich2RJe5wxCrOSaa6YwlC
GI-650 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR â€“ Chiller M2R1_6_CH_2 tripped, generating a Chiller Fault alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627335&prj=263&rqi=lswKheUqUgBPlQ87DYnmRPQUmV
GI-469 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | MOT - Testing at the Fuel Control panel for loss of external fuel pipe heaters. The alarm on the HMI is not matching the labeling on the unit in the field. The system is not monitored by the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627363&prj=263&rqi=iwuyerqLuYXbQ0UyCLGUApF0GG
GI-639 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR_5_2 â€“ Evaporator Low Alarm received at 15:05. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627305&prj=263&rqi=ZMeWUK9mjDvjwKxALyJiRmVDm0
GI-641 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR_3_1 â€“ Evaporator Low Alarm received at 12:40 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627309&prj=263&rqi=O5isu0o80IwheD47Ho96R1RmNd
GI-651 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR â€“ Chiller 5_1 HMI recorded multiple alarms between 14:37 and 14:48, including Compressor 2 & 3 Overloads, Turbocor 2 Inverter Temperature Alarm, and Turbocor 1 Offline. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627336&prj=263&rqi=0Wyb3MAKtF02mRMF7jQYczUi8d
GI-480 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | MOT - Loss of 24V to out of sequence string SCP (2 chillers in standby) The two pumps of the affected string started and went to 30 Hz. The chillers of the affected string started, then different chillers began to lock on flow. The PCP then started other chillers, creating multiple chiller failures on the cascade. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627375&prj=263&rqi=fJz4UJE3MQXZJayqEqbFk0uEYH
GI-494 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | MOT - DPT Riser 1 should be tested for communication failure. The notes mention a fault with a negative pressure value, approximately -32 Pa. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627395&prj=263&rqi=s31Qe4LG16njTffAIDGRIJtG1w
GI-486 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Design Correction Needed | Design | [6 empty] | MOT - Refrigerant leak detection system (centralized system) testing Ã¢â‚¬â€ Refer to schematic drawing "48 points system" page 11. Opening the closed contact on one relay connected to chiller from Relay Board 1. If the relay board is physically damaged, it will result in opening all normally closed contacts of all relays, leading to shutting down all chillers. Same risk: In case of wire damage from the panel (same cable tray) going out from the panel, this will lead to the same result. Note: On the relay board, each relay normally closed contact is connected to one chiller. Once the relay is energized, the normally closed contact opens, opening the wire loop to the chiller and triggering chiller shutdown. Any cause of opening these wires will lead to chillers shutting down. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627384&prj=263&rqi=718ypyGtivL7cqNld2b3m1SPUo
GI-476 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | Design Correction Needed | Design |  | equipment type |  |  |  |  | MOT - Testing at the Fuel Control panel for loss to individual relays supplying components. Failing one relay inhibits the entire fuel system functionality. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627370&prj=263&rqi=oqHU2yum3l7sUi1oApogdx1Jyl
GI-487 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Design Correction Needed | Design |  | equipment type |  |  |  |  | MOT - Gas Leak Detection The panel is considered as a separate asset and did not have any commissioning tag. Some wiring in the panel is not labeled, and the schematic drawing inside the panel has hand-written modifications (updated wiring of what was installed on-site was not in place during the testing day). The panel is not connected to the BMS system. A battery connection was found inside the panel while there were no batteries connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627385&prj=263&rqi=JVHS2olYHEIXK12Tczo9MxS1L2
GI-473 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Electrical |  | General Design issue | Design |  | equipment type |  |  |  |  | MOT - On the day of testing, it was informed that a fire signal from the fire system stops the generator. Rehlko vendor could not provide further information. The signal wired from the fire system to the generators was not identified. No schematic drawing exists showing how the fire system is connected to the generators. One fire panel sends hard-wired signals to stop the generators in case of fire . A centralizing panel sending a shutdown signal to each generator poses a high availability risk. High availability risk if there is a common dependency with signals wired from the same location to all generators. In addition, a fire curtain was observed in place. No one could explain how the system works and its impact on generator availability. All relevant documentation must be submitted to assess the risk. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627367&prj=263&rqi=Y9X9F7vCiVxyM0VCq5xoYYzpZH
GI-479 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | MOT - Loss of 24V to SCP of string (2 chillers running). The two pumps of the affected string went to 30 Hz. The chillers of the affected string still had the run command but were locked on flow. The PCP started the next chillers on the cascade, resulting in multiple chiller failures on flow, while the two pumps kept recycling hot water from return to supply and overpressurizing the loop. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627374&prj=263&rqi=3pM7I8k12T71w1CwflA5SfOxqt
YT1DCOS-225-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS | L2B | Installation Damage | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_23 | DCOS - HMI Panels |  | SCH - Schneider | Protective plexiglass broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627329&prj=263&rqi=8wBAcjQgjcsExMj2GJCetJNMYB
GI-468 | PA12x-1 | N-EMEA | Closed | P3 Low CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | DCOS - Equinix |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | MOT - Testing Diesel pump for loss of communication from the PLC. A bad/loose connection was found on the pump flow switch and FCP 1. Rehlko technician intervened and corrected the connection. The flow switch is wired back to FCP 1 through a junction box fixed in a location exposed to vibration, making loose connections likely to recur. No alarms are received when losing power or connection to the flow switch, leaving the system in an unhealthy state until a fuel call occurs to initiate troubleshooting. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627362&prj=263&rqi=S7UmJQZ5cpykJ2TBkDQu8Qi9Ou
GI-474 | PA12x-1 | N-EMEA | Closed | P3 Low CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | General Design issue | Design |  | equipment type |  |  |  |  | MOT - Testing at the generator panel for TTK leak detection on Gen room. The TTK system is now fed from generator starting batteries. This change was done after IST. No schematic drawing exists for this change. Actions required: 1. Provide the intervention report conducted after IST. 2. Provide updated schematic drawings reflecting the new power supply configuration. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627368&prj=263&rqi=LWP2bCRjYtqwlrDWFnefQsZXBM
GI-475 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | Design Correction Needed | Design |  | equipment type |  |  |  |  | MOT - Testing at the generator panel for TTK leak detection on Gen room. It was informed that triggering fuel leak detection in the Gen room will open the GRMU breaker, which poses a high availability risk. Stepping on the TTK cable resulting in opening the MV GRMU breaker is not an accepted design. Actions required: 1. Provide all details related to this design. 2. Provide a list of alarms that open the GRMU without impacting generator operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627369&prj=263&rqi=VN0XDtqqaRZLkR4tuntivcsM97
GI-467 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | MOT - Testing Diesel pump for loss of communication from the PLC The way both FCPs are connected to both pump contactors differs between FCP 1 and FCP 2. Having identical systems each wired in a different way makes troubleshooting difficult. Only the Rehlko technician who installed the system is aware of the wiring differences. action to audit the two FCP's and ensure they are wired in the same way as per design intent and provide the as-built drawing (drawing not available on site during testing) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627361&prj=263&rqi=1Ozf2WO5sgQByv7cNBuOq2JlI4
GI-466 | PA12x-1 | N-EMEA | Closed | P3 Low CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | M0T - Testing (ER) Circulation fans loss of communication and loss of power Two circulating fans in the UPS room were found not connected to the CRAHs in the same room. Power supply verification testing and operation testing need to be performed on these fans in relation to the CRAHs in the same room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627360&prj=263&rqi=upxicTmNMgFD33nta9DdAZMOTj
GI-460 | PA12x-1 | N-EMEA | Closed | Outstanding Paperwork/Documentation | markb@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation Not issued/ Required | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | MOT - Testing Fuel Control panels for communication cut between FCP and GCP There is no network schematic diagram for all the FCPs and GCPs. The fiber cables connected to FCP 1 are not labeled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627088&prj=263&rqi=odKTA1jVsWShZ1k1TdnD5CDb4S
GI-455 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | LLT - The SWITCHBOARD LOCAL/REMOTE selector switch is not generating an alarm when the MVTB is placed in local mode on either the local HMI or BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627081&prj=263&rqi=JyTkzTYO6LcFs9YJtyDxFwUDzt
GI-461 | PA12x-1 | N-EMEA | Closed | Outstanding Paperwork/Documentation | markb@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | MOT - Testing at the Fuel Control panel for double skin pipes fuel leak detection The names of pipe leak detection units on the FCP HMI do not match the SLD, making it impossible to identify where the units are located on-site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627089&prj=263&rqi=YJxWOIO7oA5SfF327yag5VRL6X
GI-459 | PA12x-1 | N-EMEA | Closed | P3 Low CX | markb@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | MOT - Testing Diesel pump for loss of communication from the PLC The way both FCPs are connected to both pump contactors differs between FCP 1 and FCP 2. Having identical systems each wired in a different way makes troubleshooting difficult. Only the Rehlko technician who installed the system is aware of the wiring differences. action to audit the two FCP's and ensure they are wired in the same way as per design intent and provide the as-built drawing (drawing not available on site during testing) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627086&prj=263&rqi=MhQjaSg0cbnlMcEJGpvzcH1wPh
GT1DCOS-276-001 | PA12x-1 | N-EMEA | Open | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS General Issue | DCOS | Electrical â€“ LV | equipment | 1DCOS_1_OAP_1 | CP - Control Panel (Max Cool Announcement) |  | SCH - Schneider | Disconnecting the hardwired connection between the OAP and ECP did not generate an ECP Panel Fault indication on the OAP. As stated in the MaxCool SOO, Section 4.0 â€“ OAP Panel Description (Page 9), the "ECP Panel Fault" shall indicate when "the connection between both panels has been disconnected." This behaviour was not observed and should be investigated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627078&prj=263&rqi=AEpkLeUCeNwaSCxcoHDULUm7tW
GT1DCOS-276-002 | PA12x-1 | N-EMEA | Open | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS General Issue | DCOS | Electrical â€“ LV | equipment | 1DCOS_1_OAP_1 | CP - Control Panel (Max Cool Announcement) |  | SCH - Schneider | During testing, the ECP panel power supply was switched off. The OAP correctly activated the audible alarm; however, the ECP Panel Fault red indicator did not illuminate and the blue beacon was not activated. As defined in the MaxCool SOO, Section 4.0 â€“ OAP Panel Description (Page 9), the OAP shall indicate an "ECP Panel Fault" when the ECP power supply is unavailable, and the blue strobe light and audible alarm are used to signal that an alarm is pending. This behaviour was not observed and should be investigated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627079&prj=263&rqi=2JibCZLyIuz5aR5wp8xz5AZEjs
GI-638 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-25 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall C | Data Hall Heat Load Test Phase 2 |  |  | HLT - Issue discovered during 25% heat load testing: The pressure sensor for 1CA_M1R1_47 was observed reading out of range, exceeding 100 Pa, while adjacent pressure sensors remained stable at â‰¤15 Pa. The sensor subsequently dropped to 0 Pa before recovering. As no similar behaviour was observed on neighbouring sensors, this indicates a likely fault with the pressure sensor or its associated signal/wiring rather than an actual pressure condition. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626862&prj=263&rqi=7fmSzrsqIfKzTamE4myzkwopse
GI-450 | PA12x-1 | N-EMEA | Closed | P2 Medium DCOS | kostask@straightlineconsulting.co.uk | 2026-06-24 04:00:00.000 +0400 | AER - Aermec |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | Mechanical - The differential pressure sensor on the chiller evaporator is showing a negative value when there is no flow. The DCOS page indicates that the sensor has failed. The issue is probably be related to scaling on the DCOS side rather than a sensor fault. DCOS team to check and correct the scaling configuration for ALL the chiller evaporator DP sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626705&prj=263&rqi=eEj6W5tFgMrQMvC8d0KF2yb7mM
GI-627 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Component/Equipment Failure | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT 2 - Mechanical - 1RAS_04 - Status deviation alarm active | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626480&prj=263&rqi=GnnJAvQXjwsB1yNg32klzIN4Om
GI-630 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | AER - Aermec |  | DCOS General Issue | DCOS | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CHWSTR_M2R1_2_CH_1 - Low evaporator alarm active | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626483&prj=263&rqi=XHvEemces8WOFNVpR3ur1F78qF
GI-637 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CHWSTR Strings 1,3,5,6,7 RAS deviation Alarms | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626492&prj=263&rqi=AKx4clu19wjellissEqWaHidyJ
GI-636 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | General Design issue | Design | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - High humidity alarms - DH3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626491&prj=263&rqi=xaCKAda6nkQ59GtZviw6V1aGBU
GI-628 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Component/Equipment Failure | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1PSER_M2R1_1 - Leak alarm active | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626481&prj=263&rqi=cQ5KcSPZNIZ2c9dQTkwK3fSiU0
GI-633 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1RAS_04 - High high alarm active - 2.3 bar reached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626486&prj=263&rqi=tfz3zGuuotABo3gK4PbLSpBJaM
GI-632 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CHWSTR_3_RAS_3 - Input value 2 in alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626485&prj=263&rqi=DCEImbbIWsP8ifFy4syGoKB8qq
GI-635 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CHWSTR_5_RAS_2 - Input value 3 in alarm - negative reading | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626489&prj=263&rqi=2ri08pxmUyGCIvVsOCuuV1ZSPi
GI-634 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CHWSTR_5_RAS_3 - Input value 3 in alarm - negative reading | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626487&prj=263&rqi=A7ViCLwy888dqV3b0IPgkEAXd9
GI-631 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Component/Equipment Failure | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical -both MAU - Major fault & shutdown | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626484&prj=263&rqi=FEe5ehJ4t2ZPgmG471wKBOWMd3
GI-629 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1FCU_M1_54 - Alarm active | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626482&prj=263&rqi=ZnsCIQbbfgZKxF0eRCrF6HucRB
GI-449 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning | HVAC | system | CHW System |  |  |  | HLT - Cool array corridors build up in large amounts of water from pipe condensation. - Data hall 5 & 6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626499&prj=263&rqi=E1QbtjSyatgyHMiXNAGtpAVHAb | https://equinix.facilitygrid.co.uk/x/project/263/system/9233
GI-448 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  | system | DCOS System |  |  |  | Heat load test - Full of E & F String in communication alarm. Impact to HLT & deadline for IST | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626496&prj=263&rqi=loVdW2QIM75GOseOWNA9oOCpoy | https://equinix.facilitygrid.co.uk/x/project/263/system/10784
IST-24-001 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-06-19 04:00:00.000 +0400 | General Contractor - Electrical | L5 | General Design issue | Design |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Following issues found on Testing 17/06/2026. Smoke extract dampers in following Zones failed to operated after manual trigger for Phase 1.1 ZDA104 ZDA105 ZDA106 ZDA130 No event log from testing was able to be downloaded from Racks to to internal issue. all areas tested to be re-tested. ZDA001, ZDM039, ZDA106, ZDM049, ZDA101, ZDA104, ZDA108, ZDA105, ZDA112, ZDA130, ZDA121. DH1 HA+CA, DH2 HA+CA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626229&prj=263&rqi=KkFZYoz3ARFAI2atI3kMzfkmKG
IST-23-001 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-06-19 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Correct | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | L4 C&E Testing: 1MVHR_M1R1_01_IHM not confirmed if shutdown was achieved (Mech needed) Lift 3 not connected for shutdown, shown on Matrix. removed from Matrix, agreed by PPA Ground Floor fire curtains not fully closing Event log for Genset testing to be sent to SLC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626226&prj=263&rqi=2C91o0yyFVfaD6U4Q244xLMEy8
GI-441 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-06-18 04:00:00.000 +0400 | SCH - Schneider MV |  | Installation Not Correct | Commissioning | [6 empty] | #LLT Issue on the MVTB R2 (Test performed on the 17/06/2026) during the LLT test when we switch off the breaker energizing the P5 of the loop 2 and when we switch back on this breaker who feeding this P5 The MVTB R2 calling the Gen start | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625856&prj=263&rqi=VtSsre1XEuqlkOl8hoPIIsGa6O
GI-440 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-06-16 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | LLT issue comms failure we lost all the coms of the site during the test of the BTU A (losing power source ) DCOS server crashing many times after trying to restart DCOS on engineer laptop ( issue need to be resolved asap) please see [picture attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625501&prj=263&rqi=fBI2vSM13iCJZiNj2KboPGgV7o
GT1FD-80-003 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-06-16 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Cleaning | Commissioning | Fire Detection | equipment type | FACP - Fire Alarm Control Panel | FACP - Fire Alarm Control Panel |  |  | Cleaning: All EAE units require deep cleaning. EAE_1-23 ALL EAE Units to be cleaned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625422&prj=263&rqi=3vRMg2KpAtZVhobTVXSBpAgl91
GT1FD-80-001 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-06-16 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Cleaning | Commissioning | Fire Detection | equipment | SSI_RACK_1 | FACP - Fire Alarm Control Panel |  |  | Cleaning: of Fibre connection /DCOS rack before C&E testing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625421&prj=263&rqi=vbqrk1ekrq4Tk2dLt5m5KBpVV1
GI-418 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-06-03 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Damage | Commissioning | [6 empty] | #IST ## CRAH M1R1_10 Elec Switch need to be replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623758&prj=263&rqi=pODt56a3pyhqmNo1dionYzPWmz
GI-428 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-03 04:00:00.000 +0400 | REH - Rehlko Gens |  | General Design issue | Design | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | IST1 - FCP01 FUEL PUMP FAIL ALARM ON DCOS WHEN COMPLETING M1/R1 SWITCHING ON IST TEST 1.0 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623776&prj=263&rqi=mzkRbn9DrPaoLxpxK6q5KChJLL
GI-429 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-03 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | IST1 - LEAKAGE PIPING LDT ALARMS PRESENT FOLLOWING IST TEST 1.0 SWITCHING | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623777&prj=263&rqi=DUavW79o4SKuw11LY9use5yrEy
GI-422 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-03 04:00:00.000 +0400 | AER - Aermec |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | IST1 - CHILLER LEAK DETECTION â€“ NO COMMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623770&prj=263&rqi=hMUrf0V3pqQr58EEZvk52VCq2j
GI-417 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-06-02 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Installation Damage | Commissioning | [6 empty] | IST# Masterpack Q03 FEEDER TO 1COP_AR1_1 cover protection broken need to be replace please see picture attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623645&prj=263&rqi=Icaaj3QyUWa4wOFO9oe0rnI5Zx
GI-626 | PA12x-1 | N-EMEA | Closed | P3 Low DCOS | joshw@straightlineconsulting.co.uk | 2026-05-30 04:00:00.000 +0400 | AER - Aermec |  | DCOS General Issue | DCOS | HVAC | equipment | Heat Load Test Hall D | Data Hall Heat Load Test |  |  | HLT - During fire Test 29.05.25, Multiple communication alarms on CHW Pumps / Chillers. Still gave command feedback/ feedback as correct - DCOS to investigate further whilst remained in purple alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623493&prj=263&rqi=0koO4PpOaH4e6LtDlZ8tyctDaZ
GI-415 | PA12x-1 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-05-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | Cleaning | Commissioning |  | equipment type |  |  |  |  | Mechanical - All condenser coils of the chillers require cleaning. The dirt in the coils will effect chillers performance. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623216&prj=263&rqi=GiaCKJgaTVhw3pF8KPDD62xtDI
GI-414 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-05-22 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | All Bone tags on All CRAH's Phase 1 have been amended with permanent marker, all incorrect, BYES to change to all correct permanent tags on CRAH ATS Cables both supplies | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622776&prj=263&rqi=xrbLlFoHxrKtz0DlRW2bHpRWBT
GI-413 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-05-19 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design | [6 empty] | Mechanical/Safety - Data hall pressure causing entrance Doors to data halls & Cool array corridors to slam and potential injure someone entering or leaving. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622243&prj=263&rqi=JLAOuLHeUWR7lrwGkaBIpdGAKe
BT1MECH-529-045 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | Mechanical - RAS04 - Point 17&18 reading -0.34 Installed but not programmed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621831&prj=263&rqi=iPMKJKN2WUUj5uHTtvb8sL7Zel
BT1MECH-532-046 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall D | Data Hall Heat Load Test |  |  | Mechanical - 1CA_M1R1_08 - White space 5 temperature to be corrected. 1.3 degrees out and coming into alarm reading 28.3 all others are reading approx 27 in same area | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621827&prj=263&rqi=OGnDi82M9FugT6JzIgGEbTQKud
GI-625 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | Mechanical - TEST 7.10 HLT - Valve actuator communication alarm - when re instated the temperature increased above SLA - Suspected Valve closing during communication failure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621805&prj=263&rqi=5BI8Q70vOwzBb2KqJyx6d271Oc
GI-624 | PA12x-1 | N-EMEA | Closed | P3 Low DCOS | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | Mechanical - HLT Test - Fan fault on cool arrays not latching. changes to a Fan communication alarm due to fan spinning in reverse. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621803&prj=263&rqi=XjZmGIwTKzLygfK6s6A2NQLGKU
BT1MECH-529-038 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | General Contractor - Mechanical | L4 | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | 1CHWSTR_1_RAS_2 - Temperature sensor not reading correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621760&prj=263&rqi=FoVL7W48qiUb274058Vy7pyRKH
BT1MECH-529-037 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | 1CHWSTR_M2R1_2_CH_2 - Experienced intermittent issues that recurred throughout the day | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621759&prj=263&rqi=UKVPT86vEyWyt4LOmWpwDlhLat
BT1MECH-529-043 | PA12x-1 | N-EMEA | Closed | P3 Low DCOS | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | Mechanical - Data hall temperature & humidity sensors go into communication alarm when rising above 50 degrees | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621812&prj=263&rqi=9XaDk10FntrAdtN22mBxKKxrHS
BT1MECH-529-039 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | General Contractor - Mechanical | L4 | Component/Equipment Failure | Commissioning | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | 1CHWSTR_5_RAS_2 - Temperature sensor not reading correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621766&prj=263&rqi=OnOvKyGvLGoVeweaf2LuEmUl9J
BT1MECH-529-044 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | General Contractor - Mechanical | L4 | Design Correction Needed | Design | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | MECHANICAL - Both MAU'S major fault - to be investigated - Planned commissioning/investigation on 20.05.26 Alarming as low temperature under 15 degrees. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621823&prj=263&rqi=64hgA4DMaq0Cyb2SUI7YVSsOeU
BT1MECH-529-041 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Component/Equipment Failure | Commissioning | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | 1GEN_M3 â€“ A sensor fault caused an M3 Generator trip. Kohler will investigate the issue and replace the sensor if required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621804&prj=263&rqi=ozwgR0dDzON89ICLnWbAby4CaT
GI-411 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | jayb@straightlineconsulting.co.uk | 2026-05-07 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design | HVAC | equipment | MSB_R2 -Room - CRAH | CRAH Switch Room Redundancy Test |  |  | when UPS is on full load the room temp exceeds higher UPS temp limit causing UPs R2 to inhibit battery charging and derating of UPS output occurs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620657&prj=263&rqi=219WizoLGq5Det7xBcYYKk49vL
YT1DCOS-274-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-29 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Not Correct | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_55 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - CYT. Phase 2 asset fed from Phase 1. Temp cable installed for energisation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619886&prj=263&rqi=iFjeLyzLk7GBNtZvH99n01snhB
YT1DCOS-226-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-29 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Not Correct | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_24 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - no main earth from HMI panel to containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619885&prj=263&rqi=XVNWhEQKZBZYSLoUrEtOJSJtKE
YT1DCOS-223-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-29 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Not Correct | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_21 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - no main earth from HMI panel to containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619895&prj=263&rqi=K2YjDYNQsPOagwHR7qk4lWfd7k
GT1MECH-724-001 | PA12x-1 | N-EMEA | Closed | Outstanding Paperwork/Documentation | emanuelp@straightlineconsulting.co.uk | 2026-04-28 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Documentation Not issued/ Required | Commissioning | Plumbing | equipment | 1PSET_A_03 | CHWP - Cold Water Booster Pump |  | LOW - Lowara-xylem | MECHANICAL - live cable test report required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619710&prj=263&rqi=vtug7XU3Rt0e6RQPWGDBk8kgXG
YT1MECH-648-731 | PA12x-1 | N-EMEA | Closed | Outstanding Paperwork/Documentation | emanuelp@straightlineconsulting.co.uk | 2026-04-28 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Documentation Not issued/ Required | Commissioning | Plumbing | equipment | 1PSET_A_03 | CHWP - Cold Water Booster Pump |  | LOW - Lowara-xylem | Mechanical - earthing report missing and permanent cable report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619711&prj=263&rqi=4owwSOJVbIFjQUjH1YOJeHLCg1
GI-404 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-04-16 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | During testing of the Vertiv cooling arrays in Data Hall 01 (PA12), the DP to DT changeover time was observed at 40â€“80 seconds, which differs from the 120 seconds specified in the Sequence of Operations. This issue is related to all CRAY units in the Data Hall 1. 1CA_M1R1_01 / 03 / 05 / 07 / 09 / 11 / 13 / 15 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618331&prj=263&rqi=5yjrrgG1aHopJo1IFP2pKk1G6n
GI-403 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-04-15 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Mechanical - CRAH's D string - When failing Return sensor, Fans Do not ramp up as per SOO. Vertiv engineer had to simulate by settings after to increase fan speed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618284&prj=263&rqi=XyIFl3tEk6Bq8TEtFxy0GpCik3
GI-402 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-04-13 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Installation Not Complete | Commissioning | [6 empty] | The layout drawing for Data Hall 2 is incorrect. The CRAY units (shown in red) are positioned on the wrong side of the room, and the DP sensors (shown in blue) are also incorrectly located. Reference to the drawing: PA12-SC-IC-6140-ZZ-DC-BGMS-SCH (R06) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617961&prj=263&rqi=C07Ui9JDAcymguXNgrkOR4YkpP
GI-396 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Missing Valve Tags on the CW flexible hoses 1CA_M1R1_02 1CA_M1R1_04 1CA_M1R1_06 1CA_M1R1_08 1CA_M1R1_10 1CA_M1R1_14 1CA_M1R1_16 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617919&prj=263&rqi=PbZhWNAXGPp7v9bZaqPqWv8opB
GI-400 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-04-13 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Damaged folder holder for documents/drawings to be repaired and secured in place. M1R1_15 M1R1_15 Extension M1R1_01 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617923&prj=263&rqi=XmAjC9jG2aKj2vs2UNIJ0UR4dz
GI-395 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-04-11 04:00:00.000 +0400 | General Contractor - Electrical |  | Cleaning | Commissioning |  | equipment type |  |  |  |  | Electrical - All Vesda pipes to be cleaned. most are covered in paint | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617873&prj=263&rqi=ymVfDuQXtmCpiLa3ELRmwzbmRI
YT1DCOS-273-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | mirceag@straightlineconsulting.co.uk | 2026-04-11 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Damage | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_54 | DCOS - HMI Panels |  | SCH - Schneider | Small paint chips and minor surface damage observed on the panel door exterior. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617836&prj=263&rqi=9zYU1ZRDIT2VCgUNEOyYKi3hyi
RT1FD-181-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-11 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Installation Not Correct | Commissioning | Fire Detection | equipment | ZDA121/12150 | ASDP - Aspirating Smoke Detection Panel |  |  | Electrical - ZDA121. No hellerman sleeve used in vesda or connection box. Silver pipes covered in paint. Trunking lid doesn't fit properly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617870&prj=263&rqi=yxgZmmyehD4oUPNG1JDeasLecv
GI-393 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-11 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | Fire Detection | system | Fire Detection |  |  |  | Electrical - Hellerman sleeve not used on cables in the following connection boxes ZDA090 ZDA084 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617868&prj=263&rqi=fqbr28EDQTRu9wiFv2NXrEE3JT | https://equinix.facilitygrid.co.uk/x/project/263/system/14098
GI-394 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-11 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | Fire Detection | system | Fire Detection |  |  |  | Electrical - Hellerman sleeve not used on cables in the following connection boxes ZDA074 ZDA075 ZDA076 ZDA077 ZDA078 ZDA089 ZDA081 ZDA073 ZDA072 ZDA071 ZDA066 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617869&prj=263&rqi=duzHObWWQzqogO5kZnzQQKS8oy | https://equinix.facilitygrid.co.uk/x/project/263/system/14098
SOR-2412-002 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation Not issued/ Required | Commissioning | [6 empty] | no drawing present in the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617674&prj=263&rqi=kzx8auRo8pr9RgYVpc5mnyBlC6
SOR-2410-001 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | tayebb@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Electrical |  | Commissioning Issue | Commissioning | [6 empty] | earthing cable not terminated need to be reviewed by electrical vendor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617672&prj=263&rqi=egfayllhJTxcjXcXiqMO29H1P0
SOR-2412-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [6 empty] | no labelling on the main power supply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617673&prj=263&rqi=JXVz90OSym1QUAg2kwQLK3FCQS
GI-390 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-27 04:00:00.000 +0400 | General Contractor - Electrical |  | DCOS Installation Not Complete | DCOS |  | equipment type |  |  |  |  | Electrical - No earth torque marks on DCOS_1_HMI panels between HMI and Door THIS ISSUE APPLIES TO ALL DCOS_1_HMI PANELS 1-50 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616649&prj=263&rqi=bCgIGTn9gzms5Wz9sfuMiAnp7t
GI-388 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | stephenturner@sygna-emea.com | 2026-03-24 04:00:00.000 +0400 | Equinix Project Manager |  | Installation Not Correct | Commissioning | [6 empty] | the cables powering up the load banks in data hall 2 are passing through an open door into the data hall, these door are not forced open the door could close on the cables and damage the cables. the data hall is live and multiple door are open on the data hall letting dirt into the hall. this is also a safety issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616287&prj=263&rqi=APE6Ow6PjJ9VW2S3r5QLlPaGKp
BT1MECH-428-035 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-03-20 04:00:00.000 +0400 | Design Professional | L4 | General Design issue | Design | HVAC | equipment | UPS R1 Room - CRAH | CRAH Switch Room Redundancy Test |  |  | Mechanical - CRAH Redundancy testing, Whilst CRAH 8 is failed and running on CRAH 7, With the distance between the UPS & CRAH, the heat coming off the UPS is not reaching back to the return temperature on CRAH 7 and putting demand on. Temperatures on UPS reached in over temperature alarm at 36-37 degrees. No further increase as temperature values but clear indication the circulation in the Ventilation getting back to 'load' the CRAH. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616060&prj=263&rqi=Jr2sMNZ27gOblkw36AhR5Uclk8
BT1MECH-428-036 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-03-20 04:00:00.000 +0400 | General Contractor - BMS | L4 | Component/Equipment Failure | Commissioning | HVAC | equipment | UPS R1 Room - CRAH | CRAH Switch Room Redundancy Test |  |  | Mechanical - Whilst testing CRAH Redundancy testing, TT01 sensors were not working correctly. DCOS confirmed they changed parts with phase 2 panels but scaling from 40-50 are different. All TT01 / dcos panels linking to temperature sensors need all retesting and calibrating with a data logger. for this test we will have to rely on Data loggers. if BYES Fail to supply data logger trends a retest under full load will be required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616069&prj=263&rqi=Mtqbf0cBWBAMDA57k6Dx8EczSB
RT1DCOS-265-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-19 04:00:00.000 +0400 | General Contractor - Electrical | L2 | Installation Damage | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_13 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Damaged Perspex screen and damaged internal plastic trunking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616032&prj=263&rqi=0rbeN7QjYPE5QkBUewcbaoEbUp
RT1DCOS-272-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-19 04:00:00.000 +0400 | General Contractor - Electrical | L2 | Installation Damage | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_20 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Damaged Perspex screen | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616033&prj=263&rqi=YqHFLAcZ0EP8PLvjn1k0ejd5SI
GI-386 | PA12x-1 | N-EMEA | Closed | P3 Low CX | stephenturner@sygna-emea.com | 2026-03-18 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | on Facility grid on a weekly basis the numbers change for the Total Activities. these changes for each level of tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615969&prj=263&rqi=yOsLGXK0SAdgCh9SLz8yc5lBXJ
RT1FS-302-010 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-03-18 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Installation Not Complete | Commissioning | Fire Suppression | system | Fire Dampers - Ground Floor |  |  |  | Mechanical- 1SD_NC_0031 - cabling / Conduit to be fixed correctly after floor resin laying | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616371&prj=263&rqi=5YA5EBV3RmxaIrbXBFX7MWO4JN | https://equinix.facilitygrid.co.uk/x/project/263/system/11600
GI-389 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-03-18 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | Mechanical- conduit to be re connected correctly after floor resin install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616372&prj=263&rqi=aRS1PqESBNeDSLyJmk4oujMVEK
GI-382 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [6 empty] | CYT 1DB_M1R1_13_1 Conditional - Conditional yellow tag applied to unit - Issue will ONLY be closed once permanent supplies are installed and all documentation issued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615791&prj=263&rqi=TtKiqctD5ecwDSQbPeDUwo5HFc
SOR-2321-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | 1FCU_M6_155 Torquin is missing on the isolator Labels are missing on the wiring Labels are missing on the drainage Cleaning needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615806&prj=263&rqi=Zepa0nWiH1XfGMo1WyHpPLS0vL
GI-380 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Incomplete Connections | Commissioning | [6 empty] | CYT 1DB_M1R1_8_1 Conditional - Conditional yellow tag applied to unit - Issue will ONLY be closed once permanent supplies are installed and all documentation issued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615789&prj=263&rqi=1HnfepOc8qYVwpywar7ogACltx
SOR-2323-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | 1FCU_M4_156 Torque marks are missing on the torque and the insulator Cleaning needed Bone tags missing ID is missing on the drainage and flow direction | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615808&prj=263&rqi=hot3mNkP1fFn4sXANTSVF4fvgr
GI-383 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | Mechanical 1FCU_M5_160 Drainage not terminated Bone tag missing Earthlings missing Cleaning needed Torque mark missing on the Isolator Labels are missing on the income to the isolator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615803&prj=263&rqi=mrWsKfsAlfck3TS7qg2lod2Pyl
SOR-2317-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | Mechanical 1FCU_M6_158 Drainage not completed Bone tag missing Earthlings missing Cleaning needed Drip tray missing Torque mark missing on the Isolator Labels are missing on the income | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615802&prj=263&rqi=AIi9RvR3yadbsDhDdRR4o9CK0N
SOR-2328-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [6 empty] | Poste 4 Bone tag missing ID not attached to the pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615844&prj=263&rqi=XlK8HA2pvKXlpe3iJS8pTkMqxq
SOR-2320-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | 1FCU_R2_157 Bone tag missing The label on the drainage is missing Torque mark missing on the isolator Cleaning needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615805&prj=263&rqi=inU8REwfYu4Y0txSrWdammNEzP
SOR-2316-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | Mechanical 1FCU_R2_161 Drainage not completed Bone tag missing Earthlings missing Cleaning needed Drip tray missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615801&prj=263&rqi=zyR7DsGdicPLFd4mAiSimZwGFo
SOR-2327-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [6 empty] | Poste 1 Bone tag missing ID not attached to the pipework | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615843&prj=263&rqi=NnUoP6bnaoTO2uowt0uK1P3Ixi
SOR-2319-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | Mechanical 1FCU_M6_159 Drainage not terminated Bone tag Missing Earthlings missing Cleaning needed Drip tray missing Torque mark missing on the Isolator Labels are missing on the income to the isolator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615804&prj=263&rqi=BE38ePfqX1MIY3sfYeYEOZlWXY
SOR-2329-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [6 empty] | Mechanical: Poste 5 Bone tag missing proper support for the cables ID to be visible | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615845&prj=263&rqi=YUVCoLgOj27SQvR4Kce24ICfMy
SOR-2322-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | 1FCU_M6_155 Torquin is missing on the isolator Labels are missing on the wiring Labels are missing on the drainage Cleaning needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615807&prj=263&rqi=AWaNWITaSuIUZLVrxROnijUm7Z
GI-381 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Incomplete Connections | Commissioning | [6 empty] | CYT 1DB_M1R1_8_1 Conditional - Conditional yellow tag applied to unit - Issue will ONLY be closed once permanent supplies are installed and all documentation issued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615790&prj=263&rqi=pEquQZo3MrdRaYOgTt6sqmnBlv
SOR-2326-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | [6 empty] | Poste 6 ID tag missing Cable needs proper support Bone tags missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615842&prj=263&rqi=SE3j3KMsb9eEQ5YR0acesvJIL9
GI-379 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Incomplete Connections | Commissioning | [6 empty] | 1DB_M1R1_7_1 Conditional - Conditional yellow tag applied to unit - Issue will ONLY be closed once permanent supplies are installed and all documentation issued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615788&prj=263&rqi=my07XC0VJ2MHfydFDOjwX13zTY
RT1DCOS-229-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Electrical | L2 | Installation Damage | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_27 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Perspex screen broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615722&prj=263&rqi=4egAvEfAPcn9Yi9ZT00TtfTIa3
RT1DCOS-224-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Electrical | L2 | Installation Damage | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_22 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Perspex screen broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615721&prj=263&rqi=gtF22dlDyfy9Ypwr0uCcPEN63C
GI-378 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | MECHANICAL: The bolts on the CHWSTR system are loose, and an extra bolt should be added. Please remove the delivery brakes from the chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615720&prj=263&rqi=L1w8zywmqunnj77zyGKSQhSlsc
YT1DCOS-228-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Damage | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_26 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Earth bonding incomplete | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615710&prj=263&rqi=e9xzao0SJdOyAZzp4JaA96D7Wg
YT1DCOS-237-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Not Correct | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_35 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Earth Cable sharing same entry gland as CAT6 cable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615724&prj=263&rqi=5vFvOeFNgbrmiRPglURwaGszKU
GI-377 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | Mechanical: Bolts are loose on the CHWSTR. Remove the shipping brackets from the chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615719&prj=263&rqi=nmJvn3NMe77NRqBQicWlfykywf
GI-376 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-03-13 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS | [6 empty] | Mechanical- scaling on graphic to be amended 20l/s difference between flow meter and graphic | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615515&prj=263&rqi=QjTWkBBIADdCbADoCRvDveDTot
BT1MECH-402-030 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-12 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Installation Not Complete | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Mobile gent set pipework requires a plug/end cap on the valve. The cables and the terminal boxes to be tidied up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615452&prj=263&rqi=Ki4ApkNpKFMbKrNdnU1dpoPy4l
GI-375 | PA12x-1 | N-EMEA | Closed | P3 Low CX | stephenturner@sygna-emea.com | 2026-03-11 04:00:00.000 +0400 | Commissioning Authority |  | Installation Not Complete | Commissioning | [6 empty] | During the L4 Fuel testing, on the fuel system HMI Phase 2 equipment is visible and in Fault, at this moment in time works are unfinished in phase 2. this must be noted in the L4 script and rechecked when phase 2 is undergoing L4 testing . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615343&prj=263&rqi=PY7Ejhywv07gonMsiAcdkYUr3V
BT1MECH-402-029 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-11 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Component/Equipment Failure | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - The HMI is freezing during L4, KOHLER team is fully aware about the issue but they cannot provide a solution. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615340&prj=263&rqi=kIRdaNkZSmEokxpZKFefqcSLAw
BT1MECH-402-026 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-10 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | DCOS Graphics Issue | DCOS | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Police valve on HMI appears as Fire Valve Daily Tank --> Gen Set Pompier Valve Â appears on HMI as Fire Valve No1 Tank and Â No2 TankÂ The DCOS has the correct labellingÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615264&prj=263&rqi=cjsMyhDqa12Cfu4rZxH57btH3T
BT1MECH-402-027 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-10 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | DCOS Graphics Issue | DCOS | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - No Â alarm on HMI for pompier valve. There is Pompier Alarm on DCOS. Â Graphics issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615266&prj=263&rqi=3Fh0eeqqCtz7ZzH0DA3vveAycq
BT1MECH-402-025 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-10 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Cleaning | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - All bulk tanks require cleaning. Bulk tank 1 is used as a storage and bulk tank 2 is flooded from rain water. See attached pictures. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615259&prj=263&rqi=hmjFZC2J3RiuBvRVOv1gO0M0CN
BT1MECH-402-028 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-10 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | DCOS Graphics Issue | DCOS | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - HMI Graphics to be adjusted with correct labelling. Alarms description should be specific to the equipment: i.e. Alarm Police Valve GS M1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615297&prj=263&rqi=qLPfHRkLAsHQypV6sUytJ5RQti
BT1MECH-402-024 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-10 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Component/Equipment Failure | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Bulk tank 3, solenoid valves not responding on manual and close request. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615222&prj=263&rqi=0Q9QTfsCtyJDM85NFNBqHy8mIj
BT1MECH-402-023 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-09 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Component/Equipment Failure | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - HMI not responding, issue with time response of HMI between tabs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615143&prj=263&rqi=16yynNszPLiZedHwUpIhg81TD1
SOR-2284-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-03-06 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Installation Not Correct | Commissioning | [6 empty] | scratch on the front panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614903&prj=263&rqi=Oc99xEO8lowv2QBTkifVGdk8eu
SOR-2283-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-03-06 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Commissioning Issue | Commissioning | [6 empty] | scratch on the panel inside | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614902&prj=263&rqi=uY20lcIs8OHafDcuaPwVubb4ns
GI-374 | PA12x-1 | N-EMEA | Closed | P2 Medium DCOS | joshw@straightlineconsulting.co.uk | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | DCOS/MECHANCIAL - TT01 in UPS Room M1 seems to be reading way off actual temperature off the room BYES/DCOS Team to provide document showing all TT's in phase 1 + calibrations commissioning is complete. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614799&prj=263&rqi=Bfstz8OEoS8tEaLaHKZbRl4KFY
BT1MECH-402-022 | PA12x-1 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-03-04 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Design not as Specified | Design | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Fuel bulk tank set points are not matching the SOO. There is not enough fuel and have been adjusted to allow available tanks during the L4 test. Kohler to revert set points | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614707&prj=263&rqi=KgksOd6utYscKSZJz8Wa07P2KT
GT1MECH-729-062 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-03 04:00:00.000 +0400 | REH - Rehlko Gens | L3 | Installation Not Complete | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Ad Blu manifold Flow Sensor Missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614610&prj=263&rqi=Cc0leUcdl6dGCQx4Fcmo2aghls
GI-372 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-26 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Damage | Commissioning | [6 empty] | Scratches on the pump 1CHWP_M1R1_02 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352221&prj=263&rqi=0KJcvhU2gLufaOHOhMjBXrRb12
GI-373 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | emanuelp@straightlineconsulting.co.uk | 2026-02-26 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | [6 empty] | 1CHWP_M1R1 01 Mechanical earthing not terminated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352222&prj=263&rqi=fyzF3UDs5s63E4UxkuT2iCbC24
SOR-2258-002 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-02-25 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | drawing is not up to date as per checks on site picture attached should be Version 6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212868&prj=263&rqi=wCG1ctlOwtpJjF1A6kyswXITdp
SOR-2354-004 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-24 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | Fire Detection | equipment | EAE_22 | EAE Fire Panels |  |  | No bone tags on Cables | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616000&prj=263&rqi=3EU88tV4ObXOx3ABBBWJkudbvc
SOR-2351-004 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | grantw@straightlineconsulting.co.uk | 2026-02-24 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning | Fire Detection | equipment | EAE_11 | EAE Fire Panels |  |  | Damage to panel Bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615999&prj=263&rqi=5wfIWicgTw4xAgBfU01ARqpg6K
GI-371 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | grantw@straightlineconsulting.co.uk | 2026-02-23 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation Not issued/ Required | Commissioning | [6 empty] | ELECTRICAL L3 LIVE Cable test reports missing for the following cables\\\\\\\; CBL-1UMDSB_M1R2-01 CBL-1UMDSB_M1R2-02 CBL-1UMDSB_M1R2-03 CBL-1UMDSB_M1R2-04 CBL-1UMDSB_M1R2-05 CBL-1UMDSB_M1R2-06 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199773&prj=263&rqi=G384VnzJ9We1ZMdWPHgPIEVJso
GI-387 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-18 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning | Fire Detection | equipment | EAE_18 | EAE Fire Panels |  |  | panel has damage to paintwork | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615997&prj=263&rqi=YAkOkacZURutyMyZkzYg2Ypeuw
SOR-2340-005 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-18 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning | Fire Detection | equipment | EAE_19 | EAE Fire Panels |  |  | Paintwork damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615998&prj=263&rqi=hSqlENwWcwHbXG5MjB2nCwpUdV
RT1ELEC-634-393 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Installation Not Complete | Commissioning | Electrical â€“ LV | equipment | 1DCOS_1_OAP_1 | CP - Control Panel (Max Cool Announcement) |  | SCH - Schneider | 1DCOS_1_OAP_1 Mechanical: End Caps missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199345&prj=263&rqi=7MQmDYSEh1C6WV5p9cSWd44FA5
GI-370 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | adamb@straightlineconsulting.co.uk | 2026-02-16 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [6 empty] | Mechanical- flow meter from CHWP 5-2 Incorrect showing 30 l/s with pump running at approx 25 Hz when pump delivering approx 65l/s and running at 50 Hz | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199328&prj=263&rqi=yF9n3Dsa3SUltDAlJME7K7LwsG
GT1MECH-729-058 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-11 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Commissioning Issue | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Urea filling request on the HMI remains off during filling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199061&prj=263&rqi=4ANpzl1UY13O3TNJi9XgAittXA
GT1MECH-729-060 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-11 04:00:00.000 +0400 | REH - Rehlko Gens | L3 | Installation Not Correct | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Urea pump 1 - flexible hose stretch. To be replaced with the correct size | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199063&prj=263&rqi=EmlvFQdaI0pnAyEcRNDlOAutHZ
GT1MECH-729-059 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-11 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Commissioning Issue | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - fuel level on alarm at 47% and 2minutes later the alarm disappears still at 47% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199062&prj=263&rqi=6g9ynS40htu9VBSCMj1EdTpe8i
GT1MECH-729-061 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-11 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Documentation Not issued/ Required | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Urea SOO L3 carried out based on R05 SOO, the R06 is for review Â at the moment and KOHLER advised that revision 7 (R07) will be the last oneÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199064&prj=263&rqi=eVlOZCgziLXp0z6YQdjGqBFMkP
GI-361 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | Fire Suppression | system | Sprinkler System |  |  |  | Extra support needed and end caps on the bar Poste 28 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198924&prj=263&rqi=oWMJMvRKFw3paHAeUiTFfEblmt | https://equinix.facilitygrid.co.uk/x/project/263/system/10985
SOR-2199-002 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical |  | Torque required | Commissioning | Fire Suppression | system | Sprinkler System |  |  |  | Sprinkler System Poste 12 Cx L2A 10/02/26 EP torque missing End caps missing Painting | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198926&prj=263&rqi=q6ItviT373yBTBgiPbVdZfLFaV | https://equinix.facilitygrid.co.uk/x/project/263/system/10985
GT1MECH-729-057 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Commissioning Issue | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - graphics in hmi not matching with SOO and Equinix standards | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198928&prj=263&rqi=66O9qm1F2uFH9WXHnfQ0oq6ayG
SOR-2199-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning | Fire Suppression | system | Sprinkler System |  |  |  | Sprinler fittings need touch-up painting Poste 28 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198925&prj=263&rqi=vRer8hDVp5AEJI2rbUwJDfXVYR | https://equinix.facilitygrid.co.uk/x/project/263/system/10985
SOR-2196-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1CHWSTR_M3R1_8_ELC_1 | CP - Control Panel |  |  | Income power needs to be torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198882&prj=263&rqi=0er340HHkQNWZlL1Kk2Mu1kmCE
GI-360 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical |  | Torque required | Commissioning | Fire Suppression | system | Sprinkler System |  |  |  | Bolts not torqued Poste 28 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198923&prj=263&rqi=KIVQFEPzSkutP7v3lFG7ulRA1q | https://equinix.facilitygrid.co.uk/x/project/263/system/10985
GT1MECH-729-056 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Commissioning Issue | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - fuel low level alarm in SOO R06 is not matching with HMI setpoints. There is not enough fuel in bulk tanks to be able to have low level alarm at 50% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198927&prj=263&rqi=Mld0TnhAY65fmXRGqOpGtj0Xyv
RT1FS-301-003 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-02-04 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Incomplete Connections | Commissioning | Fire Suppression | system | Smoke Dampers - First Floor |  |  |  | Electrical - 1SD_NC_0025 - exposed wire to be wagoed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198633&prj=263&rqi=RHfmCdeQxCNziLWXj1bS4rCwKg | https://equinix.facilitygrid.co.uk/x/project/263/system/11603
SOR-2149-006 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | Fire Detection | equipment | EAE _05 | EAE Fire Panels |  |  | Electrical No Cable ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198254&prj=263&rqi=WdvYsvOMv1UHm1sZaz4I43zYNS
GI-356 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | stephenturner@sygna-emea.com | 2026-02-03 04:00:00.000 +0400 | Equinix Commissioning Manager |  | Commissioning Issue | Commissioning | [6 empty] | in all data halls permanent light must be on before energisation for PDCs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198246&prj=263&rqi=Elxavy1FKLMBUVYMCP1nuYQrqx
GI-357 | PA12x-1 | N-EMEA | Closed | P3 Low CX | stephenturner@sygna-emea.com | 2026-02-03 04:00:00.000 +0400 | Equinix Project Manager |  | Installation Not Correct | Commissioning | [6 empty] | Earthing cable next to the transformer to be fixed in a better position see photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198247&prj=263&rqi=TYh8DQFEI7tCWiZpWgsVkx5y9e
SOR-2149-005 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | Fire Detection | equipment | EAE _05 | EAE Fire Panels |  |  | Electrical No Asset ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198252&prj=263&rqi=P0qLqJdYrV7a6m6SLSnbED7gSD
SOR-2149-004 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | Fire Detection | equipment | EAE _05 | EAE Fire Panels |  |  | Electrical no End caps in trunking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198251&prj=263&rqi=Pi8kWQ32H0l5C8m7F6VogtqeUR
RT1FS-301-002 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Incomplete Connections | Commissioning | Fire Suppression | system | Smoke Dampers - First Floor |  |  |  | electrical_earth not connected or protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198249&prj=263&rqi=CxC0av0eTd7SVKu4OUn8Cb0ZA8 | https://equinix.facilitygrid.co.uk/x/project/263/system/11603
RT1FS-301-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Incomplete Connections | Commissioning | Fire Suppression | system | Smoke Dampers - First Floor |  |  |  | Electrical- earthing cable cut and not protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198248&prj=263&rqi=xWiiDTGq66yAiBuQOrfqw8AeNT | https://equinix.facilitygrid.co.uk/x/project/263/system/11603
SOR-2150-006 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | Fire Detection | equipment | EAE _06 | EAE Fire Panels |  |  | Electrical no End caps in Trunking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198256&prj=263&rqi=U7aoxhFK3PP36FUaTnql6qgjO6
SOR-2150-004 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | Fire Detection | equipment | EAE _06 | EAE Fire Panels |  |  | Electrical i Cable ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198253&prj=263&rqi=uRBZZEQEds2sdGj4Z5Smd6zFA1
SOR-2150-005 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | Fire Detection | equipment | EAE _06 | EAE Fire Panels |  |  | Electrical No Asset ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198255&prj=263&rqi=WynfPNQ80HcGceJZqeCddwlvfY
GI-353 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | stephenturner@sygna-emea.com | 2026-01-29 04:00:00.000 +0400 | Equinix Project Manager |  | Installation Not Correct | Commissioning | [6 empty] | On all MVTB'S the MV cables have noÂ glandes, this will effect the IP rating and it seams that foreign objects will can enter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197940&prj=263&rqi=OgXJvho6gYhqPQVA5H2fGIt2EV
GI-355 | PA12x-1 | N-EMEA | Closed | P3 Low CX | stephenturner@sygna-emea.com | 2026-01-29 04:00:00.000 +0400 | Equinix Project Manager |  | Cleaning | Commissioning | [6 empty] | energised data hall are no condition to be energised due to poor house keeping planks of wood and other objects need removing and dust is also an issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197944&prj=263&rqi=2wUjTvzP7JIVJO6Mk92nGFOdWl
GI-354 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | stephenturner@sygna-emea.com | 2026-01-29 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | [6 empty] | on all transformers the earth cable is only connected with a cable tie this can fail in the future. there are only 1 torque mark on each tightened bolt 2 marks are needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197941&prj=263&rqi=7zDTyRR8W3fv2V2HZW0C6ylylF
GI-352 | PA12x-1 | N-EMEA | Closed | P3 Low CX | stephenturner@sygna-emea.com | 2026-01-29 04:00:00.000 +0400 | Equinix Project Manager |  | Installation Not Complete | Commissioning | [6 empty] | It is imperative that permanent lighting be installed in all data halls when electrical equipment is energized. Unfortunately, this is not currently the case in Data Halls 3, 4, and 5, and this issue requires immediate attention. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197937&prj=263&rqi=8TltUglRYileziW5747GleSJIt
SOR-2126-002 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-28 04:00:00.000 +0400 | General Contractor - Electrical |  | Cleaning | Commissioning | [6 empty] | Electrical BB requires cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197796&prj=263&rqi=xmeXcfG0omULzgLk9ayA5Qkh20
GI-351 | PA12x-1 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-01-28 04:00:00.000 +0400 | General Contractor - Mechanical |  | Torque required | Commissioning | [6 empty] | Mechanical - earthing torque marks required in all three panels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197802&prj=263&rqi=eE65xjQSJ1gEOGB1Cf09Q5h39U
GI-349 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-01-28 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Correct | Commissioning | [6 empty] | Mechanical - exposed copper on secondary power supply L1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197800&prj=263&rqi=HpJ8DbXIZe3n4ElW6kzSAOLwws
GI-350 | PA12x-1 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-01-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Not Correct | Commissioning | [6 empty] | Mechanical - glands not in use to be capped off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197801&prj=263&rqi=cg2CTOOoacdCmYjoOqzJurqVIs
GI-345 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Correct | Commissioning | [6 empty] | Electrical- Conduit to be fitted correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197673&prj=263&rqi=47wSZczjU9iYOdGX2OwTzjq9GB
SOR-2105-005 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [6 empty] | Electrical- Fire cable to be supported by cable tray and conduit to be made good | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197666&prj=263&rqi=ZP6nYoHuNP4hpsjugb6nEaLwgE
GI-344 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [6 empty] | Electrical- No Bone Tag Fitted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197672&prj=263&rqi=fhXcgYhydAuuR8hbEl5xszAxSO
GI-346 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Damage | Commissioning | [6 empty] | Mechanical- Coil Fins to be combed prior to energisation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197674&prj=263&rqi=ydFqc6KoZDTUgbBqCFKUuKAYF9
GI-347 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [6 empty] | Electrical- No Bone Tag fitted and Conduit to be made good (1CU_M1R1_29) Gen Building Roof | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197676&prj=263&rqi=6pVS5Jgnk6ugkGwojl09Pee2Nr
SOR-2074-004 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-22 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [6 empty] | Electrical- Containment to be extended for Fire Cables | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197462&prj=263&rqi=worIT14UPRY3hwT9WBNYUv31Z6
YT1FS-303-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-22 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Cleaning | Commissioning | Fire Suppression | system | Smoke Dampers - Ground Floor |  |  |  | Mechanical - All Data Hall 1 & 2 Low level ductwork behind dampers to be cleaned and to be free of dust and debris before Fan start up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197445&prj=263&rqi=xl5CuAuYQTgNk9l6WOc9LZOFKD | https://equinix.facilitygrid.co.uk/x/project/263/system/11604
SOR-2076-004 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-22 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | [6 empty] | Electrical - containment to be re routed to gain access to Fire damper Acuator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197464&prj=263&rqi=XXTSdHLDcfB8F2Nh6EkXAXdoOR
YT1FS-305-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-21 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Labelling | Commissioning | Fire Suppression | system | Smoke Dampers - Second Floor |  |  |  | Electrical - All Bone Tags to have correct reference in Data Hall5 & Data Hall 6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197352&prj=263&rqi=23tpm63yk8MiVZTtKREiWjqenX | https://equinix.facilitygrid.co.uk/x/project/263/system/11605
SOR-2083-005 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-20 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [6 empty] | Life Safety No Asset ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197468&prj=263&rqi=prESlqx1cwZVvI7lnJDBnWtmiA
RT1FS-304-023 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-20 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning | Fire Suppression | system | Fire Dampers - Second Floor |  |  |  | Electrical - All bone Tags to Low Level Smoke Dampers in Data Hall 5 have incorrect reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197303&prj=263&rqi=R9piybNBMqyH48Impcdu3Vvsgp | https://equinix.facilitygrid.co.uk/x/project/263/system/11602
GI-342 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-19 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [6 empty] | Electrical Holding down bolt for Rear compartment Section 2 the thread is worn/ Criss threaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197191&prj=263&rqi=abJbWr71r74DiB3XxR8P29oMxg
GI-340 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-15 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | [6 empty] | Electrical No Ferrels on Earth cables | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197016&prj=263&rqi=rUErR8iZskol9F7bGcKXdcYDEM
SOR-2049-006 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Cleaning | Commissioning | [6 empty] | Electrical Panel requires repaint/ Cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197015&prj=263&rqi=O6Is2yGCJBujvpSggd9x9snNrV
SOR-2049-005 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Documentation Not issued/ Required | Commissioning | [6 empty] | Electrical Drawings need to be updated as | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197014&prj=263&rqi=YWUtWEr1Gfjc774SAKhhPHvr6W
SOR-2032-002 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | Electrical No Red Tag QR code for Yellow tag to be placed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196808&prj=263&rqi=xTck23qt09zAKLFPRIU3JcAd3a
GI-339 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [6 empty] | ELECTRICAL Torque on BB messy need to be cleaned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196805&prj=263&rqi=z6EFhYKTPIsYjJWfFxPbzym0IG
GI-338 | PA12x-1 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [6 empty] | Mechanical - cable tray earthing missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196486&prj=263&rqi=udYKIkHXRK5ZukFyRb4rCKlQtn
FPT-765-001 | PA13x-2 | N-EMEA | Closed | Outstanding Paperwork/Documentation | gregm@straightlineconsulting.co.uk | 2026-04-14 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation Not issued/ Required | Commissioning | Mechanical â€“ Water | system | PA13.2 Post Sec Chilled Water System Integration Verification Test Script |  |  |  | Mechanical - MER /KES to issue the results from the on site water analysis test taken 18/3/26 of the Sec CHW system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618095&prj=406&rqi=vKodueaEGtUVak2IQnvamgwjZN | https://equinix.facilitygrid.co.uk/x/project/406/system/14161
GT1MECH-450-001 | PA13x-2 | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-03-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Installation Not Complete | DCOS |  | equipment | 1-MVHR-M5-1 |  |  |  | 1-MVHR-M5-1 DCOS and temp checks not carried out by DCOS team and Temperatures to be taken,. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616192&prj=406&rqi=QmPT0sdvPLfs6geUmKuDKmrG5b
DCIML4-1-001 | PA13x-2 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-18 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCIM Cooling Zone issue | DCIM | Controls | system | DCIM |  |  |  | Location Vectors missing for Leak detection phase 2 assets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615974&prj=406&rqi=mJmj6F58qIlXShOylWYJnwiCJT | https://equinix.facilitygrid.co.uk/x/project/406/system/11776
DCIML3-1-001 | PA13x-2 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-18 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCIM Sync service Issue | DCIM | Controls | system | DCIM |  |  |  | Template Valve not upserted on DCIM | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615972&prj=406&rqi=HgZAlOgc9doFiFojRBPvtcDdq9 | https://equinix.facilitygrid.co.uk/x/project/406/system/11776
FPT-763-001 | PA13x-2 | N-EMEA | Closed | Outstanding Paperwork/Documentation | gregm@straightlineconsulting.co.uk | 2026-03-05 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation Not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | Cooling String 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12 String Failure | Cooling String 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12 String |  |  | Cooling String 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12 String Failure test - As left settings still to be issued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614794&prj=406&rqi=XBf9KF9JkYJPMhv8s2l1x5cq0S
FPT-762-001 | PA13x-2 | N-EMEA | Open | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-02-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS General Issue | DCOS |  | system | Fuel System |  |  |  | Fuel system Â Pressure switches on fuel pumps are sticking and need to be adjusted Pump 2 was alarming momentarily. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199774&prj=406&rqi=aTR6g0nTH9v4UnlmRW3dcYzkj6 | https://equinix.facilitygrid.co.uk/x/project/406/system/7699
GI-282 | PA13x-2 | N-EMEA | Closed | P2 Medium CX | michaeld@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Component/Equipment Failure | Commissioning |  | equipment | 1-ATS-JR2-1 |  |  |  | Electrical - During IST J it was noticed that ATS-JR2-1 was in alarm and not switching to redundant source. A thorough investigation is required by ITEC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197670&prj=406&rqi=4gjwMsvlHmem8p9ucPOenyuY8Q
WTIST-15-004 | PA13x-2 | N-EMEA | Closed | P2 Medium CX | seanh@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | SCH - Schneider Electric |  | Commissioning Issue | Commissioning |  | equipment | IST Phase 2A Hall I | Intergrated System Test Phase 2B I |  |  | Electrical - Failure of Utility (Test 1) during transfer to Gen after the Generator start signal was confirmed however the generator breaker failed to remain closed on 2 occasions. 51N was the ansicode that was received at the time of failure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196784&prj=406&rqi=1jYDToYhTTGrY8KfhQ1TtrI7RI
L3-13-002 | PA13x-2 Mickey | N-EMEA | Open | P3 Low CX | richardw@straightlineconsulting.co.uk | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Documentation Not issued/ Required | Commissioning |  | system | FIRE - Fire detection / Alarm system |  |  |  | Documentation - Latest documentation related to the tests performed for the DH. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631412&prj=554&rqi=wpGcEqoepRz92fSNbL2ULvlSZa | https://equinix.facilitygrid.co.uk/x/project/554/system/13897
YT1MECH-438-002 | PA13x-2 Mickey | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation Not issued/ Required | Commissioning | Fire Suppression | equipment | Fit Out - MFD-3130 | FD - Fire Damper |  |  | Fire Suppression MFD-3130 GC YT checklist missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627581&prj=554&rqi=xT4G6drc3vwBYwG9D2gIzvT3R5
RT1MECH-424-001 | PA13x-2 Mickey | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | Fire Suppression | equipment | Fit Out - MFD-3131 | FD - Fire Damper |  |  | Fire suppression Â MFD-3031 Damper label required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627576&prj=554&rqi=z4vlMxyJYLrwzpX0fsZBcX222r
YT1MECH-439-001 | PA13x-2 Mickey | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Correct | Commissioning | Fire Suppression | equipment | Fit Out - MFD-3131 | FD - Fire Damper |  |  | Fire Suppression - MFD-3031 fire damper access panel in Mickey office badly cut in to ductwork sharp edges - CUT risk | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627572&prj=554&rqi=A2gjca75zgrRGctaIjDl5UWZGE
YT1MECH-439-002 | PA13x-2 Mickey | N-EMEA | Open | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation Not issued/ Required | Commissioning | Fire Suppression | equipment | Fit Out - MFD-3131 | FD - Fire Damper |  |  | MFD-3031 - Chubb Cable test docs missing for MFD | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627578&prj=554&rqi=o7nBK4huBIZ3wMkD0icrb3z3xH
RT1MECH-423-002 | PA13x-2 Mickey | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning | Fire Suppression | equipment | Fit Out - MFD-3130 | FD - Fire Damper |  |  | Fire Suppression - MFD-3030 fire damper access panel in Mickey office badly cut in to ductwork sharp edges - CUT risk | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626710&prj=554&rqi=iSAAXtoVr65Fg5vCmC93AHzYUJ
RT1MECH-423-001 | PA13x-2 Mickey | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | Fire Suppression | equipment | Fit Out - MFD-3130 | FD - Fire Damper |  |  | Fire Suppression - MFD-3030 ID label missing from actuator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626707&prj=554&rqi=D1SnQqzy6fIULuEc6xVQziqTyv
YT1MECH-438-001 | PA13x-2 Mickey | N-EMEA | Open | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-06-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation Not issued/ Required | Commissioning | Fire Suppression | equipment | Fit Out - MFD-3130 | FD - Fire Damper |  |  | Fire Supression MFD-3130 Chubb cable test doc required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625340&prj=554&rqi=ukJ97IgRE8nGWJ99cHE5M14qUS
L3-10-001 | PA13x-2 Mickey | N-EMEA | Closed | P3 Low CX | richardw@straightlineconsulting.co.uk | 2026-06-11 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Documentation Not issued/ Required | Commissioning |  | equipment | 3-PA-11 |  |  |  | Mechanical - 3-PA-11 Missing documents ( Updated drawing, System) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624919&prj=554&rqi=20Ts1tJdsbD911nZyJHnWB0Eue
GI-236 | PA13x-2 Mickey | N-EMEA | Closed | P3 Low CX | richardw@straightlineconsulting.co.uk | 2026-06-10 04:00:00.000 +0400 | General Contractor - Electrical |  | Commissioning Issue | Commissioning | [6 empty] | Electrical - Missing Arc Flash label for DB, STS and UDP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624754&prj=554&rqi=AT375Butt4zXUJLYMN7xZkoQVf
GT1ELEC-510-002 | PA13x-2 Mickey | N-EMEA | Open | P2 Medium CX | richardw@straightlineconsulting.co.uk | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | Electrical | equipment | Fit Out - Lighting / Emergency Lighting | LITE - Lighting Control |  |  | Electrical - Confirm LUX levels have been checked against global standards (normal lighting). Lux levels not achieved - Minimum 500 lux | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622452&prj=554&rqi=jGFDySLQYyQimt4Ygz4wfG3rxa
GT1ELEC-510-001 | PA13x-2 Mickey | N-EMEA | Open | P3 Low CX | richardw@straightlineconsulting.co.uk | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | Electrical | equipment | Fit Out - Lighting / Emergency Lighting | LITE - Lighting Control |  |  | Electrical - Confirm all associated distribution panels for lighting controls and power have been level 3 commissioned and signed off accordingly. DALI system needs to be reviewed and handed to OPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622449&prj=554&rqi=lQCmqnt7irYGik7d33gu6eKV4e
L3-13-001 | PA13x-2 Mickey | N-EMEA | Open | P2 Medium CX | richardw@straightlineconsulting.co.uk | 2026-05-19 04:00:00.000 +0400 | Equinix Commissioning Manager | L3 | Commissioning Issue | Commissioning |  | system | FIRE - Fire detection / Alarm system |  |  |  | Confirm that battery back-up autonomy meets specification (isolate mains supply for â€˜24â€™ hours then operate fire detection and ensure sounders operate for specified time) Battery needs to be replaced and test needs to be re-done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622265&prj=554&rqi=sy9IZ29B63bCGDfl0f1K10gr06 | https://equinix.facilitygrid.co.uk/x/project/554/system/13897
GI-235 | PA13x-2 Mickey | N-EMEA | Closed | P3 Low CX | richardw@straightlineconsulting.co.uk | 2026-05-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | [6 empty] | Electrical - Missing labels on all busbars | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620116&prj=554&rqi=Wexn227JwADNoU4VFXLoq84P8L
GI-021 | PA13x-SWGR | N-EMEA | Closed | P2 Medium CX | Iuliant@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | VER - Vertiv Electrical |  | Comms Issue/Fault | DCOS | Electrical | equipment | 1-COP-D2 | COP - Customer Operating Panel |  |  | Circuit breakers B12;C2;C3;C4 show issues/fault on DCOS trip status . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198862&prj=526&rqi=0JInk4k586kcqMxBN2k8LOjZTw
SOR-72-004 | PA13x-SWGR | N-EMEA | Closed | P3 Low CX | Iuliant@straightlineconsulting.co.uk | 2026-01-09 04:00:00.000 +0400 | VER - Vertiv Electrical |  | Labelling | Commissioning | Electrical | equipment | MSB-D | MSB- Main Input Switchboard |  |  | MSB-D Bus-bar Phase Sequence Label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196647&prj=526&rqi=Oyzz9Y4qqN9M2XdvHNDMVT6qRk
SOR-52-003 | PA13x-SWGR | N-EMEA | Open | P3 Low CX | Iuliant@straightlineconsulting.co.uk | 2026-01-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS not Complete | DCOS | Electrical | equipment | 1-COP-D1 | COP - Customer Operating Panel |  |  | Confirmation is required regarding the current status of the MCB for COP-D1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196646&prj=526&rqi=eVDbfh2u5lf2ObiceQhZJQzZ25
L2L3 Sun-166-001 | PA14-1 | N-EMEA | Open | P3 Low CX | steved@straightlineconsulting.co.uk | 2026-08-14 04:00:00.000 +0400 | General Contractor - Electrical |  | Incomplete Connections | Commissioning | Electrical â€“ MV | equipment | 1HMTX_1 | HMTX - Primary Substation Transformers |  |  | Thermal Relay fed by temporary power, needs a permanent supply, and has a temporary label, plus has a few scratches on the door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633621&prj=553&rqi=AoggHH5FXo623skbcglgeY3PIR
GI-019 | PA14-1 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [6 empty] | 1PCP_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625303&prj=553&rqi=DSTxXtAoCiloL3opDi3sQkU2mX
GI-016 | PA14-1 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [6 empty] | 1PCP_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625300&prj=553&rqi=BKL1CUXzFrvgZWwq6NVNf9ofjC
GI-017 | PA14-1 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [6 empty] | 1PCP_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625301&prj=553&rqi=EZw4z4two5uN3KtZrR9Yklr7ou
GI-018 | PA14-1 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [6 empty] | 1PCP_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625302&prj=553&rqi=iAWLzILQnG5S7bfh2foEa0IxSZ
GI-015 | PA14-1 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-14 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [6 empty] | 1PCP_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625293&prj=553&rqi=NGxu5aSsHcrxhso7Lw3btrIA5a
GI-012 | PA14-1 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-09 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Commissioning Issue | Commissioning | [6 empty] | 1UDP_C2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624695&prj=553&rqi=nGVINIldSSQ6BsZYIVoF9Xs3z2
GI-011 | PA14-1 | N-EMEA | Open | P3 Low CX | hajar.banan@spie.com | 2026-06-04 04:00:00.000 +0400 | SOC - Socomec |  | Commissioning Issue | Commissioning | [6 empty] | 1STS_C2R_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623938&prj=553&rqi=cerUyacp1nFJmnq3vTt6Vum0sU
RT1ELEC-12-001 | PA14-1 | N-EMEA | Closed | P3 Low CX | steved@straightlineconsulting.co.uk | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider MV | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1GRMU_B | GRMU - Generator Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme. Missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623599&prj=553&rqi=Xow31qkknyzyvyxTe8Nq0eIDls
RT1ELEC-11-001 | PA14-1 | N-EMEA | Closed | P3 Low CX | steved@straightlineconsulting.co.uk | 2026-05-26 04:00:00.000 +0400 | SCH - Schneider MV | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1GRMU_A | GRMU - Generator Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme, labels missing for breakers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623136&prj=553&rqi=NnYvappD3zyWrOsIwAdZ7eBwgc
RT1ELEC-11-002 | PA14-1 | N-EMEA | Open | P3 Low CX | steved@straightlineconsulting.co.uk | 2026-05-26 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1GRMU_A | GRMU - Generator Ring Main Unit |  |  | Verify the switchgear tool board is secured to a wall. Missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623137&prj=553&rqi=IKT31Bf78q6c7NKGfhrCIpOT6G
GI-010 | PA14-1 | N-EMEA | Closed | P2 Medium CX | simonm@straightlineconsulting.co.uk | 2026-03-26 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | system | CWTR |  |  |  | Installation in progress without approved test packs/QA process in place. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616658&prj=553&rqi=CLg17zOtyELwLPUSGNvsxyLy0l | https://equinix.facilitygrid.co.uk/x/project/553/system/12491
GI-008 | PA14-1 | N-EMEA | Open | P3 Low CX | simonm@straightlineconsulting.co.uk | 2026-02-25 04:00:00.000 +0400 | Project Manager |  | Design not as specified | Design | [6 empty] | Mechanical - Technical Submittal of TW240. The approved tech sub has a statement on page 13 stating that the CHW return temperature must be reduced to from 28Deg C to 27.4Deg C, achieved by increasing the flow through the balancing valves. And on page 15 the return air temperature to be increased from 37Deg C to 37.5Deg C This means that all the assets withing the CHW system will need to have recalculated specification to accommodate this, but there doesn't seem to be addressed anywhere. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221135&prj=553&rqi=jkNdltib6qP4pXj6wuIFyGihkC
GI-002 | PA14-1 | N-EMEA | Open | P3 Low CX | steved@straightlineconsulting.co.uk | 2026-01-19 04:00:00.000 +0400 | SCH - Schneider MV |  | Documentation not issued/ Required | Commissioning | [6 empty] | Electrical - Issue found during FWT of PUSP Panel :- â€¢ Schneider: To update the nameplate of each cubicle according to SPIE instructions and Equipment naming to be added to each panel like : 1PUSP_1 / 1PUSP_2 â€¢ Schneider: To add the cell serial number to the PUSP schematics to avoid errors during assembly â€¢ Schneider: Key number: R1T to be differentiated between the 2 stations according to SPIE's instructions (R1T_1 / R1T_2) â€¢ Schneider must provide the connection recommendations (Cable heads, etc.) â€¢ Schneider: Place a warning label on the emergency stop button of each PUSP panel. â€¢ Schneider: To update the schematics by taking into account the various issues raised. â€¢ Schneider: must submit to SPIE a control/monitoring cable schedule (eg. P643 cabinetâ€¦) following the same method implemented by Schneider MCE. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197156&prj=553&rqi=qtfTDyIxWJa5bL9K9GkQQ1bypU
BT1MECH-1-006 | PA3-DH7 Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-30 04:00:00.000 +0400 | Equinix Project Manager | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | EPIVE 07,02,06 - Glycol Concentration 60% compared to other valves at 24% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616876&prj=676&rqi=2oBYr9FZ3ZTcIHlB3Zg0Mw9nIV | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
BT1MECH-1-005 | PA3-DH7 Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-29 04:00:00.000 +0400 | Equinix Project Manager | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | CDU status not changing to 'Tank filling' during pump fill process. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616804&prj=676&rqi=6bgxGKQjE9krrpU847wwwnC359 | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
BT1MECH-1-002 | PA3-DH7 Liquid Cooling | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-27 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Commissioning Issue | Commissioning | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | CDU-01 HMI not responding to some setpoint changes. Changes are reverting back to original settings after a few seconds. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616661&prj=676&rqi=T3dfS9ZgWxvBkrHCnXkTWRl0xT | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
BT1MECH-1-001 | PA3-DH7 Liquid Cooling | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-27 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Installation not correct | Commissioning | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | All CDU airvents installed with PTFE tape, some o-rings appear damaged/mishapen and some airvent caps are missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616660&prj=676&rqi=EZ1eOY4ARxrTPCvMnws90tX0UD | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
BT1MECH-1-003 | PA3-DH7 Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-27 04:00:00.000 +0400 | Equinix Project Manager | L4 | Installation not correct | Commissioning | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | PTFE tape and brass/galvanised steel connections used on temporary connections to Manifold. All materials used must comply with wetted materials list and a suitable anaerobic sealant used instead of PTFE tape. PTFE tape can disintegrate and contaminate TCS/SFN causing blockages to filters and equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616663&prj=676&rqi=74glFqqZWS07QQGfoBvqBQAEQf | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
BT1MECH-1-004 | PA3-DH7 Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-27 04:00:00.000 +0400 | Equinix Project Manager | L4 | Labelling | Commissioning | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | All valves to be labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616705&prj=676&rqi=G1Bt7Qxk68ER2j5zSvUXZJVc9Z | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
GI-023 | RJ03-2 | AMER | Open | P3 Low CX | jesse.oliveira@b2dc.com | 2026-09-15 04:00:00.000 +0400 | Subcontractor |  | Missing Components | Commissioning | [6 empty] | Conduit box without cover | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638233&prj=651&rqi=LPj6SIOYRSCSSkjPD13B2dkMd6
GI-024 | RJ03-2 | AMER | Open | P3 Low CX | jesse.oliveira@b2dc.com | 2026-09-15 04:00:00.000 +0400 | Subcontractor |  | Installation not complete | Commissioning | [6 empty] | missing the support for the hydraulic line | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638234&prj=651&rqi=GofNn0e7nAEGbt8V1XvXnJcwyU
GI-025 | RJ03-2 | AMER | Open | P3 Low CX | jesse.oliveira@b2dc.com | 2026-09-15 04:00:00.000 +0400 | Subcontractor |  | Installation not complete | Commissioning | [6 empty] | missing teamwork | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638235&prj=651&rqi=GT92WZIN1i0tHMOiOukJmhA0eG
GI-022 | RJ03-2 | AMER | Open | P3 Low CX | jesse.oliveira@b2dc.com | 2026-09-10 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning | [6 empty] | The arc flash sticker was not found on the equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637624&prj=651&rqi=RO75Z2Bld3r043xqi78UOqzfNZ
GI-015 | RJ03-2 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-22 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Drawings are out of date within panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634805&prj=651&rqi=10X5dIFTRiP1IMluAB4cbXjqOG
GI-017 | RJ03-2 | AMER | Open | P2 Medium CX | mt.uchoa.eng@gmail.com | 2026-08-22 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Vesdas VEU-15 and VEU-16 installed in previous Phase 1: Existing pipes have not been removed. New pipes in circulation have not been installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634808&prj=651&rqi=MIL75mlh6aNpNME2uZ3o3mTcNO
GI-018 | RJ03-2 | AMER | Open | P2 Medium CX | mt.uchoa.eng@gmail.com | 2026-08-22 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | VESDAs - Asbuilted and approved ASPIRE hydraulic calculation and isometrics not delivered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634809&prj=651&rqi=pZDft6Ai3hBSYnt9AvQe2HQ4Bz
GI-016 | RJ03-2 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-22 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Drawings are out of date within panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634807&prj=651&rqi=pkyAJubtDaOZzUGemqMvIizDTE
GI-013 | RJ03-2 | AMER | Closed | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-20 04:00:00.000 +0400 | General Contractor |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | VESDAs - Quick connect benchmark fittings specified in design are not installed in testpoints. -- Issue closed (repeated) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634542&prj=651&rqi=9keqvWhdhOcWoXZzLVbXUWXCGx
GI-008 | RJ03-2 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-20 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | VESDAs - L2A GC checklist signed-off not presented. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634535&prj=651&rqi=SNunJZ3pVZpt8HyNVvaPaAzfYi
GI-006 | RJ03-2 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-20 04:00:00.000 +0400 | General Contractor |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | VESDAs - Batteries not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634527&prj=651&rqi=fG7Qwl6OTvkVAVsE0ITDmpQDhu
GI-007 | RJ03-2 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-20 04:00:00.000 +0400 | General Contractor |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | There are some loose clamps in sampling pipes - VES-03; VES-014; VEU-07; VEU-08; VEU-09; VEU-17 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634534&prj=651&rqi=o1p7QRoSjEqqHpVtf0iXiIDTIQ
GI-012 | RJ03-2 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-20 04:00:00.000 +0400 | General Contractor |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | VESDAS Model VES - Quick connect benchmark fiiting specified in design are not installed in endpoints. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634541&prj=651&rqi=4weSDq13ElqdCj0WZqf77eqGCd
GI-004 | RJ03-2 | AMER | Ready for Verification | P3 Low CX | Julio@b2dc.com | 2026-08-15 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | The LOTO procedure complete with organogram structure are not available on Sharepoint The LOTO procedure posted on SharePoint does not mention the equipment in Blocks B and C or how to lock them out | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633851&prj=651&rqi=lkLADUH4VZ9gdcU6Q9pzx5w2rL
YT1ELEC-163-001 | RJ03-2 | AMER | Closed | P2 Medium CX | Julio@b2dc.com | 2026-07-30 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment type | TX - 480v-208/120 Transformer | TX - 480v-208/120 Transformer |  |  | The L2B documentation is not available on SharePoint for analysis and inspection of the equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631615&prj=651&rqi=03ODQmhqW3PPU2AzDGIXiRTNZN
GI-002 | RJ03-2 | AMER | Open | P3 Low CX | cassiano.ferreira@b2dc.com | 2026-07-24 04:00:00.000 +0400 | SCH - Schneider Electric |  | Documentation not issued/ Required | Commissioning | [6 empty] | An analysis of the available documentation was conducted, and it was found that the documents listed below were missing, MSB, UDP e RMU-BTU. The torque wrench calibration certificate was not found on Asite The approved technical documentation (description) was not found on the Project Portal MCE was unable to find the electrical panel installation and operation manual on the Project Portal | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630749&prj=651&rqi=dZz4SYrVygXpwAUOUqxVv5ucOF
GI-001 | RJ03-2 | AMER | Ready for Verification | P3 Low CX | bruno@b2dc.com | 2026-05-22 04:00:00.000 +0400 | VER - Vertiv |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Actual Submittal evaluated from projects ""PW161 (AAN).pdf"" to CRAH Vertiv equipment requires additional specification described below: 1) Specification of the CRAH outlet air deflectors. This issue requires the aprooval from design for the specification of the air deflectors to be closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622830&prj=651&rqi=lLBTOixUi7MyGGpLqkf4beNdSw
L2L3 Sun-238-001 | SG03-P4 | APAC | Open | P2 Medium CX | MarcusGoh@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-5 | CPR2 - UPS |  |  | HMI OS and APP version for UPS-R-CPR2-5 differs from the approved setting list. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636549&prj=615&rqi=iTOG1L9tYZldATPigjVXRqzYct
GI-042 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-31 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical | equipment | DB MP-R-CPR2-02 | CPR2 - Mech DB |  |  | [Power Meter Test with PQMS]: During the test, the power factor readings for power meters F01 and F02 were displayed incorrectly on PQMS. In addition, the THD-V and THD-I readings for F02 were also not displayed correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636080&prj=615&rqi=r8VCBcjwazlxY8bXrYCpbXqpvN
GI-037 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | Redundant alarm notifications were observed in the BMS alarm log. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633599&prj=615&rqi=D35V9oFTACmGH4DUqr4JNIgi3n
GI-040 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | SMS notification to AlertOps was not ready for testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633602&prj=615&rqi=7mrv8i7O7L2OdVahcIbP4zdsmD
GI-039 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | During Overload Stage 1 (110%â€“125% load), the inverter transferred to Static Bypass after 7 minutes 40 seconds instead of the required 10 minutes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633601&prj=615&rqi=UXjNrIsndS8z9HZlfbx2tHMLWU
GI-038 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | During the battery discharge test, the BMS received a Low Battery alarm; however, the corresponding Low Battery alarm was not displayed on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633600&prj=615&rqi=oSt0zWhhbzdYpMqIwONI7kyrDM
GI-041 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | No approved UPS setting list was available at the time of testing. Testing was initially conducted based on the UPS settings proposed by Eaton. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633603&prj=615&rqi=OInh1AqjchGeNzt5gCqDohx0lJ
GI-036 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | Battery remaining runtime was not displayed on the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633598&prj=615&rqi=6OJ2ntjCJPKVpGIHAOxmWpTMv6
GI-035 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | The UPS has separate Overload and Output Overload alarms. When the Output Overload alarm was triggered, the corresponding Output Overload alarm was correctly received by the BMS. However, when the Overload alarm was triggered, the BMS continued to display Output Overload instead of the corresponding Overload alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633597&prj=615&rqi=3aWXWmp44yR2nX6qmSG4ITkwtU
GI-034 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | Upon simulating high-level communication loss by disconnecting the CAT6 communication cable, no SMS notification was generated to AlertOps. As a result, Operations may not be aware of the communication loss. However, the BMS interface at the respective UPS displayed â€œ?â€ indicators against the affected AI points, indicating the loss of communication. BMS vendor to configure SMS notification as an alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633592&prj=615&rqi=0tCIv8rWeYnydvMCk5NsaeqE3B
GI-033 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | PLC-R-CPR2-01 | CPR2 - BMS |  |  | Revealed during Cx3 FCU with BMS: It was observed that the BMS graphics only display the FCU tag/name without indicating the corresponding room layout or the specific room served by each FCU. As the approved GUI was not available during the inspection, the BMS team shall update the graphics to include the room location served by each FCU. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630924&prj=615&rqi=ixF2smpE0G8DqvqJyktsQD6nUT
GI-032 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | [CHSB Breaker Modification Works]: The BMS team shall update the GUI (SLD) in accordance with the approved naming convention and SLD. It was observed that CHSB CPR2 still shows an outgoing feeder to CP-CHWP. Therefore, the team shall ensure that the BMS SLD is updated prior to conducting the CHSB breaker modification works. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630921&prj=615&rqi=wvZ0veeYeMdDW4wVte0LVofYGt
GI-030 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical | equipment | CP-FCU-R-CPR2-04 | CPR2 - FCU CP |  |  | There was no approved setting for overload thermal relay for both MV fans and FCU visible during inspection. WL to confirm with design consultant/LEW. This issue applicable to all 12 nos of FCU and 12 nos of MV Fan at CPR2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624675&prj=615&rqi=fFinJQb5GOGBeAUCFZdmRh0m52
GI-029 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | PLC-R-CPR2-01 | CPR2 - BMS |  |  | Few issues revealed during Cx2A for PLC panel: 1) Vendor to provide and submit the SLD/control diagram drawing for design consultant's approval. This drawing was not visible during inspection. 2) To update GA drawing as per built on-site. 3) There were two different MCB type installed for both PLC panels. One panel was equipped with Type B 6A while another one was equipped with Type C 6A MCB. To confirm with design consultant. 4) To install earth bonding between panel door and panel 5) To put component's sticker labelling for clarity | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623900&prj=615&rqi=RxzzUSJD3zqUN5CCFSvkfaA3w3
FPT-16-002 | SG04-4A | APAC | Closed | P2 Medium CX | MarcusGoh@commtechasia.com | 2026-08-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Installation not correct | Commissioning |  | equipment type |  |  |  |  | After the CRAC unit restarted following a power failure, the EBIV failed to open to Vmax as specified in the SoO. Instead, the valve returned to 0% open and resumed modulating based on the Supply Air Temperature (SAT) control logic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632816&prj=663&rqi=8rU83BWihEXbCJu6V5yP7XUBjb
FPT-49-001 | SG04-4A | APAC | Closed | P2 Medium CX | MarcusGoh@commtechasia.com | 2026-08-09 04:00:00.000 +0400 | General Contractor | L4 | Installation not correct | Commissioning | Multi-Discipline | system | Heat Load Test (DH 5-2) |  |  |  | DH5-2 cold aisle temperature increased to 26.8Â°C at RLE Sensors 11 and 18 when the CHW ring valves between CRAC Units 9 and 10 were closed. It was also observed that one of the CHW ring valves between CRAC Units 8 and 9 was not fully opened. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632815&prj=663&rqi=LvgFlPeT9nJxXCLyz2Wxa418zs | https://equinix.facilitygrid.co.uk/x/project/663/system/14481
GI-048 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | 1. There are questions mark on top of all the faceplate in granular control overview page.Granular control 2. PLC connection status on graphic not ready, to be configured. 3. Existing Prosoft Gateway for RLE manger keeps showing alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629920&prj=663&rqi=Xsp5v0c6qkHlwQO1BeKUS9olTw
GI-050 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | CRAC did not fall back to local unit SAT setpoint when signal from Granular Control is lost. CRAC will be running based on last SAT setpoint commanded by Granular System. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629922&prj=663&rqi=ksNOHX7kc5VvMlQNOfZI25kwMj
GI-049 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-19 04:00:00.000 +0400 | General Contractor |  | Component/ Equipment Failure | Commissioning | [6 empty] | RLE-24 temperature and humidity readings different with other sensors. The sensor was unable to recover back after RLE Wing Manager power failure test. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629921&prj=663&rqi=65YrHZiR2WG3rl3alLmhAffQQa
GI-047 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Comms Issue/ Fault | DCOS |  | equipment type |  |  |  |  | When CU loss of power and communication loss with DCOS, there is no loss comm alarm at DCOS. Parameters loss comm but communication alarm still show inactive. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628312&prj=663&rqi=2kbBu3osSIxCGalKgAVik20W1d
GI-045 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | DCOS summary and face plate naming need to be changed from 5_BATTR_A_1_PREACT to 1-GSCP BATTR 5A and 1-GSCP BATTR 5B. Applicable for all gas suppression panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628310&prj=663&rqi=ioEGIzlgBakGhpDA5F61fTiVa3
GI-046 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Fire Mimic panel needs to reflect the latest battery room layout 5A and 5B. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628311&prj=663&rqi=lX6rInmQ934pwNaxcI19uJwBl7
GI-044 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | To provide LEW endorsed drawing and place inside the LCP. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628136&prj=663&rqi=Ci661fd1hKFGGSRoKYTNd49fqt
GI-042 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | 1. Rockwell is required to check whether the RLE sensor will still be included in the calculation when it is placed in maintenance mode. 2. Rockwell is required to check the meaning of the triangle with a question mark symbol shown on the RLE sensor graphic. 3. Two parameters are missing from the Machine Learning faceplate. Rockwell is required to add these parameters. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627195&prj=663&rqi=lLZTVCi2Vj6wWXFli4jdu4GGPB
GI-038 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | 1. The layout of the ProSoft and FiberTek communication gateways differs from the drawing. 2. The labeling of the ProSoft gateway does not match the drawing. 3. The quantity of the TB-24V1 fuses does not tally with the drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627098&prj=663&rqi=lE7qAlzfJ8ux1diU4hSe8Jg0hW
GI-035 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | There is no labeling for smoke detector signal cables inside the unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626875&prj=663&rqi=ABOcAnUG3gBpUvLJUFuRpgayjd
GI-029 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-21 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | 1. The name of LCP need to reflect actual room name "5A" and "5B". 2. MCB for damper, control and 230V XFMR inside the LCP are not labeled. 3. Fuse for cooling fan and power sensing "NSF", "ESF" are not labeled. 4. To provide labeling for incoming power cables. 5. Labeling of LCP trunking and conduit are inadequate and some are not labeled. 6. The fan isolators, hydrogen and methane sensor are not labeled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626314&prj=663&rqi=vKxE6PYMrtf3BVVfMLg8yvecq7
GI-031 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-21 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | 1. The installed manual release and abort switch for GSS are different with approved layout. 2. The installed Pre-action pipe and sprinkler head quantity/location are different with approved layout. 3. Location of pre-action sprinkler pipe drain point are different with approved layout. 4. The location of fireman intercom panel is different with approved layout. 5. There is no drawing placed inside the GSS panel. 6. The height of GSS panel installed is different with approved drawing. 7. There is no breathing apparatus installed outside the battery room. 8. There is no zone chart installed. 9. The painting of trunking and conduit need to touch up. 10. There is no zone chart installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626329&prj=663&rqi=GUM1hdPyCBk31iZk3p1QfYY1fu
GI-028 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-21 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | 1. Table of primary and secondary source need to be updated in LCP SLD as per site installation. 2. Battery room 5A equipment layout is different with the drawing. 3. The rating of fuse for LCP cooling fan is not tally with SLD, update in SLD is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626313&prj=663&rqi=QaRYCo40XpxrLhVWdQZOCYoqa3
GI-032 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-21 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | 1. External fire modules are not labeled. 2. There is no labeling of all the cables inside the GSS panel. 3. There is no labeling of all pipes, conduit and trunking. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626330&prj=663&rqi=Tj9gIrhQrKMYC4MsyvSiPwwjml
GI-023 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | 1. There is no equipment labeling for condenser unit. 2. There is no circuit labeling for power isolator. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625562&prj=663&rqi=nmqzCYsKsn6QL7mqdYEEVDzcbs
GI-024 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | 1. The gradient of condensate drain pipe has been lift up by power conduit, to rectify. 2. The condensate drain pipe armaflex insulation is incomplete and not properly sealed. 3. There is no equipment labeling on DxFCU and its thermostat. 4. There is no labeling on condensate drain pipe and trunking. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625566&prj=663&rqi=hQHVeiLJu0LPhzp6RCv6MTCUTg
GI-022 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | 1. All the labeling of outgoing cables terminal blocks are not tally with the circuit number. 2. The labeling of relay is not tally with the outgoing circuit. Refer to the photo attached. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621850&prj=663&rqi=SoqBsQmTqnX4N2RAOG7drr33if
DCOS-1-002 | SG04-4A | APAC | Closed | P2 Medium DCOS | MarcusGoh@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L1 | DCOS Template Issue | DCOS | [6 empty] | ERCS/QA required to raise RFI regarding the alarm severity that is not stated in SPL â€‚â€‚â€‚ UPS: - Blower fan failure 850 - Emergency power off 850 CRAC: - Loss of air flow 450 - Loss of power 650 - Supply air RH high / low 650 - Return air RH high / low 650 - Return air temp high / low 650 - SAT sensor failure 650 - RAT sensor failure 650 - RH sensor failure 650 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621310&prj=663&rqi=Bnn9oLXdQQUWy79bm5kMAQwRmK
DCOS-1-001 | SG04-4A | APAC | Closed | P2 Medium DCOS | MarcusGoh@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L1 | DCOS Graphics Issue | DCOS | [6 empty] | DCOS SFAT Issues and Observations: 1. UPS "load on bypass" and "low battery alarm" alarm severity to change from critical 950 to urgent 850 as per SPL 1.0. 2. The summary page of UPS did not show any alarm when the alarm was triggered. 3. Static text for UPS tagging needs to be corrected and the text â€œtemplateâ€ shall be removed. 4. UPS high limit and low limit alarm thresholds shall be user-editable. 5. All equipment Maximo IDs have already been provided by ERCS. DCOS is required to deploy and update the IDs in the graphics. 6. ERCS is required to request the location vector from EQIX and provide it to DCOS for updating. 7. Equipment naming in DCOS shall follow the UIUX naming format. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621309&prj=663&rqi=OVRTcdAwKvgPCrCn14m2Q4TICj
GI-017 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Kindly provide sticker labeling for the breaker settings, in accordance with the approved discrimination study, for all new SUDP and PDU. Including Arc Flash sticker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620702&prj=663&rqi=YfiWYQyL42xvX6uvhJvn2bxNtx
GI-015 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | 1. Missing cable labeling for CAT6 cables as per photo attached. 2. To provide drawing pocket and attach LEW endorsed drawings for SUDP. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619995&prj=663&rqi=MF2YnappeMDwwA5ANVrQugnh28
GI-014 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | To provide drawing pocket and attach LEW endorsed drawings for SUDP and PDU. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619994&prj=663&rqi=8nomCuW0vKBAxloy86TuhK2hoM
GI-013 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | When the unit stops due to loss of air flow, there is no loss of air flow alarm showing at the unit HMI. The unit only shows fan failure alarm, Stulz to check and clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619992&prj=663&rqi=U4E7OF93Tsl82NreJxR25elWcf
GI-009 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | To provide labelling for signal cables at E2 controller terminals J14. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619397&prj=663&rqi=XmrHLXygTttKjlDI7lALExrCJQ
GI-002 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Torque required | Commissioning |  | equipment type |  |  |  |  | To provide torque markings on all earth cable terminations. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617411&prj=663&rqi=ZnOMHjF6BwICtuUqVTgp5D0SAq
GI-004 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | 1. The fuse F02 rating of "6A" does not tally with the approved drawing, which specifies "4A". To update the drawing. 2. The overload contactor F31 range of "26Aâ€“32A" does not tally with the approved drawing, which specifies "2.5Aâ€“32A". To update the drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617413&prj=663&rqi=KEw7s2udpvirs4gWQudqvBsz5O
GI-008 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | To standardize the SAT sensors under the raised floor to face toward the CRAC units, except where obstructed by other services. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617417&prj=663&rqi=wVDtuA08qnFK24LmWcUIWkSKu1
GI-006 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | The Armaflex insulation for CHW pipes inside the units is not properly wrapped and has come loose, to rectify accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617415&prj=663&rqi=SOPc56z6dDguG4biCopaWZVe8Z
GI-003 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | To provide labelling for signal cables at E2 controller terminals J10 and J4. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617412&prj=663&rqi=kCa99U6srCWOLXUEao4vye9zJ4
GI-007 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Condensate drain pipes after passing through the units are not properly secured, to secure accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617416&prj=663&rqi=ZtLNz5o4vktcs4hqFKmpDmb2j2
GI-005 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | To cap off the cooling coil drain point. Applicable to all CRAC units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617414&prj=663&rqi=Ap4kAetxIr9BiM1ohGhYiYmaiC
GI-001 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | All the CAT 6 cables connecting between Adapter Board and MCMS Port are not labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617001&prj=663&rqi=0km2qDfeiZYPZQbJcZfP6bjWvS
GT1SEC-2-005 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-11-09 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not complete | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx3: Level 5 : D137 no BG D153 no KCU D147 cannot test door cannot close D152 cannot test door cannot close D148 cannot test door cannot close | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637847&prj=618&rqi=JD5ENuotcnV3qidPPIaFSUdYAo | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GT1DCOS-13-001 | SG06-1 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-09-16 04:00:00.000 +0400 | General Contractor - BMS | L3 | General Design Issue | Design | Controls | equipment | 1CPOS_RIO_01 | DCOS - Control Panels |  |  | It was observed that the Power Supply Common Alarm refers to the PSU failure alarm. During the simulation of Primary Source and Secondary Source failures individually, no alarm was triggered to provide notification. (Apply to all CPOS Panels) Based on the control wiring, the two sources are combined to supply the two PSUs. Therefore, a failure of only Source 1 or Source 2 will not trigger the PSU failure alarm. The PSU alarm will only be triggered when both the primary and secondary sources fail, resulting in a loss of supply to the PSUs. Kindly clarify with the EoR to confirm the design intent and verify whether the current alarm logic is in accordance with the approved design. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638239&prj=618&rqi=420OniNhjEJfjdD6k7TFEtuCBO
GI-512 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-09-16 04:00:00.000 +0400 | Electronic Safety and Security Contractor |  | Commissioning Issue | Commissioning | Security | system | Security - Card Access System |  |  |  | L8 CX Issues - D224 DC always open - D222 DC always open | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638425&prj=618&rqi=lzKpFIf7fEOni63glDGIFO3Fnu | https://equinix.facilitygrid.co.uk/x/project/618/system/14513
GI-511 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-09-15 04:00:00.000 +0400 | Electronic Safety and Security Contractor |  | Commissioning Issue | Commissioning | Security | system | Security - Card Access System |  |  |  | L7 CX - D197 DC always open - D211 DC always close - D212 EL no power - D210 no BG - D208 DC always open | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638424&prj=618&rqi=1pFASZ1fYmdzcv27wA9Xy8dwgy | https://equinix.facilitygrid.co.uk/x/project/618/system/14513
RT1ELEC-552-001 | SG06-1 | APAC | Open | P3 Low CX | KeeLeongLee@commtechasia.com | 2026-09-14 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | For Level 8 IT busduct, please rectify the following: 1. To replace label for J-21,56,67, 2. To ensure the joint label is installed properly for J-043 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637901&prj=618&rqi=ltBvvRdCdfhHAeuzH53Ya6IE9y | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GT1SEC-2-006 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-09-14 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not complete | Commissioning | Security | system | Security - CCTV System |  |  |  | L6 CX3 Issues - D172 DC always close - D173 EL Issue - D169 no BG - D714 EL Issue - DR181 no BG - D184 DC always close - D184 no BG - D180 DC always close | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637903&prj=618&rqi=q1wFQGKhjIfXeNlqnU1O2i6fdV | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GT1SEC-2-004 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-09-10 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not correct | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx3: Level 4 Issues D108 No REX MC1 No Siren D119 No REX D121 DC always open MC3 No Siren | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637587&prj=618&rqi=f4IDtjVfypsVjQuFVW3s3cVXjk | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GT1SEC-2-002 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not correct | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx3: CCTV CX3 : Cam 153 : View is partially obstructed by the exit light | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637399&prj=618&rqi=f91rIKBrdcirJWcAuDOefouB5Z | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-504 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Electronic Safety and Security Contractor |  | Installation not complete | Commissioning | Security | system | Security - CCTV System |  |  |  | L3 CX Issues - D85 DC always closed - D81 DC always open - D94 DC always closed - D96 open without scanning card | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637450&prj=618&rqi=nq6WU653T9eh6g2kRktnyldJ9i | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GT1SEC-2-003 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not correct | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx3: Level 2 to 9: 1.Fire fighting lobby 2A to ext corridoor biometric reader need to shift 2. Level 2 TER Room A door access have issues 3. E wall A door access have issue 4. Door 65 Cool spine 1 has issues Camera: 1. L1 to L9 (Staircase 1 to 4) CCTV is removed as per SCDf comments , thus the view of the respective cameras is blanked out during the CX3 test | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637400&prj=618&rqi=71fcCQQPRQtj2wzLAeAzv06i3g | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-500 | SG06-1 | APAC | Ready for Verification | P2 Medium CX | jessyong@commtechasia.com | 2026-09-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General Design Issue | Design |  | equipment type |  |  |  |  | Observed incorrect voltage readings and negative kw readings at the ACB micrologic for STSSB. Socomec to rectify for all STSSB. Dcos has feedback when load test with s2, no negative values observed and voltage readings are normal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637058&prj=618&rqi=5DVjxjSqc5kkY5jVqXw9okCRy6
GI-497 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2 A/ B: General Defects : 1SF Z 18, 1SF Z 5, 1EF M1 3 , 1EF M1 2 , 1FCU A 05 , 1FCU A 06 1. Document pocket to be affixed on all FCU / SF 2. Ducting needs to be labelled 3. Drawing needs to be updated as per components installed on the panel 4. Trunking to be sealed properly 1FCU A 06 (incoming earth not terminated) 1. Document pocket to be affixed on all FCU / SF 2. Ducting needs to be labelled 3. Drawing needs to be updated as per components installed on the panel 4. Trunking to be sealed properly 1SF A 12 1. Document pocket to be affixed on all FCU / SF 2. Ducting needs to be labelled 3. Drawing needs to be updated as per components installed on the panel 4. Trunking to be sealed properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636505&prj=618&rqi=bbjUMpy9893bRIQ6jfgyCosFIL
GI-496 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx L2A - General Issues for FCU / EF / SF 1. Please ensure that there are permanent labels affixed to the Equipment / Control Panels 2. Ensure that there is a document pocket affixed to the control panel 3. FCU - Ensure that permanent labels are affixed to the thermostats of the FCU when they are installed 4. FCU name plate is installed on to the Control panel as per GA drawing 5. Ensure that the earthing cable (Trunking) is terminated 6. Unit strut needs to be shortened with end caps installed on them 7. The Ducting needs to have label applied to them | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636499&prj=618&rqi=Y7vRRpLkRsPHzXWJ4WksLLmqYH
GT1SEC-2-001 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not complete | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx3 : L1 to L9 (Staircase 1 to 4) CCTV is removed as per SCDf comments , awaiting waiver from scdf if it would be reinstalled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636413&prj=618&rqi=yVVqyb5Dt47sMEdlYseoHwVUJr | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
RT1ELEC-553-001 | SG06-1 | APAC | Open | P3 Low CX | RyanWu@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Component/Equipment Failure | Commissioning | Electrical â€“ LV | system | Mechanical Busduct System |  |  |  | To replace torn off tags for: Lvl 2 joint 20 Lvl 5 joint 14 Lvl 8 joint 64 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636226&prj=618&rqi=A230A0mOYlOciUp50Du1BxqeTk | https://equinix.facilitygrid.co.uk/x/project/618/system/14864
GI-491 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CX2 - White glove : 1USP_C1R1_2_1 1USP_C1R1_2_2 1USP_C2R1_3_1 1USP_C2R1_3_2 1USP_C2R1_4_1 1USP_C2R1_4_2 1USP_C1R1_2_3 1USP_C2R1_3_4 1USP_C2R1_4_4 1RPP_C1R1_2_1_3 1RPP_C1R1_2_1_4 1RPP_C2R1_3_2_3 1RPP_C2R1_3_2_4 1RPP_C2R1_4_2_3 1RPP_C2R1_4_2_4 1RPP_C1R1_2_3_3 1RPP_C1R1_2_3_4 1RPP_C2R1_3_4_3 1RPP_C2R1_3_4_4 1RPP_C2R1_4_4_3 1RPP_C2R1_4_4_4 1. USP Name plate to which RPP spare need to indicate on the panel 2. Engie needs to update USP outgoing circuit 3. Overall schematic needs to be made available in the room and to be attached to a visible place Assigned to woh hup / Engie / SMBE - Please update with responses here | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636305&prj=618&rqi=irHZaPPTjpXlEZMIIggX5lWsOl
GT1DCOS-19-006 | SG06-1 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-31 04:00:00.000 +0400 | General Contractor - BMS | L3 | General Design Issue | Design | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | Observed that only one CT is running to support two CWPs during string rotation. Kindly confirm with the design consultant/EoR the design intent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636034&prj=618&rqi=7dR4b3thPizTzGTwty8x5igr9r
GT1DCOS-19-007 | SG06-1 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-31 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | Observed that CWP 4 starts running before CT 4 FCV-01 valve opens during the stage-up sequence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636036&prj=618&rqi=WdjXLnl8hewq8BqbEL0iCiNMO8
GT1DCOS-17-003 | SG06-1 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-31 04:00:00.000 +0400 | General Contractor - BMS | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1CPOS_RIO_05 | DCOS - Control Panels |  |  | Requires fine-tuning of the CHWP PID settings, bypass valve opening, and timer. When both CHWP are running, the system repeatedly triggers a CHW low-flow alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636035&prj=618&rqi=UDBBsM9fG929szqgVU9DWsOYCE
GT1DCOS-16-001 | SG06-1 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-31 04:00:00.000 +0400 | General Contractor - BMS | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1CPOS_RIO_04 | DCOS - Control Panels |  |  | Observed that when the operating string fails, the next available string is automatically called to run. However, the failed string is commanded to stop immediately, and the pumps will stop after a 60-second time delay based on the current timer settings. This occurs before the next available string has successfully started and achieved a proven run status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636037&prj=618&rqi=D92DS5dGvYMg0oegSIL8KA540s
GI-484 | SG06-1 | APAC | Ready for Verification | P2 Medium CX | RyanWu@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not correct | Commissioning | Electrical â€“ LV | system | Mechanical Busduct System |  |  |  | To move the unistruts and obstructions away from the joints of the mechanical busducts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635241&prj=618&rqi=iYjZEVWigDEatu6RK6ZW91Bs4r | https://equinix.facilitygrid.co.uk/x/project/618/system/14864
GI-483 | SG06-1 | APAC | Ready for Verification | P2 Medium CX | RyanWu@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not correct | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | To move unistruts and other obstructions away from the joints of the IT busducts as shown in the screenshots | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635236&prj=618&rqi=LlPJaGmzOyVV3bWB0Lb7Kh1TsA | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GT1DCOS-19-005 | SG06-1 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor - BMS | L3 | General Design Issue | Design | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | As per SoO, initial chiller start sequence, one cooling tower will run . Observed that chiller string still able to stage in although after sequentially reset the faulted latching alarms and attempt to start the towers one at a time for three times maximum and "insufficient devices available to run" activated. Kindly confirm with the design consultant/EoR the design intent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635218&prj=618&rqi=6uAoKekIOlhv3O6cIFuT4VRriL
GT1DCOS-17-002 | SG06-1 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning | Controls | equipment | 1CPOS_RIO_05 | DCOS - Control Panels |  |  | Observed that during string rotation, while CH was still in VSD precharge, CPOS considered String 2 as already run and stopped String 4. Kindly check with the JCI chiller team whether the system can take the chiller run status as the run point signal to CPOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635216&prj=618&rqi=rBzUjS8tADLJdrt7KcPKDxuWYY
GI-471 | SG06-1 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | PACV 1 when doing the trip and flow test of PACV 1 the pipe was found to a loud sound and have excessive vibration that lead to bits and pieces of the wall and ceiling came out and sprinkler pipe leak . Please find out whatâ€™s the cause and rectify 31/08/2026(Updated): Please note that a similar incident happened on PACV 11 (level4) trip test on the 31/08/2026 , where a loud sound was heard at the corridor here the trip test is occurring | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634303&prj=618&rqi=YnHFoD5sOsthUopFzyiHxYExMm
GI-467 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-08-18 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Cx3: 1. Flood light outside e- wall 3 A is found to be yellowish , to find out is it the same model of light that is installed or its a different kind that is installed 2. Chilled water riser (LC) Light is not installed yet 3. It riser 3A-1 Light is not installed yet / might have been removed from the vendor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634118&prj=618&rqi=g2UJg8tr8DDle3UkEZXoq8wDBo
GI-462 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-08-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | To update submittal 6211 lv schematic diagram z swing, to include secondary circuit to 1mdsb_z2 source 2 from 1mdsb_r1_2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633910&prj=618&rqi=UFEWDc4P7ME8HvLkjOjQw9Rvti
GI-459 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-08-14 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not correct | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | BUSDT cx2A observation 1.GA dwg to update, sld to upload in FG(incorrect dwg indicating the placement of the components) 2. earth bond to install at panel door 3. to install labels on equipment as per approved maximo list 4. Missing otdr passing critieria in mos and testing wavelength. (vendor mentioned is 850nm and less than 3db/km) 5. To install labels the incoming source to the thermal monitoring panel on the power socket 6. Unable to find patching panel in equipment layout | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633586&prj=618&rqi=dB2iLqQREHDHbkcodrs58ggBfG | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-458 | SG06-1 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Observed signs of possible water/moisture ingress and including discoloration/rust-like staining within the loadbank enclosure. Engie to investigate the condition of the enclosure seals, joints, cable glands and other potential entry points, and implement the necessary corrective action to prevent recurrence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633389&prj=618&rqi=tFPOhpXjWwioQclyR43n0Ui2Rf
GI-455 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | CX3: SAP Test N2L06D037 N2L06D032 - Labels need to be updated N2L05D07 - Label need to check N2L05D073 - RP / SAP panel update N5L01D077 - Needs to be updated N2L02D062 - Label is wrong and needs to be updated N2L02D064 - Label is wrong and needs to be updated N5L02D065 - Location needs to update N5L02D056 - Location needs to update | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633139&prj=618&rqi=ActB5QvcXUeZpjO69oOLOuf3ma
GT1DCOS-23-004 | SG06-1 | APAC | Closed | P2 Medium CX | hemendrrajeganathan@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning | Controls | equipment | 2CPOS_RIO_04 | DCOS - Control Panels |  |  | Cx3 2CPOS_RIO_04 Temperature readings during sensor verification and current status are out of range. To check the condition of temperature sensors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633145&prj=618&rqi=teII2EDSSUEHmE5QSvLugK3KFt
GT1DCOS-18-001 | SG06-1 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS | Controls | equipment | 1CPOS_RIO_06 | DCOS - Control Panels |  |  | Observed that FCV01 will automatically open when Cooling tower and Valve Control Panel are in Auto mode, while the VFD is manually commanded to run via DCOS. Kindly confirm with the EoR the intended design philosophy and sequence of operation during manual override. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632958&prj=618&rqi=JOlm0f1i40Zr7iFTazNmpaCCRm
GT1DCOS-23-001 | SG06-1 | APAC | Open | P3 Low DCOS | siakhongneogh@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS | Controls | equipment | 2CPOS_RIO_04 | DCOS - Control Panels |  |  | Vendor to cross-check all alarm names and alarm descriptions to ensure they accurately reflect the corresponding alarms. Apply to all strings. Including Bypass valves and Temperature/DP/ flow sensors in Chiller Plant Room 2 (South), all indicated wrong location in faceplate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632971&prj=618&rqi=VUGBOMscuVVyW1XvSHtoziFZBb
GT1DCOS-23-003 | SG06-1 | APAC | Open | P3 Low CX | siakhongneogh@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS | Controls | equipment | 2CPOS_RIO_04 | DCOS - Control Panels |  |  | Observed that was a command of 30% speed command during DCOS manually override to command run. Vendor to investigate and cross check the logic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632973&prj=618&rqi=5yyabCsYmOWHVFDSPZ21TeeH9g
GT1DCOS-23-002 | SG06-1 | APAC | Open | P3 Low CX | siakhongneogh@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS | Controls | equipment | 2CPOS_RIO_04 | DCOS - Control Panels |  |  | Vendor to cross-check and ensure all alarm shall reflect corresponding alarms correctly on the CPOS HMI. Apply to all strings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632972&prj=618&rqi=pazPh7DuW4ICUUy1zXXMIdWzlR
GT1DCOS-26-001 | SG06-1 | APAC | Closed | P3 Low CX | hemendrrajeganathan@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning | Controls | equipment | 2CPOS_RIO_05 | DCOS - Control Panels |  |  | Cx3 2CPOS_RIO_05 TT-14 sensor is out of tolerance limit (more than 12 deg difference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632399&prj=618&rqi=hUjK0FCq2PjR2MAi0SXhdR3iRP
GT1DCOS-17-001 | SG06-1 | APAC | Closed | P3 Low CX | hemendrrajeganathan@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning | Controls | equipment | 1CPOS_RIO_05 | DCOS - Control Panels |  |  | Cx3 1CPOS_RIO_05 TT-17 sensor is out of tolerance limit (more than 12 deg difference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632401&prj=618&rqi=2X1w9XvOOVg2w8tAysdWuVUGVg
GI-442 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-08-04 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | Cx3: Level 9 : Temperature Sensor HMI and DCOS / Sensor While performing the sensor verifications of the temperature sensors , the following below was observed : Sensor 1 reading is out by 1 degrees Celsius Sensor 8 Reading is out by 0.57degrees Celsius Sensor 15 reading is out by 0.5 Degrees Celsius Sensor 14 reading is out by 0.6 Degrees Celsius Sensor 7 reading is out by 3.5 Degrees Celsius The allowed tolerance is +/- 0.5 degrees Celsius Please refer to the table attached to this Issue for your reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632158&prj=618&rqi=7dUxJDIfcolFDcC5hk1b2fq7jL
GI-430 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Cx3: JF with DCOS 1JF_Z_1 DCOS 1JF_Z_2 DCOS 1. 1JF_Z_2 DCOS - Stop button is damaged , as its slightly chipped and need to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631462&prj=618&rqi=AgtSV6prCt7D5ADfALYfqfuziD
GI-431 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Cx3: 1JF_Z_2 DCOS, 1JF_Z_1 DCOS 1. Graphics showed that for JF there is no name on the graphics that would state what is the name of the jet fan , only when it is being hovered above when / where the name of the jet fan can be seen 2. Observed that there is no status that tells if the JF is in high or low speed on the graphics 3. When fire alarm is triggered , the Jet Fan unit would stop and not automatically resume after the fire alarm is reset (Remains off) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631463&prj=618&rqi=G2fYDXpd2XukrzGI9dPkX8lA77
GI-422 | SG06-1 | APAC | Open | P3 Low CX | jessyong@commtechasia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | To install labels as per approved maximo list and/or sld. Observed at 1RMU_A, Q01 and Q02 installed labels do not align with approved mv sld. ABB to rectify and attach photos of all RMU and BTU showing correct labels installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631119&prj=618&rqi=7rvwQXlpfG599sTIJBf9TABNcY
GI-424 | SG06-1 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | To update ATS settings for 3914 and 3904 voltage imbalance only able to set minimum at 0.02s instead of 0s. To resubmit the revise settings to EOR for review and approval. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631122&prj=618&rqi=VE0S9CUt7RpVJsVmwSMJznBeHa
GI-423 | SG06-1 | APAC | Ready for Verification | P2 Medium CX | jessyong@commtechasia.com | 2026-07-29 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | To update mech ATS/socomec settings and SOO and submit to EOR for review and approval, unable to set as per approved settings during cx3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631121&prj=618&rqi=rt1pmYMTHj3JiQUKwhlefpOi4H
GI-425 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-07-28 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Cx3: Jet Fan (JF) When the JF is started in high speed mode , the JF would jerk and move in violent manner | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631142&prj=618&rqi=Olw42ut6vcncbPYR5nXtzA5Cfh
GT1DCOS-19-003 | SG06-1 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | The CHWP and CWP cannot be ramped up or down from the CPOS HMI. To investigate and enable this functionality. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630639&prj=618&rqi=orXCNv6KSb3XXnUOOgX9lI0Rdi
GT1DCOS-19-004 | SG06-1 | APAC | Closed | P3 Low DCOS | siakhongneogh@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | General Contractor - BMS | L3 | Labelling | Commissioning | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | On the CH DCOS faceplate, the refrigerant temperature displayed refers to the saturation temperature. To confirm that this is correctly labeled or revise the display if necessary to avoid misinterpretation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630640&prj=618&rqi=sUx7fPIiyGMOgZVf2ct63nhbfl
GI-420 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Cx3: All Battery Container Battery container FCU Supply / return pressure gauge needs to be changed to a bigger capacity pressure gauge as the current one is out of range and could not take any readings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630488&prj=618&rqi=xegO1IUa9BUUwE6KK9c7z8XHt3
GI-413 | SG06-1 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: To upload the compile picture file for hard to access joint for level 2 for MECH, IT and LB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630048&prj=618&rqi=IXOiAXBDhYJTIOrrYrN4zztZfy | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-417 | SG06-1 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: To upload the compile picture file for hard to access joint for level 9 for MECH, IT and LB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630052&prj=618&rqi=fOkxcMCYhZMIi05MtUrK9JsKUk | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
YT1DCOS-18-001 | SG06-1 | APAC | Open | P3 Low CX | hemendrrajeganathan@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - BMS | L2B | Documentation not issued/ Required | Commissioning | Controls | equipment | 1CPOS_RIO_06 | DCOS - Control Panels |  |  | Cx2B 1CPOS_RIO_06 To revise schematic and panel drawing and upload into checklist once completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630058&prj=618&rqi=OCJGTrw5b3IUg6Q0kq2dqEWXZX
GT1DCOS-19-002 | SG06-1 | APAC | Open | P3 Low CX | siakhongneogh@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | The CPOS HMI and DCOS are unable to identify or indicate which system currently has manual control overriden. There is no clear status or indication to distinguish whether the equipment is in CPOS Manual Mode or DCOS Manual Mode, resulting in ambiguity over the active control source. Attached D2SD screenshot was during Local panel in Auto mode, CPOS HMI in Local mode and DCOS in auto mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630046&prj=618&rqi=PnKTeXl7RQMWJQCP3GenbA6Zb8
RT1SEC-2-005 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L2A | Installation not correct | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx2a: Level 9 : DR216: FIRE FIGHTING LOBBY 1 BIOMETRIC SCANNER IS DISLODGED | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630112&prj=618&rqi=rJXXG9Z9lX6LpEtPgLQLyJJm5v | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-415 | SG06-1 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: To upload the compile picture file for hard to access joint for level 7 for MECH, IT and LB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630050&prj=618&rqi=yUpGFCrL49JEwkZFr72S0ichz8 | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GT1DCOS-19-001 | SG06-1 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | DCOS is unable to execute manual ramp-up and ramp-down commands for the CWP and CHWP because the control is being overridden/ affected by CPOS although HMI in Remote mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630045&prj=618&rqi=pWOEjgkYzwa1JqEEdapVuw6IB5
GI-416 | SG06-1 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: To upload the compile picture file for hard to access joint for level 8 for MECH, IT and LB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630051&prj=618&rqi=Svn1NWUPQhA1MLPrqG1mGyiZqb | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-414 | SG06-1 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: To upload the compile picture file for hard to access joint for level 5 for MECH, IT and LB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630049&prj=618&rqi=OETVBkSeiMXkHXAx0W8OMWYpKK | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-410 | SG06-1 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-18 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: Load Bank busduct During inspection it was found that some busduct is unaligned and the jointing was block but Unistrut support. To rectify and upload proof of rectification Unaligned joints - LB-L5-J-028, LB-L5-J-027, LB-L5-J-026, LB-L5-J-020, LB-L5-J-019. Blocked by Unistrut - LB-L5-J-018, LB-L5-J-007, LB-L5-J-003 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629894&prj=618&rqi=gvYLjTqUu3DMDOQRT0hB5QJuOk | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-409 | SG06-1 | APAC | Closed | P2 Medium CX | alifasyraf@commtechasia.com | 2026-07-18 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: Load bank busduct At Level 9 the joints of LB-L9-008 was not installed to rectify and upload the proof of works | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629893&prj=618&rqi=2IYu1MwrXdyQyCB5iACmfzlnxv | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-403 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | CxL2A 1FCU_M1_07 1FCU_M1_08 - FCU is missing the equipment label that is supposed to be affixed onto the FCU - FCU Control panel is also missing an equipment label on top of its run stop trip light - Document pocket needs to be attached to the FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629299&prj=618&rqi=jpw3SxJV5I29w7FXewWIiQdlFQ
GI-406 | SG06-1 | APAC | Closed | P3 Low CX | RyanWu@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | To update routing of bus ductors on drawing where necessary, as there are changes to the locations to some of the panels where the ductors are supposed to go | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629350&prj=618&rqi=3aZQP6TjvNFgXFgtje8pvs1wLN | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-407 | SG06-1 | APAC | Open | P3 Low CX | jessyong@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | To update the hv power study for the curve characteristic for RMU Z, C, A, R1, M1 and D hi set settings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629351&prj=618&rqi=QVRDgZR337UMDCOHOa7R9I3km6
GI-401 | SG06-1 | APAC | Closed | P2 Medium CX | RyanWu@commtechasia.com | 2026-07-14 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Observed misalignment in the IT busduct installed in the STS RM D, from joint IT-L5-J-72 to IT-L5-J-77. Engie to rectify and call for reinspection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629134&prj=618&rqi=AgerKxUXGRnHWsnrAeQKYHPzXk | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-400 | SG06-1 | APAC | Closed | P2 Medium CX | RyanWu@commtechasia.com | 2026-07-14 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Observed misalignment in the IT busduct installed in sts room 2A from joint IT-L2-J008 to J009. Engie to rectify and recall for reinspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629133&prj=618&rqi=XpgXRCUy0bU8dQrUotdZ7djxBS | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-396 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-11 04:00:00.000 +0400 | Electronic Safety and Security Contractor |  | Labelling | Commissioning | Security | system | Security - CCTV System |  |  |  | C2A: Level 5 Security System Labels wrong for some security camera in E- wall room A side need to be rectified Some camera alignment appears to be slanted and needs to be rectified | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628769&prj=618&rqi=KGG9plnXqIejLXC1JdeaMJI8yN | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-389 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2a / Cx2b: 1JF_Z_1 1JF_Z_2 1. Document pocket not affixed to the panel 2. 1JF_Z_1 button gasket need to be adjusted / fixed 3. 1JF_Z2 stop button is slightly damaged and need to be fixed 4. Please confirm on site , the OL Relay model is stated as LRD07 , while the other OL Relay model is LRD12 , please also confirm the overload setting 5. DCOS cable is not terminated for 1JF_Z_1,, 1JF_Z_26 6. Please update the drawing where there are components installed in the panel , but is not reflected in the drawing : - Fuse F7/ F8 is missing in drawing - Power supply converter is missing from the drawing -Relay position is swapped in the drawing 7. JF Terminal block for thermostat has two more blocks cable in it , drawing to be updated (Terminal Block 09/10) This defect is applicable to all other jet fans at other levels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628457&prj=618&rqi=hE2zVHp6TX08sQp8KIKtHRczx3
GI-388 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2a/Cx2b: 1JF D 1 Drawing to be updated Trunking to be sealed Document pocket to be included in panel 1JF D 2 Drawing to be updated Document pocket to be included in panel 1. Please confirm on site , the OL Relay model is stated as LRD07 , while the other OL Relay model is LRD12 , please also confirm the overload setting 2. DCOS cable is not terminated 3. Please update the drawing where there are components installed in the panel , but is not reflected in the drawing : - Fuse F7/ F8 is missing in drawing - Power supply converter is missing from the drawing -Relay position is swapped in the drawing 4. JF Terminal block for thermostat has two more blocks cable in it , drawing to be updated (Terminal Block 09/10) This defect is applicable to all other jet fans at other levels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628238&prj=618&rqi=4K2qJaIM5JLMWL6tQpWpZTwtuG
GI-384 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CX3 : Fire Level 7 N12L03D015 and N12L04D012 RP mimic LED wrong Mimic drawing to be updated, riser 7A medium voltage is L7-Z87 Mimic drawing need to change the zone name for the following zones: L7-Z44 (change to 5A) L7-Z45 (change to 4A) L7-Z46 (change to 3A) Trouble detectors: N12L04D016 N12L03D021 N12L04D050 N12L03D018 N12L04D015 label on detector wrong N12L03D040 image very dark, unable to check label N12L04D045 changed to exposed for panels and fire PC N12L03D044 change label sticker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627950&prj=618&rqi=KYzm2ayNKuyH4YmMY10IDcL55Q
GI-386 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3: Fireman intercom Testing : L8: Genset B / E - Wall B Handset call quality was found not be to clear L8 Cool Spine 8-2 / Level 7 Genset B there is significant feedback occurring while using having the call at the same time Notes: 1. When having 1 way communication , the one way light does not light up and appears in 2 way 2. Sometimes when having a 3 way communication , the 3 way communication light does not light up Hand Sets with physical issues: 1.L9-E-WALL 9B HANDSET Missing Glass 2.L9-FFL 9B HANDSET Missing Glass / this handset is also missing in the drawing 3.L9- Goods lift HANDSET Missing Glass - label to be updated in full - Goods Lift Lobby 4.L8- Goods lift should be rename as goods lift lobby 5.L7- Goods lift should be rename as goods lift lobby 6.L7-Cool spine 7-2 - Break glass needs to be changed 7.L6- Goods lift should be rename as goods lift lobby 8.L6-FFL 8B HANDSET Missing Glass 9.L5-STS 5B HANDSET Missing Glass 10.L8 STS 6A HANDSET Missing Glass 11.L6 Cool spine 6-2 HANDSET Broken Glass 12.L1 Security Room HANDSET Missing Glass 13.L6 - E- Wall 6A HANDSET Broken Glass 14.L1 Battery Container 1A HANDSET Missing Glass 15.L5- FFL 5A HANDSET Missing Glass 16.L1 SPK PUMP Room - HANDSET Break glass needs to be changed - label spelt wrongly 17.L5- STS 5A - HANDSET Missing Glass 18.L3- Goods lift should be rename as goods lift lobby 19.L5- cool spine 5-1 - HANDSET Missing Glass 20.L1- Good Lift - HANDSET Missing Glass / should be rename as goods lift lobby 21.L4- cool spine 5-1 - HANDSET Missing Glass 22.L6 FFL 6a - Handset missing glass 23.L5- E Wall 5A - HANDSET Missing Glass Suggest that L1-L8 goods lift lobby the label to be changed to full Goods lift Lobby Label Handset issues : 24.L6-Cool spine 5-1 Handset - LED light is not working 25.L4-FFL Handset - LED light is not working | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628051&prj=618&rqi=sos8QnHQcifwb0tkzrh1UkRMAu
GI-385 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | L8 CX3 SAP : 1. Drawing needs to be updated on the location of the bell / strobes as they are missing 2. Handicap toilet missing strobe light in the drawings 3. Genset missing strobe light in the drawings 4. Positions of some strobe lights need to be Changed on the drawings L8 Data Hall 1 1. Detector found wrapped with plastic : N15L01DD014 2. Mimic panel diagram / zone of the DH8-1 and cool spine needs to be updated as those two separate zones have been merged into one zone L8 Data hall 2 : Detector Sticker label was found and need to change: N15L04D007 N15L03D014 N15L04D020 N15L03D027 N15L04D033 N15L03D034 N15L04D014 N15L03D008 N15L04D021 N15L03D028 N15L04D034 N15L03D039 Mimic panel data hall number need to change. Should be DATAHALL 14 (DH8-1) and DATAHALL 15 (DH8-2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628050&prj=618&rqi=w4KJDvzD2D1uCtwVAiD0QMIYn4
GI-382 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CX3: Level 7 Smoke Detector Testing Strobe light location on drawing to be updated. (Markup on drawing) N12L04D024 and N12L04D034 wrong location name & zone on panels and fire PC N12L04D035 panels, fire PC and mimic drawing need to change to 5B Mimic drawing need to change the zone name for L7-Z70 (should be 5B) and L7-Z71 (should be 3B) N12L03D010 change new sticker label (cause the current sticker label roll up a bit) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627748&prj=618&rqi=Qe834uXueTr7SUqQtnCd0r58MF
GI-383 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | 1SF A 3 - drawing to be replaced with lew approved drawing 1 SF A 6 - drawing to be replaced with lew approved drawing 1 SF A 5 - drawing to be replaced with lew approved drawing 1SF A 4 - drawing to be replaced with lew approved drawing 1SF C 3 - sticker to be paste on the fan unit 1SF Z 25 - fan no label All SF to have document pocket affixed to the panel All SF drawings ducting should have labels attached to them | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627949&prj=618&rqi=NQ3NoAfu5mJMppcV71uJuemGPF
GI-381 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx3: Level 8 NER Room 1FCU_A_22 1FCU_M1_19 - No label installed on the thermostat - thermostat temperature is out by 1 degrees celcius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627591&prj=618&rqi=KdVXpgqrUYiAF9axZYPB4F4zyU
GI-377 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2a / Cx2B : 1FCU M1 07 1FCU M1 08 1) drawing to be updated 2) trunking to be sealed 3) redundancy cable is not connected 4) Thermostat to be installed and labelled 5) Document pocket to be affixed to the panel 6)Labels to be affixed to the FCU 7) Labels is missing on the ducting | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627429&prj=618&rqi=yyrpPdmQo3PzBsIG0kXz2HDKya
GI-380 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3: Level 6 fire protection 1. extra call point in the system N10L05M003 2. Call point N10L04M008 label need to change 3.DH6-1 HR call point RP zone number wrong Level 7 fire protection Strobe light need to update on drawing (placement wrong/missing) N13L01D001 label need to change N13L01D025 label need to change N13L01D021 and N13L01D015 fire PC and panels need to change to exposed Drawing need to update: N13L01D046 and N13L02D046 swap location N13L01D044 and N13L02D044 swap location Mimic panel drawing need to update to latest version N13L01D034 zone number wrong | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627439&prj=618&rqi=C6THUrvhHzpvWx170eqZuVeeWr
GI-378 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2a/ 2B: 1SF Z1 30 1SF Z1 31 nameplate to be change to the correct name drawing to be updated isolator to be installed phase label to be installed trunking to be sealed excess cable to be terminated dcos cable to be terminated Labels to be attached to the equipment 1SF Z1 29 1SF Z1 28 nameplate to be change to the correct name incoming and outgoing cable to be terminated to isolator drawing to be updated dcos cable to be terminated trunking to be sealed excess cable to be terminated Labels to be attached to the equipment 1JF A 1 1JF A 2 drawing to be updated trunking to be sealed trunking earth missing For 1JF A 1, fuse is rusty dcos cable not yet terminated Labels to be attached to the equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627436&prj=618&rqi=j74UpSW8GsY8PiILCYHOmLoPZX
GI-375 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Level 6 Cx3: Mimic drawing need to change the E-WALL no.A and E-WALL no.B to the same as the drawing. N10L03D011 detectorâ€™s label need to change N10L04D019 has issue - detector failed to trigger | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627166&prj=618&rqi=wd47dt9P1Y96fwrId0TupzTmYo
GI-371 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Observed the lamp test at the gen annunciator, does not light up the low coolant level alarm. Rehlko to rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626882&prj=618&rqi=yv9ptWBpuU2dgPQpsnlUsRt5Gh
GI-372 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A/Cx2B 1FCU Z 08 drawing to be updated thermostat label missing 1FCU Z 09 drawing to be updated thermostat label missing trunking earth missing ducting label missing 1 JF M1 1 missing incoming cables (engie side) missing isolator label drawing to be updated trunking to be sealed trunking earth missing Missing Labels on the JF 1 JF M1 2 missing incoming cables (engie side) missing isolator label drawing to be updated trunking to be sealed trunking earth missing all 6 amps fuse rusty Missing labels on the JF | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626928&prj=618&rqi=AVizE7rTQqcRyKKup2i6pVbuZm
GI-369 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | FCU: Cx3 CSR Room A: 1FCU_Z_22 1FCU_Z_23 1. Damper opening and feed back of the actuator needs to be adjusted / fined tuned so that the damper opening and feed back would be correct 2. FCU : Type 1 FCU / it has damper opening and closing controls , which is not monitored on the DCOS side , Access tech and DCOS to check why is that so , and only local trip can be seen 3. There is No SOO mentioning of what should be the behavior of the damper in the SOO 4. When the damper fails ( Fail To open ) the alarm comes on and the fan stops running 5. when the unit is trip the fan would stop running and then the damper would remain open , which deviates from the check list which says when the unit trip the damper should close and the PICV is closed (manual mode) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626724&prj=618&rqi=Fd6HTWWQZZoSTzRHU2dDcTbeFr
GI-370 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A/Cx2B: 1SF M1 3 : drawing to be updated trunking to be sealed incoming cable missing incoming phase label missing isolator missing phase label missing from outgoing cable Cx3: 1FCU Z 22 and 1FCU Z 23 drawing to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626733&prj=618&rqi=LVILhOJZ9oA9TIChkrM6Bx2T7Q
RT1DCOS-1-002 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment type |  | DCOS - Control Panels |  |  | Cx2B: 1DCOS CP 01 cable not terminated due to a module needs replacement 1DCOS CP 02 Drawing holder did not stick on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626929&prj=618&rqi=Ig8Fs3fne9Utb2vXZLeNcZYiXX
GI-365 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3 : Level 6 Detector N10L04D008 pic only able to see the 8 as they were unable to take clear photo but the panels etc shows correct number Mimic drawing need to update (including panel): 1. L6-Z14 missing on drawing (data hall lobby 6A) 2. Both data hall HR zone labels are wrong N11L05D010 mimic panel shows 2 LED (should only be 1) N11L05D004 and N11L06D004 detectors label unclear N10L04D010 label on detector missing RP mimic panel canâ€™t see the word L6-Z54 on it Drawing needs to be updated: Data hall 1 HR location should be 6A-4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626533&prj=618&rqi=nHvEvP2NMkAqLp9nQ9a7e9Z5rD
GI-366 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Cx3 : 1FCU_C_10 1) when normalizing thermostat, PICV will close then open. 2) During auto mode, DCOS summary alarm and supply fan cmd mismatched lights up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626537&prj=618&rqi=8zY37v37elHNpVGb8rwb2CfAG5
RT1DCOS-13-002 | SG06-1 | APAC | Open | P3 Low CX | Weihaolim@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1CPOS_RIO_01 | DCOS - Control Panels |  |  | During the Cx2A inspection, the following observations were noted (apply to all PCP and RIO panels): To update network architecture and earthing connection diagram, connection on site don't tally with drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626336&prj=618&rqi=kWXMP8RYe4sJ9h0MeLsJJtOUAR
GI-362 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | FCU Cx3: 1FCU_Z_27 1FCU_Z_06 1FCU_M1_54 1FCU_M1_50 1FCU_M1_49 Observations 1FCU_M1_50: - Unit keep tripping spontaneously through the overload relay - need to check if the overload settings are too sensitive - That only happened after the dirty filter alarm is triggered manually at the unit - Setting is 250 - DPS - Find out why the PICV Valve feedback takes some time to come after the actual PIVC Valve is closed at the panel (Measured at feedback) - Unable to access unit to attach TA scope to check flow - When thermostat of the FCU fails ,the PICV is supposed to remain at last position / however what happened was the valve closed instead of remaining fully opened | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626378&prj=618&rqi=GskqrlNCpb5dkL4bn4iStvW9zD
GI-359 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3: Level 6 Fire protection Drawing needs to be updated. Such as strobe light location, smoke detectors location and labelling. Smoke detectors (physical) needs to change the label N11L01D033 N11L01D016 Data hall number needs to be updated on mimic drawing, fire PC and all the panels. From DATA HALL 6 (wrong) to DATA HALL 10 (correct) From DATA HALL 7 (wrong) to DATA HALL 11 (correct) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626279&prj=618&rqi=SdDTiAjayGS40rYgGcJ4eyA3ub
GI-361 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | FCU Cx3: 1FCU_M1_33 Find out why the PICV Valve feedback takes some time to come after the actual PIVC Valve is closed at the panel (Measured at feedback) - Unable to access unit to attach TA scope to check flow - When thermostat of the FCU fails ,the PICV is supposed to remain at last position / however what happened was the valve closed instead of remaining fully opened | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626374&prj=618&rqi=tn3yxliSPL6Zn4e10uQqWrkPg5
GI-358 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | CX3: Find out why the PICV Valve feedback takes some time to come after the actual PIVC Valve is closed at the panel (Measured at feedback) - Unable to access unit to attach TA scope to check flow - When thermostat of the FCU fails ,the PICV is supposed to remain at last position / however what happened was the valve closed instead of remaining fully opened Applicable to levels FCU . Level 1: 1FCU_Z_06 - PICV valve operation not aligned as per SoO 1FCU_M1_54 1. Moxa switch/ BMS card issue, unable to comms DCOS, PICV valve operation not aligned as per SoO, MOXA card needs to be replaced / Fixed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626277&prj=618&rqi=yRt97Xa2XKPE5xbxA5ZBPpskgf
GI-353 | SG06-1 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2 A/ B: General Defects : 1SF Z 18, 1SF Z 5, 1EF M1 3 , 1EF M1 2 , 1FCU A 05 , 1FCU A 06 1. Document pocket to be affixed on all FCU / SF 2. Ducting needs to be labelled 3. Drawing needs to be updated as per components installed on the panel 4. Trunking to be sealed properly 1FCU A 06 (incoming earth not terminated) Condensate tray and label outstanding on fcu need to be installed - P2 issue 1. Document pocket to be affixed on all FCU / SF 2. Ducting needs to be labelled 3. Drawing needs to be updated as per components installed on the panel 4. Trunking to be sealed properly 1SF A 12 1. Document pocket to be affixed on all FCU / SF 2. Ducting needs to be labelled 3. Drawing needs to be updated as per components installed on the panel 4. Trunking to be sealed properly 5. incoming cable yet to be terminated - P2 issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625869&prj=618&rqi=6DKFTTs6SzE3Vh6MePao7XUjzK
GI-349 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3: Fire Level 5 Point to Point testing : Mimic drawing need to update on locations such as: 1. Data Hall lobby 2. â L5-Z16 need to update to L5-Z18 3. â corridor 5A zone update to L5-Z25 Corridor 5A on mimic panel (physical) need to update to latest drawing then test the zoning LED again For detector N8L03D031, mimic LED light up at wrong place | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625682&prj=618&rqi=9zbVxam0IiqMdMm9QEynEah0NP
GI-350 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A : 1FCU_A_04 1FCU_Z_07 1SF_A_04 1. thermostat to be installed 2. Document pocket to be affixed to the panel 3. trunking to be closed up and sealed 4. 2A fused to be replaced (rusty) 5. Ducting to be labelled with stickers stuck to it 6. Drawing to be updated as per components installed on site 1SF_A_04: 1. trunking to be sealed 2. Ducting to be labelled with stickers stuck to it 3.. Drawing to be updated as per components installed on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625683&prj=618&rqi=H957s0NHNXHk1Jhmgfs6bEDVVc
GI-351 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | CX3: 1FCU_C_13 - Sponteneous tripping of the unit for no apparent cause , and it happened 3 times - Find out why the PICV Valve feedback takes some time to come after the actual PIVC Valve is closed at the panel (Measured at feedback) - Unable to access unit to attach TA scope to check flow - When thermostat of the FCU fails ,the PICV is supposed to remain at last position / however what happened was the valve closed instead of remaining fully opened 1FCU_M1_35 Find out why the PICV Valve feedback takes some time to come after the actual PIVC Valve is closed at the panel (Measured at feedback) - Unable to access unit to attach TA scope to check flow - When thermostat of the FCU fails ,the PICV is supposed to remain at last position / however what happened was the valve closed instead of remaining fully opened 1FCU_C_12 Find out why the PICV Valve feedback takes some time to come after the actual PIVC Valve is closed at the panel (Measured at feedback) - Unable to access unit to attach TA scope to check flow - When thermostat of the FCU fails ,the PICV is supposed to remain at last position / however what happened was the valve closed instead of remaining fully opened - Find out why after i did the thermostat failure for the unit , this unit is an AHU / but is classified as an FCU , and it has two EC fans , after failure of the thermostat and its reinstatement , only one fan is found to be working while the other fan remained off , it was confirmed to be off after measuring the fan feedback | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625867&prj=618&rqi=IqdBm4AaorX3cN5QR6e5OQqShy
GI-348 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Cx3: Fire Pump Panel 1. Fire pump panel date and time is not set yet on the HMI 2. Fire Pump panel please check why is there a battery mode on the pump panel 3. Please check if data such as voltage / ampere / trending records can be extracted / down loaded from the pump 4. record / wrote firm ware version up here | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625554&prj=618&rqi=U22AFSHtAeT3xG2RH6bRnKvibr
GI-343 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A 1EF_Z_8 1. Document pocket need to be affixed to the EF 2. Labels need to be attached to the EF / Ducting 3. Grilles need to be installed in its correct location 1FCU_Z_46 1FCU_Z_58 1FCU_Z_59 1FCU_C_07 1FCU_D_07 1FCU_C_03 1FCU_D_03 1FCU_Z_47 1) drawing to be updated due to incorrect position/wire label. 2) thermostat missing for all FCU/ to be installed 3) trunking to be sealed off for act and dcos (light can pass through) 4) wires to be terminated. 5) Document pocket to be installed for the FCU 6) Labels to be attached onto the drain pan | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625336&prj=618&rqi=sJLseX21A9N8bavaVh2R9SYBkC
GI-344 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3: LEVEL 5 : Label on detector is wrong: N8L04D040 N8L03D040 N8L04D031 Please update the detector and attach photos here Drawing label wrong N11L01D047 (on drawing) change to N9L01D047 N11L02D049 (on drawing) change to N9L02D049 N8L04D040 (on drawing) change to N9L04D040 N8L03D040 (on drawing) change to N9L03D040 Please update drawing and attach here Mimic Panel issues N8L04D032 mimic LED did not light up when triggered | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625338&prj=618&rqi=bStHSOf3ohuHgPBMl77B16W54J
RT1SEC-2-004 | SG06-1 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L2A | Documentation not issued/ Required | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx2A: L7 Card Access Panel ACP-13 and ACP-14 L8 Card Access Panel ACP-15 and ACP-16 L4 Card Access Panel ACP-07 and ACP-08 L6 Card Access Panel ACP-11 and ACP-12 1. PSU needs to be labeled to show where /what devices it is connected to 2. Battery needs to be labelled (Installation / Start using date) 3. Earth cable within the PSU units need to be attached / installed 4. Panel earth needs to be installed on the door 5. Internal wiring needs to be terminated with proper labelling 6. Applicable to all ACP units 7. There needs to be a GA drawing of the main ACP unit so that people can identify the components within 8. In the drawing , label the PSU units 01- 07 as shown on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625189&prj=618&rqi=trFHmiwnDeh71x9Jn0aHNZG0Ir | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-341 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3 Fire : Level 5 SAP 08, 09: Drawing : Drawing missing strobe light at the genset area (5A / B) Detector Label on the following detector is wrong: N9L04D026 N9L04D033 N0L04D008 N9L01D026 N9L01D032 N9L02D025 N9L01D010 N9L02D047 (drawing need to update to N9L02D048 + need to change label on detector) N9L02D001 N9L01D008 Please update Bell strobe Data hall 1 near N9 L01 D008 is left hanging and not installed properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625193&prj=618&rqi=xpKHRQI0icMYs3Ct6nIVFSg29l
RT1DCOS-28-001 | SG06-1 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - BMS | L2A | Installation not correct | Commissioning | Controls | equipment | 2CPOS_GWP_01 | DCOS - Control Panels |  |  | Onsite 1Q2 , 1Q3 and 1Q4 MCB model was not tally with the bill of materials. Onsite was model A9F84110, however BOM indicate A9F84106 (apply to 1CPOS_GWP-01 and 2CPOS_GWP-01) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624885&prj=618&rqi=Ks1mPP8FVKhyeB8K5Gk7zbqVgx
RT1DCOS-28-002 | SG06-1 | APAC | Closed | P3 Low CX | siakhongneogh@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 2CPOS_GWP_01 | DCOS - Control Panels |  |  | During the Cx2A inspection, the following observations were noted (apply to 1CPOS_GWP-01 and 2CPOS_GWP-01): 1. The equipment layout plan / setting-out drawings have not been updated to reflect the current site conditions. 2. General housekeeping and cleaning works are required. 3. To install flexible conduit/ trunking for the incoming cables 4. Pending power earthing details explanation 5. Drawings to be in place 6. Permanent labelling shall be properly installed for incoming cables and screw terminal 7. To retighten and torque as per manufacturers guildelines | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624889&prj=618&rqi=WRmtJ8FRHO4MyiqkirOPJOniol
RT1DCOS-28-003 | SG06-1 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - BMS | L2A | Installation not correct | Commissioning | Controls | equipment | 2CPOS_GWP_01 | DCOS - Control Panels |  |  | Onsite the input card/ multiplexer quantity was not tally with the bill of materials. Onsite was only 1 set of input card and secrew terminal, however BOM indicated 2 sets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624890&prj=618&rqi=fhBGZH5Bqf6CzwAY4LrxlxGChE
GI-335 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3: SF : 1SF_D_02 - overload settings issue 1. Overload settings may be wrong as when i tried to measure the amperes i did not get a reading and only got 0 amps, Please check 2. When fire alarm is triggered / fan is supposed to resume last status when the fire signal is triggered / - It did not do so in local mode , the unit shut down , however in auto mode , the unit restarted after the alarm is cleared | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624951&prj=618&rqi=36CyU6GwIclBfvTlwQuELRI0DL
GI-337 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2a: 1FCU_Z_20 1FCU_Z_21 1FCU_Z_29 1FCU_Z_30 1FCU_Z_34 1FCU_Z_35 1FCU_Z_32 1FCU_Z_33 1. Document pocket to be affixed to the units 2. Ducting labels should be installed 3. Labels missing on the FCU 4. Drawings to be updated 5. Thermostat missing and not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624953&prj=618&rqi=yw7aYgrs8T3pwYJ5Hh1BgJuzNe
GI-336 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2a: 1SF_Z_4 1SF_Z_8 1SF_Z_9 1SF_Z_16 1. Document pocket needs to be installed on the SF 2. Labels are missing on the SF as well as on the ducting itself | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624952&prj=618&rqi=HiGYykZrjIVrmWHiX4ZCupsSXV
GI-332 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor - Mechanical |  | General Design Issue | Design |  | equipment type |  |  |  |  | FCU Cx3: Observations: 1. SOO states that when FCU in shut down or off mode the PICV valve should return to close state (0% position) 2. When tested on site the FCU shuts down or go into Off mode , in local / Auto / The PICV valve remains as open 3. Accesstech to confirm if the valve should remain open / close when the unit is shut down 4. Dirty Filter alarm , when it is in local mode , it stays on , but when its in auto mode , it switches off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624516&prj=618&rqi=x1q8ZDtDXqhae0X0HmDqMXF6vZ
RT1SEC-2-003 | SG06-1 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L2A | Documentation not issued/ Required | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx2a: L4 Card Access Panel ACP-07 L4 Card Access Panel ACP-08 L6 Card Access Panel ACP-11 L6 Card Access Panel ACP-12 1. PSU needs to be labeled to show where /what devices it is connected to 2. Battery needs to be labelled (Installation / Start using date) 3. Earth cable within the PSU units need to be attached / installed 4. Panel earth needs to be installed on the door 5. Internal wiring needs to be terminated with proper labelling 6. Applicable to all ACP units 7. There needs to be a GA drawing of the main ACP unit so that people can identify the components within 8. In the drawing , label the PSU units 01- 07 as shown on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624520&prj=618&rqi=1Gi2I5SO03VHglJAtZfCbzTKdq | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-333 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2a: 1FCU_Z_35: 1) INCOMING LIGHT missing white plastic cover/ It should be replaced 2) SLD to be update/remedied 1FCU_Z_34: 1) SLD to be updated/remedied 1FCU_Z_33: 1) SLD to be updated/remedied 1FCU_Z_30: 1) SLD to be updated/remedied All panels must have document pocket to be included Labels should be affixed to the FCU Ducting labels should be affixed to the duct Thermostat should be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624518&prj=618&rqi=rySArbT1znoOievGya2uEhjzhZ
GI-331 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3: Level 1 SAP Point to Graphics test: Strobe missing at the following locations: 1. Janitor Room 2. Shipping and recieving room 3. need to update in drawing that a bell / strobe was relocated near inventory storage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624341&prj=618&rqi=KDH6jf8YPGbbTfD6AJe2JiFsRn
RT1SEC-2-002 | SG06-1 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L2A | Documentation not issued/ Required | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx2A: L2 Card Access Panel ACP-03 L2 Card Access Panel ACP-04 L3 Card Access Panel ACP-05 L3 Card Access Panel ACP-06 1. PSU needs to be labeled to show where /what devices it is connected to 2. Battery needs to be labelled (Installation / Start using date) 3. Earth cable within the PSU units need to be attached / installed 4. Panel earth needs to be installed on the door 5. Internal wiring needs to be terminated with proper labelling 6. Applicable to all ACP units 7. There needs to be a GA drawing of the main ACP unit so that people can identify the components within 7. In the drawing , label the PSU units 01- 07 as shown on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624008&prj=618&rqi=ShdmbRrVtnslAZNmgg0B0vTumK | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-330 | SG06-1 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | To update the approved settings to include the change in the PT100 sensor setpoints change and excitation current limit change from 23% to 40%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624010&prj=618&rqi=YlkX43IjESkCydZlF0qLe1dTxJ
GI-329 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A: Cx2a: 1FCU_M1_05 1FCU_M1_06 P2 Issues: 1. Condensate tray is not installed on the FCU 2. BMS cabling has not been terminated yet / finished terminating 3. Equipmment tag is missing on the FCU 4. Pipe flow direction / labelling is missing 5. Isolators is not installed yet 6. FCU thermostat is not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624009&prj=618&rqi=1u8uNfGxL8lMKOwH74qMXarrpG
RT1SEC-2-001 | SG06-1 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-05-29 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L2A | Documentation not issued/ Required | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx2A: ACP_1 and ACP_2 ACP_9 and ACP_10 1. PSU needs to be labeled to show where /what devices it is connected to 2. Battery needs to be labelled (Installation / Start using date) 3. Earth cable within the PSU units need to be attached / installed 4. Panel earth needs to be installed on the door 5. Internal wiring needs to be terminated with proper labelling 6. Applicable to all ACP units 7. There needs to be a GA drawing of the main ACP unit so that people can identify the components within 7. In the drawing , label the PSU units 01- 07 as shown on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623494&prj=618&rqi=vl40pY951dTbiktl9Ty3QM09FA | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
RT1DCOS-9-001 | SG06-1 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-05-29 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1CPOS_PCP_1_CPU | DCOS - Control Panels |  |  | Onsite PCP Prosoft model was not tally with the drawing. Onsite was PLX31-EIP-MBTCP, however Drawing indicate PLX32-EIP-MBTCP (apply to all PCP panels) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623462&prj=618&rqi=KoLRd9m3eXOdmcxzWJvnJrS2Ja
GI-322 | SG06-1 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2B: 1CHWSTR_1_CHWBT_1 1CHWSTR_3_CHWBT_1 2CHWSTR_1_CHWBT_1 1. Labels missing from the buffer tank , a label identifying the buffer tank needs to be installed 2. Bolts are missing from the legs of the buffer tank - where it is connected to the i beam 3. Temperature sensors are not installed on the buffer tank 4. Auto Air vents needs to be installed 5. Water directional flow needs to be added onto the pipings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623354&prj=618&rqi=d4cgQYpwFHQMgOQmLyQ3hbW7tz
GI-320 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A: 1FCU_Z_24 1FCU_Z_31 1FCU_Z_76 1. Labelling missing from the control panel 2. Document pocket is missing and not attached 3.Fuse layout in the drawing missing F3,F4,F5 4.MCI and over load relay position need to be updated in the drawing 5.TS must be removed from the drawing as it does not exist 6.Relay THR1 / DFR1 relay in the drawing is switched , and needs to be updated 7.FCU missing equipment tag 8. FCU CHW supply and return do not have their directional / flow ,markings yet on the pipe 9 . All equipment tag must be update to the latest equipment naming 10. Drawing needs to be updated 11. FCU thermostat is not installed 12. Ducting Missing tags that need to be included 13. gaps between the trunking etc needs to be sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623173&prj=618&rqi=CYHUBpSkYOUlzLwrGcb2B7hDPS
GI-321 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A: 1SF_Z_1 1EF_Z_1 Cx2A : 1SF_D_1,1SF_D_2,, 1SF_C_1 , 1SF_C_2 1SF_D_1, 1SF_D_2, 1SF_C_1 , 1SF_C_2 1. Missing document pocket 2. SF missing the tag on the equipment 3. Ducting missing the tag 4. All equipment tag must be update to the latest equipment naming 5. Drawing needs to be updated for the missing tag that is not indicated in the drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623174&prj=618&rqi=DLgwYuERDTnnAU8kPdmTTA3OAb
GI-316 | SG06-1 | APAC | Open | P3 Low CX | jessyong@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | SMBE to ensure all DPM settings are set as per approved DPM alarm setpoints. Observed all levels DPM during DCOS cx3 inspection alarm setpoints are not as per approved settings. Please submit the approved settings DPM, crompton relay settings, sync check relay settings, UOVR in procore for EOR review and approval | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622957&prj=618&rqi=8DjQ5oUpy2qZ8TU6NdGsTYClml
GI-317 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jessyong@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | SMBE to ensure all labels installed are as per the revised approved dwg and in addition breaker ratings AT/AF should follow as per approved studies. Please ensure the dwg indicated breaker ratings follows the approved power studies. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622958&prj=618&rqi=CkC52rqr5iMzaRouui6n04PaLe
GI-314 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2a 1FCU_C_06 ,1FCU_D_06,1FCU_C_02 ,1FCU_D_02 1. Labelling missing from the control panel 2. Document pocket is missing and not attached 3.Fuse layout in the drawing missing F3,F4,F5 4.MCI and over load relay position need to be updated in the drawing 5.TS must be removed from the drawing as it does not exist 6.Relay THR1 / DFR1 relay in the drawing is switched , and needs to be updated 7.FCU missing equipment tag 8. FCU CHW supply and return do not have their directional / flow ,markings yet on the pipe 9 . All equipment tag must be update to the latest equipment naming 10. Drawing needs to be updated 11. FCU thermostat is not installed 12. Ducting Missing tags that need to be included 13. gaps between the trunking etc needs to be sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622888&prj=618&rqi=yNdoa8u7fgEw1o94UjHdWwGbB1
GI-315 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A : 1SF_D_1,1SF_D_2,, 1SF_C_1 , 1SF_C_2 1SF_D_1, 1SF_D_2, 1SF_C_1 , 1SF_C_2 1. Missing document pocket 2. SF missing the tag on the equipment 3. Ducting missing the tag 4. All equipment tag must be update to the latest equipment naming 5. Drawing needs to be updated for the missing tag that is not indicated in the drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622889&prj=618&rqi=MPK7fG1YV3junNKTVLwfU9Woto
GI-311 | SG06-1 | APAC | Closed | P2 Medium CX | ericchong@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A: 2CHWSTR_M1R1_CTSF_2 1CHWSTR_M1R1_CTSF_1 1CHWSTR_M1R1_CTSF_2 1CHWSTR_M1R1_CTSF_3 1CHWSTR_M1R1_CTSF_4 1CHWSTR_M1R1_CTSF_8 1CHWSTR_M1R1_CTSF_9 1. SLD & Panel GA to be amended to reflect the correct set up. ACT to call for reinspection upon drawings approval. 2. Vessel to be cleaned prior to sand filling. 3. Missing equipment labels. 4. Typo on control panel indications 5. Missing isolation valves before the skid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622615&prj=618&rqi=PT5WamQyBewI3QF4p7f5ikrUsc
GI-308 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A: SG6-1PACV_27,26,28,29 Nitrogen panel :SG6-1NG_16,SG6-1NG_17, 1. Ensure that the condensate drain is installed 2. Document pocket needs to be affixed to the panel 3.Permanent labels to be installed 4. Wires need to be labeled Piping 1.PSV-D is not installed on the pipings 2.Ensure that the piping have its flow markings and direction as well as its permanent labels 3. Ensure that the drain pipe has drain markings affixed to it 4. Permanent labels to be installed 5. Ensure that SCV/ PACV pipings have its labels affixed on to it SAP SG6-1SAP_16,19 1. Wires need to be labeled PACP : SG6-1PACP_16 3. Wires need to be labeled Isolators for PACP / ING / SAP not installed yet at that time of the inspection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622572&prj=618&rqi=MhClZPKePn9t0L7mCgFcY4W2VJ
RT1DCOS-13-001 | SG06-1 | APAC | Closed | P3 Low CX | siakhongneogh@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1CPOS_RIO_01 | DCOS - Control Panels |  |  | During the Cx2A inspection, the following observations were noted (apply to all panels): 1. The equipment layout plan / setting-out drawings have not been updated to reflect the current site conditions. 2. General housekeeping and cleaning works are required. 3. To install flexible conduit/ trunking for the incoming cables 4. Pending incoming feed earth stud to loop on earth bar 5. Drawings to be in place 6. Permanent labelling shall be properly installed for incoming cables 7. To retighten and torque as per manufacturers guildelines | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622407&prj=618&rqi=UonnZFAzVX7OgKts5HXRaehBzQ
RT1DCOS-17-001 | SG06-1 | APAC | Open | P3 Low CX | siakhongneogh@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - BMS | L2A | Installation Damage | Commissioning | Controls | equipment | 1CPOS_RIO_05 | DCOS - Control Panels |  |  | Observed that the HMI has been scratched. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622408&prj=618&rqi=L0KFCmBKDcExVrkWCWeW5TOpab
GI-304 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2a 1FCU_z_57 , 1FCU_z_57 1. Labelling missing from the control panel 2. Document pocket is missing and not attached 3.Fuse layout in the drawing missing F3,F4,F5 4.MCI and over load relay position need to be updated in the drawibng 5.TS must be removed from the drawing as it doe snot exist 6.Relay THR1 / DFR1 relay in the drawing is switched , and needs to be updated 7.FCU missing equipment tag 8. FCU thermostat is not installed 10. Ducting Missing tags that need to be included 11. gaps between the trunking etc needs to be sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622304&prj=618&rqi=ULfFArfLCp5XAECELv9mOxHIbX
GI-301 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | CX2B: Jockey pump missing its flow direction arrows , it needs to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621892&prj=618&rqi=R0wZVCQcSQBFGlf6pb95Dfcgzs
GI-300 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Cx2 A : L9 Domestic water tank 1. Tank / pump plinth at the corners need to be touched up 2. Water direction/ flow markings need to be installed 3.Anti Mosquito netting is not installed 4. Pipe overflow marking sis not indicated on the pipe yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621674&prj=618&rqi=ihTTMxmJzapVgbdTYzFPoETyzB
GI-293 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A: SG6-1PACV_27,26,28,29 Nitrogen panel :SG6-1NG_14,SG6-1NG_15, 1.Ensure that incomming wires from isolator to panel is installed 2. Ensure that the condensate drain is installed 2. Document pocket needs to be affixed to the panel 4.Permanent labels to be installed 5. Missing ethernet module - need to check if it needs to be installed 6. Wires need to be labeled Piping 1.PSV-D is not installed on the pipings 2.Ensure that the piping have its flow markings and direction as well as its permanent labels 3. Ensure that the drain pipe has drain markings affixed to it 4. Permanent labels to be installed 5. Ensure that SCV/ PACV pipings have its labels affixed on to it SAP SG6-1SAP_14,15 1. Please ensure that batteries are installed at the sap panels 2. This defect applies to all sap panels in the building 3. Wires need to be labeled PACP : SG6-1PACP_14,15 1. Please ensure that PACP panels have batteries installed in them 2. This defect is applicable to all PACP panels 3. Wires need to be labeled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620403&prj=618&rqi=pUhiQTBjOoL6eCFiUUY9Utwh2F
GI-290 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A: SG6-1PACV_19,18,20,21,23,22,24,25 Nitrogen panel :SG6-1NG_10,SG6-1NG_11, SG6-1NG_12, SG6-1NG_12 1.Ensure that incomming wires from isolator to panel is installed 2. Ensure that the condensate drain is installed 2. Document pocket needs to be affixed to the panel 4.Permanent labels to be installed 5. Missing ethernet module - need to check if it needs to be installed 6. Wires need to be labeled Piping 1.PSV-D is not installed on the pipings 2.Ensure that the piping have its flow markings and direction as well as its permanent labels 3. Ensure that the drain pipe has drain markings affixed to it 4. Permanent labels to be installed 5. Ensure that SCV/ PACV pipings have its labels affixed on to it SAP SG6-1SAP_10, 11,12,23 1. Please ensure that batteries are installed at the sap panels 2. This defect applies to all sap panels in the building 3. Wires need to be labeled PACP : SG6-1PACP_10,11,12,23 1. Please ensure that PACP panels have batteries installed in them 2. This defect is applicable to all PACP panels 3.Wires need to be labeled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620260&prj=618&rqi=C1fxKZwIFjCXk4qVx5NKe97wNj
GI-287 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Cx2B: NER Room: 1 FCU_Z_75 1 FCU_Z_13 Isolators installed is not the correct one , please check | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619916&prj=618&rqi=isPTkNEWjeqzXbpZB6smCrd3yf
GI-285 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A : UG make up water tank & accessories (All 4 Tanks) in underground room 1. Please check the tank capacity and ensure that the volume and etc is correct 2. Please ensure the electrode height is correct and accurate for all tanks 3. Net for the overflow is not installed (anti Mosquito Netting) / waring pipe also 4:Drain overflow label needs to be attached to the pipe Domestic water Tank 1. Please affix the water flow indicator on the pipe 2. Net for the overflow is not installed (anti Mosquito Netting) / warning pipe also 3. Please ensure the electrode height is correct and accurate for domestic water tank 4.Drain overflow label needs to be attached to the pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619869&prj=618&rqi=LOSLZabJbTQAvhJDYAufFDIRO0
GI-288 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A : Sprinkler water tank / Pipe 1.Sprinkler water tank have not spray painted the sprinkler tank capacity onto the tank / walls yet 2.The discharge pipe should be labelled 3.The water directional flow markings should be installed / affixed to the pipes | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620150&prj=618&rqi=taVJj1QahKqh5awre4V1OblXSm
GI-284 | SG06-1 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CX2A: 1FCU_Z_75, 1FCU_M1_13, 1MAU_C_2, 1MAU_M1_07, 1MAU_D_2 & 1MAU_M1_08 In the General Lay out drawing , the position of the relays do not follow as per the as GA drawings , please check and update the position of the relay in the GA drawings , as per what that is in the panel Please also trace and check the wiring of the fuse before updating the drawings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619677&prj=618&rqi=8bPXiMzvAipFn9oqPmltia1reF
RT1DCOS-7-001 | SG06-1 | APAC | Closed | P2 Medium CX | RyanWu@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - BMS | L2A | Installation not complete | Commissioning | Controls | equipment | 1DCOS_CP_7 | DCOS - Control Panels |  |  | put a missing 50mA fuse at compartment 13 for 2x1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618995&prj=618&rqi=lS5jUc1W8vuLpivJ3pkVVUK5tQ
RT1DCOS-5-001 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_CP_5 | DCOS - Control Panels |  |  | To provide updated dwg in panel pocket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618324&prj=618&rqi=tY2OiraThNEZttloGZARkmcQL5
RT1DCOS-4-001 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_CP_4 | DCOS - Control Panels |  |  | To provide updated dwg in panel pocket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618323&prj=618&rqi=7tGX7gfy6hvuI31LIXhFOWzkjQ
RT1DCOS-6-001 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_CP_6 | DCOS - Control Panels |  |  | To provide updated dwg in panel pocket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618325&prj=618&rqi=eyjY3slPPR6W86gpD8GeqzNP0W
RT1DCOS-3-001 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_CP_3 | DCOS - Control Panels |  |  | To provide updated dwg in panel pocket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618321&prj=618&rqi=ZaxI1u1TyhJcCY9lfWJ4tG900w
GI-266 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A : MAP : 1. MAP drawing , needs to be updated , please insert and resubmit the drawings for review 2. Batteries need to be installed in the PACP / SAP/ MAP , with the date of installation affixed to the battery 3. Permanent labels to be installed PACP : 1. PACP GA drawing , needs to be updated , as total power failure module is not included in the GA drawing , please insert and resubmit the drawings for review 2. PACP GA drawing : Patent CP - the module needs to be named in the GA drawing 3. Permanent labels to be installed PACP / SAP: 1. Batteries need to be installed in the PACP / SAP , with the date of installation affixed to the battery This general defect is applicable to all PACP / SAP panels MAP / SAP / RP / Mimic Panels 1. Please ensure that the incoming power cables are terminated prior to CX2B inspections 2. Permanent labels to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618261&prj=618&rqi=gjKoMKtlu6m31qSocxiG6y5rPt
GI-264 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor - BMS |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | CX2A visual inspection conducted for 1DCOS_CP_3,4,5,6, observed the following issues 1. Cable sheath to reinstall at enclosure, not at gland plate once trunking is installed 2. Missing danger sign 3. Missing engraved sign for PE and TH1 4. Incorrect PLC part number in dwg 5. To update dwg on IE grounding 6. Provide additional 50mA fuse within the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618201&prj=618&rqi=aDVmy5jxWSoAmCZaOVMcRICOUd
GI-263 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General Design Issue | Design |  | equipment type |  |  |  |  | LVSB SOO to include transferring system to maintenance bypass procedures and the panels involved in the transfer process, including but not limited to ups system, udp/umdsb/or any associated panels and MSBs. Update soo to submit to procore for EOR review and approval. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618105&prj=618&rqi=QM8RUCY8Y1WFSm20l25niBr402
GI-262 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A SG6-1SCV_10,12,11 1.Ensure that the piping have its flow markings and direction as well as its permanent labels 2. Ensure that the drain pipe has drain markings affixed to it 3. Flow meter for SCV is not installed yet 4. Permanent labels to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617960&prj=618&rqi=RXLwlsxKLQ5OuHZTJT57CrHhI5
GI-261 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A: SG6-1PACV_13,12,17,16,15,14 Nitrogen panel :SG6-1NG_07 ,SG6-1NG_09 , SG6-1NG_08 1. Missing labels within the nitrogen panel 2. Requires SLD / GA drawing to be placed / affixed in panel / sent to HDR for approval 3. Ensure that incomming wires from isolator to panel is installed 4. Ensure that the condensate drain is installed 5.Document pocket needs to be affixed to the panel 6.Permanent labels to be installed 7. Missing ethernet module - need to check if it needs to be installed 8. Wires need to be labeled Piping 1.PSV-D is not installed on the pipings 2.Ensure that the piping have its flow markings and direction as well as its permanent labels 3. Ensure that the drain pipe has drain markings affixed to it 4. Permanent labels to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617959&prj=618&rqi=W04bPP5lPhq5QiBnaD6EC5QxGx
GI-254 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A: SG6-1PACV_11,10,07,06,09,08 Nitrogen panel :SG6-1NG_06 ,SG6-1NG_04 , SG6-1NG_05 1. Missing labels within the nitrogen panel 2. Requires SLD / GA drawing to be placed / affixed in panel / sent to HDR for approval 3. Ensure that incomming wires from isolator to panel is installed 4. Ensure that the condensate drain is installed 5.Document pocket needs to be affixed to the panel 6. Permanent labels to be installed 7. Missing ethernet module - need to check if it needs to be instaled 8. Wires need to be labeled Piping 1.PSV-D is not installed on the pipings 2.Ensure that the piping have its flow markings and direction as well as its permanent labels 3. Ensure that the drain pipe has drain markings affixed to it | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617834&prj=618&rqi=ptGKFC3INrpFWzi3WAeYV5Gmpx
GI-248 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A SCV 05,06 1.Ensure that the piping have its flow markings and direction as well as its permanent labels 2. Ensure that the drain pipe has drain markings affixed to it 3. Flow meter for SCV is not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617728&prj=618&rqi=ZWJDQSelt5DAZAveLpVOhqdBLE
GI-255 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A SCV 09,07,08 1.Ensure that the piping have its flow markings and direction as well as its permanent labels 2. Ensure that the drain pipe has drain markings affixed to it 3. Flow meter for SCV is not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617835&prj=618&rqi=2j1Nc0hFc2ccCNWGR6DSzHGKyJ
GI-247 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A: SG6-1PACV_02,0304,05 Nitrogen panel : SG6-1NG_02, SG6-1NG_03 1. Missing labels within the nitrogen panel 2. Requires SLD / GA drawing to be placed / affixed in panel / sent to HDR for approval 3. Ensure that incomming wires from isolator to panel is installed 4. Ensure that the condensate drain is installed 5.Document pocket needs to be affixed to the panel 6. PSV-D is not installed on the pipings 7. Permanent labels to be installed on panels 8. Missing ethernet module - need to check if it needs to be installed 9. Wires need to be labeled Nitrogen panel :SG6-1NG_03 1. Panel has scratches on it that needs to be buffed out 2. Panel wording below has been damaged , please touch up 3. Permanent labels to be installed on panels 4. Missing ethernet module - need to check if it needs to be installed 5. Wires need to be labeled Piping: 1.PSV-D is not installed on the pipings 2.Ensure that the piping have its flow markings and direction as well as its permanent labels 3. Ensure that the drain pipe has drain markings affixed to it 4. Permanent labels to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617676&prj=618&rqi=zENPKVNN0XmBLch6wJCVWEenbG
GI-246 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A Mimic Panel / Repeater panel 1. SLD and GA is required of the mimic / repeater panel pending submission and approval from HDR 2. Permanent labels to be installed on panels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617546&prj=618&rqi=7M4ZUaDYYei3b6P3QmwkG81tf9
GI-243 | SG06-1 | APAC | Closed | P2 Medium CX | RyanWu@commtechasia.com | 2026-04-08 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Replace the earth cable "FROM MFEB ELEC RISER 5B-2" at level 5 FEB STS 5B as insulation is scratched to the point can see copper inside | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617515&prj=618&rqi=xo4vsyB9FmfJ41A7rflO0BrzkL
GI-245 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A SCV 1,2,34 1.Ensure that the piping have its flow markings and direction as well as its permanent labels 2. Ensure that the drain pipe has drain markings affixed to it 3. Flow meter for SCV is not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617540&prj=618&rqi=TmKvlqwkqn1ASdMqxH34HpmVnB
RT1DCOS-1-001 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-02 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_CP_1 | DCOS - Control Panels |  |  | Cx2A : DCOS_CP_01: 1. Cable entry edge needs to be protected by a rubber sleeve to prevent the sharp edge from cutting / damaging the cable 2. Light needs to be indicated in the GA drawing 3. The door panel earth needs to be checked its the approved type 4. Danger stickers to be affixed to panel before energization 5. Document pocket needs to be affixed to panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617166&prj=618&rqi=zNm35woRCF6Slu3rBNlI4TIEW9
RT1DCOS-2-001 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-02 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_CP_2 | DCOS - Control Panels |  |  | Cx2A : DCOS_CP_02: 1. Cable entry edge needs to be protected by a rubber sleeve to prevent the sharp edge from cutting / damaging the cable 2. Light needs to be indicated in the GA drawing 3. the door panel earth needs to be checked its the approved type 4. Danger stickers to be affixed to panel before energization 5. Document pocket needs to be affixed to panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617168&prj=618&rqi=sjHbka2qJu7K0Unimjq0yilfIK
GI-234 | SG06-1 | APAC | Ready for Verification | P3 Low CX | KeeLeongLee@commtechasia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Observed during Cx2B earthing inspection, all the earth bar is not labelled. Affected earth bar as below: 1. MFEB ELEC RISER 9A-2 2. FEB-1-E-WALL-9A 3. FEB-2-E-WALL-9A 4. FEB UG MUWP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616629&prj=618&rqi=gTb8On3AN19o06sSPVUwF6iYbo
GI-231 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2a 1CHWSTR_03_HX 1CHWSTR_02_HX 1CHWSTR_04_HX 1CHWSTR_09_HX 1CHWSTR_10_HX 1. The hex is missing a equipment label to be affixed to the hex 2. The name on the nameplates need to be updated to the newest naming 3. 1CHWSTR_02_HX - there is a dent that needs to be combed on the hex -CLOSED 4 . The chilled water / condenser water pipes need to have label on where is supply and return 5., Pipe flow arrows / naming is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616361&prj=618&rqi=E7jyqN8jLtZSfkaBmmkPJz5FzG
GI-228 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-23 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2a LV MFEB B to FEB UG MUWP Room : 1, Label on the earth wires ( 1/2 ) in the MUWP underground room needs to be changed From LV MFEB 1B -(1) ( L1 CSR 1B) / From LV MFEB 1B -(1) ( L1 CSR 1B) " 1" Prefix in front of the B is advised to be removed . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616166&prj=618&rqi=AWpavHEcSrkqRH9qIyTVbU8k4N
GI-229 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-23 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CxL2a: LV MFEB B for LV to MFEB ELEC RISER 5B-2 Drawing needs to be updated on the position if the Note one ( Cable Tray Earth) , as well as the position of the Incomming earth wire from LV MFEB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616167&prj=618&rqi=naQ8yss6ebdfL3HNnwimZcyCfJ
GI-226 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-20 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx L2 A : 1FCU_Z_73 / 1FCU_7_74 /1FCU_C_04 /1FCU_D_04 /1FCU_A_15, 1FCU_A_16 1. Label tag is missing on the FCU panel 2. Thermostat is not installed on the FCU 3. There is no TS in the panel , but there TS shown and indicated on the drawings 4. The relay THRI / DFR1 position in the GA is shown as swapped , GA needs to be updated 5. Location of the MC1 needs to be shifted down in the GA drawing 6.OL1 - Model in the panel is shown as LRD06 , drawing shows as LRD08 , drawing needs to be updated 7. Dirty Filter Status of the field device X1.3 , X1.4 - needs to change to 13/A / 14 /A 8. Fan Speed Command needs to change X3.18 to 21 B 9. Document pocket is not attached to the panel 11. Label on FCU needs to be affixed 12 . Labels need to be attached to the ducting 13. gaps between the trunking etc needs to be sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616122&prj=618&rqi=gIGcarwyCl9OMymTRqxN2Pc7g9
GI-208 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CxL2a 1 SF _Z_6 , 1 SF _Z_7 1. Please ensure that plastic wrapping for the SF are removed 2. Please ensure that there is a big visible label for the SF 3. Please ensure that the earth cable is labelled 4. Please update the GA to show that the transformer is installed at the bottom of the panel and not at the top 5. Please check if the FIRE SIGNAL is labelled as 15/A , 16 A ( drawing ) or 13 / 14 A ( installed on site ) 6. Terminal block is missing its label , in the panel , please install the label 7. Please update the General Arrangement drawing the FCU - Fuses Behide door , should be fuses behind door 8. Document pocket is missing and is not added to the panel 9. Ensure that the fuses behind the door is has a label affixed to it 10. In the GA , fuses behide the door should be updated 11. Unit strut needs to be shortened with end caps installed on them 12. Ducting Missing tags that need to be included 13. gaps between the trunking etc needs to be sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615448&prj=618&rqi=tlJu7jRQcfIzfQcYRNMEthyOCh
GI-209 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx L2 A : 1FCU_C_09 / 1FCU_D_09 /1FCU_D_10 /1FCU_C_10 /1FCU_M1_29 1. Label tag is missing on the FCU panel 2. Thermostat is not installed on the FCU 3. There is no TS in the panel , but there TS shown and indicated on the drawings 4. The relay THRI / DFR1 position in the GA is shown as swapped , GA needs to be updated 5. Location of the MC1 needs to be shifted down in the GA drawing 6.OL1 - Model in the panel is shown as LRD06 , drawing shows as LRD08 , drawing needs to be updated 7. Terminal block for field device should be shown as X1, X2 - safety provision switch /- needs to be updated in the drawing 8. Common alarm status wire U13/14 appears to be swapped 9. PICV Feed back X3.21 - Missing Cable and cable is not attached 10. Document pocket is not attached to the panel 11. Label on FCU needs to be affixed 12. Ducting Missing tags that need to be included 13. gaps between the trunking etc needs to be sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615450&prj=618&rqi=uvwf0r1K4ZRtlhxbBrPcQRV86t
GI-205 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CX2A 1SF_Z_10, 1SF_Z_11, 1SF_Z_14,1SF_Z_15 1. Fuses behind the door spelling in the GA is wrong 2. Transformer location in the GA is also wrong and needs to be updated in the GA drawing 3. OL Settings need to be confirmed 4. Labels need to be attached on the Supply Fan it self 5. Labels also need to be attached to the ducting 6. Document pocket is not attached to the panel 7. Unit strut needs to be shortened with end caps installed on them | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615341&prj=618&rqi=jv3UspdwEITMdmZBxpRhFDJquV
GI-206 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx L2 A : 1 FCU_D_08, 1 FCU_C_08,1 FCU_Z_61, 1 FCU_Z_62 1. Label tag is missing on the FCU panel 2. Thermostat is not installed on the FCU 3. There is no TS in the panel , but there TS shown and indicated on the drawings 4. The relay THRI / DFR1 position in the GA is shown as swapped , GA needs to be updated 5. Location of the MC1 needs to be shifted down in the GA drawing 6.OL1 - Model in the panel is shown as LRD06 , drawing shows as LRD08 , drawing needs to be updated 7. Terminal block for field device should be shown as X1, X2 - safety provision switch /- needs to be updated in the drawing 8. Common alarm status wire U13/14 appears to be swapped 9. PICV Feed back X3.21 - Missing Cable and cable is not attached 10. 1 FCU_Z_61 - cable came off during the inspection , and needs to be tightened 11. Document pocket is not attached to the panel 12. Label on FCU needs to be affixed 13. Ducting Missing tags that need to be included 14. gaps between the trunking etc needs to be sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615342&prj=618&rqi=W2ZVDtB5n2T3FqFNUWBtXax3fh
GI-203 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A, 1 FCU _Z_ 43 , 1 FCU _M1_49 , 1 FCU _Z,49 , 1 FCU _Z_50 1. FCU thermostat is not installed 2. FCU Control panel missing the equipment tag 3. There is no TS in the panel , but it is shown in the drawing 4. Location of the MC1 needs to be updated in the General Arrangement Drawing 5. F5 needs to be added into the General Arrangement Drawing 6. Relays THRI / DFRI position in the general arrangement is swapped 7. Terminal block X1 ( Provision safety switch ) / (EC Fan Fault Signal) / Dirty Filter Alarm status needs to be updated in the drawing as the naming does not tally on site and also at the drawing 8.Document pocket is missing and is not added to the panel 9. Label on FCU needs to be affixed 10. Ducting Missing tags that need to be included 11. gaps between the trunking etc needs to be sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615198&prj=618&rqi=tMQQHieZ0KJllptwSpaKx4LGjm
GI-201 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CxL2a 1 SF _Z_10 , 1 SF _Z_11, 1 SF _Z_14, 1 SF _Z_15 1. Please ensure that plastic wrapping for the SF are removed 2. Please ensure that there is a big visible label for the SF 3. Please ensure that the earth cable is labelled 4. Please update the GA to show that the transformer is installed at the bottom of the panel and not at the top 5. Please check if the FIRE SIGNAL is labelled as 15/A , 16 A ( drawing ) or 13 / 14 A ( installed on site ) 6. Terminal block is missing its label , in the panel , please install the label 7. Please update the General Arrangement drawing the FCU - Fuses Behide door , should be fuses behind door 8. Document pocket is missing and is not added to the panel 9. Ensure that the fuses behind the door is has a label affixed to it 10. In the GA , fuses behide the door should be updated 11. Unit strut needs to be shortened with end caps installed on them | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615116&prj=618&rqi=SRhFM1q3UavLLS9e5fPQwmecO2
GI-200 | SG06-1 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | CX2A MV Fan: 1EF_Z_4 1EF_Z_5 1. Missing label on the ducting. 2. Debris to clean. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615048&prj=618&rqi=Q3JYLySVKvOfnLaJxSc3aEkhGG
GI-193 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-03-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Earthing Cx2A Earthing from MV FEB B / A to CSS ( RMU ) 12 way Earth bar type and dimensions installed on site in the RMU differ from type / dimension shown in the drawing The 12 way EB shown in the drawing is split into two and has a test link connected to it where else on site the bar is just straight, without a test link and is different from the one that is installed Please check and advise on the dimensions on which one is correct | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614805&prj=618&rqi=ExgbRXnDccRb4XRrYfe1KJBTaS
GI-191 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A : During CX2a visual inspection it was observed that the STS enclosure IP rating ,does not match approved drawing 1. Please refer to the email thread attached 2. Please also include pictures of the rectified enclosure as reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614765&prj=618&rqi=JsdmLMwMGsf3M9JvPsoEFQK2ux
GI-192 | SG06-1 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CX2A Buffer tank: 1. 2CHWSTR_2_CHWBT_1 has damaged insulation and dented. 2. All three Buffer Tanks 1CHWSTR_01_CHWBT_1, 2CHWSTR_2_CHWBT_1 & 1CHWSTR_02_CHWBT_1 leg insulation below the base is incomplete and not fully covered. 3. Issue with 1CHWSTR_02_CHWBT_1 and 1CHWSTR_04_CHWBT_1, on the approved drawing 1CHWSTR02_CHWBT_1, have "1CHWSTR_04_CHWBT_1" on its name plate and 1CHWSTR_04_CHWBT_1 have "1CHWSTR02_CHWBT_1". AccessTech to check approved drawings and change name plates. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614789&prj=618&rqi=sCZE4wzyRhBQSx0dws3bJsFFc3
GI-190 | SG06-1 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A Issues FCU_M56 & FCU_Z27 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Only FCU Panels have labels, No Labelling for the FCU itself. 3. Temperature Thermostat to be installed in all FCU rooms. 4. Approved drawing, general arrangement discrepancy of components. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. PSU 50W is also in the incorrect area. Drawing to be updated and approved. 5. Incoming Terminal for FCU Panel, termination is incomplete 6. Dirty Filter Alarm Status, X1.3 & X1.4, drawing indicates 1B & 13/A, on site shows 13/A & 14A. 7. Fan Speed Command, X3.18, drawing indicates 6/B, on site shows 2/B. 8. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 9. Drawing Pocket to be installed in FCU panel 10. Not able to tally FCU S/N due to inaccessibility. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614690&prj=618&rqi=BTlK5OSVCK9Jt8FRgdc12GbiCU
GI-188 | SG06-1 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CX2A Issues FCU_Z53, FCU_Z54 & FCU_Z55 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Only FCU Panels have labels, No Labelling for the FCU itself. 3. Temperature Thermostat to be installed in all FCU rooms. 4. Approved drawing, general arrangement discrepancy of components. Magnetic Contactor (MC1) and Overload (OL) Relay is in the incorrect area. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. TS Relay to be remove in drawing. Drawing to be updated and approved. 5. Incoming Terminal for FCU Panel, termination is incomplete 6. Dirty Filter Alarm Status, X1.3 & X1.4, drawing indicates L1B & 13/A, on site shows 13/A & 14A. 7. Fan Speed Command, X3.18, drawing indicates 6/B, on site shows 2/B. 8. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 9. Drawing pocket for panel to be installed 10. FCU_Z53 location to be update in the floor plan layout 11. FCU_Z54 cable pulling test failed. 1FCU_Z_54_CP_LCP_UI1 cable is broken during the cable pull test. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614687&prj=618&rqi=nOYADAZuBwP72c3ng6S69rv2WK
GI-189 | SG06-1 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CX2A Issue FCU_M40 & FCU_Z60 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Only FCU Panels have labels, No Labelling for FCU itself. 3. Temperature Thermostat to be installed in all FCU rooms. 4. Approved drawing, general arrangement discrepancy of components. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. PSU 50W is also in the incorrect area. Drawing to be updated and approved. 5. Incoming Terminal for FCU Panel, termination is incomplete 6. Dirty Filter Alarm Status, X1.3 & X1.4, drawing indicates 1B & 13/A, on site shows 13/A & 14A. 7. Fan Speed Command, X3.18, drawing indicates 6/B, on site shows 2/B. 8. Control Circuit Diagram 1 Drawing indicates OL1 LRD16 (9 ~ 13), onsite shows LRD08 (2.5 ~ 4) 9. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 10. Drawing Pocket to be installed in FCU panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614688&prj=618&rqi=0SlnjbI8HbxU8dA9x9B1tvOKZH
GI-185 | SG06-1 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A Issue 1FCU_M1_33, 1FCU_C_12, 1FCU_M1_34, 1FCU_D_13 in STS ROOM A & STS ROOM B 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Only FCU Panels have labels, No Labelling for the FCU itself. 3. Temperature Thermostat to be installed in all FCU rooms. 4. Approved drawing, general arrangement discrepancy of components. Magnetic Contactor (MC1) and Overload (OL) Relay is in the incorrect area. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. PSU 50W is also in the incorrect area. Drawing to be updated and approved. 5. Incoming Terminal for FCU Panel, termination is incomplete 6. Dirty Filter Alarm Status, X1.3 & X1.4, drawing indicates 1B & 13/A, on site shows 13/A & 14A. 7. Auto Mode & Common Alarm, drawing indicates U12 & COM respectively, on site it is swapped COM & U12. 8. Fan Speed Command, X3.18, drawing indicates 6/B, on site shows 2/B. 9. Control Circuit Diagram 1 Drawing indicates OL1 LRD16 (9 ~ 13), onsite shows LRD10 (4 ~ 6) 10. STS ROOM A & B, unable to check the S/N of FCU Units 11. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 12. Drawing Pocket to be installed in FCU panel 13. Not able to tally FCU S/N due to inaccessibility. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483507&prj=618&rqi=20gEk1BbjEx2oiuZoXZVaXeK1q
GI-187 | SG06-1 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A Issues 1FCU_M1_55_CP & 1FCU_Z_26_CP 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Temperature Thermostat to be installed in all FCU rooms. 3. Approved drawing, general arrangement discrepancy of components. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. Drawing to be updated and approved. 4. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 5. Drawing Pocket to be installed 6. For 1FCU_M1_55_CP, earth cable is not terminated to the panel earth bar. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483511&prj=618&rqi=YeeeH4G9YaeufOtfjq8GwK8fE2
GI-186 | SG06-1 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A Issue 1FCU_C_11, 1FCU_D_11 & 1FCU_D_12 in TER 5A & TER 5B2 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Only FCU Panels have labels, No Labelling for the FCU itself. 3. Temperature Thermostat to be installed in all FCU rooms. 4. Approved drawing, general arrangement discrepancy of components. Magnetic Contactor (MC1) and Overload (OL) Relay is in the incorrect area. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. TS Relay is missing in drawing. Drawing to be updated and approved. 5. Incoming Terminal for FCU Panel, termination is incomplete 6. Dirty Filter Alarm Status, X1.3 & X1.4, drawing indicates L1B & 13/A, on site shows 13/A & 14A. 7. Fan Speed Command, X3.18, drawing indicates 6/B, on site shows 2/B. 8. Control Circuit Diagram 1 Drawing does not indicate OL1 Model and Range 9. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 10. Drawing pocket for panel to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483508&prj=618&rqi=sIVZH8WYajroKlFQx5oGFa8MCo
GI-216 | SG06-1 | APAC | Closed | P3 Low CX | ericchong@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - BMS |  | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_CP_3 | DCOS - Control Panels |  |  | Cx1 FWT: 1DCOS_CP_03, 1DCOS_CP_04, 1DCOS_CP_05, 1DCOS_CP_06 1. Danger sign not pasted during FWT. RVS to paste on site after confirming the sign design. 2. Incoming/outgoing cable management to be done onsite. 3. Drawing: DO relays (1XO, 2XO) to be updated in the drawing, tally with existing panel. 4. Drawing: To change the incoming cable labelling to â€œTBX:L / TBX:Nâ€, tally with existing wire tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615692&prj=618&rqi=w8IkGTI4aBWShfYEqD0kcB5L0K
GI-217 | SG06-1 | APAC | Closed | P3 Low CX | ericchong@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - BMS |  | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_CP_7 | DCOS - Control Panels |  |  | Cx1 FWT: 1DCOS_CP_07: 1. Danger sign not pasted during FWT. RVS to paste on site after confirming the sign design. 2. Incoming/outgoing cable management to be done onsite. 3. To add label on trunking lid adjacent to respective terminal block. Missing label are GWP_01, 1XO and 2XO. 4. To change the wire tagging of DI terminal blocks connected to Extension PLC module, to tally with latest as-built drawing. 5. Drawing: DO relays (1XO, 2XO) to be updated in the drawing, tally with existing panel. 6. Drawing: To change the incoming cable labelling to â€œTBX:L / TBX:Nâ€, tally with existing wire tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615696&prj=618&rqi=ha2RcK2QC1dPnDS5mv2BC5yyPz
GI-184 | SG06-1 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-02-26 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | As per HDR comment, for OPSFLEX Rm, STS Rm and Ewall Rm to install 50x6mm2 earth bar. Engie to rectify as per HDR comment and submit the revise dwg to procore for official approval. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483397&prj=618&rqi=0dRaeSZ6WmecQGZf8cUmMkAsKo
GI-183 | SG06-1 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Engie to update the following, 1. Earthing overall SLD to update FEB EWALL 2A-1 and 2 cables connection, including incorrect location installed as per the approved layout, submittal 1502. 2. MFEB elec riser 2A to update in overall SLD, current earthing cables connection does not align with the approved SLD 3. Missing main label for all earthing bar 4. Observed earthing cable sleeve installed at cable tray. Engie to replace. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483396&prj=618&rqi=KqkRqr2K30TS8fhLH0BWOShldS
GI-177 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-02-22 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A - 1FCU_Z_72,1FCU_M1_45, 1FCU_C_13, 1FCU_Z_26, 1FCU_M1_35 1. Labelling not installed on the FCU 2. Thermostat is not installed yet 3. Ensure that the earthing cable (Panel) is terminated 4. FCU name plate is installed on to the Control panel as per GA drawing 5. Relay THRI / DFRI location is swapped in the drawing and needs to be updated in the GA drawing 6. Incoming cable needs to be terminated and labelled 7. Fuse F3 needs to be updated in the SLD , F3 / F4 should be labelled as F4 / F5 respectively in the SLD | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199741&prj=618&rqi=QUdGDbIfWX1AFOwPkpmFETdyCx
GI-181 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-02-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Incorrect heater watt installed for all LVSB panels. As per dwg is 55W. 1UDP_C1, 1UDP_C2, 1UDP_D1, 1UDP_D2, 1MDSB_C, 1UMDSB_C, 1UMDSB_D, 1MDSB_Z2, 1MDSB_Z3, 1MDSB_R1_2, 1MSB_Z 1LBSB_ZR1_2, 1MDSB_M1_1_1_5, 1UDP_Z, 1 MDSB_Z1, 1LBSB_ZR1_1, 1LBSB_ZR1_2 To update for all LVSB panels and insert the updated approved dwg in the panel pocket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199750&prj=618&rqi=JNpN0BBkAP50PtlCFtjCJbWRJT
GI-182 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-02-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Observed incorrect cable size installed for all UMDSB panels. Drawing indicated internal power cables size as 50 sqmm but on site/actual installation measured 35sqmm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199753&prj=618&rqi=ePbSJyRzF6pZC78vVDZjjDmWNm
GI-176 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-02-22 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A - 1FCU_Z_05, 1FCU_Z_65, 1FCU_Z_66,1FCU_Z_67 1. Labelling not installed on the FCU 2. Thermostat is not installed yet 3. Ensure that the earthing cable (Trunking ) is terminated 4. FCU name plate is installed on to the Control panel as per GA drawing 5. Relay THRI / DFRI location is swapped in the drawing and needs to be updated in the GA drawing 6. There is no TS relay in the panel , please check and update the drawing 7. Incoming cable needs to be terminated and labelled 8. Fuse F3 needs to be updated in the SLD , F3 / F4 should be labelled as F4 / F5 respectively in the SLD | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199740&prj=618&rqi=VTED3Q8LY5tmgGqjCZLiAcLeFN
GI-173 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx L2A - General Issues for FCU / EF / SF 1. Please ensure that there are permanent labels affixed to the Equipment / Control Panels 2. Ensure that there is a document pocket affixed to the control panel 3. FCU - Ensure that permanent labels are affixed to the thermostats of the FCU when they are installed 4. FCU name plate is installed on to the Control panel as per GA drawing 5. Ensure that the earthing cable (Trunking) is terminated 6. Unit strut needs to be shortened with end caps installed on them 7. The Ducting needs to have label applied to them | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199135&prj=618&rqi=qmA0qpoTblyCB8VPkXiYMjK6bV
GI-171 | SG06-1 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-02-11 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A General Issues for all FCUs 1. Thermostat for FCU only installed in Rooms FER B-2 and TER B-2 for mockup, before Cx2B testing all thermostat to be installed -CLOSED 2. Only FCU Panels have labels, the FCUs itself do not have labelling, all FCUs to have labels before Cx2B. -CLOSED 3. Unable to check the fan coils and identify the sensors/components inside the FCU due to either inaccessibility or already joint with duct, arrangement to be made to verify condition of coil and any components such as sensors or dampers (if applicable). -CLOSED 4. 1FCU_Z_65, 1FCU_Z_66, 1FCU_Z_67, 1FCU_Z_72, 1FCU_M1_45, 1FCU_C_13, 1FCU_M1_35 signaling and power cable not terminated, unable to do Cx2A. -CLOSED 5. 1FCU_Z_05 Unable to do Cx2A, because FER ROOM 1B-2 not accessible. -CLOSED 6. 1FCU_Z_06_CP, 1FCU_M1_54_CP, 1FCU_Z_48_CP, 1FCU_M1_50_CP, Typical panels. Approved drawing, general arrangement discrepancy of components. Magnetic Contactor (MC1) and Thermal Overload Relay is in the incorrect area. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. PSU 50W is also in the incorrect area. Drawing to be updated and approved 7. 1FCU_Z_03_CP, 1FCU_Z_04_CP, 1FCU_Z_40_CP, 1FCU_Z_41_CP, 1FCU_Z_42_CP Typical Panels. Approved drawing, general arrangement discrepancy of components. Magnetic Contactor (MC1) and Thermal Overload Relay is in the incorrect area. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. TS Relay is not shown in the approved drawing but is present inside the panel on site. Drawing to be updated and approved. 8. Second Labelling above the R/S/T Light on panel missing, However GA Drawing shows Labelling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199127&prj=618&rqi=qx5UzTBVnNFkZxhAJvcjj3C2S9
GI-166 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-02-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | CxL2A : 1.Pump label to be updated as label to be updated as per latest approved naming. 2. Document pocket is missing and is not added to the panel Issue is applicable also to hose reel pump and jockey pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199044&prj=618&rqi=vJrLDwOkW2FY5QqfVUC0H3DuqU
GI-138 | SG06-1 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | For ALL STSSB observed the following issues 1. Incorrect fuse installed at F18, instead of 20A, 10A was installed instead - CLOSED 2. no fuse rating label install for F18, 18A, 18B, 18C, 18D - CLOSED 3. install label for MOXA - CLOSED 4. Missing terminal numbering on 1X2, to include control drawing for 1X2 circuit in drawing - CLOSED 5. Missing phase label indication on busbar - CLOSED 6. Missing busbar mimic label on panel - CLOSED | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198099&prj=618&rqi=K3W0hzHb5fErlKGOrrXwGbhxkU
GI-139 | SG06-1 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | For All STS panels Observed the following issues 1. IP21, however there is no cover at the bottom of the panel 2. No GA, no fuse breaker/rating, no PCBs (QB540S1/2, QB120.4, QB102.1, QB102S1/2, ST630 S1/2 etc) labels indicated in approved drawing. 3. Incorrect fuse numbering on approved dwg 3. no phase labels installed at busbar 4. to install on/off label at isolator Q51 5. missing label for key exchange box and key lock 6. to check if busbar mimic label can be installed on panel door 7. Poor adhesion observed on heatshrink(bubbling on heat shrink tubing) 8. socomec to check as per IEC on the minimum distance between phase busbar and ensure design comply Socomec to rectify before Cx2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198100&prj=618&rqi=aJqUg9Pw6tVkVN9Tp9eNAh6k1o
GI-067 | SG06-1 | APAC | Closed | P1 High DCOS | ericchong@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | General Contractor - BMS |  | Documentation not issued/ Required | Commissioning | Controls | equipment | 1CPOS_PCP_1_CPU | DCOS - Control Panels |  |  | Cx1 CPOS SFAT (19-Jan): Refer to issue tracker in attachment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197212&prj=618&rqi=4Q4dI7L5Vp3PqfVJhVMSzutAm8
GI-068 | SG06-1 | APAC | Closed | P2 Medium CX | ericchong@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Cx1 DCOS SFAT2 (19-20 Jan) Refer to issue tracker in attachment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197213&prj=618&rqi=O7VoA4qV411IoaFCIJ3aoNPEaY
GI-066 | SG06-1 | APAC | Closed | P3 Low CX | YenBinChai@commtechasia.com | 2026-01-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | 1. Common cosmetic issue: -Missing engraved nameplate -Observe no drawing pocket in CRAH (closed) -Debris present in CRAH Equipment affected: 1CRAH_ZR1_1, 1CRAH_ZR1_2, 1CRAH_ZR1_3, 1CRAH_ZR1_4, 1CRAH_DR2_1, 1CRAH_DR2_2, 1CRAH_DR2_3, 1CRAH_DR2_4, 1CRAH_CR1_1, 1CRAH_CR1_2, 1CRAH_CR1_3, 1CRAH_CR1_4, 2. Chilled water coil to be combed (closed) Equipment affected: 1CRAH_DR2_3, 1CRAH_ZR1_4, 1CRAH_CR1_4, | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197078&prj=618&rqi=7T5A4b7hvM3QhZ30QbM3gMs6lF
GI-064 | SG06-1 | APAC | Closed | P3 Low CX | YenBinChai@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Equipment: 1UMDSB_R1_7, 1UMDSB_M1_2_1, 1DB_Z2_1_01, 1DB_Z2_2, 1DB_Z1_1, 1DB_Z2_2_03 Issue: The outgoing label is currently missing because the existing SLD does not indicate any outgoing feeders. It will be finalized based on the approved naming convention and updated SLD. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196922&prj=618&rqi=przgT6ZrJ7nVcceHluwjPGydd6
GI-061 | SG06-1 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-01-09 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | CxL1 Rehlko KD-3500-E FWT DCOS Issues DCOS(Action from DCOS Team, to update the deviation in the elec points list and coordinate with WH to submit for approval) â€¢ Incorrect Genset command status in faceplate â€¢ Incorrect gen operating status(status remained in gen fault) in faceplate â€¢ Incorrect gen run status(running emergency service/running non-emergency service) in faceplate â€¢ Alarm severity not as per dcos elec points list rev.4 â€¢ Incorrect load capacity % status on summary page â€¢ SMS/Alertops to test during Cx2/3 (not available during FWT) â€¢ Load current, kVAR shown out of limits range during load test with DCOS â€¢ To enquire low coolant level alarm on alarms page. (As per Rehlko, GEN only has low coolant level shutdown) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196654&prj=618&rqi=SfBX56OP5G3SIZP1QoEao512Au
WTELEC-3-002 | SL02x-2 | APAC | Closed | P3 Low CX | youngjinkim@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Multi-Discipline | system | Electrical system |  |  |  | (Cx-Elec-L5) 1ATS_M3R2_75 common alarm observed during M3 block's dead bus test. During the ATS transfer for VRFOD, a common alarm was observed temporarily. While the ATS transfered successfully, the feedback received by ATS controller was otherwise, leading to the common alarm. The alarm normalized automatically in a few min. Please check the ATS condition on site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615742&prj=450&rqi=BExt69cEohiwuDjI9zItX3KgOn | https://equinix.facilitygrid.co.uk/x/project/450/system/13552
WTMECH-9-002 | SL02x-2 | APAC | Closed | P3 Low CX | donghunsong@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | General Contractor | L5 | Missing Components | Commissioning | Multi-Discipline | system | Mechanical system |  |  |  | ( CxA-L5-MECH IST(4F)) During the UPS Room N-condition test, one SLA temperature in the UPS room exceeded 35Â°C. Therefore, the airflow limit of the relevant CRAH was increased from 80% to 100%, after which the UPS room temperature was maintained at or below 35Â°C. Confirmation from the design team is considered necessary regarding this temperature exceedance. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615105&prj=450&rqi=1JaRtfN29owQwc3q9wVU4qaOzl | https://equinix.facilitygrid.co.uk/x/project/450/system/13553
WTELEC-2-001 | SL02x-2 | APAC | Closed | P3 Low DCOS | junghohan@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Subcontractor |  | DCOS General Issue | DCOS | Multi-Discipline | system | Electrical system |  |  |  | (L5-CxA-DCOS) PUE and total IT load cannot be monitored on the DCOS dashboard graphics. The Tranche 2 IT load is not combined with the Tranche 1 value. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197512&prj=450&rqi=vSZtveT4iTOB9E0R5akJ1z25ES | https://equinix.facilitygrid.co.uk/x/project/450/system/13552
GI-103 | SL02x-2 | APAC | Closed | P3 Low DCOS | youngtaekkim@commtechasia.com | 2026-01-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | (L4-CxA-MECH) During the ICOM failure test process, a Temperature High-High alarm is being triggered due to a fault value, although it should not occur under this test condition. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196628&prj=450&rqi=h4FqaW7YQ5o8DIBfyvRsk72lDq
GI-102 | SL02x-2 | APAC | Closed | P3 Low DCOS | seungdeokseo@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | (L4-CxA-Elec) The circuit breaker status is not displayed correctly after server integration during LIB test During the Battery L4 discharge test conducted after server integration, it was observed that the UDP_E2_OUT_3 circuit breaker was closed and supplying load, but its status was not displayed correctly. After correction, it appears necessary to perform the test again to verify proper operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196320&prj=450&rqi=pI85LjfjCXd9ZtGji8SKxIfhgv
GI-050 | SL2x-F2 | APAC | Closed | P3 Low CX | youngtaekkim@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | (CxA-MECH-L3) The 4F STS RM text on DCOS is hidden by overlapping SIM text, making it unreadable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196415&prj=509&rqi=xc8q7ScmDyoEUf2qePGi5BEsXe
RT1ELEC-35-001 | SP03-P2 | AMER | Open | Outstanding Paperwork/Documentation | celso.okuyama@lzaengenharia.com.br | 2026-08-26 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | TX-PG-AUX-1.1 | TX - 480v-208/120 Transformer |  |  | GC Inspection checklist is approved on Project Portal and appended to the document section of this checklist | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635335&prj=693&rqi=os7REggOTrjhnY97iSR3NCxehP
SOR-4-001 | SV11-P2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-03-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs BMS) Fan status not working correctly at the BMS. Confirmed by Delta that the Modbus point for Fan Status (Binary) is not functioning correctly. Will need to be resolved and potentially applied to new projects as a software / firmware update. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615862&prj=624&rqi=MmtrQjTKkcT4QL1kN6GwxV0nMI
GI-135 | SV11-P2 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Incomplete Connections | Commissioning | [6 empty] | UDP-C-2 breakers C-4, 5, 6 Micrologic screens are not energized. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614731&prj=624&rqi=8198eUo3dZ4d4fTrlszRSMkpu8
GI-134 | SV11-P2 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Incomplete Connections | Commissioning | [6 empty] | UDP-C-1 breakers C-4, 5, 6 Micrologic screens are not energized. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614729&prj=624&rqi=i5MNNrRinlWYy89dl1Kzs5M6Er
GI-130 | SV11-P2 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-26 04:00:00.000 +0400 | Design Professional |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (Both Chillers C-04 and D-05) L4 If the JCI Chillers go into "Cycling Shutdown" due to leaving liquid low temperature - Full Free Cooling, while the Skid is in the process of proving, the proving process will get interrupted and the Skid will "Fail to Start". JCI Chillers always start when receiving an enable (regardless of current CHW temps), and will shut down if their CHW supply is low. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352248&prj=624&rqi=x765PmPTEeI3W85w4mv3c8zwAH
GI-129 | SV11-P2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-02-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | (All Delta CRAHs BMS) L4 Fan status not working correctly at the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352245&prj=624&rqi=1dv8CQRfYQJO86KCmkv0HbeTHE
GI-132 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-26 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (Both Chillers C-04 and D-05 BMS) L4 Cooling Tower Bypass does not properly increment open when it's setpoint is not met. Timer counts down but the valve never get's the incremented command. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352250&prj=624&rqi=7Vw3HtJMqWYly4jE3GrvTFSmUG
GI-128 | SV11-P2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-02-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | (All Delta CRAHs BMS) L4 CHWV mismatch alarm not working correctly at the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352244&prj=624&rqi=xeTzqcrE8Yb20bC2VD6euUvNEP
GI-127 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-25 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (Both Chiller Skids BMS) L5 No communication alarm comes in when comms are lost to the JCI Chiller control panel (or the Chiller is completely de-energized) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221117&prj=624&rqi=pIekWY3rVdSkQcynPQT0aZtdnv
GI-125 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-25 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | (All Chiller Skid BMS) Remove the following points at the chiller skid module on the "Chiller" layout screen on the BMS: - CHWDP - Chiller Cap | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221112&prj=624&rqi=Q7aOzSOsj6YzGwTJbeKBzfLjTs
GI-126 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-25 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (BMS general) L5 Trending graphs for Chiller Skid sensors and Delta CRAHs do not track to the specified value, no data appears. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221115&prj=624&rqi=Ksx6SdUSE9ID409ss5o41Xnko3
GI-121 | SV11-P2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (All Chiller Skids) CWP VFD would fault on overcurrent during fast restart. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199968&prj=624&rqi=tRwV1VfXQH4fsYzpZHNDWH22Ze
GI-122 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-24 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | (All Chillers BMS) When accessing the Chiller faceplate in the skid pop up from the Chiller layout button, it shows updated information. However, when accessing the skid pop up from anywhere else (Equipment control, roof layout, etc), there is information missing (DT value) and several points not matched/updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199969&prj=624&rqi=CVhCyA9eDOxJPNlP0kV9FyVkjv
GI-114 | SV11-P2 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-21 04:00:00.000 +0400 | Design Professional |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (Both Chiller Skids C-04 and D-05) L4 The categorization of multiple abnormal conditions as "Cycling Shutdowns" (0 on HOA, 0 on hardwired fault, 1 on hardwired cycling shutdown) by the JCI Chillers causes various system PLC integration issues in the following scenarios: Full Free Cooling: - Full free cooling is not available, will remove Skid from rotation - Unless loss of HOA is supplemented by the "Cycling Shutdown" bit Any other "Cycling Shutdown" condition, including loss of suction pressure transducer, loss of condenser flow, and loss of evaporator flow: - Will stay in Cycling shutdown indefinitely and not be removed from rotation - If loss of HOA is supplemented by the "Cycling Shutdown" bit to allow for full free cooling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199717&prj=624&rqi=pAl8de3NsT0PtP5t5FKuJUU4Mb
GI-109 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-20 04:00:00.000 +0400 | Design Professional |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | (Both Chiller Skids C-04 and D-05 BMS) L4 The System bypass valve will continue to climb open when flow through the skids is below minimum in the following states: - There is no run status from the CHWP - The Skid is performing an initial start-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199706&prj=624&rqi=gnw0GggCVuT8JIB6EQXniMUpHF
GI-108 | SV11-P2 | AMER | Closed | P3 Low DCOS | alec.dughi@veolia.com | 2026-02-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Chillers C-04 and D-05) L4 When values become negative (ex. evaporator / condenser approach temps) the Modbus data from Chiller to BMS goes high >6000F even though the Chiller HMI correctly displays the negative value (ex. -0.5 deg F) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199705&prj=624&rqi=Hq3zYLaVFMNxWF0X6otFWEdyQN
GI-112 | SV11-P2 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-20 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (Both Chiller Skids C-04 and D-05 BMS) L4 Faulting a running Chiller does not create the proper latching fault status in the BMS to allow for it to be successfully rotated off of. Causes the Skid enable to be constantly opened and closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199710&prj=624&rqi=ovhO1r1lSYPORAnve2u6u3TNJN
GI-104 | SV11-P2 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-20 04:00:00.000 +0400 | Design Professional |  | General Design Issue | Design |  | equipment type |  |  |  |  | (All Chillers C-04 and D-05) L4 Allowing the Chiller to cycle off of it's compressor for the purpose of full free cooling (Cycling Shutdown) does not send the expected signals (HOA status) to the BMS to allow it to stay in the CHW plant rotation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199684&prj=624&rqi=pmWRZob8qlyXuBaI4wcz10o8JB
GI-105 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-20 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | (All Chillers CH-C-04 and D-05 BMS) L4 Chiller block graphics on the BMS display a nuisance "Warning" message even when the Chiller does not present any warnings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199686&prj=624&rqi=B12Qy1yYioNEnxiVRhp8XvxE1v
GI-110 | SV11-P2 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-20 04:00:00.000 +0400 | Design Professional |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | (Both Chiller Skids C-04 and D-05) L4 Failing the CHWP on a running JCI Chiller Skid will not cause a hardwired fault status from the Chiller, so the Chiller Skid will not be faulted and removed from the rotation until the debounce timers count down (3 min total, 1 min for CHWP, 2 min for Skid). During this time, the System Bypass Valve will continue to open, eventually reaching 100% with N-1 pumps running, causing an unrecoverable building DP crash. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199707&prj=624&rqi=eXvSwM4kSJv7d4MDZ7ieOb43EQ
GI-107 | SV11-P2 | AMER | Closed | P3 Low DCOS | alec.dughi@veolia.com | 2026-02-20 04:00:00.000 +0400 | Design Professional |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Chiller Skids) L4 TST mode change center point does not track Chiller supply temperature setpoint. Currently acts based on a hard coded value written in each PLC (inaccessible). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199702&prj=624&rqi=VG7cXKJgQzDa7TCuRVT7cexfA6
GI-102 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-19 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs) L3 Valve mismatch alarm is missing from alarm summary page | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199624&prj=624&rqi=0MAEQdGivlgMRLTVqIZxWVLYbE
GI-100 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-18 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (Both Chiller Skids BMS) L3 Cooling Tower Bypass needs it's setpoint adjust added to front end BMS graphics. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199497&prj=624&rqi=oKb9AcbekojvXcPmXXDV24H2Pn
GI-099 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | (All Chiller Skid BMS) CV-02 and CV-07 graphically are colored green indicating that the valves are open but physically they are not. Those should be grey on the Chiller Skid graphics. See attached. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199383&prj=624&rqi=lxuENzvbYw1Pe9kGDpJP5UAJzc
GI-098 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-12 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | (All Chiller Skids BMS) Current (Amps) value for CWP and CHWP display as off by a factor of 10. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199145&prj=624&rqi=WeSF5JPdUzUUQ2UhRQU4SOOyDF
GI-095 | SV11-P2 | AMER | Open | P3 Low CX | nick.shawger@veolia.com | 2026-02-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Design not as specified | Design |  | equipment type |  |  |  |  | (All Chillers C-04 and D-05) L4 Chillers are throttled due to over amperage when at 90-100% load. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199097&prj=624&rqi=OnxgKrv3UGLIiezUGjpsKVp0jn
GI-091 | SV11-P2 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-11 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Chiller Skids BMS) L3 When the entire Skid has it's enable removed, the Cooling Tower enable stays activated and it continues to run, even when all other components have shut off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199093&prj=624&rqi=9T4OS7zDRWX7f3HuHjFUvZO5gR
GI-093 | SV11-P2 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-11 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Chiller Skids BMS) L3 The Chiller cycling off it's compressor due to low CHWST is treated as a hard fault by the BMS, which will remove it from the rotation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199095&prj=624&rqi=H6mLzMNmFSKnWymNhTXUd3vNvd
GI-090 | SV11-P2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | (MSB-C) MSB-C did not have appropriate UL certification stickers installed on any of the switchboard panels. Issue was identified during an external inspection and not noted during Cx testing *LESSON LEARNED* | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198935&prj=624&rqi=jstsdgEEoRA0znLH781PHk6r9K
GI-081 | SV11-P2 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (All Chillers) L3 Modbus data unable to be received from JCI control panel. BMS communication established, but no register data able to be pulled in. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198713&prj=624&rqi=w79mlxE0IjW6RlbHbOIva1PBBW
GI-084 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (All Chiller Skids BMS) L3 Graphics and control for CV-03 do not function from the BMS, works from local HMI | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198716&prj=624&rqi=IAHSf8x71HgnMP78wfrWLyvOj7
GI-085 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (All Chiller Skids BMS) L3 CV-09 (CHWP isolation) has associated graphics even though it does not exist as a control valve | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198717&prj=624&rqi=SClfY0N6j9jMHRNgkkN7OHA8ov
GI-080 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs) L3 Re-arrange required to alarm summary page graphics, should neatly represent reduced quantity of alarms that are available from the Delta CRAHs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198711&prj=624&rqi=gKzG4ypKsu2xT7Wv914GQjMxGV
GI-083 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (All Chiller Skids BMS) L3 BMS graphics show blank (% open) boxes for two-position valves. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198715&prj=624&rqi=zhvt5ZXxrJpcjVHzaA0VVEMcpV
GI-082 | SV11-P2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Design correction needed | Design |  | equipment type |  |  |  |  | (All Chillers) L3 Head pressure control not functioning, signal sent to valves from JCI panel does not correspond to minimum open percentage setpoint during Chiller operation, unit always faults on "No Condenser Flow". | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198714&prj=624&rqi=uiREwABs2RmHSEnroTRQdPW6nZ
GI-075 | SV11-P2 | AMER | Closed | P3 Low DCOS | alec.dughi@veolia.com | 2026-02-03 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs) (BMS) L3 Chilled water valve mismatch alarm is missing from Alarms page on BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198260&prj=624&rqi=lZMbUe0QpQf44Co3cTHlE3WdxP
GI-074 | SV11-P2 | AMER | Closed | P3 Low DCOS | alec.dughi@veolia.com | 2026-02-03 04:00:00.000 +0400 | Controls Contractor |  | DCOS Template Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs BMS) L3 Entering water temperature and leaving water temperature are switched in BMS faceplate. Leaving water temperature on BMS seems to be monitoring entering water temp of the CRAH (70F). Entering water temp on BMS seems to be tracking supply air temperature of the CRAH. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198259&prj=624&rqi=QFkqKducA8NUPktMkB6ObiF0VP
GI-071 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs) L3 Data Points to add: - Supply fan command (%) - Supply fan feedback (yes/no) Alarm Points to add: - Communication alarm - CHW Valve mismatch alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198155&prj=624&rqi=Bb2CRArgwFsyqAAWWlZlkjeNp5
GI-068 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS Template Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs) L3 Duct static pressure is not needed on CRAH faceplate. (+scaled incorrectly and incorrect units) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198152&prj=624&rqi=kAIw1lvY0XMy6eo8G70fpyVY2P
GI-069 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs) L3 Return Temp and Supply Temp in BMS seem to be tracking Return and Supply humidity of the actual CRAH, respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198153&prj=624&rqi=ZqfPYJ3UYXWL4UcEvWXR5ZgKqq
GI-070 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs) Graphics for Chilled Water Valve command are monitoring Fan Speed command. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198154&prj=624&rqi=zR9qQUhqPhfvngzMmVQs0MfpVk
GI-065 | SV11-P2 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-01-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | (Chiller Skid C-04 and D-05) L2B Wires terminated between load side A and B phase lugs do not allow 1" clearance over air and no barrier is present. Per UL580A c 10.2, 1" clearance over air is required for 480V applications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197700&prj=624&rqi=1PqiYBD5yCwmKhqtXLLS79JVaG
GI-063 | SV11-P2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-01-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning | [6 empty] | (CH-C-04) Refrigerant monitor exterior alert light bracket has broken off. Replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197590&prj=624&rqi=VBryODYTLSIGnvleSC4JXr3G2G
GI-062 | SV11-P2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Component/Equipment Failure | Commissioning | [6 empty] | (Electrical SKID-C) A badge reader has been knocked off its housing and is dangling by a small clip and some wires. The badge reader needs to be reinstalled correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196897&prj=624&rqi=2FXxr1erVAiqgQsanFWQF2Hi8Q
GI-060 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-01-13 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (All Delta CRAH's) Delta CRAHs do not have grouping mode. Please remove the following from the BMS faceplate graphic: Lead unit status, grouping mode status, grouping unitary demand status, group hot aisle SP, group hot aisle temp, group A/M slider. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196818&prj=624&rqi=0isfbjyXB4EMJWu6lqdVN4KgXk
GI-056 | SV11-P2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-01-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (All Chiller Skids) L3 Permant labels for CHWP breaker is currently labeled as spare. New permanent label is needed to depict the new termination. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196664&prj=624&rqi=mdhACHJ8jHhAuW10mx5mJRVhz4
SOR-272-001 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | 1MAU_R1_01 & 1MAU_B_02 CMS investigated the issue with the previously reported low flow to the Heating cooling and Dehumidifiers Hx's, found both units locked out on cooling and dehumidification modes, due to Low Pressure switch activation on the DX system, opened the liquid solenoid and checked the saturated refrigerant pressure against the pressure temperature chart using ambient temperature and the charges are found to be low in both units. CMS to schedule a resource to leak test and repair the leaks and tope up the refrigerant levels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638418&prj=479&rqi=CtdSzM3O2i3etRjKx09SeGk9Xo
SOR-271-003 | SV18-1 | AMER | Open | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | After adding the control wires, the Maintenance bypass breaker on the mimic for UPS_A3/B3/C3/D3/E3/F3/R1_3 should be added. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638021&prj=479&rqi=1ivlG4EV6rWcm9IvWLPCauWnIC
SOR-271-001 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-09-14 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | MEGA CRAH Automatic Transfer Switch Timers If the Reserve S2 fails and the utility power is available on S1 ... Currently sequence is Immediate Design requirement is a 3 second delay switching back from Reserve S2 to Utility Power S1, aligned with the intention of a minimum of 3 second break before make timer, can this be achieved with a late break auxiliary contact on a contactor, if deemed acceptable? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638018&prj=479&rqi=mG0Dme8D3F3OrDqcnpj6QpU9kt
SOR-270-005 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-09-10 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | To provide cap for all exposed terminal for power supply 24VDC at MDSB to prevent shorting and trip the control breaker. Note: Applicable for all MDSB at Skid A/E/F/B/C/D | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637589&prj=479&rqi=CClGY5RJbXQ6Y6rRIMWa7Tc1Cf
SOR-270-001 | SV18-1 | AMER | Open | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-09-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | To upgrade the STS, 800AMPS firmware for UM1 Control card to V7.0 as per the Equinix approved Firmware release Aug. 26. Applicable for block A/B/C/D/E/F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637285&prj=479&rqi=8xER8xgWQOdPenGuDzAW8Cvrvf
SOR-269-001 | SV18-1 | AMER | Ready for Verification | P1 High CX | jordan_dubose@fsttechnical.com | 2026-09-02 04:00:00.000 +0400 | Controls Contractor |  | DCIM BCM Issue | DCIM |  | equipment type |  |  |  |  | Equinix Operations is not able to see the programmed 44 (A/E/F) 1RPP_X2s on Level 2. This prevents FST from starting the primary injection testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636628&prj=479&rqi=Zn3AGvLYab70LhEVaQwcVSBisE
SOR-267-001 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Vertiv Control Panel wiring needs to be cleaned up the large coils of wiring is putting strain on the points of connection, which will lead to component failure. This has already manifested itself on 1CRAH_D_07 HMI THIS APPLIES TO ALL 36 UNITS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635881&prj=479&rqi=C1VNwMWZSMkLzSFuvEfBtC6qmY
SOR-267-002 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-08-28 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | FST observed that the 1RPP panels in Data Hall B & Data Hall F are in different locations than what is in the E130.2A & E130.2B drawings. 1RPP_F2_1_3 1RPP_F2_2_3 1RPP_F2_1_4 1RPP_F2_2_4 1RPP_F2_1_6 1RPP_F2_2_6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635912&prj=479&rqi=kIJlmzfVBgt81SliUj45vcpg3J
SOR-266-001 | SV18-1 | AMER | Ready for Verification | P1 High DCOS | jordan_dubose@fsttechnical.com | 2026-08-27 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | The breaker frame sizes in the all the blocks (A-Z and also the 2nd phase) MSB One-Lines were changed to all be 4000A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635745&prj=479&rqi=GKKf2sCjQk7CKZMwr9S8ZBKEuQ
SOR-264-004 | SV18-1 | AMER | Open | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | The SCR at Gen A was found faulted and didn't run when the GEN A was running with 1.4MW load. The fuse 4Amps at the control panel is randomly busted during the lost of utility and transfer to Generator source. Note: This is happening on Gen E and F. Cummins to revisit the size of the fuse if that is the correct size. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635098&prj=479&rqi=CPkihUUFoTH5Sp8rqvRKFaX52R
SOR-264-003 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-08-24 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | The labeling of the 1STS_A2's are incorrect in Oneline_A_UDP_PDU as it should go 1STS_A2_1, 1STS_A2_2, 1STS_A2_3, and 1STS_A2_4 from left to right to match E603.05 Drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634979&prj=479&rqi=laHnoD38mbsLLOpUTI0fyVDbMw
SOR-263-003 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Fan rubbing noise coming from the fan section of the Vertiv MEGA CRAHs, this issue applies to: 1CRAH_C_06 1CRAH_C_10 1CRAH_D_12 THE FIX APPLIES TO ALL VERTIV CRAHs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634824&prj=479&rqi=kLJhRqz1hZiBhvknEPM6pLRPtk
SOR-263-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | As found condition - buzzer active no alarms on HMI, this issue applies to units: 1CRAH_B_07 1CRAH_B_09 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634825&prj=479&rqi=toSjOtmkheg7Pewiae3JZLg08F
SOR-263-007 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | The 30 second-time delay is not deployed for the loss of utility power S1, transfer to reserve power S2, it needs to be to protect the fan motors. This applies to all Vertiv CRAH units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634847&prj=479&rqi=qiW1FHcVLxGsfNFI4txeMlYR1n
SOR-263-002 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Air Flow Sensor - not alarming when tubes are disconnected, this applies to the following units: 1CRAH_B_01 1CRAH_C_01 1CRAH_C_08 1CRAH_B_09 1CRAH_D_06 1CRAH_D_09 1CRAH_D_10 1CRAH_D_12 airflow sensor only works when one tube is connected. . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634823&prj=479&rqi=Dj8oyqYuArDq3J6t5EwH0QtJzH
SOR-263-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Vertiv MEGA CRAHs not transferring back from S2 to S1 when utility power is reinstated, thus applies to the following units 1CRAH_C_06 1CRAH_D_08 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634822&prj=479&rqi=yzDGJkduaQ8w1nKffsLdhucRZw
SOR-263-005 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Align all Vertiv MEGA CRAH - Transfer Time from S2 to S1 per agreement, reference Matrix attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634826&prj=479&rqi=OoOlTMXoR75B6eJY06LbhTzRxw
SOR-262-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-21 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | Chiller 1ACC_A_03 & 1ACC_A_04, there is an issue with the auto alarm reset function, after three unsuccessful try's the loop goes into a lock down scenario. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634679&prj=479&rqi=dD1AjBfZiyaR4NwdNiJvUHhqAz
SOR-262-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-21 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning | [6 empty] | The following Flow transmitters are generating repeater status deviation alarms on flow CWR_FT_C1 CWR_FT_C5 CWR_FT_C10 Thais needs to be investigated to determine root cause. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634673&prj=479&rqi=NQSZJ4evbxSVKB7tpjpaH2rsgl
SOR-261-003 | SV18-1 | AMER | Open | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Investigate the ON and OFF battery low alarm in the UPS_X3 Note: Applicable for 1UPS_A3/E3/F3/D3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634438&prj=479&rqi=ZFKICWKyfhkTDDOTcMWnIMIiQR
SOR-261-001 | SV18-1 | AMER | Open | P3 Low DCOS | jordan_dubose@fsttechnical.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | The 1STSs are missing a general alarm in DCOS. This was shown when 1STS_E2_4 had abnormal fan alarm locally but not in DCOS detailed in Issue 1092. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634295&prj=479&rqi=NPDIYHJq6YlKLbsRdc9XAZDch8
SOR-260-001 | SV18-1 | AMER | Open | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-18 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [6 empty] | During the event, the 20 A breaker (1UPNL_E3, L1#1) feeding the secondary source of the DMARC was found in a tripped condition. At the same time, the primary source was unavailable due to the loss of 1MSB_A during the pre-IST condition, resulting in a complete loss of communications for all equipment associated with Skid A, including MLTX_A, GEN A, and 1RMU_A. Need to re-evaluate the proper size of the breaker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634163&prj=479&rqi=9SgMfEPATa5TbWyXs5A8iOS77e
GI-104 | SV18-1 | AMER | Open | P2 Medium CX | daniel_chavez@fsttechnical.com | 2026-08-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | UPS_X3 (Mechanical UPS's) for the below skids require an expansion card in order for the MSB interface to be integrated. UPS_B_3 UPS_C_3 UPS_D_3 UPS_R1_3 UPS_A3 UPS_E3 UPS_F3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634136&prj=479&rqi=TTXrFxfhirkTCpZefHJQ8yVUu6
SOR-257-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Investigate/troubleshoot and rectify the On and Off low battery alarm for 1UPS_F3 that is showing at DCOS. The actual battery readings at HMI are normal and not showing low battery alarm at the UPS unit. However, in the DCOS is showing battery alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633723&prj=479&rqi=Hz73mapoS4HIAaHGNMrIAbeQRQ
SOR-258-001 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | The MAUs Roof FOH, 1MAU_R1_1 & 1MAU_B_2 have had numerous alarms on low chilled water flow, inhibiting the dehumidification and heating modes of operation, Suspect the chilled water strainer to units is blocked. Issue Raised on Facility Grid to investigate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633741&prj=479&rqi=zqT7ZiWyLB9CyWlUBzWfm81T8W
SOR-257-001 | SV18-1 | AMER | Open | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Investigate the missing battery voltage readings at DCOS. The reason might be the modbus register from the UPS wasn't the same with the DCOS. Note: The issue is also the same with 1UPS_A3/E3/F3/D3.- Delta needs to resolve the issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633434&prj=479&rqi=46aHrph5cRhjkyEFFkaxPsKphq
SOR-257-002 | SV18-1 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-13 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Hanley to provide the missing terminal block for breaker auxiliary contact for 1UPS_X3 Breaker input at 1MDSB_X. The breaker auxiliary contact will provide information to the UPS_X3. The missing terminal block is applicable for 1MDSB_R1/B/C/D | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633580&prj=479&rqi=VWlvhcU0r6XPKGLIOy3F07RiaY
SOR-255-007 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | The modification you rightly completed to the units to avoid drawing in FOG into the OSA air section, since this air is heated in the first section with an electric heater. The eliminator (photo for clarity is attached) is now clogging up with air borne dust. Can you please have one of your guys tidy this up so the filter can be easily removed for cleaning and/or replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632365&prj=479&rqi=O52jbvtWGXHCVPTTwRE0ZVTQxQ
SOR-255-005 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-31 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Replace the defective Phase sequence relay at 1MSB_F | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631735&prj=479&rqi=YuPckW1gAMRIvQ9zs2y7xqOjAu
SOR-255-004 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-31 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Missing Auto/Manual label at the HMI for the following. 1. 1MSB_Z 2. 1MSB_A 3. 1MSB_E Replace the phenolic label that will include the missing Auto/Manual. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631734&prj=479&rqi=9pJqDeKiMxGbXi3hvw0iyi37xI
SOR-255-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-31 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Check the loss of PM3 PQM communication with the DCOS in 1MSB_F | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631730&prj=479&rqi=FAsnx6dtQ626HilQrY5Un1WvpC
SOR-255-006 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-31 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | CMS humidifier has been attributed to High water consumption, please review the current design with a view to improve water consumption. This applies to all units | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631845&prj=479&rqi=W4sZak0T2iYiTvegModuqIT6xa
SOR-255-002 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-31 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | The maintenance mode illuminated selector switch doesn't work at IOB breaker for 1UPS_A2 and Q09 OUT TO 1LBSB at 1MSB_A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631729&prj=479&rqi=OJPn1sxUM4Y5sDiokWE0ldlXJt
SOR-254-004 | SV18-1 | AMER | Closed | P2 Medium CX | Jessie_Salita@fsttechnical.com | 2026-07-29 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Side cover canâ€™t fix at 1UDP_A1_1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631336&prj=479&rqi=snHbE6Uf4f1YmXBPlSbv1alfus
SOR-250-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | All of the TRANE heat pumps Condensate Pumps in areas A, E & F , condensate pumps discharge connection leaked on start-up- Therma repaired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630601&prj=479&rqi=kaNhSWOjkU8TD5KFLzEqkZfR4R
SOR-249-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-21 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [6 empty] | Request of information on missing indication at DCOS for input, output and MBB breaker status for 1UPS_X3. Applicable for all 1UPS_A3/E3/F3. Note: Phase 1 doesn't have also the Breaker status at 1UPS_X. It might also, apply as well. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630209&prj=479&rqi=Kpb5SfNDn7g83RyPDM2fmVL1q5
SOR-248-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | Powerhouse A "VESDA system" the UPS side of the PH: the orifice on the sniffer Pipe EOL is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630040&prj=479&rqi=UtZJn6jPfRj21QlOvPmPbLFH3m
SOR-246-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-16 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | PDU voltage monitoring to be changed: From: Phase to Neutral To: Phase to Phase. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629796&prj=479&rqi=8GBx6dZsXOWLZB8hITmpAXvdx4
SOR-246-005 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-07-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | The cover 1RPP_E1_2_5 are the incorrect size resulting in the exposure of the breakers for the branch circuits 69 and 71. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629799&prj=479&rqi=enJpdjmFuUnLbtS1rrjC3gy1Bq
SOR-242-004 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | The 1MAU_Z_01, Q11 at 1MDSB_Z1 breaker can't set the Overload Protection, to 60Amps per the Protection coordination study. The breaker was 250Amps and the minimum to set was 100Amps. Need to replace the CB to 150Amps. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628781&prj=479&rqi=DyFOMVBadHKh6Z9M7ypgV9mHyz
SOR-242-006 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-12 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [6 empty] | 1MTS_Z2_C was added recently at 1MDSB_C. In order to accommodate 1MTS_Z2_C breaker required which is 250AT, Redwood took the 250AT from 1MAU_C_3 and used to 1MTS_Z2_C. The 1MAU_C_3 transferred to 150AT breaker which was spare breaker before. It satisfies the Overload settings for 1MAU_C_3 but the short circuit and Instantaneous canâ€™t set to 2500AT which is the required setting. The minimum setting is 1500Amps only. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628783&prj=479&rqi=U1yta4BPfV8130jxFbMs14LTVA
SOR-242-007 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-12 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [6 empty] | In MPS interconnection wiring between 1MSB_X and 1UPS_X3, there was a control cable for input to PLC for 1MBB signal for 1UPS_X3. The 1MBB breakers are located in 1MDSB and 1UMDSB_X. There's no cabling between these two switchboards to 1UPS_X3 for 1MBB indication to UPS. Please advise how we can get the 1MBB input signal to PLC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628790&prj=479&rqi=3LREezzwEDEoV8xlV6zTdiL0aE
SOR-242-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | 1MTS_Z2B breaker at 1MDSB_B can't set the Overload protection to 225Amps as per Protection Coordination. The trip unit was 600AT and the minimum to set the Overload protection was 240Amps. We might replace the trip unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628780&prj=479&rqi=nNTAHk4FWmLfY1k5tzL1w8qoOx
SOR-242-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Generators All Generators vibration isolators - the bushings are damaged and needs replacing on the guide associated with this assembly. Cummins have agreed to replace all of them. Issue raised to trace to closure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628773&prj=479&rqi=mwtIahx64nr5WeVDeI8nWakpuI
SOR-241-001 | SV18-1 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Replace the failed rectifier for 1UPS_A2 that was found during the load banking. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628756&prj=479&rqi=7y3lNXZgQavUQkSkq63ic6IPIc
SOR-239-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment | Fire Alarm |  |  |  | 1. VESDA unit started and air flow-maintained constant, but unit did not normalize- programming required. 2. Install of VESDA piping at PH door diagonal to VESDA equipment is incomplete, variety of deficiencies noted: a. Pipe not glued to valve, b. Missing air cap, c. Missing valve, There is a deadline of 7/17 for the completion of this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628440&prj=479&rqi=OEf4X8XGRUUlRpDkk4uPnQoB5b
SOR-239-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment | Fire Alarm |  |  |  | 1. VESDA unit started and air flow-maintained constant, but unit did not normalize- programming required. 2. Install of VESDA piping at PH door diagonal to VESDA equipment is incomplete, variety of deficiencies noted: a. Pipe not glued to valve, b. Missing air cap, c. Missing valve, There is a deadline of 7/17 for the completion of this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628435&prj=479&rqi=rlx85mFDpzAHGao8Tcwe3UVIpk
SOR-239-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment | Fire Alarm |  |  |  | 1. VESDA unit started and air flow-maintained constant, but unit did not normalize- programming required. 2. Install of VESDA piping at PH door diagonal to VESDA equipment is incomplete, variety of deficiencies noted: a. Pipe not glued to valve, b. Missing air cap, c. Missing valve, There is a deadline of 7/17 for the completion of this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628438&prj=479&rqi=LW0WC22844XKVAvgHcWe9KO2Gp
SOR-238-001 | SV18-1 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Investigate and rectify the SCR abnormal fault alarm. Note: Applicable for the following. 1. 1STS_A2_1 2. 1STS_A2_2 3. 1STS_A2_3 4. 1STS_A2_4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628205&prj=479&rqi=mzB6DkUheYVKclcgj1zHwcE14d
SOR-236-003 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | The labels for phases are incorrect and will need to be replaced for RPP's. The labels should show A-B-C from left to right. Note: This issue is applicable to the additional 28 RPP panels added after Bulletin 1. 18 in Block C 10 in Block F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627616&prj=479&rqi=d1m2lmI5fyjNakkuiadP93hkuh
SOR-235-002 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | To transfer the cables from 1MSB_X external status of the RIB breaker to 1MDSB for 1UPS_A3/E3/F3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627571&prj=479&rqi=ivUIBAnXXLeRZTSYn32dQb4mGp
SOR-236-004 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | The motherboards in the A2/E2/F2 RPP panels on Level 2 have screws of incorrect lengths. The screws in the 44 1RPP_X2_X _X blocks below have this issue A Block: 22 E Block: 2 F Block: 20 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627627&prj=479&rqi=sH0xuLYWcLy1vBtZfslujtTZRU
SOR-235-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Current at Phase A is not showing readings while Ig showing current which is not correct.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627455&prj=479&rqi=TKXeiSaFIhsIYj4RcA410bYpfe
SOR-233-002 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-28 04:00:00.000 +0400 | TRN - Trane |  | Installation not complete | Commissioning | [6 empty] | Warning sticker missing from heat trace j-Box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627185&prj=479&rqi=GqZQUw8YO30WFwLLwJZ8qjTjnq
SOR-233-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-27 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [6 empty] | Chiller 1ACC_A_04 Chiller Pump Non-Drive Bearing noise, and today when we ran it at low RPM, we realized it has deteriorated to a point where the bearing will need to be replaced. Trane have taken to bearing details from the pump nameplate and have ordered a replacement. The work to change the bearing can be completed with the pump in situ. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627184&prj=479&rqi=hBGa8xs8nfp7mtuwtqrzh10ARB
SOR-230-004 | SV18-1 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-24 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | When simulating the Emergency Stop, the Phase Overcurrent alarm & Shutdown alarm were also initiated, and those alarms shouldn't be activated. We expect Emergency Stop to be activated. Note: Applicable for Gen A & E | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626837&prj=479&rqi=0V4i29QBwj02i9VKBl8bV0yZxG
SOR-230-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Breaker status at DCOS is not changing when breaker is Open or Closed. Note: Applicable for Gen A & E. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626834&prj=479&rqi=CGixk54ND6Ub3PSVJlm3VsvL3W
SOR-229-005 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-24 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | When simulating Emergency Stop, the Phase Overcurrent alarm & Shutdown alarm are also initiated and should not be the case. Note: Applicable for Gen A & E. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626836&prj=479&rqi=TwvJlrzCul5PsXFxpqmKkAENik
SOR-229-002 | SV18-1 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Replace the defective CT for Phase A in 1UPS_F1. Note: The defective CT was originally found in 1UPS_A1. The replacement was taken from 1UPS_F1 and installed to 1UPS_A1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626629&prj=479&rqi=D0u0U7r4i05mTXYlq5tjcU7JQC
SOR-228-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-23 04:00:00.000 +0400 | Design Professional |  | General Design Issue | Design | [6 empty] | Potential issue with the Chilled water make-up station: The check valve resides on the discharge after the bypass line on the chilled water make-up station, if it did stick closed situation may be difficult to recover. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626547&prj=479&rqi=LX8AuvaDVoKDf83e92x32TjMU6
SOR-225-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Investigate the fluctuating voltage reading from 476V to 482V from 1UDPR_C2 breaker which should be stable voltage from 1UPS_R1_01 & R1_02. The breaker voltage sensor might be an issue. The voltage IOB from 1UPS_R1_1 & 1UPS_R1_2 are stable with voltage reading of 479VAC and the voltage should be the same with 1UDPR_C2. The voltage reading at 1UDPR_C1 is the same with 1UPS_R1_1 & R1_2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625695&prj=479&rqi=eQt3jjSCbKgcQs0FcIGQsGdKDs
SOR-225-004 | SV18-1 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Replace the defective MCU card for 1UPS_A2. In order to troubleshoot and rectify the issue. Delta took MCU card the 1UPS_F2 and installed in 1UPS_A2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625698&prj=479&rqi=oZOCKsSNPhJPzBsrUxyDQ7YbcP
SOR-222-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-13 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | This week we had to split the chilled water system to facilitate chiller load bank testing. Part of the test we had to valve the headers feeding the 1CRAH_D_01 THRU 1CRAH_D_12. Since it's an open space, we left the units running to help cool down the areas. When we reinstated the chilled water system back to normal configuration, the Vertiv CRAH alarm for "loss of Cooling" alarm had to be manually reset before the units returned to normal cooling operation mode. FST think this alarm should be an auto reset. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625201&prj=479&rqi=UY7YKDYdU4ApfTpizaFC5AADme
SOR-222-003 | SV18-1 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Troubleshoot and rectify the SCR 1 SRC OVER TEMP WARNING during load banking and the load is around 780amp at 1STS_D1_4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625198&prj=479&rqi=DdZmXX439cskyR5hQwBRitam37
SOR-221-007 | SV18-1 | AMER | Open | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-06-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | 1STS_A2_1, 1STS_A2_2, 1STS_A2_3 are missing knobs on top of the A2 sets in the top hats and 1STS_ E2_3 has the missing hardware detailed below. -13 screws missing meant to secure back cover. - 8 top hats knobs either missing entirely or is missing the screw that mounts it inside the knob. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625173&prj=479&rqi=wnotxT21kq8SCq1tWTR1UkZbLx
SOR-220-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Replace the breaker from 20AT to 15AT for Heat Pump at 1PNL_R1_1_H1 feeding HP_A , E and F according to the manufacturer recommendations. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625039&prj=479&rqi=ZHHg5BeLd7v3fk20uaQf6zCFjR
SOR-217-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Provide missing power two (2) units module for 400KW for 1UPS_A3, 1UPS_E3 and F3. The installed modules are good for 300KW. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624353&prj=479&rqi=0efwRHfYffmB398x03eX9aLmeF
GI-102 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-05 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [6 empty] | p3E-Tech surveyed leak Detection tape located in PHs A, E, F: MPS-installed leak tape is missing the EOL (â€œEnd of Lineâ€) terminators for all of the sense lines in these PHs. Issue raised on facility Grid to Track to completion. E-Tech can install when parts are received from MPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624162&prj=479&rqi=jDQQvyC8XGNYJWIHeA5pDisi0P
SOR-215-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | To find the missing wire for SKRU release signal. The wire 2015 & 2016 are terminated at 1MSB but on UPS terminal, the wires can't be found. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624192&prj=479&rqi=KoXw1FIl8sXGc7aMjmH8GIxUTu
SOR-214-001 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-06-04 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | The LTD settings of the PRX10 LSI trip units in the Eaton breakers in 1UDP_A1_1., 1UDP_A1_2, 1UDP_E1_1, 1UDP_E1_2, 1UDP_F1_1, and 1UDP_F1_2 are fixed and cannot be adjusted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623970&prj=479&rqi=G2UJe60DkniU2EpFbcOvdQIvPo
SOR-213-002 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-04 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [6 empty] | Provide missing settings for 1UDP's_A1_1/2; 1UDP_E1_1/2; 1UDP_F1_1/2.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623877&prj=479&rqi=A9qsG6NcKbdBBmFUefKmPzldwe
SOR-213-001 | SV18-1 | AMER | Closed | P2 Medium CX | jordan_dubose@fsttechnical.com | 2026-06-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1RPP_F2_1_2 | RPP - Remote Power Panel |  | RPP-208-250-60 | The 1RPP_F2_1_2 is missing the lug cover. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623861&prj=479&rqi=Ufn6RAXGQDTiN46hvoCsNsuOAD
SOR-211-006 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-02 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Replace the defective CAT6 cable for gateway 2 to switch at 1MSB_A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623581&prj=479&rqi=L20Ai1WxGTVqLNzJN0JhuQ6qmH
SOR-212-001 | SV18-1 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | The door is difficult to open at skid R1 front left door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623713&prj=479&rqi=4BHNPT8HnOp0EH2A0axBATM0XG
SOR-256-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-01 04:00:00.000 +0400 | TRN - Trane |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Minor damage to Armaflex Insulation Damage, Needs Patched. Applies to Chillers 1ACC_E_19 1ACC_E_20 1ACC_F_22 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623540&prj=479&rqi=lZSpQeTK5VykMwvzwCAUIFt22e
SOR-211-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-01 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [6 empty] | Powerhouse F: 1CRAH_F_15 SV18.1RLEM_F_LEAK_15 Leak Detected - Leak detection in alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623577&prj=479&rqi=wGlUeJd3lIBVuNcxWsRZisgDdM
SOR-211-002 | SV18-1 | AMER | Open | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-06-01 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Labelling | Commissioning |  | equipment type |  |  |  |  | The labelling for the Q#'s of 1MSB_A/E/F is different in the SV18-2 submittal than in the engineering drawings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623567&prj=479&rqi=qEYQEpl3a5U1UTm0gAdKjX2pDt
SOR-211-003 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-06-01 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Engine hours at the local HMI are not the same with the DCOS. Information for both should match. This is applicable for the following. 1. GEN B 2. GEN C 3. GEN D 4. GEN R1 5. GEN Z | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623572&prj=479&rqi=OcTyxUi73LAZhwkJY0KUr4OI5S
SOR-211-001 | SV18-1 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | The door is difficult to open at skid D front left door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623554&prj=479&rqi=QjrGcntQ2BPanaJbcS6a1S36y4
SOR-210-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Provide the connecting bar for Transformer tap 4-5 to compensate the voltage drop on Transformer output. Provide- 48 pieces. 1PDU_B2_4 1PDU_C1_4 1PDU_D1_4 1PDU_D2_4 1PDU_E1_1 1PDU_E1_2 1PDU_E1_3 1PDU_E1_4 1PDU_F1_1 1PDU_F1_2 1PDU_F1_3 1PDU_F1_4 1PDU_A1_1 1PDU_A1_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623488&prj=479&rqi=Eu34JauNYeooo2Ntq4J3RAdlSO
SOR-209-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Provide the missing Ethernet cable for the following. 1. 1HP_A_1 and 2 2. 1HP_E_1 and 2 3. 1HP_F_1 and 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623393&prj=479&rqi=OWKOUG8mTyWsvaDdo8SELS3fsa
SOR-208-001 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1RPP_C2_2_2 | RPP - Remote Power Panel |  | RPP-208-250-60 | There is a damaged door in RPP_C2_2_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623240&prj=479&rqi=QOa0f0MiN1yaU83OxIepwTFRqh
SOR-207-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | The clearance of 1â€ phase to phase wasn't maintain for B & C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623150&prj=479&rqi=nf35Zmu9xHgZN8KyKXED6Z7Smp
SOR-206-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-25 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [6 empty] | To provide new updated setting to reflect the breaker model Square D instead of ABB for the following PDU's 1. 1PDU_A1_1. 2. 1PDU_ A1_2, 3. 1PDU_A1_3 4. 1PDU_ A1_4. 5. 1PDU_E1_1 6. 1PDU_E1_2 7. 1PDU_E1_3 8. 1PDU_E1_4 9. 1PDU_F1_3 10. 1PDU_F1_4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623058&prj=479&rqi=kglZs8PPSQlX39lxbNUCQp1AKV
SOR-206-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-22 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [6 empty] | Provide missing protection settings for the following. 1PDU_B2_4 1STS_B2_4 1STS_C1_4 1PDU_C1_4 1STS_D1_4 1PDU_D1_4 1STS_D2_4 1PDU_D2_4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622857&prj=479&rqi=irrsSdXroGL4LMtPErXMikBMe1
SOR-206-002 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-22 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [6 empty] | Provide missing protection settings for the following. 1UTX-F3-L1 1UTX_A3_L1 1UTX_E3_L1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622879&prj=479&rqi=3QvEBBhx4m6wiVDdm98tJOmtY7
SOR-201-002 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-05-16 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  | system | CHW System |  |  |  | The following Chilled Water Riser, Onicon flowmeters need to be replaced FT401 FT601 FT903 As they are reading outside of the 10% range. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622028&prj=479&rqi=ezDfjarNF8GQaCmM5NG4M1EfyU | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-200-001 | SV18-1 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-14 04:00:00.000 +0400 | Equinix Ops |  | DCIM BCM Issue | DCIM | [6 empty] | Tested all the CTs (100% with 72 CT's) for each panel and found sensor 37 to 42 doesn't show current readings in BCM. This is consistent to all 18 panels. Completed as follow's 1RPP_B1_1_1 1RPP_B1_1_2 1RPP_B1_1_3 1RPP_B1_1_5 1RPP_B1_1_6 1RPP_B1_1_7 1RPP_B1_2_1 1RPP_B1_2_2 1RPP_B1_2_3 1RPP_B1_2_4 1RPP_B1_2_5 1RPP_B1_2_6 1RPP_B1_2_7 1RPP_B1_3_1 1RPP_B1_3_2 1RPP_B1_3_3 1RPP_B1_3_5 1RPP_B1_3_6 1RPP_B1_3_7 1RPP_C2_1_1 1RPP_C2_1_2 1RPP_C2_1_3 1RPP_C2_1_4 1RPP_C2_1_5 1RPP_C2_1_6 1RPP_C2_2_1 1RPP_C2_2_2 1RPP_C2_2_3 1RPP_C2_2_4 1RPP_C2_2_5 1RPP_C2_2_6 1RPP_C2_3_1 1RPP_C2_3_2 1RPP_C2_3_3 1RPP_C2_3_4 1RPP_C2_3_5 1RPP_C2_3_6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621917&prj=479&rqi=dLJTpIyr9FODvWAjSF4EuY3gCx
SOR-195-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-08 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Replace the breaker 2/0 to 350 lugs to 14 to 1/0 lugs to fit the 2AWG that was pulled for 1UTX load at 1UMDSB_A3/E3/F3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621010&prj=479&rqi=5W2hUZwVUOSbytonKLEBPQFW6F
SOR-193-002 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | FST observed that they are several screws in the different 1PDUs that are stripped. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620627&prj=479&rqi=hwPhUC9BHl6Qs6TlyO43ApE93E
SOR-187-004 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Incomplete Connections | Commissioning |  | equipment type |  |  |  |  | Perform neutral connection modifications to all STS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619816&prj=479&rqi=stxPtDjlUSFLtna8YIL00OgRAB
GI-094 | SV18-1 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-04-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Generator Output Breaker is missing the K1 kirk key and cylinder. K1 Serial Number is 64393. This is applicable to GEN_A, GEN_E, & GEN_F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619964&prj=479&rqi=QyCwjTdGLcl0njUV5Qg1zrhcGS
SOR-187-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Bolts missing on the following units: 1CRAH_D_12 1CRAH_D_10 1CRAH_D_09 1CRAH_D_05 1CRAH_D_04 1CRAH_D_02 1CRAH_C_10 1CRAH_C_09 1CRAH_C_08 1CRAH_C_07 1CRAH_C_04 1CRAH_C_03 1CRAH_B_01 1CRAH_B_02 1CRAH_B_03 1CRAH_B_04 1CRAH_B_07 1CRAH_B_08 1CRAH_B_09 1CRAH_B_10 1CRAH_B_11 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619805&prj=479&rqi=1FvcvsH3kPo9snEiSTAPGo6ad6
SOR-187-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Provide missing parts for breaker key interlock. 1. Missing TABS for breaker drum kirk key Gen A/E/F 2. To provide whole set of kirk key for Gen A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619793&prj=479&rqi=3Ya2f5n3oAaB9YTKd6HpvNgLVI
SOR-186-003 | SV18-1 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | To perform the neutral modification for STS to meet Equinix standard. Applicable for all STS for Block A/E/F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619661&prj=479&rqi=6pxePsvNjfzq1CXmdDfKNKhAkl
SOR-186-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Power Houses A, E & F Heat Pump - Smoke Detector Circuit: The power wire at the smoke detectors at the Trane WSHPs has not been pulled. Currently they have only pulled the control wiring that shuts the units down. See Attached Photo's for clarity | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619586&prj=479&rqi=Fi5qvdSKdxqx6t6h7rydye30UT
SOR-186-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-27 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Power Houses A, E & F - Trane Heat Pumps Trane representative reviewed the panel wiring and discovered the units have been set up for BACnet so they will need a gateway to change the protocol, issue raised in facility grid to track this to closure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619646&prj=479&rqi=atcUOVwwJlj9tux1T0yUVkmqnb
SOR-183-002 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | Two ceiling junction boxes in Skid K are incomplete and/or not labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619421&prj=479&rqi=wmM8EWJyQV2WMKromY1jlY94hC
SOR-183-001 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | In 1MSB_K there are missing bonding cables to ground the top hats in the sections 05A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619372&prj=479&rqi=lgcboVxOwFiKbd4zS9fLxBXYyn
SOR-181-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1RPP_C2_3_2 | RPP - Remote Power Panel |  | RPP-208-250-60 | To provide the missing bar and bolts connecting to the main incoming cable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619258&prj=479&rqi=OHxx0vp2BX4TSZBrpQHg8gALMv
SOR-182-002 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-23 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not complete | Commissioning | [6 empty] | In 1UDP_K2 the lugs for the termination to 1STS_K2_3 in BKR#4 are incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619277&prj=479&rqi=Vk31X2vfLCAcrLg67asiGQ2ykJ
SOR-182-001 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-23 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning | [6 empty] | In 1MDSB_K the lugs are not correct for the 1PNL_K_HP_BKR & 1UPS_K3_BKR terminations. Hanley to send (3) lugs for #1/0awg to support the 1PNL_K_HP_BKR and (6) lugs for 3 #500kcmil to support the 1UPS_K3_BKR | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619274&prj=479&rqi=u3SFglqF2nPdziQiqI6g4pi6xj
GI-092 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-04-22 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS | [6 empty] | topserver is reflecting several errors & warnings & hundreds of connections | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619142&prj=479&rqi=TcmA7jrpYEOh2CjSnFLS2HmzxG
GI-091 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-04-22 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS | [6 empty] | aalogmonitor is still showing errors and warnings in the platform | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619141&prj=479&rqi=7U3Qx2NlNJB6Ps58Cp5br8ICqJ
SOR-180-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-22 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Provide missing SKRU key (K7 & K8) for 1MSB_A for 1UPS's. 1. 1UPS_A1- 3 pieces 2. 1UPS_A2- 3 pieces K7 Serial Number is 64155. K8 Serial Number is 64156. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619146&prj=479&rqi=sfCGP9RAuCbnNdPzk6eyws7OHu
SOR-180-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-22 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Provide missing SKRU key (K3) at 1UMDSB_A3/E3/F3 for UPS_A3/E3/F3. K3 Serial Number is 6440 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619148&prj=479&rqi=3Zp67zvIiBh3wdN3cuXMdET1QE
GI-088 | SV18-1 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | On Powerhouse Skid A; Door B does not fully close/latch. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618917&prj=479&rqi=xwG7zOgXSL3zA6gt1pJBsglmmU
GI-090 | SV18-1 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | On Power Skid E; the Mortise/Cassette has a short/blown security panel fuse. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618919&prj=479&rqi=3yj3h97TeIISWdPT3lqqLaXSwj
SOR-179-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-21 04:00:00.000 +0400 | TRN - Trane |  | Installation not complete | Commissioning | [6 empty] | Chiller ball valve plugs missing issue raised on Facility Grid. Chiller C_12 Supply BV Drain Plug Missing. Chiller D_18 _ 2 X Pump & Suction Diffuser drain Plugs. Chiller R1_01 Suction Diffuser Drain Plug Missing. Chiller R1_01 Supply BV Drain Plug Missing. Chiller R1_02 Supply BV Drain Plug Missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618913&prj=479&rqi=edloPhvEdRgHKLUdAySSFiShlu
SOR-179-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-21 04:00:00.000 +0400 | TRN - Trane |  | Installation Damage | Commissioning | [6 empty] | Armaflex insultation on chiller pumps, needs protection from UV light, it would need to be covered/Jacketed or painted. see attached photo the damage is already occurring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618915&prj=479&rqi=IRfNQGkiJbj93jfZ4BXGt7Jk1j
GI-089 | SV18-1 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | On Powerhouse Skid A; Door D does not fully close/latch. Furthermore, the door is not level. The door contact was removed to prevent further damage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618918&prj=479&rqi=6dUIAjFOAhRnqzUp6wviDO2QHo
SOR-178-006 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [6 empty] | Chiller 1ACC_D_18 Chiller failed on phase loss during IST. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618781&prj=479&rqi=Hegg8Qbx90eXWutRqAZ7Hi2LAp
SOR-178-003 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning | [6 empty] | The mechanical lugs for 1UMDSB_X3 terminations to Q09 in the 1MDSB_X are incorrect in skids A, E, & F. Six (6) lugs are for the (2) #500kcmil wiring. Six (6) lugs are for the needed for (2) #2/0 ground. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618778&prj=479&rqi=IaBIpJdSi2vBtOGDsCguPRdcXs
SOR-178-001 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning | [6 empty] | 1UMDSB_A3 has mismatching lugs as they have 3/0 - 350kcmil lugs installed but need lugs to support 3 #2 & 1 #8G, 1-1/4"C wiring for the 1UMDSB_A3 to the 1UTX_A3_L1 breaker. Three (3) lugs are needed for the #2 wiring. One (1) lug is needed for the #8 ground. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618776&prj=479&rqi=epGhC0WBETYsNmF5aPtlB27Ma1
SOR-178-005 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [6 empty] | Chiller 1ACC_C_12 failed following UPS power loss testing. Both control fuses located in the harmonic filter housing and fuses feed the main controls circuit; they blew with the inrush current. there are two sets in series 15 amps in the harmonic filter & 10amp in the power panel. TRANE have agreed to upgrade the 10-amp fuses to 15amp. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618780&prj=479&rqi=QLtDApxpKKzstnRS45nCuc37Te
SOR-178-002 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning | [6 empty] | The mechanical lugs for 1PNL_GEN_X terminations to Q04 in the 1MDSB_X are incorrect in skids A, E, & F. Nine (9) lugs are needed for the #4 wiring. Three (3) lugs are needed to support the #8 ground. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618777&prj=479&rqi=JkmANuywqi69ncQJJEKSn9ysOI
SOR-178-004 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | [6 empty] | The current 1PNL_X_HP_BKR in the 1MDSBs in Blocks A, E & F has only LSG ground protection and not the LSIG ground protection required in both the Hanley submittal and engineering drawings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618779&prj=479&rqi=DaL1z0XEe4byEJedNiOzR7DmZW
SOR-170-004 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-04-19 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | To remove the "Heat Traced" alarm from the General alarm through the hardwire from Chiller control to RIO panel. This is preventing the Chiller lockout every time there was a momentarily loss of supply voltage to the "Heat Traced" circuit which is non-UPS source. Separate the Heat Traced alarm by pulling new cable from Chiller control panel to I/O input at the RIO panel. Etech will program the additional input for DCOS. Note: Applicable for all Chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618674&prj=479&rqi=uU7o20suTicZLkAf59N2ZRK56D
SOR-176-013 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [6 empty] | MV-1 & MV-2 Power Houses - Air conditioning units Graphic need to be deployed. This issue applies to the following units: 1SUDB3_AC_1: MV-1 North Yard. 1SUDB3_AC_1: MV-1 North Yard. 1SUDB1_AC_1: MV-2 South Yard. 1SUDB1_AC_2: MV-2 South Yard. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618615&prj=479&rqi=6ARHYaYlmwM0RmuhOaueAi2ATv
SOR-176-012 | SV18-1 | AMER | Closed | P2 Medium CX | James_Kenny@fsttechnical.com | 2026-04-18 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | This one applies to all TRANE chillers The location of the Thermal Dispersion is not ideal as these switches respond better to laminar flow as opposed to turbulent flow. Chiller manufacturers use Tube Grooving to Improve Heat Transfer The use of grooved copper tubes in chiller systems is a method to enhance heat transfer efficiency. Grooves can induce a swirling motion in the fluid, which helps to displace the fluid and increase the heat transfer rate. This technique is effective when the Reynolds number is between 500 and 5000, as it can lead to a significant increase in heat transfer capacity. The grooved design is particularly beneficial in heat exchangers where the goal is to maximize thermal energy transfer between fluids. The thermal dispersion switch is installed right at the end of the tube bundle, this switch is sensitive the turbulence, please review. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618604&prj=479&rqi=q7kfXuF9SlUZ0xXgOtlVdvn6Pe
SOR-176-011 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | MAU_D_4 Smoke detection alarm test | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618603&prj=479&rqi=oZDETFoWohbAtZ6BAJjdw11ECF
SOR-174-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | To investigate the current harmonic on B-phase of Rectifier input is high in comparison with phase A & C. The 9.09% current harmonic in phase B is the total for two units of UPS. Phase A & C have almost the same harmonic value of 1.5% average. Take note that we applied 1100KW each UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618587&prj=479&rqi=C45NTEzOIIRaBHZyNMKShu1max
SOR-176-010 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-17 04:00:00.000 +0400 | Subcontractor |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | MPS to resolve why Skid D Heat Pumps are not responding to their corresponding room thermostats | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618601&prj=479&rqi=qSfBDlM8nlnHteY2rvUXAY7k6n
SOR-176-009 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-04-17 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | The SF6 alarms for Breakers and other compartment wasn't able to get the alarms in DCOS at 1SUDB_2. Schneider will need to verify the Modbus register to match with DCOS. The SF6 alarms is assumed to be the same issue in 1SUDB_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618599&prj=479&rqi=4bJa5u95nquDArsaxcTXOgTdqX
GI-087 | SV18-1 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Provide the materials the was taken from STS _F2_1 for the replacement of damaged components for 1STS_D2_3. As follow's. 1. Control cables. 2. Set of control breakers strip. 3. Electronic Modules (Oumar from Delta knows the model. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618602&prj=479&rqi=WrxPTCcdTCoZIjVhhRGE1pTLzh
SOR-173-002 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Investigate the tripped occurred on the breaker 60AT feeding 1TX_R1_2_R1 at SKID R1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618265&prj=479&rqi=btb7vMEy9UCJrmqB85adrgwUCz
SOR-174-002 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | The humidifier sump has gone numerous times into drain down mode, since these units are fed by softened water so the conductivity probe may not be readying reliably, please have your technician check this out to verify the proper functionality. This applies to MAU_R1_01, MAU_B_2, MAU_C_3, & MAU_D_4. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618293&prj=479&rqi=vcNfuGaAXQMKS5EzxZz3B0k2hG
SOR-173-001 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [6 empty] | 1ACC_R1_02 Compressor 3 Fault - Compressor failed The compressor failed the bearing levitation recalibration tests. The chiller sub cooler circuit the liquid solenoid valve & EXV were creating a lot of noise/hammer, it was found the chillers number 3 compressor was running with the suction isolation valve closed, due to an actuator fault. Tech support asked the Trane service engineer to isolate the compressor for troubleshooting tomorrow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618182&prj=479&rqi=z7EFBwaeY26H1n1QwADQIXFFoC
SOR-172-004 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning | [6 empty] | Skid D Heat Pumps are not responding to the thermostats. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618007&prj=479&rqi=gskLi5KjAKM4GMhn9sp2z4jxDG
GI-086 | SV18-1 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-04-11 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning | [6 empty] | Control board was taken from one of the 1st floor MEGA CRAH units. Note that the asset nomenclature has not yet been identified for this unit, but the serial number for this unit is T26C006449. This was to resolve Issue #762. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617874&prj=479&rqi=A9V6lQRJjGe6dRf2M5IOIRnMVt
SOR-170-001 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-10 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS | [6 empty] | In DCOS the "Electrical" screen cuts off the kW values for the PDUs on the right side of the screen. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617828&prj=479&rqi=W47zpya1FcDwzbll7IKA0l2HKa
SOR-169-003 | SV18-1 | AMER | Closed | P2 Medium CX | James_Kenny@fsttechnical.com | 2026-04-10 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | A T3C A78 General Heaters Protection Alarm notification associated with loss of Heat Trace activated during power transfers for the following units: ACC_B_07 ACC_D_17 ACC_R1_01 ACC_R1_02 If the chiller is in idle mode, this alarm caused the chillers to lock out on DCOS. To avoid a reoccurrence of this issue this point need to be changed to a monitored point. TRANE to provide information on how they recommend the points to be managed, this is required for the associated RFI | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617786&prj=479&rqi=wZTLELACJk7cPc1ENTC835y6Vy
SOR-168-007 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-09 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [6 empty] | PRE-IST 1ACC_R1_02 FAILED ON MOTOR BEARING ALARM | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617632&prj=479&rqi=FANLJnOmEDMGs56bYjqLtziL1I
SOR-168-006 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-09 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [6 empty] | PRE-IST TESTING CHILLER 1ACC_C_11 FAILED ON LOW FLOW | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617631&prj=479&rqi=zxkiAZYYGYT77UYQEkGtd20ij7
SOR-166-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [6 empty] | PRE-IST TESTING Chiller 1ACC_R1_02 FAILED ON LOW FLOW DURING BLOCK R UTILITY POWER TRANSFER TO GENERATOR | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617522&prj=479&rqi=eK2Mx0kr93UcAEjjy38yjhLrVc
SOR-166-006 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [6 empty] | PRE IST TESTING Chiller 1ACC_B_08 FAILED ON LOW FLOW THROUGH NORMAL OPERATION | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617525&prj=479&rqi=1buFPYuNpNVCH1etIVWR59Nhk0
SOR-166-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [6 empty] | PRE IST TESTING Chiller 1ACC_C_11 FAILED ON LOW FLOW THROUGH BEING SEQUENCED ONLINE | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617523&prj=479&rqi=UxNWgEVJpbzHaDhdD7Sjm4NSd6
SOR-166-009 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | PRE-IST TESTING Chiller plant manager dialed up to the sequencer all 18 chillers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617528&prj=479&rqi=ZNb6xZrjRRagNVsahb6SDwxKm2
SOR-166-007 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning | [6 empty] | PRE IST TESTING Chiller 1ACC_B_08 CHILLER PLANT MANAGER DIDNT RESET IT | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617526&prj=479&rqi=zyZm2pMYIfXbGjq3eXiWEVsZAa
SOR-166-008 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [6 empty] | PRE IST TESTING Chiller 1ACC_B_08 FAILED ON LOW FLOW FOLLOWING BEING RESET AND RESTARTED & THROUGH BEING SEQUENCED ONLINE | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617527&prj=479&rqi=7rRLLpuqG5UbVccsLpbUEarc7h
SOR-166-010 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | MAU's depict wrongly 2 supply fans There is one supply and one return Fan | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617564&prj=479&rqi=IUf9qOPOTGSVHF0TbpiFAavCP2
SOR-166-005 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | TRN - Trane |  | Commissioning Issue | Commissioning | [6 empty] | PRE IST TESTING Chiller 1ACC_C_12 FAILED ON LOW FLOW THROUGH BEING SEQUENCED ONLINE | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617524&prj=479&rqi=yyyZh9LGjUKM9JMk7q4vEGqKBb
SOR-166-002 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | 1UPS_D3 is not communicating with the DCOS/BMS. Delta will need to investigate as E Tech confirmed they are not able to ping it. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617475&prj=479&rqi=cip6Mc3uFwOSZJBpRB58t22ZBi
GI-085 | SV18-1 | AMER | Closed | P1 High CX | daniel_chavez@fsttechnical.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1RPP_B1_2_5 | RPP - Remote Power Panel |  | RPP-208-250-60 | A hot spot was discovered during load bank testing on RPP_B1_2_5 panel bussing. Refer to attach photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617460&prj=479&rqi=LZHAGMVETj0jXRTdGGUhBzTu5F
SOR-165-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Alarm Screen Shots for Data Hall H including Mega CRAHs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617382&prj=479&rqi=piP5ieCiiRhAlreVHCqR95aA3I
SOR-165-007 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | The Block A, E, & F 1BATT cabinets are missing batteries. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617388&prj=479&rqi=momeL777ZY6fsGIt32TigkvWga
SOR-165-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Alarm Screen shots for Data Hall B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617364&prj=479&rqi=bSJGpA5PNjmWAWEPVeoNPb5Ayi
SOR-165-006 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Alarm Screen Shots for the Chilled Water System | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617386&prj=479&rqi=spQOF28Nk9zR7xJ60ipAEQ4w34
SOR-165-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Alarm Screen Shots for DH D and associated Mega CRAH units | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617383&prj=479&rqi=wqHIwV1czr6LaQeZmHKZjSHNy7
SOR-165-005 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Alarm screen shots for DATA HALL F + Mega CRAHs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617384&prj=479&rqi=6fgzNGuv3D0HXT9Ns8US3EFena
SOR-165-008 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Delta CRAHs - Powerhouse Issues | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617389&prj=479&rqi=FXq9tI5Z3htM5OwV9D6FFAE7TD
SOR-163-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | 1MAU_C_3 Alarm on Low Pressure Limit Switch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617245&prj=479&rqi=uDtG5GdBvs45HBHGgn60FAwWuZ
SOR-162-001 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-04-02 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Clear alarms for GEN R1, Z and B. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617157&prj=479&rqi=OCzxMSryFtC3s82ThhFzYRnNAI
SOR-158-010 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-01 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [6 empty] | Freeze Protect valve on chiller 1ACC_R1_02, appeared to respond slower that the valves on the other chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617099&prj=479&rqi=xxmKjuzQIqPxUFi3lIJ54nMPOg
SOR-161-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-01 04:00:00.000 +0400 | Design Professional |  | General Design Issue | Design | [6 empty] | There was no information where to get the UPS source for 1MSB_A/E/F feeding the controls as per Hanley submittal. DLB should provide direction what 1STS to use for feeding the 1MSB_A/E/F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617095&prj=479&rqi=493M4zz17mgy3B1DbuLNeXf59d
SOR-158-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  | system | CHW System |  |  |  | Chiller Transfer from Utility Power to Generator Power testing 1ACC_R1_01 & 1ACC_R1_02 failed on DCOS as the plc did not capture the power loss event and apply the 30 seconds delay on the external chiller alarm for phase loss. Without phase loss event capture the plc thinks it's in normal mode and will alarm and latch any alarm from external source. Trane troubleshooted the issue with tech support and lessons learned from DC22, they found that the phase loss relay was wired incorrectly to the normally closed contact on the phase loss relay. Trane corrected this and set the voltage to 480V. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616914&prj=479&rqi=yGllLg4CK8STHd9YqK8SOp4e9q | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-158-008 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | All energized Equipment should have While Line background to indicate that were energized. This is applicable for all 1MSB's.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616973&prj=479&rqi=NFlKV5BimXn2iHlIZQNqxiNwrg
SOR-158-004 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS | [6 empty] | E-Tech to include the Bard Units in the DCOS at MV1 and MV2 for monitoring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616960&prj=479&rqi=UzTwv1qHOEhglG7BTFK7DEAutz
GI-081 | SV18-1 | AMER | Closed | P1 High CX | daniel_chavez@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Washer discovered in MSB_A lineup, located in the 1BB_LB cabinet, far back against the bussing. Refer to attached photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616985&prj=479&rqi=sPb7q9PWIsDVAt2gnf7kxFfx7B
SOR-158-009 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Leak Detector LD2100 RLE controller from MPS found not communicating to BMS/DCOS and needs to be replaced. Powerhouse D | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616984&prj=479&rqi=ff5zNDFdG4k4DCSaO6l9KOmqVP
SOR-158-007 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | I noticed that every day we are losing communication for all the equipment and come back in. Then your need to come back for each equipment's to clear the alarms. Could you please investigate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616971&prj=479&rqi=8lEVGZK37wT2uEHeOYoh7KpSTw
SOR-156-002 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-03-28 04:00:00.000 +0400 | Subcontractor |  | Installation not correct | Commissioning | [6 empty] | Rectify the loss of communication for Leak Detection for the following. 2. Clear all the alarms. 3. Level 1 & 2 FOH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616760&prj=479&rqi=MJ0pu6VALPDvfyYsDpbR65lS9l
SOR-156-003 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-03-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | The SCR Common Alarm is active on 1GEN_B, 1GEN_R1 & 1GEN_Z. E Tech is to troubleshoot and resolve. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616762&prj=479&rqi=K7hwxSLnfUxkHYbtT5TDgijHGr
SOR-155-001 | SV18-1 | AMER | Open | P2 Medium CX | jordan_dubose@fsttechnical.com | 2026-03-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | The Carrier Heat Pumps natively speak BAC-NET communications to the BMS system at Equinixâ€™s SV18 facility. However these units will require BAC-NET gateways to allow proper communication to this BMS system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616631&prj=479&rqi=2mdLxJINXH9S7KvhXogWFgbn8U
SOR-155-002 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-03-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Duplicate of issues 661-677. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616632&prj=479&rqi=c4RRtmJHsM3fpSa9twdA1DYuBi
SOR-154-004 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-03-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | The exhaust fan didn't energize, and damper didn't open during the simulation of battery temperature rise for UPS's for PH D and R1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616472&prj=479&rqi=1H80yl5uyzdwPcYrQRtJKvnznW
SOR-151-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-24 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not correct | Commissioning |  | system | CHW System |  |  |  | Riser 4 and riser 9, when all other risers were closed, we had a no flow condition on the riser suggesting the bypass is closed, needs to be cracked open for corrosion protection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616272&prj=479&rqi=5Duiwpd2Mmv8gDSguNhwqBNkGC | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-151-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-24 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not complete | Commissioning |  | system | CHW System |  |  |  | Riser 1 & 6 was using 600 gpm cooling; issue raised on facility grid to track to closure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616270&prj=479&rqi=QIu3Yg0GxoYAbJhGNz9ksESX7N | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-149-002 | SV18-1 | AMER | Closed | P2 Medium CX | James_Kenny@fsttechnical.com | 2026-03-22 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning |  | system | CHW System |  |  |  | Chilled water - Chiller flowmeter to riser flowmeter alignment - CDU risers 1 & 6, 4 & 9 Pressure control valves, not available to view or operate on the DCOS graphic, | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616136&prj=479&rqi=QNTfzJvdwpcccDlx9Vh270tnVD | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-149-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-21 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Issues with Utility Power Loss and transfer to generator for all Trane Chillers, Issue raised on facility Grid and Trane contacted in this regard. See attached report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616135&prj=479&rqi=Q2BNnZie5sTj65USgqPK6DnJRz
SOR-148-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Humidifier Piping, from pump to humidifier needs to be supported. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616058&prj=479&rqi=W7CrS2mSACAYekRNuiBboxhXhS
SOR-147-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [6 empty] | Currently the chiller sequencer does not react appropriately staging down and there have been a number of chiller failures as a result. When the load on HVAC equipment associated with the chilled water distribution loop drops off the sequencer doesn't react quickly enough as the valve close so does the flow path the chillers run at minimum flow and fail when flow is reduced further. This issue can be resolved by implementing the low flow control strategy, where the recharge valve is brought online to maintain minimum flow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615992&prj=479&rqi=nuY5SDCpByYTOcUrP3vInP5rwr
SOR-147-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Equinix engineering and design team, need us to isolate one riser and one chiller at a time run the chiller into the riser, the reason for this exercise is to match the chiller flow to the riser flowmeter as it seems there is a very large error between the two. This procedure will take place when Leo is finished load banking. Detail to follow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616013&prj=479&rqi=6xVqfwqRH2xLNfJZtn0lVMa2lM
GI-078 | SV18-1 | AMER | Closed | P3 Low CX | Rangsiya_Faihin@fsttechnical.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | The internal connection cable labeling for the battery cabinets is not consistent with the MPS.322 submittal. As shown on the attached page, the red boxes highlight the field-observed conditions. Please re-assign this item to the appropriate responsible party if needed. UPS_R2_2 & UPS_R2_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615834&prj=479&rqi=takl1JrJrYSwWghumUF5NTCIvv
GI-077 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Buttons without filler color once they are selected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615774&prj=479&rqi=44xdqoZKdT3KM9U3g4b2BashEn
SOR-139-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | All Make-up Air handling units need to have droplet eliminators installed after on the inlet air hood of the unit, to deal with ambient fog conditions outside. Applies to the following: 1MAU_R1_01 1MAU_B_02 1MAU_C_03 1MAU_D_04 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615320&prj=479&rqi=HIlR6kFGRUH27MTPhS1IffDCqS
SOR-101-008 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-09 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [6 empty] | RESULTS OF SURVEY CONDUCTED BY THERMA TAB ON ALL OF THE CHILLED WATER PRESSURE TRANSMITTERS THE FOLLOWING TRANSMITTERS WERE READING OUT OF RANGE: DCOS Input numbers 1, 2, 5, 6, 7 & 8. See attached Table for reference, pressure readings were taken with a calibrated meter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615145&prj=479&rqi=wdOMvYrcg2W8mL8vRLf4fGCQy8
SOR-138-006 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | The soft point "Logic Failure" per 2.16 DCOS Table of the Record - Delta STS 800A Submittal 480v V2 is not visible for the 1STSs to the customer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615190&prj=479&rqi=sgdnnQsW7bsbl5PLbjwlEOgWvJ
SOR-138-005 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Carrier Heat Pumps: The TCV within the unit is limited to 2.5 to 13 GPM, design flow for this unit is 18 GPM, this applies to the following units: HP_R1_01, HP_R1_02, HP_B_01, HP_B_02, HP_C_01, HP_C_02, HP_D_01, HP_D_02 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615178&prj=479&rqi=KMlpMqq0IbzbyR14COT18F4huK
SOR-137-009 | SV18-1 | AMER | Closed | P1 High CX | James_Kenny@fsttechnical.com | 2026-03-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Delta CRAH units located in the Power house Skids, do not transfer back from Reserve power to Primary power following power reinstatement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614987&prj=479&rqi=AnoSN0S3ebye1PfB3onGemhUbI
SOR-137-007 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Delta CRAH Units located in the Powerhouse Skid: R1 A B C D E F Units do Not shut down on smoke detector activation when the units operate in manual. In automatic the units will only work when the Fire Shutdown is enabled "ON". This is not acceptable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614985&prj=479&rqi=YaaFVO5N95eEDba6zCBjH9iuQP
SOR-137-010 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | VESDA CONTROLLER Units located in the Power house Skids & the MV-1 & 2 Power houses are in constant alarm. Relating to: R1, B, C, D, MV-1 & MV-2. WE NEED A REPRESENTATIVE FROM VESDA HERE ON SITE TO RECTIFY THE ISSUES WE ARE ENCOUNTERING. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614988&prj=479&rqi=5dytEPgecaqWdSLi5yIC4bKXHj
SOR-137-008 | SV18-1 | AMER | Closed | P1 High CX | James_Kenny@fsttechnical.com | 2026-03-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Condensate Pump not activating on Delta CRAH unit located in the Power House Skids | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614986&prj=479&rqi=Vv4Zd1fIvMP3lt7TZfSjUFsyQH
GI-076 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | PDUs are not reflecting the output CB in the onelines | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614921&prj=479&rqi=uXrgFNq0IFuJbcXyOqp7sNwM5M
SOR-135-004 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Condensate Hi level switch interlock with the unit's compressor works but the unit's points integration to DCOS is not complete and this alarm needs to be verified once communications are established. This applies to the following units: make repairs necessary. 1HP_R1_1 1HP_R1_2 1HP_B_1 1HP_B_2 1HP_C_1 1HP_C_2 1HP_D_1 1HP_D_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614853&prj=479&rqi=GyanBgPpUhvgKXB56AMDEIvDxk
SOR-135-003 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Smoke Detector is shutting the unit down locally but the unit's points integration to DCOS is not completed and this alarm needs to be verified once communications are established. This applies to the following units: HP_R1_2 Â HP_B_1 1HP_B_2 1HP_C_1 1HP_C_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614852&prj=479&rqi=KgyTBAyfkgCajbKzoI3gVNZC9G
GI-068 | SV18-1 | AMER | Closed | P2 Medium DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS | [6 empty] | DP sensors are reading a wide variety of numbers, suggesting are missing scaling or not reading well | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614737&prj=479&rqi=ITnVlugSazgH6tEWHCBAugtqiw
GI-065 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [6 empty] | Need confirmation whether these meters are the first monitoring point upstream of the SUSPs; if yes, Utility digital assets must be created per Appendix 7. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614734&prj=479&rqi=tcbLsFKj28uDrR38Z725hmwhEn
GI-070 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | The UI does not highlight the selected item, making it unclear which item is currently active. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614739&prj=479&rqi=HH3OZFvI3Rh4S6Ly86VBOW5jh4
GI-071 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Hot/cold aisle selection is reversed; cold selects hot and viceâ€‘versa. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614740&prj=479&rqi=uYVigUmjMXxIrkrDJ6C2tXPQUw
GI-067 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [6 empty] | PQM data shows incorrect voltage and PF due to negative incoming power; polarity must be corrected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614736&prj=479&rqi=7AW5ezfLq9F9aOrXW1HtzMQulf
SOR-134-002 | SV18-1 | AMER | Closed | Outstanding Paperwork/Documentation | jordan_dubose@fsttechnical.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | Missing BMS/ ENMS signed documentation (Point to point check sheet and fibre results) for SV18-1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614722&prj=479&rqi=akkPDkVMCaN8pGzSDUjzhd5Xag
GI-064 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS | [6 empty] | 1. Chiller Flow Low Alarm Logic Incorrect Category: DCOS Design Issue (Alarm logic implemented incorrectly â†’ design/config logic error) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614733&prj=479&rqi=dKyuZC6YfIM15Gx5itJe14WPDu
GI-069 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | The CRAHs overviews are not setup yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614738&prj=479&rqi=7Ti7tb0ewpDXQOnu0nkLDqod4I
GI-072 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Floorplan does not visually show which element is currently selected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614741&prj=479&rqi=e37jp0ztz4okKcCd4ceGojbrZs
GI-066 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS | [6 empty] | SPARE and FUTUREâ€‘SPARE breakers must not be monitored or ingested. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614735&prj=479&rqi=6j3oR2NlFDbrLpbCcsMK0h37h9
GI-074 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Missing weblinks/deep links for assets (CRAHs, UPSs, etc.) from graphics to their detail/faceplate pages. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614743&prj=479&rqi=wKLJu3ISVjwevivtmVgYPrryya
GI-075 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS | [6 empty] | Battery Time Remaining is missing for all UPSs on the graphics/monitoring views. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614744&prj=479&rqi=9FjQjpfJsZPM8WXyIaNtSI7A2k
GI-073 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Risers are displayed in the detail view but missing in the overall floor plan view. Riser labels do not show which data halls each riser supports (operational context is missing). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614742&prj=479&rqi=UVVwGyusVOVjFR01T9STGpWNlU
SOR-132-007 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Skid C & D CRAH fan speed control All units were placed in automatic during testing, chillers and associated pumps were started and rooms cooled down to temperature set point. All fans continued to run at full speed, the expectation is the fan speed reduces as the temperature comes within range of setpoint. Suspect issue with the CRAHs Units remote temperature transmitter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614633&prj=479&rqi=zeGMQ7DpoWsIHUDWEQeRhdV4uJ
SOR-132-006 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Some DCOS issues uncovered during our Powerhouse Skid CRAHs -Smoke detection testing. Skid B 1CRAH_B_13 - Successful Test - Not Depicted on the unit's faceplate in DCOS - E-Tech notified Skid C 1CRAH_C_13 - Successful Test - Not Depicted on the unit's faceplate in DCOS - E-Tech notified. 1CRAH_C_15 - Successful Test - Not Depicted on the unit's faceplate in DCOS - E-Tech notified. Skid D 1CRAH_D_14 - Successful Test - Not Depicted on the unit's faceplate in DCOS - E-Tech notified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614632&prj=479&rqi=WLNg4BfmvQ7OiOWela84BSnjp6
SOR-133-003 | SV18-1 | AMER | Closed | P1 High CX | daniel_chavez@fsttechnical.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | The transformer for the VESDA system on Power House Skid B doesn't provide output voltage on the secondary side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614659&prj=479&rqi=Byfyi8JQjSCgBu6O1Rik4mWVTL
SOR-132-005 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | PID pop-up settings are not working well: -scale is bad -name on buttons is wrong - EU range is wrong In GENERAL all pop-up settings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483499&prj=479&rqi=6aHnk8b7mcq3R93AqyBNMZKL7p
SOR-132-004 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS |  | equipment type |  |  |  |  | Gateways for the RPPs (BCM) connection can be move 2-3 Us above the current position so the cables won't be curved like now, which will affect the comms in the future | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483495&prj=479&rqi=eTUDmvYJut2Q8Z7ny5KGkmvDvy
SOR-131-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Fan spring isolators to be replaced on all units | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483382&prj=479&rqi=vAm7vtHvZFlmMVn3ldMb9BIvSY
SOR-130-003 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1RPP_B1_3_1 | RPP - Remote Power Panel |  | RPP-208-250-60 | During the PEI FST found a CT Senser had been damage possibly from installation on 1RPP_B1_3_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352261&prj=479&rqi=jDZaxAC1tEwlsecL4NFmFPj66D
SOR-130-004 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1RPP_F2_2_6 | RPP - Remote Power Panel |  | RPP-208-250-60 | 1RPP_F2_2_6 is missing two CT sticks due to them being used to replace the damaged CTs in 1RPP_B1_3_1 and 1RPP_B1_3_6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352262&prj=479&rqi=ueJKtEHoC19PkPr7tDzJyNaFPC
SOR-127-005 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-27 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Discharge Valve oriented, there is a risk with the operation of the valve the mechanism may loosen up, and the handle would drop and disengaged from the actuator in its current position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483372&prj=479&rqi=t1opJLKZddl7rm7MIY4pCmZvAG
SOR-117-005 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-27 04:00:00.000 +0400 | Owner |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | 1ACC_R1_01 - rode through the test and alarms reset thereafter, all UPS circuits were healthy during the test. 1ACC_R1_02 - House 120V UPS power was removed and the alarms didn't reset. The reason it didn't ride through is the Trane UPS in their control panel is programmed to provide power for a 3 second drop in power An extension of this timer from 3 seconds to 12 seconds would get us through the transition to Gen power. Trane Panel UPS is an Emerson Sola-HD 300w and backs up the chiller controller only. During test of the generator back up circuits on Saturday, Chillers 1ACC_B_07 & Chillers 1ACC_B_07 Phase Loss alarm activated and latched. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483373&prj=479&rqi=mATqcdC5c3V8XBr9nmKplP8CwM
GI-061 | SV18-1 | AMER | Closed | P3 Low CX | adrian_brown@fsttechnical.com | 2026-02-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1RPP_B1_3_6 | RPP - Remote Power Panel |  | RPP-208-250-60 | During the PEI we found a CT Sencer had been damage possibly from installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352241&prj=479&rqi=6b8KiSrXN9gAfXGAeHWzg1MCda
SOR-130-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-26 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | CONDUIT CONNECTIONS Covers missing on the conduit leading to the field devices on TST_B_07, See attached Photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352246&prj=479&rqi=zeJWSqDXxXxUMyO53B38DOW5Qo
GI-060 | SV18-1 | AMER | Closed | P3 Low CX | adrian_brown@fsttechnical.com | 2026-02-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1RPP_B1_1_3 | RPP - Remote Power Panel |  | RPP-208-250-60 | During the PEI we found a missing cover for the small terminal under the main terminal | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352240&prj=479&rqi=U6f0sKU6EeL8acRgGbH0SUaJEx
GI-059 | SV18-1 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-02-24 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Dummy Issue for JTM requested by Pat. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204066&prj=479&rqi=vhoyvolHsJsJLqODIY8zhr4V4s
SOR-122-017 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | [6 empty] | The mechanical lugs for 1PNL_X_HP terminations to Q06 in the 1MDSB_X are incorrect in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199681&prj=479&rqi=U0DT2CHCBhSrB3L2FYQuQNrz4w
SOR-122-005 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | The three pulling gutters shown in MPS.301 were not installed in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199637&prj=479&rqi=FzX2AnpJtQCgVyQj9RUaZPMaPx
SOR-122-011 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | The ball valve is missing from the section 2 VESDA conduit in front of 1CRAH_A3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199643&prj=479&rqi=aVQEDzJqOoxTKO9fSDt6C73XKD
SOR-122-003 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | The top external tabs shown in MPS.000 are not installed in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199635&prj=479&rqi=VfodAh32vUK6KhoO9PECn8YJIl
SOR-122-002 | SV18-1 | AMER | Open | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design correction needed | Design | [6 empty] | 1MDSB_X Q01 in SV18-2 Hanley Submittal should be Spare. Refer to DLB Engineering Drawing Single Line Drawings E602.05, E602.009 & E602.10. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199633&prj=479&rqi=ecEnftqQI52gk6Vp3ksF0gIkni
SOR-122-001 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design | [6 empty] | The positions of 1WSHP_X_1 & 1WSHP_X_2 in skids A, E and F in E403 are different from latest approved MPS submittal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199627&prj=479&rqi=15PP5buq4wg5HcZQOL9qJs9GgQ
SOR-122-009 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | FST observed that a third branch junction box above the 1BTUs in skids A, E, & F shown in MPS.400 was not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199641&prj=479&rqi=adX3fhWTfDm5QxwBKDtCpNvCwP
SOR-122-008 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Mechanical Contractor |  | Missing Components | Commissioning | [6 empty] | The 1WSHPs in skids A, E, & F are missing drain pans underneath them per the request of Equinix. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199640&prj=479&rqi=5kAd6Zjpaqrk99WR0h4Q3WvmC9
SOR-122-007 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | [6 empty] | The mechanical lugs for 1UPS_X_3 terminations to Q07 in the 1MDSB_X are incorrect in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199639&prj=479&rqi=IeR6RHHiUMz3d1QYyH6S5DoTCY
SOR-122-006 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | The ethernet connection from 1UPS_X_3 to DMARK shown in MPS.521 were not installed in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199638&prj=479&rqi=hQ1kBLAEEgKclm2DzhqosmRgnJ
SOR-122-004 | SV18-1 | AMER | Closed | P2 Medium CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | The external small green stub in between the condensate piping and the light shown in MPS.000 is not installed in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199636&prj=479&rqi=MewCmFF0BmH3sLZS29yhmzTRYK
SOR-122-015 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning | [6 empty] | 1MSB_E sections 5, 6, 11, 12, and 13 each had a screw that was screwed into the ground bus bar. MPS successfully removed the screws in the 5 sections of 1MSB_E. This has resulted in the ground bus bar plates in the 1MSB_E sections 5, 6, 11, 12, and 13 each having a hole in them. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199647&prj=479&rqi=G7TpWk0288nz8HkavesOs2K7RL
SOR-122-016 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | The ball valve is missing from the section 2 VESDA conduit in front of 1CRAH_E3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199648&prj=479&rqi=5NZYCuYqGrfYHN3HBPO7ONXV57
SOR-117-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-18 04:00:00.000 +0400 | Owner |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | Soft Points that are not available from the chiller: Flow switch COP Condenser Fan Fault Condenser Fan Summary Fault Evap. Approach Temperature Evap. DP Sensor. TXV 1 TXV 2 Free Cooling mode enable Free Cooling valve % Hot Gas 1 Hot Gas 2 Liquid Level 1 Liquid Level 2 Liquid Refrigerant Temperature Ambient Temperature Lockout. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199503&prj=479&rqi=h5MdFgj0ZloEwtCR05uYTM9JOi
SOR-119-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [6 empty] | Chilled water make-up skid - Pressure transmitter needs to be wired and represented on the DCOS graphic. The flow switch is not on the graphics either, this needs to be tested to ensure an alarm is posted to the DCOS alarm page. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199502&prj=479&rqi=Cdh7O74xuwd5YqZntzziJYEuSj
GI-055 | SV18-1 | AMER | Closed | P3 Low CX | manuel.gomez@eu.equinix.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | The Alarm border overlaps multiple objects. The objects need more spacing between them so they can be reflected correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199400&prj=479&rqi=RRRWIFluPiHZZt8dvatUUwtIF8
SOR-118-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Clean debris and rust off all generator roofs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199379&prj=479&rqi=bclbeXwrrg8t6Hm2MjWOkqlmCd
GI-054 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS | [6 empty] | The statistics alarms app is not properly configured, furthermore, not working | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199399&prj=479&rqi=a9avYTEDBnabrnAbEXo5PFhpzA
SOR-118-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Remove lifting eyes from all Generators on site: | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199378&prj=479&rqi=TGEpyWoTqT84Mu9pmHouSLDmb5
GI-056 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | The alarm border is overlapping the objects in different dashboards. The objects need more spacing between them to show correctly the alarm border | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199401&prj=479&rqi=hG0x6fUvna6bSZZGaoaLVVmxOG
GI-057 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | STS faceplate issues with : - power factor not communicating - overview content not available - lines in the hierarchy are not showing the right flow, you can see on source one there is a piece of line at the top right corner that is not white. - The voltage in the table is not showing all the values as per the object (kwh, Vab, Vbc are different) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199402&prj=479&rqi=8SX65ki3IgeMMyeB9LfyhgmtN5
GI-053 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [6 empty] | Autolunch of OMI app is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199397&prj=479&rqi=NpvhM55gtqsCgRRXFn2bwKEU3x
GI-050 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Template Issue | DCOS | [6 empty] | Fire in the footer are not clickable, so we can not go to the respective faceplace/object page | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199281&prj=479&rqi=DM8rsoH6T8OvOwPdN3NRnVQAxT
GI-044 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | On Chiller ACC Overview the headers are repeated on each row, per DCOS Configuration Guide this is not acceptable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199275&prj=479&rqi=07c0uWsopUlNsUntSOhJ3yHwam
GI-052 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Missing name of the data halls (floorplan and tooltip) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199283&prj=479&rqi=B4KCNnBoUtWCLjcwLlutmDaIjm
GI-048 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | On the Data Hall Overviews, there is not a trace for the Leak Detection, this is against the DCOS configuration guide. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199279&prj=479&rqi=msSl53WT3iseJ1i8Q60x8Lhjp7
GI-045 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | The CWST screen appears to have overlapping issues; this screen needs to be revisited once we have more value. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199276&prj=479&rqi=PJWs3BG2fseCHHABTlRk5XkOZj
GI-046 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Chilled water overview graphics have several issues as the sensors are misplaced or not located with dashes or pipping leads to nothing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199277&prj=479&rqi=hChaCXPzcA8EllUcDBvIBQCqpU
GI-051 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | I understand the previous apps bring the oversize for the "csv export," but let's standardize now across the alarm apps | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199282&prj=479&rqi=redjphCiuhmuyEpj6Wk1IqPITW
GI-047 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Chiller Overview has no arrows, and the pump is not in the right direction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199278&prj=479&rqi=wdt5v4WEvnYdCucAqI8Y9x5fta
GI-049 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | The Overviews for each MSB are inconsistent, leading to a graphical issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199280&prj=479&rqi=5PurkZL13FLNWgrYks4cMheLSF
GI-043 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | This is a dummy issue to confirm that JTM is receiving email notifications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199223&prj=479&rqi=3ZKzsnADeTAjs9T2T8nB6Nd8bb
SOR-110-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-09 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Scaling to be addressed on all Chillers & Pumps, this applies to the following chillers: 1ACC_R1_01 1ACC_R1_02 1ACC_B_07 1ACC_B_08 1ACC_C_11 1ACC_C_12 1ACC_D_17 1ACC_D_18 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198826&prj=479&rqi=7z9yUzh6K0aMD64FDVikcMLvak
SOR-109-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-02-09 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | 1MSB_Z is not communicating with the DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198755&prj=479&rqi=JWdZu57xasVYjVKC9J8AG7KZuP
SOR-109-001 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-02-09 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | 1SUDB 1 & 2 are not communicating at DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198753&prj=479&rqi=Qwv1yqx8GgsjKx1r80ubOiSdDV
SOR-109-002 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-02-09 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | 1RMU_R1/B/C/D/Z are not communicating with DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198754&prj=479&rqi=geNm5k0xsD99dHtB50TINZY5Tz
SOR-110-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-09 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  | system | CHW System |  |  |  | Issues with the Chiller RIO Panel wiring to be addressed, applies to the following RIO Cabinets: CHILLER-RIO-01 CHILLER-RIO-02 CHILLER-RIO-07 CHILLER-RIO-08 CHILLER-RIO-11 CHILLER-RIO-12 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198827&prj=479&rqi=zdZRT6qyhMYbCXVfVJl3DM3d1w | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-108-002 | SV18-1 | AMER | Closed | P1 High DCOS | jordan_dubose@fsttechnical.com | 2026-02-07 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | During 1UPS's battery drain testing FST observed that the "Low Battery Alarm" did not turn on in DCOS system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198728&prj=479&rqi=OXlqfei58vVVLCN8ajAWJ0MmXX
SOR-108-003 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-02-07 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | FST observed during testing that Soft Points listed below requested by Equinix are not available in the DCOS system for the different 1UPS's. -Battery Cycle Buffer Full -Battery Time Remaining Status -Battery Time Remaining -Control Power Failure -DC Bus Voltage -DC Cap Fuse -Emergency Power Off -Input Current Unbalance -Output Voltage AN -Output Voltage BN -Output Voltage CN -Rectifier Fuse -Static Switch Disable -kWh | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198729&prj=479&rqi=BwZEObykaFvCnAUftzheCczeiY
GI-038 | SV18-1 | AMER | Closed | P3 Low CX | adrian_brown@fsttechnical.com | 2026-02-05 04:00:00.000 +0400 | General Contractor |  | Installation Damage | Commissioning | [6 empty] | Mega CRAH cosmetic issues Observed Issues / Damage: â€¢ CRAH C-06: Front grille is discolored with visible damage. Deep scratches were observed on the left-side panel. â€¢ CRAH C-04: Front grille shows visible damage, discoloration, and scratches. â€¢ CRAH C-03: Front grille has similar damage and discoloration as C-04, though less severe. â€¢ CRAH C-12: Front grille is damaged and discolored. â€¢ CRAH C-10: Significant dent and scratches on the front panel, consistent with possible impact from a lift. â€¢ CRAH C-11: T2 sensor wiring is damaged and stripped. Therma has been notified of this issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198645&prj=479&rqi=RLKrhoj1EVlTFwLOslLAI6Ny7r
SOR-104-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Incomplete leak detection cable installation for all Skids. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198185&prj=479&rqi=hYC4mehnlYVXGHV58kF5iRBfmk
SOR-102-006 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Power to the Smoke detectors is not installed from the Fire Alarm panel to the smoke detector, in this case the Carrier representative could not complete his scheduled start-up for the equipment. 1WSHP_C_01 1WSHP_C_02 1WSHP_D_01 1WSHP_D_02 Inline plugs for fans and pressure switches found unplugged in the unit, increasing the time troubleshooting. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198072&prj=479&rqi=TCwZbClVl8qJUcuoUBBa6dZHEa
GI-035 | SV18-1 | AMER | Closed | P3 Low CX | baron_brown@fsttechnical.com | 2026-01-31 04:00:00.000 +0400 | Owner |  | Commissioning Issue | Commissioning | [6 empty] | Verify interfaces and interlocks with EMS / Generator control / HV & LV switches Confirm alarms and indicators are operable Confirm CxA Level 4 (Blue Tag) Functional Performance test script available and approved Complete DCOS/ ENMS signed documentation is attached as a document to this checklist. (Point to point check sheet) DCOS Point to Point check complete 100% DCOS status/ alarming verified to ENMS workstation DCOS Point to Point check complete. 100% DCOS status/ alarming verified to DCOS workstation. 100% SCADA status/ alarming verified to DCOS workstation Local Alarms/ statuses are proven to HMI 1HMI SCADA 1MSB Input checklist these items are open and checked NO at this time. FST will verify during Level 4 Testing . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198071&prj=479&rqi=HvLXC3W8bkzI0B70oTbmclKn4C
SOR-102-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Powerhouse Skids CRAH's All panels appear to have been tightened up with a cordless drill and the captive nut broken from its anchor, or threads have been damaged, this has caused significant delay on the commissioning of the Equipment. MPS to better manage the QA Process in their shop, issue raised on Facility Grid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198058&prj=479&rqi=n8VIbQUNZLnT6rVYkMVIkxWRHd
SOR-102-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | 3 x Supply air sensors are missing from the Powerhouse Skid CRAHs. Delta is swapping the sensors to enable their commissioning process. Parts on order. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198059&prj=479&rqi=qdLX7JQwi8WaZ8WmhH0taCKrnT
SOR-101-003 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-29 04:00:00.000 +0400 | Design Professional |  | Design not as specified | Design |  | equipment type |  |  |  |  | FST observed that source of the Skid Heat Pumps in the field, and engineering drawings did not match. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197957&prj=479&rqi=2pQnFmU2imHE7Z08mT83ARjEQD
SOR-101-004 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | FST observed that the labeling of conduits and junction boxes for the panel sources of the Heat Pumps in Skid R1 are not accurate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197959&prj=479&rqi=mpDmFiJaGqvA5yeyersk4sR0At
SOR-101-006 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | Raceway ran in the way of access panels for the Air filter section on 1CRAH_ C_14, needs to be moved. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197961&prj=479&rqi=Xz9OIlyDT0C1iUYvdw1jSuS8ru
SOR-101-005 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | FST observed that the labeling of conduits and junction boxes for the panel sources of the Heat Pumps in Skid B are not accurate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197960&prj=479&rqi=8LpZC4FtfAPVWhTwzpbf91hNfS
SOR-101-002 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-29 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design |  | equipment type |  |  |  |  | FST observed that labeling of the Skid Heat Pumps in the field, engineering drawings and approved MPS submittals did not match. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197956&prj=479&rqi=jdFgz4LqJ2yyId5SyMsP2kHqWC
SOR-96-011 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-24 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | In the absence of reliable Chiller flowmeters, Cx & Trane representative made the call to install Pete's plugs on the inlet and outlet of the chiller evaporator. This way Trane can connect a pressure differential meter to the petes plugs and determine the actual differential using the manufacturers chart for the evaporator Flow plotted against differential pressure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197542&prj=479&rqi=kgjKWa8XeLVzRr1enxIBn90O5m
SOR-97-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-24 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | IP addresses to be uploaded into the chiller Pumps, Danfoss VFD: 1ACC_R1_01 1ACC_R1_02 1ACC_B_07 1ACC_B_08 To be done following start-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197545&prj=479&rqi=gEOwdj1YrCgQKwwXJFIvN4L2KZ
SOR-95-008 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-23 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [6 empty] | Chiller Return flowmeter was not operating - screen was not illuminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197527&prj=479&rqi=1M4WgO54JDzFVuo2dTMjVbV1Sx
SOR-96-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-23 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [6 empty] | Chiller condenser fan junction boxes had water ingress, blew fuses on start-up on chiller circuit 3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197530&prj=479&rqi=64PyTzmdARvYjorBBlKABNeOwR
SOR-91-009 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-20 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1-EGB-Z-2-2 | BUS - Busbar |  |  | FST observed on 1TGB-Z-2-2 that the cables for connections to 1TBG-Z-2-3 and the ladder rack are thin wires instead of #4/0 AWG CU identified in E604.01-SINGLE-LINE-DIAGRAMS---GROUNDING-Rev.7. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197269&prj=479&rqi=VouLH74yD3uNsYclzD6uwECyb9
SOR-91-002 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-16 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design | [6 empty] | In the latest R3 coordination study, E709 panel schedule and in the field both 1UPNL_B1_H1 & 1UPNL_C1_4_H1 have one 125A and three 80A circuit breakers but those panels have one 125A and three 100A breakers in the E603.06 & E603.07 UPS_DISTRIBUTION Single Lines from Bulletin 2 & 3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197068&prj=479&rqi=fsXeH8NREnTlzInkwxO7rsjbYz
SOR-86-001 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-10 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design | [6 empty] | FST observed that the E602.03-E602.14 Single Line Block Diagrams incorrectly state that only the 1MSB_Xs, 1MSB_X Remote HMIs, 1UPS_X1s, 1UPS_X2s, 1BATT_UPS_X1s, and 1BATT_UPS_X2s are pre-wired by the skid Manufacturer as it also lists the 1MDSB_Xs, 1UPS_X3s, and 1BATT_UPS_X3s as well. Attached are the Single Line Block Diagrams for blocks installed in the current phase but is applicable to every block. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196677&prj=479&rqi=YaJGYLQShaxUaRBCzmfaACUiDL
SOR-83-004 | SV18-1 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-01-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | Missing communication ethernet cable for 1MSB_D at Dmark. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196537&prj=479&rqi=IK0Y04QpYnbCr91S6IWtJ4rX5M
GT1ELEC-357-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_2 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_2)Â HMI on UPS failed to turn on when energizing.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638387&prj=684&rqi=qaNSOXv5YDQn4drTFcj5VF6paq
GT1ELEC-350-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UPS_J_1 | UPS - Uninterrupted Power Supply |  |  | (1UPS_J1) HMI failed to turn on when energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638409&prj=684&rqi=orSe1dC2zFiWm9tTORRYQhyzoz
GT1ELEC-348-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UPS_H_2 | UPS - Uninterrupted Power Supply |  |  | (1UPS_H2) HMI failed to turn on when energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638408&prj=684&rqi=OdjQ53wny7mBARi12QvPREwJ4m
GT1ELEC-347-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UPS_H_1 | UPS - Uninterrupted Power Supply |  |  | (1UPS_H1) HMI failed to turn on when energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638407&prj=684&rqi=mtLOvgVQfIfY3F8NNxhiab6bto
GT1ELEC-356-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_1 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_1) HMI on UPS failed to turn on upon energization.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638388&prj=684&rqi=uYakldwT12k3bN12o67dfjsdcT
GT1ELEC-106-001 | SV18-2 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-09-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1PDU_G1_1 | PDU - Power Distribution Unit |  |  | Sub feed 4 has a communication alarm inÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638236&prj=684&rqi=KAcfrHMzflejluw6aI80Jtkkcg
GT1ELEC-344-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-09-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UPS_G_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G1 L3 Several failed components identified during startup of the equipment. Issues include the inverter assembly, power supply module, and several cards. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638187&prj=684&rqi=U5yN3e1WC0oyc0adAaup43mQn9
GT1ELEC-254-001 | SV18-2 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-09-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1RPP_K1_2_6 | RPP - Remote Power Panel |  |  | Top hinge for door came off and door was falling out of placement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638237&prj=684&rqi=3My29OP7nAFq9CcMbI5PCnfj7O
GT1ELEC-183-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1RPP_E1_2_2 | RPP - Remote Power Panel |  |  | 1RPP_E1_2_2 L4 During HLT, a thermal deficiency was noted and the equipment was shut off. After further inspection, a bolt on the bus bar was found not properly installed or torqued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638038&prj=684&rqi=pGAUBAPGMNrDLHUfNtZUQo1nYf
GT1ELEC-101-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1PDU_E1_4 | PDU - Power Distribution Unit |  |  | (PDU E1_4): HMI failure. HMI is not showing subfeeds.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638005&prj=684&rqi=MPSkzgm0IuGWZMdsGFM0EcikKF
GT1ELEC-126-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1PDU_J2_2 | PDU - Power Distribution Unit |  |  | (1PDU_J2_2) HMI displays aux power fail.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638026&prj=684&rqi=WCOaoWkgyzTUXzh1xjLMkD1739
GT1ELEC-126-002 | SV18-2 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1PDU_J2_2 | PDU - Power Distribution Unit |  |  | Missing disconnect for HMI power supplyÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638027&prj=684&rqi=s3nCk65sMfjAJY1oy9wObUinbP
BT1MECH-41-001 | SV18-2 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-09-11 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Comms Issue/ Fault | DCOS | Mechanical â€“ Water | equipment | 1CRAH_H_01 | CRAH - Computer room air handler |  |  | (All H-fed Data Hall CRAHs) L4 None of the H CRAHs are viewable on BMS, check if the MOH Network cabinet is up and working correctly? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637824&prj=684&rqi=G3tHYvm1rkoakNfseHKHa7OQ5C
BT1MECH-80-001 | SV18-2 | AMER | Open | P2 Medium CX | alec.dughi@veolia.com | 2026-09-11 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Comms Issue/ Fault | DCOS | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (HP_G_1) L4 HP_G_ 1 port at network switch in D mark panel suspected to be bad. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637813&prj=684&rqi=q8c4SAkrXTWDBTaxssQzlV2jvi
BT1MECH-80-002 | SV18-2 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-09-11 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (HP_G_01) L4 BMS Graphic is switched in Aveva. HP-G-01 is showing data from HP-G-02 and vice versa. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637823&prj=684&rqi=s5BWVpfRr3Lob5nt3lP9rlvukM
BT1MECH-64-001 | SV18-2 | AMER | Open | P2 Medium CX | ethan.hang@veolia.com | 2026-09-09 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_12 | CRAH - Computer room air handler |  |  | (1CRAH_K_12) L4 Two EC fans were taken and given to K_02 and K_04. New fans are needed for K_12. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637551&prj=684&rqi=hIgl1PI9iGtvLZSnQLW2U93kPJ
BT1MECH-56-002 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-09 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_04 | CRAH - Computer room air handler |  |  | (1CRAH_K_04) L4 Unit produces significantly lower airflow than all other units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637509&prj=684&rqi=tprmgyXLIa0swH8ryBCdoUq8ha
BT1MECH-56-001 | SV18-2 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-09-08 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Incomplete Connections | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_04 | CRAH - Computer room air handler |  |  | (CRAH-K-04) L4 Condensate pump discharge copper piping has a leak at brass fitting that sprays water during pump operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637327&prj=684&rqi=K4wRsmwL11RTSqCdDDv1JGOJBk
BT1MECH-54-003 | SV18-2 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-09-08 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (CRAH-K-02) L4 Condensate pump discharge copper piping has a leak that sprays water during pump operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637323&prj=684&rqi=pfH2x2a1h2dr4tN4SlZv1ai1MK
GT1MECH-42-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-09-08 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1CRAH_G_01 | CRAH - Computer room air handler |  |  | (All K CRAHs) L3 At the BMS floor layout, all K CRAHs are labeled as J CRAHs. Etech relabeled to K. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637287&prj=684&rqi=Nfc943P9r2FO6Vq0jdZ1Cakfbd
BT1MECH-55-002 | SV18-2 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-09-04 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Incomplete Connections | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_03 | CRAH - Computer room air handler |  |  | (CRAH-K-03) L4 Leak detection module is wired incorrectly. Not using the correct 2 out of 3 wires in both power and signal bundles going into the module itself. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636922&prj=684&rqi=lrkMAlXJN2dZY9LqveuufIzAWI
BT1MECH-37-002 | SV18-2 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-09-03 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_09 | CRAH - Computer room air handler |  |  | (CRAH-G-09) L4 Condensate pump discharge copper piping has a leak that sprays water during pump operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636755&prj=684&rqi=Dc9aaaG9rDxiJo9f75HTLZbAht
BT1MECH-36-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_08 | CRAH - Computer room air handler |  |  | (1CRAH_G_08) L4 Failing RAT sensor does not make the fan speed go to 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636599&prj=684&rqi=GKFUFi4K7IwATpkGXxe5cWm4kU
BT1MECH-55-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_03 | CRAH - Computer room air handler |  |  | (1CRAH_K_03) L4 Failing RAT sensor does not make the fan speed go to 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636596&prj=684&rqi=KDl0REKPuZ5dsUFhCvg3NyMaV7
BT1MECH-35-003 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (1CRAH_G_07) L4 Failing RAT sensor does not make the fan speed go to 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636597&prj=684&rqi=IR9t7BtXaJBEeYzneRoyVwGOFn
BT1MECH-57-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_05 | CRAH - Computer room air handler |  |  | (1CRAH_K_05) L4 Failing RAT sensor does not make the fan speed go to 100%. EDIT 9.9.26: Hidden setting "Sensor Fail Fanspeed" found. Units require firmware update PA2.08.17R Build 20260303-185731 for this setting to be active. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636594&prj=684&rqi=VCYL0bcTKp2Cp8NZKQzcRqqYST
BT1MECH-54-001 | SV18-2 | AMER | Closed | P1 High CX | alec.dughi@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Incomplete Connections | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (1CRAH_K_02) L4 CHW valve 2 has no power. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636568&prj=684&rqi=d9zRIHeajuZRFI4FUk96ybkNmx
BT1MECH-54-002 | SV18-2 | AMER | Open | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (1CRAH_K_02) L4 K10 contactor is defective, preventing the correct operation of the ATS function. Replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636593&prj=684&rqi=I3lj67JM5n70ZKbgUXLi3EaROZ
BT1MECH-37-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_09 | CRAH - Computer room air handler |  |  | (1CRAH_G_09) L4 Failing RAT sensor does not make the fan speed go to 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636600&prj=684&rqi=s2NXYdLqrvGk5aqKzLK7LKKAh9
YT1ELEC-155-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1RPP_A1_1_1 | RPP - Remote Power Panel |  |  | All RPPs L2B A single screw on all 4 corners of the panel board is too long and requires replacement. AMG is tracking this issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636356&prj=684&rqi=FwGpKcCjnVj2qtjbAUhCaVQwbk
BT1MECH-35-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-31 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (DH CRAH) L4 Supply fan speed command is not showing correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636165&prj=684&rqi=uro7P0AjPUOYbs6KpLaOnnmxWB
BT1MECH-35-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-31 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (DH CRAH) L4 Supply fan speed command is 1 input behind at the BMS. ex: default starts at 50%, inputting 60%, fans go to 60% but BMS stays at 50%, inputting 70%, fans go to 70% but BMS goes to 60%, etc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636164&prj=684&rqi=vkUvaohFCrZndQV8FpDqoulwyu
GT1MECH-18-001 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-08-31 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_01 | CRAH - Computer room air handler |  |  | (1CRAH_G_1) L3 Source 2 50A fuse bracket was found to be broken during L3. Replacement bracket and fuse needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636119&prj=684&rqi=WxOW0JmRgDlwkF6Z9fhuhujKTQ
GT1MECH-38-001 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-08-27 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_09 | CRAH - Computer room air handler |  |  | (1CRAH_H_09) L3 Control board was donated to higher priority CRAH_K_04. CRAH_H_09 needs new control board. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635759&prj=684&rqi=QysKqfyG2EkrWsFByOxuWiMphN
YT1ELEC-355-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_J3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_J3 L2B Broken Dry Contact Card that requires replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635695&prj=684&rqi=udvwwrAmowSV5mTf6eRAATI2TT
BT1MECH-61-001 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-08-27 04:00:00.000 +0400 | Controls Contractor | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_09 | CRAH - Computer room air handler |  |  | (1CRAH_K_09) L3 Upper CAT6 port is not sending data to the Moxa switch for U2U communications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635758&prj=684&rqi=HD5l96LLb8GgGTjkqL209LOqiG
GT1ELEC-91-002 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | UPS_J_2 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635468&prj=684&rqi=8Ir0sDJOJSgsOq7xHAjhGD73sc
GT1ELEC-89-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | UPS_G_1 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635461&prj=684&rqi=rKUWpwrjvezSnDWNugEde2E0vV
GT1ELEC-89-002 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | UPS_G_2 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635462&prj=684&rqi=w123woIDJEJqiCYcGOVmRiT7DZ
GT1ELEC-383-001 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_R2_3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | UPS_R2_3 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635478&prj=684&rqi=pD2ZtlGnXlWxN3zdgIkqzVhNpZ
GT1ELEC-380-001 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_H3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | UPS_H3 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635475&prj=684&rqi=AYiKSxmyDpFU3M8Y6ezFvBZw0F
BT1MECH-65-004 | SV18-2 | AMER | Closed | P3 Low CX | abdul-qadeer.bilal@veolia.com | 2026-08-26 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1CRAH_G_13 | CRAH - Computer room air handler (Skid) |  |  | (All Skid CRAHs) L4 Supply air temperature on CRAH BMS faceplate is not actually tracking the SAT that the valve controls to. Please use address 0x0017 dec 23. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635452&prj=684&rqi=A3P8Ae38OFDc6BrI7StPDgdHfn
GT1ELEC-381-001 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_J3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | UPS_J3 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635476&prj=684&rqi=tjjpNMNFcLkY8n76C8YosCodpw
GT1ELEC-93-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | UPS_R2_1 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635472&prj=684&rqi=AoWCEylkLZn7r3fTBhz2jMzUDw
GT1ELEC-93-002 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | UPS_R2_2 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635473&prj=684&rqi=JY9Abl8NBRxu4MUI2DBUy6Uvqq
GT1ELEC-91-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | UPS_J_1 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635466&prj=684&rqi=99xmFGKwuNxk2uNf554XG6xK75
GT1ELEC-90-003 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | UPS_H_2 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635465&prj=684&rqi=HtGhJfbnrk1oNHMvSdK9DLFqeG
GT1ELEC-90-002 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | UPS_H_1 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635464&prj=684&rqi=Gqjy2apNkQhQepNHucw2RF4Ris
YT1ELEC-237-001 | SV18-2 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-08-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1RPP_H2_2_5 | RPP - Remote Power Panel |  |  | Found a broken/damaged connector piece during normal inspection of RPP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635337&prj=684&rqi=3fm0dBkHUpNt2XPvaJSRl9hgQs
GT1ELEC-92-002 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | UPS_K_1 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635470&prj=684&rqi=o0cZK1AMFNCqAPOYS8WAvYWYF2
GT1ELEC-92-003 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | UPS_K_2 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635471&prj=684&rqi=wYyS3QXYQBKDr1maD8LlY2Hmwm
GT1ELEC-379-002 | SV18-2 | AMER | Work Completed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | UPS_G3 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635474&prj=684&rqi=6zYxIHJEoaqY6Dhtrfj0fWLekM
GT1ELEC-382-001 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_K3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | UPS_K3 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635477&prj=684&rqi=twoaA9tXjCahnQXZrqixLSoAMp
BT1MECH-73-001 | SV18-2 | AMER | Ready for Verification | P3 Low DCOS | ethan.hang@veolia.com | 2026-08-25 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1CRAH_J_15 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_J_15) L4 Unit is mapped to J_13 on the floor layout, and J_13 is mapped to J_15 on the floor layout. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635191&prj=684&rqi=2VoTW80ksjf6hEyrqL4GhhPP5G
BT1MECH-65-003 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-25 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Comms Issue/ Fault | DCOS | Mechanical â€“ Water | equipment | 1CRAH_G_13 | CRAH - Computer room air handler (Skid) |  |  | (All Skid CRAHs) L4 Writing SAT and DT setpoint from the HMI does not update at the BMS. If a new number is then written from the BMS, it overrides the HMI as usual. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635131&prj=684&rqi=6mt43lN5htyxbiRsuGMqFvg3Ki
BT1MECH-65-002 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-08-21 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1CRAH_G_13 | CRAH - Computer room air handler (Skid) |  |  | (All Skid CRAH's) L4 Fan command mismatch does not come in when command wire is pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634682&prj=684&rqi=TSc9MkywwKFLNhCYRjaMAZ08p0
BT1MECH-65-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ethan.hang@veolia.com | 2026-08-21 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1CRAH_G_13 | CRAH - Computer room air handler (Skid) |  |  | (All Skid CRAH's) L4 Fan command 1 does not exist. Please remove or map to the same point as fan command 2. There is only one speed command for both fans. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634681&prj=684&rqi=d0nJshAOZrGLF99WGeO6QcsW4X
GT1MECH-82-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L3 Trane FSR found Bellimo Valve to not be functioning correctly. Trane has contacted MPS and they will work on getting a replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634485&prj=684&rqi=jhwaVAm05hMlFsLl3h7EDlnXdX
GT1MECH-76-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (HP-H-1) L3 Thermostat damaged during startup procedures, needs replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634443&prj=684&rqi=KEcnFLvTWWSAGA3L5Ems3klOhS
GT1ELEC-379-001 | SV18-2 | AMER | Work Completed | P3 Low CX | chase.negich@veolia.com | 2026-08-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | (1UMDSB_G) L3: Kirk key interlock does not provide indication on UPS or UMDSB.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634554&prj=684&rqi=6WH16i2WfV1RncntBthbhOCUzB
GT1ELEC-346-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_G3) L3: Battery breaker status on HMI is backwards. When breaker is shut, it indicates open.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634552&prj=684&rqi=cnz2wwlg6xn7USH3FIE8ulgsMV
GT1ELEC-346-002 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_G3) L3: MBB does not indicate position on UPS HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634553&prj=684&rqi=7BHp0XU71IZjmBh2DHoJxWHmqI
YT1MECH-90-004 | SV18-2 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-08-19 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (HP-R2-1) L2B Phenolic circuit labeling (circled in red) is incorrect (labels are swapped between HP-R2-1 and HP-R2-2). To clarify, east-most HPs are HP-X-1 and west-most units are HP-X-2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634293&prj=684&rqi=KO4KBdNjm3JW6KWuMZBzrF3F2X
GT1MECH-69-001 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1EF_G_1 | EF - Exhaust Fan |  |  | (Skid Leak Detection) L3 Etech has found a bad leak detection cable section on the DMARK wall. New replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634236&prj=684&rqi=rIh90miVaXlFPcQZHThgwJ3Gct
YT1ELEC-358-002 | SV18-2 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-08-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_K3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_K3 L2B:Â Torn door filter on cabinet panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634144&prj=684&rqi=23NZPjKQKbvI9DveyOdQvRXrLp
BT1ELEC-4-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1GEN_K | GENL - Generator (LV) |  |  | 1GEN_K L4 Failed pneumericator motherboard for 1GEN_K. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634012&prj=684&rqi=NBZY0wxGKF8G9JmoQBYsmkuQqY
GT1MECH-75-001 | SV18-2 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-08-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (HP_G_2) L3 Thermostat control wiring insulation is damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633996&prj=684&rqi=4YOkaYS1Gf6e9jYxCxgV4iPLwA
BT1ELEC-3-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1GEN_J | GENL - Generator (LV) |  |  | 1GEN_J L4 Failed speed indication in 1GEN_J during testing. Warning came in early into testing labeled '689 ECM.C3 Crankshaft Speed Error'. This did not stop the test from completing but needs to be resolved. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634005&prj=684&rqi=gow1YHkdlWgMQSlNq04Go73zsK
YT1ELEC-349-002 | SV18-2 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G3 L2B Torn filter on UPS enclosure door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633730&prj=684&rqi=fuFNDkf4VLefK2W8Ixr93NjhVj
GT1MECH-83-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (1HP_R2_2) L3 Trane FSR found Bellimo Valve to not be functioning correctly. Trane has contacted MPS and they will work on getting a replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633727&prj=684&rqi=pofOG0ICMx5oWViTSEtQBfy0Mj
GT1MECH-82-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L3 BMS skid floor layout labelled incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633460&prj=684&rqi=vBFsKOcdmD4b1bVPB1863snQh5
GT1MECH-76-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (1HP_H_1) L3 BMS skid floor layout labelled incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633456&prj=684&rqi=whTSmYwCxJXKJHbiGfqah3fq6F
GT1MECH-78-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (1HP_J_1) L3 BMS skid floor layout labelled incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633457&prj=684&rqi=TKAh0ulrhya8zzSDZQTlKIqW3E
GT1MECH-74-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (1HP_G_1) L3 HP_1 and HP_2 objects are flipped on the floor layout at the BMS. See attached electrical bulletin #2 for correct asset tags. Typical for all skids. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633453&prj=684&rqi=3TRh8MrnjfJFbJ1UvzOubZMX49
GT1MECH-80-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (1HP_K_1) L3 BMS skid floor layout labelled incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633458&prj=684&rqi=OvnTnYCBYXleK4Bai8nSdW9spw
YT1MECH-80-005 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_K_1 | EF - Exhaust Fan |  |  | (Skid K leak detection) L3 CAT6 cable is too short to be terminated at the leak detection panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633532&prj=684&rqi=U2tPqP0T2j9o8c1IX4H5Gx65TW
GT1ELEC-90-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | 1MSB_H L3 1MSB_H Breaker Q15 control panel has a failed motherboard that requires a replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633267&prj=684&rqi=XY83Zox2omnFchTh6BSo36GHgh
RT1MECH-85-005 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (1HP_H_2) L2A Heat pump missing thermostat. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633268&prj=684&rqi=qtZzTVVs72zevllrhFwPDPp36Z
RT1ELEC-247-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1RPP_K1_1_1 | RPP - Remote Power Panel |  |  | 1RPP_K1_1_1 L2A FST cannabalized a set of screws for one lug kit inside of this RPP. Creating this case to track the replacement of these screws and the lug cover. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633384&prj=684&rqi=n8j6UAkGyL2oY5lpwCVt0Gyv55
GT1ELEC-92-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | 1MSB_K Tracking Purposes FST has cannabalized the Phase Sequence Relay off of 1MSB_K for installation on 1MSB_F. Please provide an update on the schedule for delivery and replacement in 1MSB_K | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633278&prj=684&rqi=QEIOdHJC5ip1fR9iKr8nHUE3IQ
GT1MECH-43-001 | SV18-2 | AMER | Closed | P1 High CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (1CRAH_K_02) L3 Fan 8 replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633075&prj=684&rqi=cIf0PKyrIxQYOpoQveMJnTQh0P
GT1MECH-28-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_11 | CRAH - Computer room air handler |  |  | (1CRAH_G_11) L3 Constant loss of airflow alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633073&prj=684&rqi=ZotJ728r4lDXOSSViFNt6bdfCz
GT1MECH-46-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_05 | CRAH - Computer room air handler |  |  | (1CRAH_K_05) L3 Unit unable to be put into manual mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633080&prj=684&rqi=IKYWOHYyO3TCENogC1cphgCeQg
BT1MECH-1-001 | SV18-2 | AMER | Open | P2 Medium CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | TRN - Trane | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1ACC_J_09 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_J_09) L4 DC/DC converter for compressor 2 communications failed on R2_06 during 4 hour HLT. Part cannibalized from J_09. Replacement delivered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633088&prj=684&rqi=ynSo10TJvhV7yggQkWVGvmNfz8
GT1MECH-44-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_03 | CRAH - Computer room air handler |  |  | (1CRAH_K_03) L3 Unable to put the unit into manual mode | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633076&prj=684&rqi=sbcqqcRFS7u1e3OtnOlwlM02bj
RT1ELEC-190-001 | SV18-2 | AMER | Open | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-08-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1RPP_E1_2_5 | RPP - Remote Power Panel |  |  | (1RPP_E1_2_5) The cover is incorrectly sized by the manufacturer resulting in the exposure of the breakers for the branch circuits 69 and 71. The serial number of the panel is F1251024EQX00647. This issue was entered originally as issue #1048 in SV18-1 before the clarification that the 1st floor 1RPPs are part of Veolia's scope. Anord Mardix Group (AMG) is already aware of this issue and needs to provide estimated date of when the replacement cover can arrive to SV18. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633137&prj=684&rqi=DvpBfuoN8oCnID4hqcedF70ppF
GT1MECH-45-001 | SV18-2 | AMER | Closed | P1 High CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_04 | CRAH - Computer room air handler |  |  | (1CRAH_K_04) L3 Fan 1 replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633078&prj=684&rqi=rA0gVi6QjZJj8GASeCxuHvYy4a
GT1MECH-24-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (1CRAH_G_07) L3 Constant loss of airflow alarm present on the unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633071&prj=684&rqi=DfvNas002Ab2Hda246X6wOUmLo
GT1MECH-27-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_10 | CRAH - Computer room air handler |  |  | (1CRAH_G_10) L3 Constant motor overload/EC fan fault alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633072&prj=684&rqi=IebdntVrtWoXHPIrWs5JCIwi6S
GT1ELEC-370-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | chase.negich@veolia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_R2 | GENL - Generator (LV) |  |  | 1Gen_R2 (L3): E-STOP did not open Gen output breaker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632951&prj=684&rqi=nhVWxzmCBGcqA9aupuHMojeITS
GT1MECH-85-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-05 04:00:00.000 +0400 | TRN - Trane | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1ACC_R2_05 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_R2_05) L3 Compressor 2 communication module was found to be faulty. Trane had a new one on hand and replaced. Adding as a closed issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632327&prj=684&rqi=1CiNjQ23EmrbU22QTU8KmyWKLv
YT1MECH-31-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-04 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2B | Incomplete Connections | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_06 | CRAH - Computer room air handler |  |  | (1CRAH_G_06) L2B Ground wire disconnected. Re-crimping needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632217&prj=684&rqi=960oEdR1y4G1kJAMmnwcDSxIiJ
GT1MECH-84-001 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-08-04 04:00:00.000 +0400 | TRN - Trane | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1ACC_J_09 | ACC - Chiller â€“ Air Cooled |  |  | (ACC-J-09) L3 During startup, CHWP VFD disconnect failed. Need new part. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632142&prj=684&rqi=Cnsp75g052vGNXCnulUF6XWn3q
GT1MECH-87-001 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-08-04 04:00:00.000 +0400 | TRN - Trane | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1ACC_J_10 | ACC - Chiller â€“ Air Cooled |  |  | (ACC-J-10) L3 CHW leak was found on return side of chiller piping, right before CHW pump. Leak has been narrowed down to the gasket betweeen Victaulic T fitting and black coupling on CHW pipe, gasket to be replaced before running pump. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632144&prj=684&rqi=8hgJIiOr2uZ1aLUNicYZhnHcSZ
YT1ELEC-95-006 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-07-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | 1MSB_K L2B Section 02A had factory installed ferrules from MPS that were too large. The ferrules installed were for gauge 14 wires but the wires are gauge 16, so the wires were pulling out of their pins with little force. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631866&prj=684&rqi=Rb2nIbox95NeThPtCXPsZV9vg2
YT1ELEC-78-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_2_4 | LIBATT - UPS Battery |  |  | 1BATT_R2_2_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631656&prj=684&rqi=T4GB8FuJNH0RQBbOhDCkTyiJ5D
YT1ELEC-59-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J2_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631514&prj=684&rqi=IjIhH9uapxzaGXVrX04Bau6OnS
YT1ELEC-71-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_1_1 | LIBATT - UPS Battery |  |  | 1BATT_R2_1_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631645&prj=684&rqi=0uJouQSuhPvhUZpQE6LU6gZjPl
YT1ELEC-68-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K2_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631639&prj=684&rqi=YusknTrdEwWRbAT8GKa4kygePJ
YT1ELEC-53-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J1_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J1_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631453&prj=684&rqi=io6nwOTkZzYzBcHrH1zQvdjfyv
YT1ELEC-58-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J2_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J2_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631513&prj=684&rqi=6dFLIh1N6GMhwbwcksToLccBEX
YT1ELEC-74-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_1_4 | LIBATT - UPS Battery |  |  | 1BATT_R2_1_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631649&prj=684&rqi=9lz3DwzHoffACZxL9saWlYc5mm
YT1ELEC-60-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J2_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J2_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631515&prj=684&rqi=oiqpGmOBqsZ3fWzHMpdYbzZtJl
GI-005 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | Common to all RPPs RPP incoming termination points labeled CBA vice ABC. RPP subfeeds labeled CBA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631642&prj=684&rqi=5rwzKoVxPx1U7Rqq1htqkLW50K
YT1ELEC-55-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J1_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J1_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631510&prj=684&rqi=3uoCxxgr282PAeWSl8aljYmSIB
YT1ELEC-62-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K1_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K1_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631517&prj=684&rqi=S5AUJIsAKFFxPhQDUUYWQVZlHB
YT1ELEC-67-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K2_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K2_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631638&prj=684&rqi=HDYjHI1MStmmcw1anVovW9YxOI
YT1ELEC-70-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631643&prj=684&rqi=Cjom1OyJydtaZiizutYKpa42bt
YT1ELEC-57-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J2_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J2_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631512&prj=684&rqi=WC6I4KwloqTn0SSbYWPYUkaYDT
YT1ELEC-65-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K1_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K1_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631636&prj=684&rqi=d2C0DPZK5TFnCr2jVr3t7iWWWd
YT1ELEC-56-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J1_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J1_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631511&prj=684&rqi=3vGKTib7zTROTRNeWWJ9AT5DHk
YT1ELEC-69-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K2_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K2_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631641&prj=684&rqi=ig1GeT1h102Qurt6wjNHcyxE45
YT1ELEC-73-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_1_3 | LIBATT - UPS Battery |  |  | 1BATT_R2_1_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631648&prj=684&rqi=u61MbiaaQYHZpdUsE523gsrqyv
YT1ELEC-54-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J1_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J1_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631509&prj=684&rqi=hg1AGBc0IgS9e6MDeLJTvI0SdK
YT1ELEC-75-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_2_1 | LIBATT - UPS Battery |  |  | 1BATT_R2_2_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631650&prj=684&rqi=Fz2FUI2JwG9DeKFOBlslmG2cCu
YT1ELEC-76-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_2_2 | LIBATT - UPS Battery |  |  | 1BATT_R2_2_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631654&prj=684&rqi=GGmZX6RbhUDdvg6uYkgyqGzsDp
GT1MECH-12-001 | SV18-2 | AMER | Open | P2 Medium CX | ethan.hang@veolia.com | 2026-07-30 04:00:00.000 +0400 | TRN - Trane | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CHWP_J_09 | CHWP - Chilled water pump |  |  | (1CHWP_J_09) L3 During start up, Trane found that the CHWP disconnect had failed. Trane is working on shipping a replacement part. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631547&prj=684&rqi=rfOit8V50WFy2WuW1IWfP0K2or
YT1ELEC-64-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K1_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K1_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631632&prj=684&rqi=ih6lUGJO5js0lc3ojeUcV4BErs
BT1MECH-8-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ethan.hang@veolia.com | 2026-07-30 04:00:00.000 +0400 | TRN - Trane | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1ACC_H_13 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_G_16) L4 For tracking purposes, during a fast restart test while the chiller was at 100% capacity, the CB218 relay intermittently failed. Trane is working on sending a replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631542&prj=684&rqi=8lVwgb8mlI5z9F7EAT0Gg6ucEQ
YT1ELEC-72-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_1_2 | LIBATT - UPS Battery |  |  | 1BATT_R2_1_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631646&prj=684&rqi=vrEyKzsMbVhJNcmt6o0FbKqbuu
YT1ELEC-347-003 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_G_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G1 L2B Several components have been cannabalized for repair on Phase-1 SKIDs by the Delta team. Equipment that was taken is as follows: 1 M-board 2 P-boards 1 H-board 2 Fans | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631592&prj=684&rqi=70Uk7pTLn3ZccytMrBvEs4uV0D
YT1ELEC-77-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_2_3 | LIBATT - UPS Battery |  |  | 1BATT_R2_2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631655&prj=684&rqi=BxBlr2Jnz4BcZr7dRH0DqiA0CV
YT1ELEC-79-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_R2_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_R2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631657&prj=684&rqi=SpFh0qevsuP3XQqbhnaBVW8r2P
YT1ELEC-66-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K2_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K2_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631637&prj=684&rqi=DxJC8UsBWr3zG2tW4fQUswGgWr
YT1ELEC-61-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631516&prj=684&rqi=S3wwqO5fRFxS2PkYTh1nODavdK
YT1ELEC-63-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K1_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K1_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631522&prj=684&rqi=eIOfaEce2lcm7ebPUz60PzlbRU
YT1ELEC-47-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H1_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H1_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631319&prj=684&rqi=0fs8i2lPyAJphZqJ8a42cqJNJD
YT1ELEC-350-002 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_H_1 | UPS - Uninterrupted Power Supply |  |  | Exhaust fan control wire from UPS_H_1/2/3 not correctly landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631286&prj=684&rqi=FCGhq68VwTyGAwOrylyf1YZcGe
YT1ELEC-43-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631307&prj=684&rqi=ZlJqaAICYatgsoOg9f2n7476KA
YT1ELEC-41-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G2_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631305&prj=684&rqi=jn8XcHjRU1uPOvSAXnA4I3YiWB
YT1ELEC-348-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_G_2 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G2 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631282&prj=684&rqi=yXaBXtkweY7qvv9xgWO08exEK6
YT1ELEC-151-001 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1PNL_R2_1_HP | DB - Distribution Boards |  |  | 1PNL_R2_1_HP 1CRAH_R2_13 (SKID CRAH_H_1) landed at 7,9,11 vice 1,3,5 1CRAH_R2_15 (SKID CRAH_H_2) landed at 1,3,5 vice 7,9,11 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631300&prj=684&rqi=oiJHAKwXMRTJRkFzOicRKdl6US
YT1ELEC-350-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_H_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_H1 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631283&prj=684&rqi=yYMLFhqecdanveGbQ4Pk4zVgrc
YT1ELEC-37-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G1_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G1_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631301&prj=684&rqi=Z8JsJRNmE56MqbsC1a1e73xrAZ
GT1ELEC-366-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Comms Issue/ Fault | DCOS | Electrical â€“ LV | equipment | 1GEN_G | GENL - Generator (LV) |  |  | 1GEN_G L4 P2P Testing - Identified discrepancy with the GCB breaker status sending inverted status signals to the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631260&prj=684&rqi=VwEEUpxB1MIugD9KwTSQfKvht5
YT1ELEC-384-001 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_J3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_J3 UPS_J_3 MBB breaker Q03 is missing its second set of aux contacts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631312&prj=684&rqi=Jss3FD2aravtDuXXMY6hkajbM9
YT1ELEC-44-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H1_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H1_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631309&prj=684&rqi=OIPYDJAC52diWREfXLTapTJj81
YT1ELEC-46-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H1_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H1_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631318&prj=684&rqi=YoQg6FcuIZyUuoAy3BpqvZ1gzt
YT1ELEC-38-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G1_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G1_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631302&prj=684&rqi=fhVVcwh5RpOTFu6G4p3Hx763KE
YT1ELEC-36-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G1_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G1_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631299&prj=684&rqi=XljlP7CX1j25Ai4QVo9TAURy4p
YT1ELEC-52-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631327&prj=684&rqi=fdk2ONNObHperI4imyO0GQR7YX
YT1ELEC-383-001 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_H3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_H3 UPS_H_3 MBB breaker Q03 is missing its second set of aux contacts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631311&prj=684&rqi=rQl6FNcuMD07TQR2U6MKIgd02R
YT1ELEC-39-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G2_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G2_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631303&prj=684&rqi=EGp5Q5rHAswuHUI5FPFrqWBGZP
YT1ELEC-385-002 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_K3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_K3 UPS_K_3 MBB breaker Q03 is missing its second set of aux contacts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631313&prj=684&rqi=rXZyzeEu1Z4Iwg4qd3oGae265j
YT1ELEC-50-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H2_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631322&prj=684&rqi=clply5DQuWzBrsfULOcmx2PHCf
YT1ELEC-40-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G2_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G2_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631304&prj=684&rqi=t2SFeDeJmVwZqXgRfXbDveGXoy
YT1ELEC-353-002 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_J_1 | UPS - Uninterrupted Power Supply |  |  | Exhaust fan control wire from UPS_J_1/2/3 not correctly landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631288&prj=684&rqi=LsYHc1IwRsUKZhZDf4ZbA7Hdq8
RT1ELEC-153-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Design Professional | L2A | Design correction needed | Design | Electrical â€“ LV | equipment | 1PNL_R2_2_H1 | DB - Distribution Boards |  |  | 1PNL_R2_2_H1 L2B SCCS lists all breakers as having fixed trip setpoints at 50A, however the EATON breakers installed, which are the correct breakers, have variable trip settings that need to be identified and adjusted on the breaker to ensure proper coordination and protection. The SCCS will need to be updated to reflect this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631222&prj=684&rqi=37saGn5xSeLY2fEXZ7e1cGmqLA
YT1ELEC-353-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_J_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_J1 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631285&prj=684&rqi=okZ0gcg0xKcVipiJQRni0iDFaX
YT1ELEC-360-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_2 | UPS - Uninterrupted Power Supply |  |  | 1UPS_R2_2 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631297&prj=684&rqi=JXUJeCbUW2e8TdNATAin2xtYY8
YT1ELEC-356-001 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_K_1 | UPS - Uninterrupted Power Supply |  |  | Exhaust fan control wire from UPS_K_1/2/3 not correctly landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631290&prj=684&rqi=OXp76tmWp7BxFPxpG29E3ZuQaj
YT1ELEC-45-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H1_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H1_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631317&prj=684&rqi=s6Nphf6PZeGMfDYC05GG4xydxP
RT1ELEC-155-002 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Design Professional | L2A | Design correction needed | Design | Electrical â€“ LV | equipment | 1PNL_R2_2_H3 | DB - Distribution Boards |  |  | 1PNL_R2_2_H3 L2B SCCS lists all breakers as having fixed trip setpoints at 50A, however the EATON breakers installed, which are the correct breakers, have variable trip settings that need to be identified and adjusted on the breaker to ensure proper coordination and protection. The SCCS will need to be updated to reflect this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631236&prj=684&rqi=XwBJv2kPaBU0ZGGJ7Z8DX3VRUn
YT1ELEC-356-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_K_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_K1 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631289&prj=684&rqi=6mw5oBJN2anLLF91XBTziE5v3l
YT1ELEC-49-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H2_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H2_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631321&prj=684&rqi=IYvNsK1L2kBM6L1SO7W2IAqk2q
YT1ELEC-386-002 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_R2_3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_R2_3 UPS_R2_3 MBB breaker Q03 is missing its second set of aux contacts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631314&prj=684&rqi=d54JEwmYtZ2PxNotNLJ6zHJPNj
YT1ELEC-357-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_K_2 | UPS - Uninterrupted Power Supply |  |  | 1UPS_K2 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631294&prj=684&rqi=I26zc77JHqjagbRa3DRgwcP2da
GT1ELEC-367-002 | SV18-2 | AMER | Ready for Verification | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Comms Issue/ Fault | DCOS | Electrical â€“ LV | equipment | 1GEN_H | GENL - Generator (LV) |  |  | 1GEN_H L4 P2P Testing - Identified discrepancy with the GCB breaker status sending inverted status signals to the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631267&prj=684&rqi=gEBmESnX67f8wFBazNHYSXctxm
YT1ELEC-35-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G1_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G1_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631298&prj=684&rqi=lCZDLjUX7lN1QLANGzV39KBnEh
YT1ELEC-351-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_H_2 | UPS - Uninterrupted Power Supply |  |  | 1UPS_H2 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631284&prj=684&rqi=WocpwIoUawlnahhmvYDz3zaTO3
YT1ELEC-95-004 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2B MSB HMI has 4 key-actuated selector switches, and only 3 are required. Per Hanley submittal drawing #HSU-5478FO-ELC-DWG02, this switch should be removed and blanked off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631208&prj=684&rqi=ss9bfaXC8cQonSLVuPF6NfNGlG
YT1ELEC-95-005 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2B The key-actuated selector switches on the MSB HMI lock the keys when not in the center position. The selector switches should not lock the keys in any position. Sheet 2 of Hanley Submittal Drawing #HSU-5478FO-ELC-DWG02 specifies this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631209&prj=684&rqi=cQ9DnauTD57u6TYpNsqQ7oKmJW
YT1ELEC-347-002 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_G_1 | UPS - Uninterrupted Power Supply |  |  | Exhaust fan control wire from UPS_G_1/2/3 not correctly landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631281&prj=684&rqi=9hgEbuf6lJxwSgQMilaHzvHNSU
YT1ELEC-382-002 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_G3 UPS_G_3 MBB breaker Q03 is missing its second set of aux contacts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631310&prj=684&rqi=FdCqrYQ4TjdBlIMo8XyKZ99juR
YT1ELEC-347-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_G_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G1 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631278&prj=684&rqi=IwF8phPnbmuppErqh7IcZJj0vy
YT1ELEC-359-001 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_1 | UPS - Uninterrupted Power Supply |  |  | Exhaust fan control wire from UPS_R_1/2/3 not correctly landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631295&prj=684&rqi=SKoRfb58rS0SChvK6rwurgtySV
YT1ELEC-354-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_J_2 | UPS - Uninterrupted Power Supply |  |  | 1UPS_J2 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631287&prj=684&rqi=ZDVoRKkeLWNzx0XdVFCjEtFFZq
YT1ELEC-51-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H2_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H2_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631326&prj=684&rqi=EHwmz2B5x3fyyBlLXxSm7xS1zJ
RT1ELEC-154-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Design Professional | L2A | Design correction needed | Design | Electrical â€“ LV | equipment | 1PNL_R2_2_H2 | DB - Distribution Boards |  |  | 1PNL_R2_2_H2 L2B SCCS lists all breakers as having fixed trip setpoints at 50A, however the EATON breakers installed, which are the correct breakers, have variable trip settings that need to be identified and adjusted on the breaker to ensure proper coordination and protection. The SCCS will need to be updated to reflect this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631235&prj=684&rqi=CRhqfUmJQo9W4ZuI7T9PP9fEBA
YT1ELEC-42-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G2_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G2_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631306&prj=684&rqi=lNtsHIEUSgXhOaoOJulRV5C3vi
YT1ELEC-359-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_R2_1 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631296&prj=684&rqi=i3U9HiA5eHylc8cYW6qeiNq4b2
YT1ELEC-48-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H2_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H2_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631320&prj=684&rqi=WOy1CTuZ2P9YotiDCgV5xHEByO
YT1ELEC-143-001 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1PNL_GEN_H | DB - Distribution Boards |  |  | 1PNL_GEN_H TRIP/CLOSE switch installed on all phase 2 generator panels. Close feature not operable IAW design. Switch not installed on phase 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631095&prj=684&rqi=PrdUiqq8fUTClxTt2BmogxQlm5
YT1ELEC-144-001 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1PNL_GEN_J | DB - Distribution Boards |  |  | 1PNL_GEN_J TRIP/CLOSE switch installed on all phase 2 generator panels. Close feature not operable IAW design. Switch not installed on phase 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631096&prj=684&rqi=mGMFJ7Hqlgna3v0JeCcK2c0Fes
YT1ELEC-145-001 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1PNL_GEN_K | DB - Distribution Boards |  |  | 1PNL_GEN_K TRIP/CLOSE switch installed on all phase 2 generator panels. Close feature not operable IAW design. Switch not installed on phase 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631097&prj=684&rqi=MZ3fBo8ZgPCPvvFvbb1GS9iWiH
YT1ELEC-147-001 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1PNL_GEN_R2 | DB - Distribution Boards |  |  | 1PNL_GEN_R2 TRIP/CLOSE switch installed on all phase 2 generator panels. Close feature not operable IAW design. Switch not installed on phase 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631098&prj=684&rqi=IMkgCRd4HqA1QvArKzXvkgJEF2
YT1ELEC-149-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1PNL_J_HP | DB - Distribution Boards |  |  | (1PNL_J_HP) L2B: Panel schedule does not match the wire tag. Verified that wire tag is correct.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631100&prj=684&rqi=YChp7aR6sFVhpMr2isGc1Va94s
YT1ELEC-142-001 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1PNL_GEN_G | DB - Distribution Boards |  |  | 1PNL_GEN_G TRIP/CLOSE switch installed on all phase 2 generator panels. Close feature not operable IAW design. Switch not installed on phase 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631094&prj=684&rqi=kSGspZD0yOplc5pU4d9Tv30Ffd
YT1ELEC-95-003 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | 1MSB_K HMI Label plate does not show all switch positions listed in the submittal. Switch label should show all three positions (Auto/Auto, Auto/Man, Man/Man). See attach example. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630757&prj=684&rqi=xcgCrNenTYWyyhvH0ZFHgXSLIL
GI-004 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design | [6 empty] | Various issue and in consistantcies found in rev 2 of SCCS: UNPL and PNL breakers listed as fixed. Breakers are adjustable. ABB breakers do not allow for S and Int setpoint to be the same value. S must be smaller than INT | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630773&prj=684&rqi=p2GLpNxHN4QXuN3s2sVlmZ8D6u
YT1ELEC-385-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_K3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_K3 L2B K3 Kirk Key (64400) is missing for this UMDSB. Hanley has spare key and will expedite a shipment to site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630750&prj=684&rqi=hKeT6G1CwFRTgeLDwiHRejGyTy
YT1ELEC-92-002 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | 1MSB_G HMI Label plate does not show all switch positions listed in the submittal. Switch label should show all three positions (Auto/Auto, Auto/Man, Man/Man). See attach example. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630761&prj=684&rqi=wICLih5z1U2z5kdleBVRNi01BS
YT1ELEC-96-004 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | 1MSB_R2 HMI Label plate does not show all switch positions listed in the submittal. Switch label should show all three positions (Auto/Auto, Auto/Man, Man/Man). See attach example. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630754&prj=684&rqi=QUHX0AQUS2a5bIcoQsZcp64WEQ
YT1ELEC-386-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_R2_3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_R2_3 L2B K3 Kirk Key (64400) is missing for this UMDSB. Hanley has spare key and will expedite a shipment to site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630751&prj=684&rqi=f9Tz2nLwfxuoBphIwWAD01CvmX
YT1ELEC-93-004 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | 1MSB_H HMI Label plate does not show all switch positions listed in the submittal. Switch label should show all three positions (Auto/Auto, Auto/Man, Man/Man). See attach example. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630760&prj=684&rqi=zPdJgtYrwgOpMHveZAJIPrPEWb
YT1ELEC-94-002 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | 1MSB_J HMI Label plate does not show all switch positions listed in the submittal. Switch label should show all three positions (Auto/Auto, Auto/Man, Man/Man). See attach example. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630758&prj=684&rqi=93U4itTHRFtVZqSDVTVByKaWQN
GT1ELEC-145-001 | SV18-2 | AMER | Open | P2 Medium CX | ian.tsurumoto@veolia.com | 2026-07-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1PNL_H_HP | DB - Distribution Boards |  |  | 1PNL_H_HP 1CRAH_H_13 (SKID CRAH_H_1) landed at 2,4,6 vice 1,3,5 1CRAH_H_14 (SKID CRAH_H_2) landed at 1,3,5 vice 2,4,6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630624&prj=684&rqi=Ozst1zoDKbyzQE4myzaLB9l2tf
YT1ELEC-88-002 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MDSB_J | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_J) L2BÂ Panel grounding strap not installed in top hat.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630480&prj=684&rqi=5U6KFJL0BscZQJzKpm67PojvYb
YT1ELEC-96-003 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-22 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB_R2) L2B Failed comm cable in MSB_R2 that connects to PQM3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630433&prj=684&rqi=aobGZStah0R8mMJNqKQIOmL32f
YT1MECH-66-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_14 | CRAH - Computer room air handler (Skid) |  |  | (CRAH-H-14) L2B Schrader valve core missing from vent point top left of coil | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630391&prj=684&rqi=kb8RvzIIumLUqDI2Dur00eruFl
YT1MECH-40-001 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-07-22 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_03 | CRAH - Computer room air handler |  |  | (1CRAH_H_03) L2B Source 2 disconnect has been broken off. Replacement needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630461&prj=684&rqi=RoE3QjllZsLptblKE3toQn46wn
YT1ELEC-86-004 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_G) L2B Ground connection to a panel cover was not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630175&prj=684&rqi=wZK6aEBv3vUA3XAWWvSFeP18Sv
YT1ELEC-86-005 | SV18-2 | AMER | Closed | P2 Medium CX | ian.tsurumoto@veolia.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | washer found the on incoming bus on MDSB_G | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630621&prj=684&rqi=MzUigQdK7LF0bISrw0bROpfdu0
YT1ELEC-86-006 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | MDSB_G panel ground inside top hat found disconnected during final inspection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630622&prj=684&rqi=Z5A1umGm7Bzvswfdyt9FXprq00
YT1ELEC-92-001 | SV18-2 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | 1MSB_G Level 2B MSB drawings do not have 240VAC control power called out on drawings or physical terminals in Section 02A in MSB for 1BATT_G_3. (Note: Typical of all MSBs.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629459&prj=684&rqi=byZTpp3DCf2oim817oZxozakVO
YT1ELEC-86-003 | SV18-2 | AMER | Open | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_G L2B Breaker 1UPS_G_3-RIB (Q07) does not have wires pulled or installed on aux contacts for UPS RIB breaker status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629468&prj=684&rqi=sSIHanxQnA8LGQr3HOVIyWnw8T
YT1ELEC-93-003 | SV18-2 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | 1MSB_H Level 2B MSB drawings do not have 240VAC control power called out on drawings or physical terminals in Section 02A in MSB for 1BATT_H_3. (Note: Typical of all MSBs.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629462&prj=684&rqi=PDmvidaJWACdBUkxbSrfJMNS2r
YT1ELEC-95-002 | SV18-2 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | 1MSB_K Level 2B MSB drawings do not have 240VAC control power called out on drawings or physical terminals in Section 02A in MSB for 1BATT_K_3. (Note: Typical of all MSBs.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629464&prj=684&rqi=JXs25qLYIXnzF0IzFPwnZswwiD
YT1ELEC-96-002 | SV18-2 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | 1MSB_R2 Level 2B MSB drawings do not have 240VAC control power called out on drawings or physical terminals in Section 02A in MSB for 1BATT_R2_3. (Note: Typical of all MSBs.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629465&prj=684&rqi=GfE59R12qqHQXF3Ws5mFSnRIAy
YT1ELEC-96-001 | SV18-2 | AMER | Work Completed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | 1MSB_R2 Level 2B Please see the images below. Need to confirm control wiring (PLC Jumpers) for 1MSB_R2 - Q12 (MBB), Q13 (LBB1), Q14 (IOB1), Q15 (LBB2), Q16 (IOB2). Currently no wiring installation is present in section 10A of MSB. Serial Number: HSUDKEX-6027DV-001 Drawing No: HSU-6027DV-ELC-DWG01 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629458&prj=684&rqi=OdINZ5U6h3w2lyJ5Y94UtiRGlr
YT1ELEC-87-002 | SV18-2 | AMER | Open | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MDSB_H | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_H L2B Breaker 1UPS_H_3-RIB (Q07) does not have wires pulled or installed on aux contacts for UPS RIB breaker status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629469&prj=684&rqi=BwBDR7po6OdMqeuSwYWtbQgsQD
YT1ELEC-90-002 | SV18-2 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design | Electrical â€“ LV | equipment | 1MDSB_R2_1 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_R2_1 Level 2B Aux contacts for breaker status on 1UPS_R2_3-RIB (Q07) are not installed. Aux contacts are installed on XQ10 which is a SPARE. Submittals will need to be updated to reflect aux contacts. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629467&prj=684&rqi=kxfM0xRvq75wbXV9vQylHMDT85
YT1MECH-88-003 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-15 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (HP-K-1) L2B Overhead junction box has an unfinished splice that should be a continuous run per Equinix electrical design. Please run a new line from PNL-R2-2-H-1 with no splice. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629434&prj=684&rqi=OJO4reHeKWimXJFlpHWm2bxujr
YT1MECH-86-003 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-15 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (HP-J-1) L2B Overhead junction box has an unfinished splice that should be a continuous run per Equinix electrical design. Please run a new line from PNL-R2-2-H-2 with no splice. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629433&prj=684&rqi=lohTo2Qd9tVyjQ8bAEvPp8WCVg
YT1ELEC-88-001 | SV18-2 | AMER | Open | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MDSB_J | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_J L2B Breaker 1UPS_J_3-RIB (Q07) does not have wires pulled or installed on aux contacts for UPS RIB breaker status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629470&prj=684&rqi=OPSPX4bRKwDfvudjxyqp89l0nM
YT1ELEC-89-001 | SV18-2 | AMER | Open | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MDSB_K | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_K L2B Breaker 1UPS_J_3-RIB (Q07) does not have wires pulled or installed on aux contacts for UPS RIB breaker status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629471&prj=684&rqi=yMWMeTk2vWMNjmaoELbEhApoVB
YT1ELEC-94-001 | SV18-2 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | 1MSB_J Level 2B MSB drawings do not have 240VAC control power called out on drawings or physical terminals in Section 02A in MSB for 1BATT_J_3. (Note: Typical of all MSBs.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629463&prj=684&rqi=FxqaLv1nRWav4Th2Y0dYd1BSC2
YT1ELEC-86-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_G (L2B) The lug kits for breaker Q03 that feed 1TX_G_R1 are the wrong size and need to be replaced. This work has been completed by Hanley and verified by Veolia. Adding this issue item as a closed case. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629416&prj=684&rqi=1FYwAV0iFOj9mC6m3nxQThlGce
YT1MECH-72-001 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_14 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_K_14) L2B The line side of both Source A and Source B breakers are missing phase separators. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629236&prj=684&rqi=e5V3wWC735ogY4gzrJYOYm0pVT
YT1MECH-73-001 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_15 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_K_15) L2B The line side of both Source A and Source B breakers are missing phase separators. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629237&prj=684&rqi=svkEx7WVkFNBqbVFk6ogZKaxYs
YT1ELEC-90-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R2_1 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_R2_1 (L2B) Grounding bushing on top of 1MDSB_R2_1 is loose and needs to be tightened. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629235&prj=684&rqi=k3knXIzs5TdYxjcF3EdtPGTr7D
YT1ELEC-9-002 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-14 04:00:00.000 +0400 | SCH - Schneider MV | L2B | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_R2 | RMU - Ring Main Unit |  |  | (1RMU_R2) L2B Missing nut insert for section 2 dead front panel.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629231&prj=684&rqi=yJrOgpnFEGCvivajNl00vEOWl4
YT1ELEC-87-001 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MDSB_H | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_H (L2B) Cable entry bushings into MDSB_H are not seated properly and need to be adjusted to sit correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629234&prj=684&rqi=uKuTABN2ZzN7fti8Y17qYJGZTU
YT1MECH-87-002 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | 1HP_J_2 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629051&prj=684&rqi=bgmXxWNEdp28xon8yxhEBCbvyv
YT1MECH-90-003 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | 1HP_R2_1 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629056&prj=684&rqi=abfH6E8qOIdrFQum4MHZRjuwKP
YT1ELEC-358-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_K3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_K3 (L2B) Green plug adapter for the control power/comm cables inside of the cabinet does not exist and needs to be installed to allow for Rosendin to terminate connections on 1UPS_K3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629090&prj=684&rqi=U48QRovNvwnpqqWlJQYNbOH7lN
YT1MECH-88-002 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | 1HP_K_1 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629054&prj=684&rqi=ybzIhRFd6UWkrsSDwemeZrtXdR
YT1MECH-77-004 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_G_1 | EF - Exhaust Fan |  |  | 1EF_G_1 L2B Control wires are pulled from UPS_1 and UPS_2, but no control wires are pulled from UPS_3 to Exhaust Fan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629062&prj=684&rqi=o9hRAP5c6U6De9nRSa7ecguK3f
YT1MECH-77-003 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1EF_G_1 | EF - Exhaust Fan |  |  | (EF-G-1) L2B Overhead junction box splices 120V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629048&prj=684&rqi=kgAhnbRm6MN9rj8qp90BJxSflt
YT1ELEC-93-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | 1MSB_H (L2B) The breaker rack in device for Q03 (LB Breaker) in 1MSB_H broke during routine testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629086&prj=684&rqi=BVIXWxCktyrzL5LGrz0NAMZFLd
YT1MECH-79-004 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_J_1 | EF - Exhaust Fan |  |  | 1EF_J_1 L2B Control wires are pulled from UPS_1 and UPS_2, but no control wires are pulled from UPS_3 to Exhaust Fan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629065&prj=684&rqi=ZNk9IZqzaRkZHhgT1C4ot2bw7N
GT1ELEC-367-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_H | GENL - Generator (LV) |  |  | 1GEN_H (L3) KW and PF indications on the GCB and HMI are negative for some values. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629028&prj=684&rqi=sL9JFmtp7UeZP7p4xW1AsaqI9s
YT1MECH-78-003 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_H_1 | EF - Exhaust Fan |  |  | 1EF_H_1 L2B Control wires are pulled from UPS_1 and UPS_2, but no control wires are pulled from UPS_3 to Exhaust Fan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629064&prj=684&rqi=E6hLBGgNVEOiOL6bjARxbyYXbr
YT1MECH-86-002 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | 1HP_J_1 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629049&prj=684&rqi=3AM01qVJWN0HWXQwu5UTeJt28v
YT1MECH-82-002 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | HP_G_1 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629033&prj=684&rqi=rxOkM1eGMEvq1EvOrx5msH5Bvo
YT1MECH-81-004 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_R2_1 | EF - Exhaust Fan |  |  | 1EF_R2_1 L2B Control wires are pulled from UPS_1 and UPS_2, but no control wires are pulled from UPS_3 to Exhaust Fan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629068&prj=684&rqi=xNnTNYbnqAphbxs5NfVmiNbPHg
YT1MECH-85-002 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | 1HP_H_2 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629047&prj=684&rqi=h0wuOq52DxfDSdNViLmy44m8xQ
YT1ELEC-361-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_R2_3 (L2B) Green plug adapter for the control power/comm cables inside of the cabinet does not exist and needs to be installed to allow for Rosendin to terminate connections on 1UPS_R2_3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629091&prj=684&rqi=DStMG8dP2pmnJ21x9gvQqZZnW6
YT1MECH-80-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1EF_K_1 | EF - Exhaust Fan |  |  | (EF-K-1) L2B Overhead junction box splices 120V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629060&prj=684&rqi=wX6noJ3lCiu7GQixwgkIHUYjvY
YT1MECH-80-004 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_K_1 | EF - Exhaust Fan |  |  | 1EF_K_1 L2B Control wires are pulled from UPS_1 and UPS_2, but no control wires are pulled from UPS_3 to Exhaust Fan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629067&prj=684&rqi=UVjdDYzllBhX1eYdmqQZpwmeDW
YT1ELEC-352-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_H3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_H3 (L2B) Green plug adapter for the control power/comm cables inside of the cabinet does not exist and needs to be installed to allow for Rosendin to terminate connections on 1UPS_H3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629088&prj=684&rqi=NXTGbiEeum1wO6lbeDvrWoYtgD
YT1MECH-84-003 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (HP-H-1) L2B Overhead junction box splices 480V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629042&prj=684&rqi=BGJFeCHxkP0mAxKJ3TQdS80Iwl
YT1ELEC-349-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G3 (L2B) Green plug adapter for the control power/comm cables inside of the cabinet does not exist and needs to be installed to allow for Rosendin to terminate connections on 1UPS_G3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629087&prj=684&rqi=xepwLf8oKPUjQFiSqbsBoGYmFJ
YT1MECH-89-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (HP-K-2) L2B Overhead junction box splices 480V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629045&prj=684&rqi=ktUvodHJhBMPsvpVTAJPI2AKWa
YT1MECH-89-003 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | 1HP_K_2 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629055&prj=684&rqi=9pFxmXuSsNut0xiPhYKGaTCq9D
YT1MECH-84-004 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | 1HP_H_1 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629046&prj=684&rqi=IjBKs1z8oI84jAEtqLJPyfj0Ge
YT1MECH-83-003 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | HP_G_12 L2B No torque marks in WSHP 20 in lb required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629043&prj=684&rqi=ypnLblZBVW4BgZokQ8AUlMPRyS
YT1MECH-82-003 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (HP-G-1) L2B Overhead junction box splices 480V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629044&prj=684&rqi=NCwoScXa9zuT1Fdz8xLXQH89nE
YT1MECH-79-003 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1EF_J_1 | EF - Exhaust Fan |  |  | (EF-J-1) L2B Overhead junction box splices 120V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629058&prj=684&rqi=RDj1hDXTk70fbSRr4RNMzK0pqC
YT1ELEC-355-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_J3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_J3 (L2B) Green plug adapter for the control power/comm cables inside of the cabinet does not exist and needs to be installed to allow for Rosendin to terminate connections on 1UPS_J3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629089&prj=684&rqi=aopuNtJzxc11xtPSlhFcG4UUof
YT1MECH-81-003 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1EF_R2_1 | EF - Exhaust Fan |  |  | (EF-R2-1) L2B Overhead junction box splices 120V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629061&prj=684&rqi=9egnauUsn9VEGYaFt0XSdqIMP5
YT1MECH-91-002 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | 1HP_R2_2 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629057&prj=684&rqi=ElangQ5FBZvnsrF8iCtkb6cGMS
YT1MECH-78-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Controls Contractor | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_H_1 | EF - Exhaust Fan |  |  | (Electrical Skid H) L2B Leak detection communication cable needs to be connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628752&prj=684&rqi=NFEM5pW2mjT7zjDQaV358qGBye
YT1MECH-80-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_K_1 | EF - Exhaust Fan |  |  | (Electrical Skid K) L2B UPS to Fan interconnection needs to be terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628749&prj=684&rqi=IGnX4YH0jVzd0poEgzczDizdyM
YT1MECH-77-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_G_1 | EF - Exhaust Fan |  |  | (Electrical Skid G) L2B UPS Fan interconnection needs to be terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628744&prj=684&rqi=vs0WhJotUXDJ8kI4TsDdBs0N8i
YT1ELEC-382-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-10 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_G (L2B) Phase C lug for Breaker Q04 is stripped and needs to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628737&prj=684&rqi=Bbc49OHaFnl0HbMoH8NecWqIVO
YT1MECH-79-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_J_1 | EF - Exhaust Fan |  |  | (Electrical Skid J) L2B UPS to Fan interconnection needs to be terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628746&prj=684&rqi=S7ph61hrjDATYlWnzBo7Zf2T8d
YT1MECH-80-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Controls Contractor | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_K_1 | EF - Exhaust Fan |  |  | (Electrical Skid K) L2B Leak detection communication cable needs to be connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628754&prj=684&rqi=odJcOeP516tcFPVC7ljygUznF3
YT1MECH-78-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_H_1 | EF - Exhaust Fan |  |  | (Electrical Skid H) L2B UPS to Fan interconnection needs to be terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628745&prj=684&rqi=RHHX40iTZQCBc2mkRySWPpmbEi
YT1MECH-77-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Controls Contractor | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_G_1 | EF - Exhaust Fan |  |  | (Electrical Skid G) L2B Leak detection communication cable needs to be connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628751&prj=684&rqi=mKJ6dbGeWvdtXvR0P1irasQyRA
YT1MECH-81-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Controls Contractor | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_R2_1 | EF - Exhaust Fan |  |  | (Electrical Skid R2) L2B Leak detection communication cable needs to be connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628755&prj=684&rqi=pd2lXI0yKG3EHZXSZVaLL6pvpn
YT1MECH-79-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Controls Contractor | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_J_1 | EF - Exhaust Fan |  |  | (Electrical Skid J) L2B Leak detection communication cable needs to be connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628753&prj=684&rqi=7GFoiA8qm4S2RfazLFP3Usc87Q
YT1MECH-81-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_R2_1 | EF - Exhaust Fan |  |  | (Electrical Skid R2) L2B UPS to Fan interconnection needs to be terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628750&prj=684&rqi=maBeCdBSNaGR1rdCBsOjYx7gHH
YT1MECH-84-002 | SV18-2 | AMER | Open | P2 Medium CX | ethan.hang@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (1HP_H_1) L2B Flex conduit connections are lose. Please connect and tighten. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628622&prj=684&rqi=wLpaecDvCw4W6JZWmRrNzjTidB
YT1MECH-83-002 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (1HP_G_2) L2B Flex conduit connections are lose. Please connect and tighten. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628623&prj=684&rqi=t4635A8lBnKhWnPp6GoqYwin6q
YT1MECH-90-002 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-09 04:00:00.000 +0400 | Electrical Contractor | L2B | Incomplete Connections | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L2B Flex conduit connections are lose. Please connect and tighten. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628621&prj=684&rqi=cUzSfOWWTXsnXPhrOsxAbYnCyw
YT1MECH-86-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (1HP_J_1) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628447&prj=684&rqi=FXKuLhIN6glRXIsV1W6zjTwUJP
YT1MECH-87-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | (1HP_J_2) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628448&prj=684&rqi=elP2A9EWiPAmMF6dv0LS0SZrwp
YT1MECH-91-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (1HP_R2_2) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628452&prj=684&rqi=Q4JlddhC5pff3ptwSpMMua1wkA
YT1MECH-88-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (1HP_K_1) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628449&prj=684&rqi=cgkicRxKsRJWzuFXojbBUWnO9f
YT1MECH-85-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (1HP_H_2) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628446&prj=684&rqi=5WSKQaAcdxAxwf4Fp7FqaDgAV9
YT1MECH-84-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (1HP_H_1) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628445&prj=684&rqi=37QFHVcejUsDPJnxR12s2gcR5n
YT1MECH-83-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (1HP_G_2) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628444&prj=684&rqi=AKj2UYi73QV0kum5FEb5h6Lfx4
YT1MECH-89-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (1HP_K_2) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628450&prj=684&rqi=3QM1wjhciXVb2KbPggkTfYeDuL
YT1MECH-90-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628451&prj=684&rqi=Zgb7AaRaA7Vbh3gfg5QO7GakkY
YT1MECH-82-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (1HP_G_1) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628443&prj=684&rqi=tFRASABRg6ayAtLF7XPSGrP0Tt
YT1ELEC-9-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-07 04:00:00.000 +0400 | Controls Contractor | L2B | DCOS Design Issue | DCOS | Electrical â€“ MV | equipment | 1RMU_R2 | RMU - Ring Main Unit |  |  | (1RMU_R2) L2B 3rd section of RMU does not communicate with BMS.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628259&prj=684&rqi=gwsxeTnsaT7aGpIkQrupUeXIPo
RT1ELEC-386-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_K3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_K3 (L2A) Breaker Q03 is not padlockable because it does not have the locking mechanism installed on the breaker. Per the submittal, drawing # HSU-5736GL-ELC-DWG01 sheet 2, the breaker should be equipped with a locking mechanism that prevents operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628215&prj=684&rqi=ANHYydRQZDChZIn8tzNCqMMaub
RT1ELEC-385-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_J3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_J3 (L2A) Breaker Q03 is not padlockable because it does not have the locking mechanism installed on the breaker. Per the submittal, drawing # HSU-5736GL-ELC-DWG01 sheet 2, the breaker should be equipped with a locking mechanism that prevents operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628213&prj=684&rqi=Mu6rgCCnpMiCF9tBIsrUagiMY6
GI-003 | SV18-2 | AMER | Closed | P2 Medium CX | dustin.haugh@veolia.com | 2026-07-07 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1PDU_F1_2 | PDU - Power Distribution Unit |  |  | All PDUâ€™s in data hall are missing one front left floor mounting bolt. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628247&prj=684&rqi=3w9GvNxiD5nrDG8reVqdD9hoWq
RT1ELEC-384-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_H3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_H3 (L2A) Breaker Q03 is not padlockable because it does not have the locking mechanism installed on the breaker. Per the submittal, drawing # HSU-5736GL-ELC-DWG01 sheet 2, the breaker should be equipped with a locking mechanism that prevents operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628210&prj=684&rqi=zx4EfO34BvBvYhAOEI15bE6l47
RT1ELEC-383-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_G3 (L2A) Breaker Q03 is not padlockable because it does not have the locking mechanism installed on the breaker. Per the submittal, drawing # HSU-5736GL-ELC-DWG01 sheet 2, the breaker should be equipped with a locking mechanism that prevents operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628206&prj=684&rqi=sL5GEUJuxAwSlrALFywSR8ECxF
RT1ELEC-387-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_R2_3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_R2_3 (L2A) Breaker Q03 is not padlockable because it does not have the locking mechanism installed on the breaker. Per the submittal, drawing # HSU-5736GT-ELC-DWG01 sheet 2, the breaker should be equipped with a locking mechanism that prevents operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628217&prj=684&rqi=tmCgA92oXL2PIUTowlYCBS7BDR
RT1ELEC-49-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H2_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_H2_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627720&prj=684&rqi=UHCLszdDnQ6TVLFxpiNdwDvvSn
RT1ELEC-63-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K1_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_K1_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627725&prj=684&rqi=AG8jYzJvAlbEYLEBjKx057srEL
RT1ELEC-54-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J1_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_J1_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627722&prj=684&rqi=9jNYhwbBCk9zulx4MJdaFpzKeG
RT1ELEC-67-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K2_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_K2_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627726&prj=684&rqi=miXTxoPrfSUJT4ekFm9oONS67r
RT1ELEC-62-002 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_J3) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627724&prj=684&rqi=4mkFdO58EuDqJhnPnZSqjB8ej7
RT1ELEC-53-002 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_H3) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627721&prj=684&rqi=WpHti8qzaOrIJXx24w4elByD5W
YT1MECH-9-003 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-02 04:00:00.000 +0400 | TRN - Trane | L2B | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1ACC_G_16 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_G_16) L2B For tracking purposes, the UPS was cannibalized and needs to be replaced. Per Ryan Vincent, for SV18-1b, the UPS failed at 2-2.5 hours at 100%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627744&prj=684&rqi=dPYAkRv8y5bH9vpqY70djjrPrd
YT1ELEC-86-001 | SV18-2 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Design Professional | L2B | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_G) L2A: In the SCCS, there is an issue across ALL MDSB where breaker 1TX_X_R1 is missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627717&prj=684&rqi=qEzZ7ggnbtZPHevmUTUW2JStqh
RT1ELEC-76-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_2_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_R2_2_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627729&prj=684&rqi=m4eAb5hsK48jhG2d6DPIBE9oce
RT1ELEC-8-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-02 04:00:00.000 +0400 | SCH - Schneider MV | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1RMU_K | RMU - Ring Main Unit |  |  | (1RMU_K) L2B Breaker operator has been bent during breaker exercising for P2P checks. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627745&prj=684&rqi=bVJuU6P7h53lx8NjoPtvILvt4V
RT1ELEC-80-002 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_R2_3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_R2_3) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627730&prj=684&rqi=byVrUhT0ZoyEs4q5D5EJD6ymH9
RT1ELEC-72-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_1_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_R2_1_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627728&prj=684&rqi=SRJC8WBO98SGZLwPESxWit8lY9
RT1ELEC-58-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J2_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_J2_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627723&prj=684&rqi=wpeNdk29ZZRqLn6h6kEHong2Nh
RT1ELEC-45-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H1_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_H1_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627719&prj=684&rqi=SVTMMTx3iezmatgOKCnMp41n3t
RT1ELEC-71-002 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_K3) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627727&prj=684&rqi=KFINZ03Y1G8lAuQ5Xzwa4Sxs9x
RT1ELEC-384-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-30 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_H3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | (1UMDSB_H3) L2A REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1UPNL_H3_H1 (Q09) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627476&prj=684&rqi=gyLS0snfq12xxoW9CW8yoBsgDY
RT1ELEC-44-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_G3) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627435&prj=684&rqi=bFAcR7sDR9bymMqEm8yh8fMX7r
RT1ELEC-40-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G2_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_G2_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627415&prj=684&rqi=vrTZXGU4D3LAWFa2Bajqb8ILiu
RT1ELEC-155-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-30 04:00:00.000 +0400 | Owner | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1PNL_R2_2_H3 | DB - Distribution Boards |  |  | (SKID R2 HP in F) L2A RFI 539: WSHP #2 Power Supply at PH F (Panel R2-2 Dependency) determined that the HP in SKID F has a power supply that is fed from 1PNL_R2_2_H3. The SKID F HP will be installed and ran on temporary power until the end of the SV18-2 project once SKID R2 has completed all Cx activities. Once ready to restore normal power to 1PNL_R2_2_H3, the temp power system and any associated conduit will need to be removed from SKID F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627450&prj=684&rqi=Wvte8t2GDrNmZIbLk0pDS8w6jv
RT1ELEC-383-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-30 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | (1UMDSB_G3) L2A REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1UPNL_G3_H1 (Q09) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627475&prj=684&rqi=NrNdn5kmtKH6tf2AYguZwVMqhp
RT1MECH-88-008 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (Electrical Skid K) L2A At the SW doors, the speaker strobe & pull station devices cannot be installed as the back boxes are too close to the adjacent conduit and security JB respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627243&prj=684&rqi=NL9eDjtSW20AoIyxQDpd5mq8hw
RT1MECH-86-008 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (Electrical Skid J) L2A At the SW doors, the speaker strobe & pull station devices cannot be installed as the back boxes are too close to the adjacent conduit and security JB respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627242&prj=684&rqi=uljqaJeM42Q0Y2zIfVRpbRGssy
RT1ELEC-360-002 | SV18-2 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_1 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_1) L2A: Battery cable missing grommet.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627152&prj=684&rqi=JFWrVjmnyUMPmvO3diK7a7idD8
RT1ELEC-361-002 | SV18-2 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_2 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_2) L2A: Multiple battery cables missing grommets.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627153&prj=684&rqi=ceYkQ7dX2TxuRUdUbXkZi7zkfO
RT1ELEC-97-005 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (MSB R2) L2A: Gen main breaker has issues with control module. Not sending power to HMI and ERMS.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627150&prj=684&rqi=Tua5YNfw9Ff56neyu2nOXu3fZt
RT1ELEC-97-006 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB R2) L2A: Missing lock tumbler for section 01C.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627151&prj=684&rqi=9BQKblrsjNlO0gj1903gXr190n
YT1ELEC-95-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2B During P2P checks, it was identified that the CAT6 cable connecting between 1MSB_K Section 02A and the DMark Panel in SKID K does not work. We verified this by connecting an external CAT6 cable between the two connections and the system worked correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626997&prj=684&rqi=UceYZXx8clJyMwJry3zifGrcw2
YT1ELEC-369-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_G | GENL - Generator (LV) |  |  | (1GEN_G) L2B GEN_G door enclosure to the HMI panel has a bent frame from the temporary rigging that was installed to gain access to the equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626250&prj=684&rqi=MJ5sj7Scmj5O7VTeQgP7JBEtn0
YT1ELEC-373-001 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-06-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_R2 | GENL - Generator (LV) |  |  | (1GEN_R2) L2B Piping feeding to the pressure transducer on the SCR is routed incorrectly and not connected to the transducer. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626259&prj=684&rqi=PxAOO7nRd3Hmd2T1QNtVm4LOLA
RT1MECH-63-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_14 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_G_14) L2A Missing screws on fan access panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625863&prj=684&rqi=G5tblYBDzWWzpkHOGMsJk42iZQ
RT1ELEC-36-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G1_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_G1_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625852&prj=684&rqi=sfrVRnib7Uxjby9resp0uhrz7J
RT1MECH-74-002 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-06-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_R2_13 | CRAH - Computer room air handler (Skid) |  |  | (CRAH-R2-13) L2A Fan power interconnections not connected correctly. Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625870&prj=684&rqi=KPog9Hb9B7dXvcZhj75XrRfadO
YT1ELEC-93-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-18 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | (1MSB_H) L2B Breaker Q15 (1ACC_H_14) failed to trip during NETA secondary injection testing of the equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625855&prj=684&rqi=V8W9PIou1fUQZqwdObikIhP4wy
RT1MECH-62-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_13 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_G_13) L2A Several missing screws on fan access panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625862&prj=684&rqi=Qg9DNNULbYb42y1Bg1fqv2zNMj
RT1MECH-68-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_J_13 | CRAH - Computer room air handler (Skid) |  |  | (CRAH-J-13) L2A Torque marks missing from fan section. Bolt pictured is hand-loose. Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625693&prj=684&rqi=UkaPjwd0vj802tf0CVYfQQMQNx
RT1MECH-67-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_15 | CRAH - Computer room air handler (Skid) |  |  | (CRAH-H-15) L2A Fan power wiring in left fan section need to be zip tied down. Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625692&prj=684&rqi=fXgxwKnCALIsSgFLtyvWJQsfxD
RT1ELEC-360-001 | SV18-2 | AMER | Closed | P2 Medium CX | ian.tsurumoto@veolia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_1 | UPS - Uninterrupted Power Supply |  |  | Verify Internal Electrical wiring is completed UPS_R2_1 and UPS_R2_2 Parallel UPS communication cable missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625689&prj=684&rqi=mTu5DZtbuaiopR0n7B3yGlXbfs
RT1ELEC-361-001 | SV18-2 | AMER | Closed | P2 Medium CX | ian.tsurumoto@veolia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_2 | UPS - Uninterrupted Power Supply |  |  | Verify Internal Electrical wiring is completed UPS_R2_1 and UPS_R2_2 Parallel UPS communication cable missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625690&prj=684&rqi=jWJSMaYD8bWwUmma8UmCKcB9Ku
RT1ELEC-370-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-16 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_G | GENL - Generator (LV) |  |  | (1GEN_G) L2A Broken bolt on grounding bar in the back of the GCB enclosure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625483&prj=684&rqi=EeM0jxw3iaI4YZVyw9RaqlZmXL
RT1MECH-42-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-16 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_05 | CRAH - Computer room air handler |  |  | (1CRAH_H_05) Filter bracket 5 back top and 6 back bottom are missing screws. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625547&prj=684&rqi=bRo3JthmqyqcKsfmeHDpUoudUT
GI-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-16 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | [6 empty] | (1_LBSB) Inspection During inspection of various equipment, it was identified that the Kirk Key cylinder on the Temp Gen breaker for the LBSB is incorrect. The LBSB Temp Gen breaker has a K1 kirk key barrel that has the serial number of '64161'. This does not match the currently installed/ordered GCB K1 kirk key barrels which have a serial number of '64393'. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625533&prj=684&rqi=pqY6LTlxFGfv36R0xj2V48uX9M
RT1MECH-73-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_15 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_K_15) L2A Top left Screw missing on supply air grate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625546&prj=684&rqi=QZNPzPe4XnUoCIDALw1CJB4Qbk
RT1MECH-87-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | (HP-J-2) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625372&prj=684&rqi=VpsbBLHowHYrEMByYhNZC9l6Bb
RT1MECH-85-004 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (HP-H-2) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625370&prj=684&rqi=UOaWgu8QriU7WkXesjZ8ZK3lXP
RT1MECH-86-007 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (HP-J-1) Merv 4 filters are currently installed. Must be Merv 8 to match skids G, H, R2. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625375&prj=684&rqi=hcCEvxVcYwC2JPY3Ri7kYDVJJH
RT1MECH-84-008 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (HP-H-1) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625369&prj=684&rqi=OJAVljV84hbtDiC0hqAO7jTPQE
RT1MECH-90-008 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (HP-R2-1) L2A Unit needs to have flex ducting installed between main fan compartment and ducting. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625380&prj=684&rqi=oKcUjlRO91CGXajvxTWDPkuJOI
RT1MECH-89-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (HP-K-2) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625374&prj=684&rqi=KUsulAKFRYOVHYlLMro4jxr09X
RT1MECH-86-006 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (HP-J-1) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625371&prj=684&rqi=hhlQ5CjPUT8cdUrlbwmm2fYZcA
RT1MECH-89-004 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (HP-K-2) Merv 4 filters are currently installed. Must be Merv 8 to match skids G, H, R2. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625379&prj=684&rqi=gHklRiHFddcEyCn3ThCZNgRvxX
GI-001 | SV18-2 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_G | GENL - Generator (LV) |  |  | (1GEN_G) L2A Broken bolt on grounding bar in the back of the GCB enclosure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625381&prj=684&rqi=K38Zy3UWrQxaAl7tkODmsBSruO
RT1MECH-88-007 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (HP-K-1) Merv 4 filters are currently installed. Must be Merv 8 to match skids G, H, R2. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625377&prj=684&rqi=LHqU3DUNNvfOHBVLAbj77dgfAQ
RT1MECH-88-006 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (HP-K-1) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625373&prj=684&rqi=23gy1zXgXl0lHO847hcJ1bSjwH
RT1MECH-87-004 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | (HP-J-2) Merv 4 filters are currently installed. Must be Merv 8 to match skids G, H, R2. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625376&prj=684&rqi=2HgtDUUUEIO6QObvjZnfsTUacF
RT1MECH-91-011 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-06-14 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (1HP_R2_2) L2A Not enough flex conduit slack to install smoke detectors onto the airflow plenum | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625247&prj=684&rqi=ApEurbXMst0MWkX5LW696wR6A2
RT1MECH-90-007 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-06-14 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L2A Not enough flex conduit slack to install smoke detectors onto the airflow plenum. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625246&prj=684&rqi=KdZeewE67mvyk67BkzqRhEmxnp
RT1MECH-32-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (CRAH-G-7) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625024&prj=684&rqi=nms0ALz0ofaAwWeBdLkRtWZaJy
RT1MECH-43-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_06 | CRAH - Computer room air handler |  |  | (CRAH-H-6) L2A Filter bracket 8 front bottom bolt loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625009&prj=684&rqi=53uLx8cZNJD09FgCmSxfSc541g
RT1MECH-41-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_04 | CRAH - Computer room air handler |  |  | (CRAH-H-4) L2A Filter bracket 5 bolt is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625008&prj=684&rqi=FJwGn7V3smOLXIC6IzeFIFlLXx
RT1MECH-48-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_11 | CRAH - Computer room air handler |  |  | (CRAH-H-11) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625016&prj=684&rqi=nk9VbrKQoMQ6tl4VYnSmpNyZVT
RT1MECH-37-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_12 | CRAH - Computer room air handler |  |  | (CRAH-G-12) L2A Filter brackets: #4 top back bolt missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625029&prj=684&rqi=BY1cbjQH0M3YiEMMs5ykucUL4P
RT1MECH-33-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_08 | CRAH - Computer room air handler |  |  | (CRAH-G-8) L2A Filter brackets: #4 Top back bolt missing #5 missing integral bolt and completely fallen down | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625026&prj=684&rqi=nIyCjozcKSvDxrb2Lobknmkx5P
RT1MECH-44-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_07 | CRAH - Computer room air handler |  |  | (CRAH-H-7) L2A Filter bracket 7 Top bolt loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625011&prj=684&rqi=KZX8Y2qk3IYNEuGHlWDPoFuGx7
RT1MECH-36-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_11 | CRAH - Computer room air handler |  |  | (CRAH-G-11) L2A Filter brackets: #4 both back both top and bottom bolts missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625028&prj=684&rqi=rx0bRojtscxUunGDhqcgbIbOfY
RT1MECH-32-002 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (CRAH-G-7) L2A Filter spacer lodged in fan | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625025&prj=684&rqi=S2j2ZyGXi9M7GKGjPdCy3dtqE4
RT1MECH-30-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_05 | CRAH - Computer room air handler |  |  | (CRAH-G-5) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625022&prj=684&rqi=gLG4tFDSQJvgt1x7kYbIqimjEc
RT1MECH-45-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_08 | CRAH - Computer room air handler |  |  | (CRAH-H-8) L2A Filter brackets 1-8 are loose (welds are broken) Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625012&prj=684&rqi=w6nZnZZipl0COFsUMtBIqLvOef
RT1MECH-45-004 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_08 | CRAH - Computer room air handler |  |  | (CRAH-H-8) L2A Debris on coil | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625013&prj=684&rqi=vboTw1Ynmf9iW0L45pecra3hNv
RT1MECH-26-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_01 | CRAH - Computer room air handler |  |  | (CRAH-G-1) L2A #4 Top back bolt loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625018&prj=684&rqi=uxzRqEZ0oM5zf30Im2n3ABKSq5
RT1MECH-46-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_09 | CRAH - Computer room air handler |  |  | (CRAH-H-9) L2A Filter brackets 1-8 are loose (welds are broken) Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625014&prj=684&rqi=UbwKJNFk8dcaYH6uwlDXEp1V86
RT1MECH-31-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_06 | CRAH - Computer room air handler |  |  | (CRAH-G-6) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625023&prj=684&rqi=JaEZ7MErR5FmPuC098kMOudpLv
RT1MECH-35-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_10 | CRAH - Computer room air handler |  |  | (CRAH-G-10) L2A Filter brackets: #4 top front, #5 top back bolts missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625027&prj=684&rqi=toQiy4GjEzcSGVRHZ8i3EcUgzG
RT1MECH-29-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_04 | CRAH - Computer room air handler |  |  | (CRAH-G-4) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625021&prj=684&rqi=58z75iXH7Hql7SyJJTeFqLRkHW
RT1MECH-47-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_10 | CRAH - Computer room air handler |  |  | (CRAH-H-10) L2A Bracket 2 top back bolt loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625015&prj=684&rqi=ffEQAc1kbLIwRISr3DLgfZ6pfw
RT1MECH-39-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_02 | CRAH - Computer room air handler |  |  | (CRAH-H-2) L2A 2 bolts missing on filter bracket 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624969&prj=684&rqi=yd1HGm6laN6TLVLp9vWrswfa2r
RT1MECH-49-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_12 | CRAH - Computer room air handler |  |  | (CRAH-H-12) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625017&prj=684&rqi=vUe8UuXfwHy7WXkhYwMZPM9rF9
RT1MECH-27-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_02 | CRAH - Computer room air handler |  |  | (CRAH-G-2) L2A Mystery screw found in top right filter section | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625019&prj=684&rqi=ixxSn6oJ0BgMHcZrpn2wW11k5X
RT1MECH-28-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_03 | CRAH - Computer room air handler |  |  | (CRAH-G-3) L2A Filter bracket 8 top bolts loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625020&prj=684&rqi=ah3fSgfYMjfRiCYTGggMeHJOiG
RT1MECH-90-006 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A Termination end of leak detection rope is missing it's end of line "Leak Tape" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624186&prj=684&rqi=94HIco5rRg4QUScSwGAoWP5Euq
RT1MECH-84-007 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (Electrical Skid H) L2A Termination end of leak detection rope is missing it's end of line "Leak Tape | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624182&prj=684&rqi=IjFcNJwKvwqM4K4YuoWVpC2KbX
RT1MECH-82-009 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A Termination end of leak detection rope is missing it's end of line "Leak Tape" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624179&prj=684&rqi=DeUUpOnNVei1VhUCpwCSZEBRMD
RT1MECH-86-005 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (Electrical Skid J) L2A Termination end of leak detection rope is missing it's end of line "Leak Tape" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624183&prj=684&rqi=3Ipd2SUvsAHDYwFn1kvuRXLkue
RT1MECH-88-005 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (Electrical Skid K) L2A Termination end of leak detection rope is missing it's end of line "Leak Tape" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624184&prj=684&rqi=5SpSf92nIbSmY9dBrpPZH9xYhM
RT1MECH-85-003 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (1HP_H_02) L2A Unit missing condensate containment curb. Present in G. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623996&prj=684&rqi=PxjBaa2PaJv9pKr3oINeq7rGdp
RT1ELEC-93-007 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A 1MSB_G Sections 05A, 06A, 11A, 12A, 13A all have extra hardware installed on the main busway with no cables connected to them. This extra hardware needs to be removed from the busway. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623706&prj=684&rqi=BQZSNatQ32PcQiM9KDnOHAlMGP
RT1ELEC-91-003 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R2_1 | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_R2_1) L2A The Q10 'SPARE' breaker is not the correct kind of breaker per the submittal. Currently installed is an XT5H 400AF / 400A Plug/Sensor breaker. Per Drawing # HSU-5736GR-ELC_DWG01 of the Hanley submittal, the breaker should be a XT5H 600AF / 600A Plug/Sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623717&prj=684&rqi=jIXoxX2KgbKCMJTKOqhNkYD1A3
RT1ELEC-362-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_3) L2A The communication interface should have an additional Relay I/O card installed in the SMART slot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623732&prj=684&rqi=KdjpEKUQM5fzOr3tIsvRpSaxTg
RT1ELEC-91-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R2_1 | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_R2_1) L2A The plastic cover plates beneath the HMI on all six 250A frame breakers (Q01 - Q06) are bent or cracked. This is likely due to the screw on the plastic cover being excessively tightened down. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623716&prj=684&rqi=Gg1x1p4KQ14xmeT8mytahoSXmv
RT1ELEC-356-003 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_J3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_J3) L2A The communication interface should have an additional Relay I/O card installed in the SMART slot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623729&prj=684&rqi=MPcLXCacmRiTphAhPqgLZZ5gSx
RT1ELEC-350-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_G3) L2A The communication interface should have an additional Relay I/O card installed in the SMART slot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623728&prj=684&rqi=sizx7QtqtPjZ6OtllKbyXW0Rts
RT1ELEC-353-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_H3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_H3) L2A The communication interface should have an additional Relay I/O card installed in the SMART slot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623730&prj=684&rqi=OWnXMitFvD4yoW8LQ7wp5PFFUz
RT1ELEC-359-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_K3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_K3) L2A The communication interface should have an additional Relay I/O card installed in the SMART slot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623731&prj=684&rqi=aqlAhwGXSrm5Vbn8oWjKBbD4HK
RT1MECH-38-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-01 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_01 | CRAH - Computer room air handler |  |  | (1CRAH _H_01) L2A Upper filter bracket is lose. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623574&prj=684&rqi=imHuwJYdjd369WWI6ItEiwJ43B
RT1MECH-38-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-01 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Cleaning | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_01 | CRAH - Computer room air handler |  |  | (1CRAH_H_01) L2A Fin section needs to be cleaned out. Miscellaneous debris present. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623575&prj=684&rqi=dYZxbfNe1jnJhBq8ImekUMhZWk
RT1ELEC-93-006 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-01 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A Protective plastic cover in section 06A of 1MSB_G is not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623570&prj=684&rqi=JT6w0TMIgasg0oya8gojvs1PEd
RT1ELEC-356-002 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_J3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_J3) L2A The cables fed from MDSB_J into UPS_J3 are not long enough to make proper connections inside of the UPS unit. There is a small amount of slack available on the cables inside of the MDSB but unsure if this is enough to make the connection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623566&prj=684&rqi=O14SMLuFawENLrH6dM0VRPnwFH
RT1MECH-40-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-01 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_03 | CRAH - Computer room air handler |  |  | (1CRAH_H_03) L2A Loose nut/bolts from filter bracket. Fallen onto the fan enclosure. Need to clean out | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623573&prj=684&rqi=fgDY76Kc2WC3YCcqtmWQo1WkNG
RT1ELEC-93-005 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-01 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A While performing light tug test on cables inside of 1MSB_G Cabinet 02A, cable J400 disconnected from 'Port 13' on the P/PSU1 unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623568&prj=684&rqi=v4HAfou8GGSXWgqGpdOZBvuLOk
RT1MECH-83-002 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (WSHP-G-2) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622856&prj=684&rqi=vgocKANUIjbZgn2BZRnrGL9ciz
RT1MECH-83-001 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (WSHP-G-2) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622835&prj=684&rqi=qgdXfjlKqmqowsfvqrIQBwN9SO
RT1MECH-84-001 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (WSHP-H-1) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622836&prj=684&rqi=4SHlpADUED3aLIiqI9rhWYI0as
RT1MECH-84-003 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (Electrical Skid H) L2A At the SW doors, the speaker strobe & pull station devices cannot be installed as the back boxes are too close to the adjacent conduit and security JB respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622853&prj=684&rqi=m05rhKGqMJZRQEjkrEPJZp9uoF
RT1MECH-86-003 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (Electrical Skid J) L2A Where insulated CHW lines are supported by unistrut, shields are missing in a couple of locations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622870&prj=684&rqi=ZDuzjuwqK1wyzzHdNWhw4gLfeT
RT1MECH-87-002 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | (WSHP-J-2) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622861&prj=684&rqi=ZQyBTawlrpWboCry4aZbPLNnjU
RT1MECH-86-002 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (WSHP-J-1) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622860&prj=684&rqi=kzGfQdWnAzffFYVsksg5OgQX6G
RT1MECH-90-003 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A At the SW doors, the speaker strobe & pull station devices cannot be installed as the back boxes are too close to the adjacent conduit and security JB respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622848&prj=684&rqi=kB6l4jNs5XrrIAnGQNYNp6gVYr
RT1MECH-85-001 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (WSHP-H-2) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622837&prj=684&rqi=VuVpoKuB0ACFsq7FxnTSDCOqL4
RT1MECH-87-001 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | (WSHP-J-2) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622839&prj=684&rqi=MFwHmsl1bgK6s8r5vOlzTxHbaw
RT1MECH-86-001 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (WSHP-J-1) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622838&prj=684&rqi=Pbix8IhsrE9RuGovqzBNkZXd9Q
RT1MECH-88-004 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (Electrical Skid K) L2A At the south end of the PH, the drain valve on the CHW supply line, extends laterally over the UPS. Piping should be modified so it drops down vertically so as to eliminate the possibility of water dripping on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622875&prj=684&rqi=noSkSv41q6lrD7IXJBQWZjyvNB
RT1MECH-84-005 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (Electrical Skid H) L2A Where insulated CHW lines are supported by unistrut, shields are missing in a couple of locations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622869&prj=684&rqi=Oq3Hotp16rzEcFhkHjGL2hoZX4
RT1MECH-86-004 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (Electrical Skid J) L2A At the south end of the PH, the drain valve on the CHW supply line, extends laterally over the UPS. Piping should be modified so it drops down vertically so as to eliminate the possibility of water dripping on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622874&prj=684&rqi=icSCFC2liRmQPpD7Fj0aSXtIad
RT1MECH-84-004 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (WSHP-H-1) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622858&prj=684&rqi=lSSpzTbPYauE6QDprUnCTT0GSV
RT1MECH-85-002 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (WSHP-H-2) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622859&prj=684&rqi=O37yXFhbpojkvPBAMvpky65tvk
RT1MECH-90-002 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (WSHP-R2-1) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622842&prj=684&rqi=nqdFflJQYx3PvZq8WCORqfJ2Oo
RT1MECH-88-002 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (WSHP-K-1) L2A Power wiring to the smoke detectors units is terminated incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622862&prj=684&rqi=d3zfhMS9xppyS8m2Y3Q6q8VfNu
RT1MECH-88-003 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (Electrical Skid K) L2A Where insulated CHW lines are supported by unistrut, shields are missing in a couple of locations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622871&prj=684&rqi=RYpdyya8FN6x5HAeeb1JRUIOyF
RT1MECH-89-001 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (WSHP-K-2) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622841&prj=684&rqi=TcYSoRcBonZKtQ67mbtiq62sF7
RT1MECH-90-005 | SV18-2 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (WSHP-R2-1) L2A No CAT 6 cables pulled to WSHP (R-4800 & R-4900 on MPS submitall dwg MPS.522). Associated conduit required as well, see Skid H for example of complete install. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622867&prj=684&rqi=lCrsLtccysMe5bPnkwcEmmgirr
RT1MECH-88-001 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (WSHP-K-1) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622840&prj=684&rqi=KqfCalTyVkClws5lIlZ9qubIgT
RT1MECH-82-008 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A At the south end of the PH, the drain valve on the CHW supply line, extends laterally over the UPS. Piping should be modified so it drops down vertically so as to eliminate the possibility of water dripping on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622872&prj=684&rqi=plvWJjNdcDHm8OaJZldhOq20Ic
RT1MECH-82-004 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A Speaker strobe boxes at each of the 4 # doors, require an extension box. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622851&prj=684&rqi=gnlUHn8T6tiLcejfTLtZzQaryu
RT1MECH-82-006 | SV18-2 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (WSHP-G-1) L2A No CAT 6 cables pulled to WSHP (R-4800 & R-4900 on MPS submitall dwg MPS.522). Associated conduit required as well, see Skid H for example of complete install. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622865&prj=684&rqi=H3wbfRUs4bhLDlyjoaBPu8vrfU
RT1MECH-82-005 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (WSHP-G-1) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622855&prj=684&rqi=G0qmDbdxwNtQVPeql9tbwwZAlE
RT1MECH-91-010 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (WSHP-R2-2) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622844&prj=684&rqi=U2rHLdyXy1rfUUE5bcjUbsWviB
RT1MECH-82-007 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A Where insulated CHW lines are supported by unistrut, shields are missing in a couple of locations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622868&prj=684&rqi=Tc7nTOXkqRbA1WGHVNUI44SMRn
RT1MECH-89-002 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (WSHP-K-2) L2A Power wiring to the smoke detectors units is terminated incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622863&prj=684&rqi=71RQOocbT7HYwweFqnIqtq1KSN
RT1MECH-90-004 | SV18-2 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (WSHP-R2-1) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622864&prj=684&rqi=uvrouonnEUK6Nygc5rntJjxYxj
RT1MECH-84-002 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (Electrical Skid H) L2A At the 2 # doors on the north side, the pull box back boxes are too close to the adjacent switch for the pull station to be installed/door opened. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622846&prj=684&rqi=nhfOpFJ0erEVYu5HaXnVnYeWkq
RT1MECH-84-006 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (Electrical Skid H) L2A At the south end of the PH, the drain valve on the CHW supply line, extends laterally over the UPS. Piping should be modified so it drops down vertically so as to eliminate the possibility of water dripping on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622873&prj=684&rqi=eFJDw92hqiEVsHPg51x9PqbMif
RT1MECH-83-003 | SV18-2 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (WSHP-G-2) L2A No CAT 6 cables pulled to WSHP (R-4800 & R-4900 on MPS submitall dwg MPS.522). Associated conduit required as well, see Skid H for example of complete install. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622866&prj=684&rqi=UAQTUze4qOJoVOpXeOA4Mh9coZ
RT1ELEC-44-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_G3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622736&prj=684&rqi=tzCqIobVqlKeJ9iPIWD0qmbOfm
RT1ELEC-53-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_H3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622737&prj=684&rqi=MM1eTioCmoldv9W7A6JWS8dymh
RT1ELEC-81-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BTU_G | BTU - Battery Tripping unit |  |  | (1BTU_G) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622746&prj=684&rqi=yKfVlKmt2HKIoOVLK507vBE15i
RT1ELEC-94-004 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | (1MSB_H) L2A FST identified during FWT that there are missing ground bonding cables connecting the MSB switchboard to the top hats on MSB sections 5A, 6A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622752&prj=684&rqi=4dMawaTjavOjbbqrGusLhdV86t
RT1ELEC-97-003 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB_R2) L2A The key-actuated selector switches on the MSB HMI lock the keys when not in the center position. The selector switches should not lock the keys in any position. Sheet 2 of Hanley Submittal Drawing #HSU-5478FO-ELC-DWG02 specifies this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622703&prj=684&rqi=bZ8p6r0dIHavL9Wmo3PZFR1lXg
RT1MECH-82-003 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (WSHP-G-1) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622706&prj=684&rqi=GAqhcx0iU8Rc193oDn1wCG5COt
RT1ELEC-362-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622745&prj=684&rqi=TZvrDqn6rkbmacExXVqVuZ1gPP
RT1ELEC-95-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | (1MSB_J) L2A MSB HMI has 4 key-actuated selector switches, and only 3 are required. Per Hanley submittal drawing #HSU-5478FO-ELC-DWG02, this switch should be removed and blanked off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622678&prj=684&rqi=57ip5wrDhS9e0tU8XrU0DZrGt8
RT1ELEC-374-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1GEN_R2 | GENL - Generator (LV) |  |  | (1GEN_R2) L2A Generator Circuit Breaker in GEN_R2 enclosure is missing the kirk key barrel assembly. The required kirk key for this breaker is: K1 (Serial # 64393) The breaker model is: SACE E6.2V-A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622707&prj=684&rqi=LhWMpvU0K2KO3lvqpmBMbVyOXw
RT1ELEC-83-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BTU_J | BTU - Battery Tripping unit |  |  | (1BTU_J) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622748&prj=684&rqi=dWTNbgmZxhGG9Xmvv2XiLIUkh4
RT1ELEC-97-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB_R2) L2A MSB HMI has 4 key-actuated selector switches, and only 3 are required. Per Hanley submittal drawing #HSU-5478FO-ELC-DWG02, this switch should be removed and blanked off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622702&prj=684&rqi=s5Qx8dMbzEw9aAEcGJ2n22sltQ
RT1ELEC-62-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_J3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622738&prj=684&rqi=W1wl3cdUFrpI91ERhJMyzSEoww
RT1ELEC-96-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2A MSB HMI is not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622701&prj=684&rqi=cdWFLvez3G9qifj5dUVSw8QFSk
RT1ELEC-94-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | (1MSB_H) L2A MSB HMI has 4 key-actuated selector switches, and only 3 are required. Per Hanley submittal drawing #HSU-5478FO-ELC-DWG02, this switch should be removed and blanked off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622676&prj=684&rqi=XAT9W0n7fuQpQlqjlTpZgs9l8W
RT1ELEC-95-004 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | (1MSB_J) L2A FST identified during FWT that there are missing ground bonding cables connecting the MSB switchboard to the top hats on MSB sections 5A, 6A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622753&prj=684&rqi=c7ditXE8wIXhKXGeyTx50F2ekH
RT1ELEC-85-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BTU_R2 | BTU - Battery Tripping unit |  |  | (1BTU_R2) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622750&prj=684&rqi=qhUehDgJICdNQm2huc9uzHsWq2
RT1MECH-45-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-21 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_08 | CRAH - Computer room air handler |  |  | (CRAH-H-8) L2A MCP1 fan overload allows user to go straight from "Trip" to "On" without opening the contact first. Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622734&prj=684&rqi=vvCENn7h4KxinNtyfkcQc5nkPG
RT1ELEC-95-003 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | (1MSB_J) L2A The key-actuated selector switches on the MSB HMI lock the keys when not in the center position. The selector switches should not lock the keys in any position. Sheet 2 of Hanley Submittal Drawing #HSU-5478FO-ELC-DWG02 specifies this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622679&prj=684&rqi=dNcX7sRG8hdBA2LT30WcQEqjQb
RT1ELEC-353-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_H3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_H3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622742&prj=684&rqi=xjj3TDhkprqzv2EFdWTGcKwIVg
RT1ELEC-96-003 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2A FST identified during FWT that there are missing ground bonding cables connecting the MSB switchboard to the top hats on MSB sections 5A, 6A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622754&prj=684&rqi=FcndmfOmjgkv7HEuvlNRJDUrbe
RT1ELEC-80-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_R2_3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_R2_3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622740&prj=684&rqi=QUOM2NWgX0x8i88KJELjnuDIhE
RT1ELEC-93-003 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A The key-actuated selector switches on the MSB HMI lock the keys when not in the center position. The selector switches should not lock the keys in any position. Sheet 2 of Hanley Submittal Drawing #HSU-5478FO-ELC-DWG02 specifies this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622670&prj=684&rqi=hFWfRXuDAlkDNjqRtz5PYfk0YD
RT1ELEC-350-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_G3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622741&prj=684&rqi=QNd97AzTPGB2I3rWPWtjer4cAW
RT1ELEC-84-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BTU_K | BTU - Battery Tripping unit |  |  | (1BTU_K) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622749&prj=684&rqi=jsChQ1NF6Nf4ndIUz9e7GldEUY
RT1ELEC-356-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_J3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_J3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622743&prj=684&rqi=18fgj10X1TWLUDe7FKXhJQiy3i
RT1ELEC-71-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_K3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622739&prj=684&rqi=tUKLOlC8OJuHLkboKweH3qlPTr
RT1ELEC-93-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A MSB HMI has 4 key-actuated selector switches, and only 3 are required. Per Hanley submittal drawing #HSU-5478FO-ELC-DWG02, this switch should be removed and blanked off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622657&prj=684&rqi=N9knX8ZPx3KV19fa1arbeZy7i2
RT1ELEC-82-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BTU_H | BTU - Battery Tripping unit |  |  | (1BTU_H) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622747&prj=684&rqi=Y2MgozakoFgnJDNlCospHdcpcx
RT1ELEC-93-004 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A FST identified during FWT that there are missing ground bonding cables connecting the MSB switchboard to the top hats on MSB sections 5A, 6A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622751&prj=684&rqi=tuaHz4m0fQgek0G4GWQiOg75bb
RT1MECH-31-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-21 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_06 | CRAH - Computer room air handler |  |  | (1CRAH_G_06) L2A HMI panel is showing visible bend. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622735&prj=684&rqi=QlDSBgHT31FrWSHWmdQGFi5suU
RT1ELEC-359-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_K3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_K3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622744&prj=684&rqi=iwIqA0du3fFiZ45u93PSlkrHuL
RT1MECH-42-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-21 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_05 | CRAH - Computer room air handler |  |  | (1CRAH_H_05) L2A Disconnect shaft for main power source 1 stats in the disconnect handle instead of the disconnect itself. See attached picture. Set screw threads appear to be stripped Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622733&prj=684&rqi=uqNVB6QSnw3WLHjZM0MoO3pjWQ
RT1ELEC-97-004 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB_R2) L2A FST identified during FWT that there are missing ground bonding cables connecting the MSB switchboard to the top hats on MSB sections 5A, 6A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622755&prj=684&rqi=kNxujUONZRVtgWFld0bjKR9AiL
RT1ELEC-94-003 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | (1MSB_H) L2A The key-actuated selector switches on the MSB HMI lock the keys when not in the center position. The selector switches should not lock the keys in any position. Sheet 2 of Hanley Submittal Drawing #HSU-5478FO-ELC-DWG02 specifies this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622677&prj=684&rqi=TqqImONa3QIpfxsR56lwlPpFFV
RT1MECH-55-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_06 | CRAH - Computer room air handler |  |  | (1CRAH_K_06) L2A Loose bolt on fan 4 Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622573&prj=684&rqi=TtCvcdQmJo6A6Rc0AttXHbLYys
RT1MECH-55-004 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_06 | CRAH - Computer room air handler |  |  | (CRAH-J-6) L2A Filter brace welds 5, 6, 7, 8 all broken Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622574&prj=684&rqi=nG5SRsFpv2HTW2WIKbp24Azk4c
RT1MECH-55-001 | SV18-2 | AMER | Closed | P1 High CX | ethan.hang@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_06 | CRAH - Computer room air handler |  |  | (1CRAH_K_06) L2A Control board was donated to a CRAH with an earlier start-up date. New control board has been installed, it needs to be programmed during start up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622524&prj=684&rqi=aG9lpQHPkH3ekodA5bM78Jatsh
RT1MECH-46-002 | SV18-2 | AMER | Ready for Verification | P2 Medium CX | ethan.hang@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_09 | CRAH - Computer room air handler |  |  | (1CRAH_H_09) L2A Therma has found that the unit has leaks internally on the Vertiv side. A weld and a few spots around the PICV are leaking. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622526&prj=684&rqi=p1xKi8RQRcAkUuCtsdjLcnemrL
RT1MECH-46-004 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_09 | CRAH - Computer room air handler |  |  | (1CRAH_H_09) L2A PICV actuator was donated to another CRAH with earlier start-up. New PICV actuator needed and installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622525&prj=684&rqi=TPxHAJdOJLJC68Y5GjOB6ZUmcf
RT1MECH-56-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Cleaning | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_07 | CRAH - Computer room air handler |  |  | (1CRAH_K_07) L2A Right fan section needs cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622576&prj=684&rqi=MdHbnRgPZCDs0tm8CgFy8uGgCf
RT1MECH-56-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_07 | CRAH - Computer room air handler |  |  | (1CRAH_K_07) L2A Filter brace 2 is missing bolts. Bolts not found! | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622575&prj=684&rqi=hCKXkwC5Sfh81k0zLzcfQ6Pedj
RT1ELEC-387-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_R2_3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | (1UMDSB_R2_3) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1UPNL_R2_3_H1 (Q07) 1UPNL_R2_3_H2 (Q08) 1UPNL_R2_3_H3 (Q09) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622338&prj=684&rqi=ddUCyWq8S2Xe4q14CX0NzYs37d
RT1ELEC-371-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1GEN_H | GENL - Generator (LV) |  |  | (1GEN_H) L2A Generator Circuit Breaker in GEN_H enclosure is missing the kirk key barrel assembly. The required kirk key for this breaker is: K1 (Serial # 64393) The breaker model is: SACE E6.2V-A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622355&prj=684&rqi=xPrS9kldC62UgioSwTkQLHxWyM
RT1ELEC-373-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1GEN_K | GENL - Generator (LV) |  |  | (1GEN_K) L2A Generator Circuit Breaker in GEN_K enclosure is missing the kirk key barrel assembly. The required kirk key for this breaker is: K1 (Serial # 64393) The breaker model is: SACE E6.2V-A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622357&prj=684&rqi=kGKRPtsYQNv6yA7MP1wfKmfn9k
RT1ELEC-5-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | SCH - Schneider MV | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_G | RMU - Ring Main Unit |  |  | (1RMU_G) L2A RMU cover plates were inadvertently swapped following L2A testing. The left most switch panel cover is currently installed over the center switch. Please refer to attached images for additional information. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622339&prj=684&rqi=f3Cyhd9l4VPWAmkI1jOQmEtHBq
RT1MECH-51-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (1CRAH_K_2) L2A dP sensor loose in left upper fan section. Inspect Equipment for missing hardware | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622315&prj=684&rqi=UFQB4lcqSDf49xSFiW770z02ov
RT1MECH-52-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_03 | CRAH - Computer room air handler |  |  | (CRAH-J-3) L2A Filter brace weld #7 is broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622316&prj=684&rqi=7PYq3L9ThJ9ae4fn5yi3Eqa606
RT1ELEC-372-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1GEN_J | GENL - Generator (LV) |  |  | (1GEN_J) L2A Generator Circuit Breaker in GEN_J enclosure is missing the kirk key barrel assembly. The required kirk key for this breaker is: K1 (Serial # 64393) The breaker model is: SACE E6.2V-A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622356&prj=684&rqi=SUnxY3Jlbk53sYOAh96s97gXCj
RT1MECH-53-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_04 | CRAH - Computer room air handler |  |  | (1CRAH_K_4) L2A Lower right panel door upright is missing a rivet. Inspect Equipment for missing hardware | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622318&prj=684&rqi=elt21hTVJuA4bZdernqBH6uaJo
RT1MECH-50-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_01 | CRAH - Computer room air handler |  |  | (1CRAH_K_1) L2A Filter brace missing 2 bolts. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622312&prj=684&rqi=Z4YqOHYRtW2DgY3OGID27GOrFS
RT1MECH-53-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_04 | CRAH - Computer room air handler |  |  | (1CRAH_K_4) L2A Filter brace #8 is missing a bolt | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622317&prj=684&rqi=MJUfYrxHWBSy6ed051Rn9n07Ng
RT1ELEC-370-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1GEN_G | GENL - Generator (LV) |  |  | (1GEN_G) L2A Generator Circuit Breaker in GEN_G enclosure is missing the kirk key barrel assembly. The required kirk key for this breaker is: K1 (Serial # 64393) The breaker model is: SACE E6.2V-A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622353&prj=684&rqi=12RlPIbHN9UGeaVoKYVMc44y25
RT1MECH-54-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_05 | CRAH - Computer room air handler |  |  | (1CRAH_K_5) L2A Very minor damage to fan 1 due to fallen filter brackets. Small scratches, adding for tracking purposes to keep an eye on it. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622319&prj=684&rqi=Miidkj4jjrW2WvlWbmUThxt3hR
RT1MECH-54-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_05 | CRAH - Computer room air handler |  |  | (CRAH-J-5) L2A Weld 5 broken Inspect all sections for dents, scratches, fit, corrosion, etc. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622321&prj=684&rqi=EQQLcO3yV6U8nn8thipDizDhlH
RT1MECH-54-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_05 | CRAH - Computer room air handler |  |  | (1CRAH_K_5) L2A Bad fitment of left upper fan door Confirm that CRAH access doors open/close freely and have adequate seals | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622320&prj=684&rqi=QoFBaglBQjhWWV0o5epvTl0WYA
RT1MECH-60-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_11 | CRAH - Computer room air handler |  |  | (1CRAH_K_11) L2A Missing bolt on #6 filter bracing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622347&prj=684&rqi=llT754zVCejPgw9UvXyZzGa3Ee
RT1MECH-58-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_09 | CRAH - Computer room air handler |  |  | (CRAH-J-9) L2A Broken filter brace welds #1 and 4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622350&prj=684&rqi=3Nf8f0pTdeySLuToSKMLPqwq5b
RT1MECH-59-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_10 | CRAH - Computer room air handler |  |  | (1CRAH_K_10) L2A Filter brace 3 missing bolt | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622348&prj=684&rqi=8r561ktnV0QJLdfhkFQ7CHupTn
RT1MECH-57-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_08 | CRAH - Computer room air handler |  |  | (1CRAH_K_8) L2A Filter bracket 3 bolt fallen off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622352&prj=684&rqi=28aobUzPSKRhh7s3LXZhxWzbWK
RT1MECH-61-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_12 | CRAH - Computer room air handler |  |  | (CRAH-J-12) L2A Filter brace weld 4 is broken. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622346&prj=684&rqi=HVrfScMIi53dBoepxVbJhYNNz7
RT1MECH-57-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_08 | CRAH - Computer room air handler |  |  | (CRAH-J-8) L2A Filter brace weld 8 broken Inspect all sections for dents, scratches, fit, corrosion, etc. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622351&prj=684&rqi=Z0MLuZSXWYJfesG6eEXuLufEy0
RT1MECH-61-001 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Cleaning | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_12 | CRAH - Computer room air handler |  |  | (1CRAH_K_12) L2A Air filter brackets have fallen into fan 8. CANNOT STARTUP UNTIL REMOVED | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622345&prj=684&rqi=f54b0fDVWl4D6FImsHy7CcPISm
RT1MECH-58-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Cleaning | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_09 | CRAH - Computer room air handler |  |  | (1CRAH_K_9) L2A Bolt missing from filter brace 7. Found as fodder above fan see photos. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622349&prj=684&rqi=PvUEYhXQzrFXD0v7gsmgOY3ijv
RT1ELEC-386-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_K3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | (1UMDSB_K3) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1UTX_K3_L1 (Q06) 1UPNL_K3_H1 (Q09) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622337&prj=684&rqi=492hUARr6hpddHFy0uqGrOjzvB
RT1MECH-51-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-13 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (1CRAH_K_02) L2A Cable coming off of CAT6 is missing a connection header. Correct photo attached. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621723&prj=684&rqi=XDVvve1EQJLHWgzyvi9RoMhHPx
RT1MECH-3-004 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-13 04:00:00.000 +0400 | Controls Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1ACC_R2_05 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers (ACC)) For tracking purposes Heat trace failures create a hardwired fault status to the BMS, creating a latching BMS fault for the chiller skid. Approved solution is to have ETech run an additional wire from the heat trace relay to use as an additional hardwire point to use for ignoring this hardwire fault status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621739&prj=684&rqi=z6cVlo5ueDPHGOJyjPbWaQBEXl
RT1MECH-56-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-13 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_07 | CRAH - Computer room air handler |  |  | (1CRAH_K_07) L2A 3A fuse cover on F5 in the power panel is broken. Replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621735&prj=684&rqi=BbvUADGBhACEA1gUdfMu6L2EUR
RT1MECH-3-003 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-13 04:00:00.000 +0400 | TRN - Trane | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1ACC_R2_05 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers (ACC)) For Tracking Purposes Please confirm that all freeze protection valves are modulating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621738&prj=684&rqi=7KMfwE1BP2AAUn4va8ZMIlhFwq
RT1MECH-26-002 | SV18-2 | AMER | Closed | P1 High CX | ethan.hang@veolia.com | 2026-05-13 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_01 | CRAH - Computer room air handler |  |  | (All Data Hall CRAHs) For Tracking Purposes Interconnection between smoke detector and control panel to be completed by Vertiv. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621740&prj=684&rqi=YM6dwtkAGkqfGFIOj5Ft1NFIxU
RT1ELEC-89-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MDSB_J | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_J) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_J_HP (Q06) 1UPS_J3 (Q07) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621162&prj=684&rqi=2450nctBhMW4RmiBJzZ2h8aFID
RT1ELEC-93-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A MSB breaker labels from the Hanley submittal do not match the electrical one line diagram. Specifically, breaker Q02 does not exist on the electrical one line diagram which causes all other breaker labels to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621152&prj=684&rqi=gsbH8gSsDaYwMZx7mNn4zhXZdd
RT1ELEC-95-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | (1MSB_J) L2A MSB breaker labels from the Hanley submittal do not match the electrical one line diagram. Specifically, breaker Q02 does not exist on the electrical one line diagram which causes all other breaker labels to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621155&prj=684&rqi=qe29SfvIsIjQVn6Fo44cgRZBty
RT1ELEC-87-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_G) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_G_HP (Q06) 1UPS_G3 (Q07) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621159&prj=684&rqi=ayk4e2t8FMNSJI646BclGFUzCc
RT1ELEC-94-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | (1MSB_H) L2A MSB breaker labels from the Hanley submittal do not match the electrical one line diagram. Specifically, breaker Q02 does not exist on the electrical one line diagram which causes all other breaker labels to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621154&prj=684&rqi=yMyQuQ1U6dvgpdoICWt0R24BX1
RT1ELEC-90-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MDSB_K | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_K) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_K_HP (Q06) 1UPS_K3 (Q07) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621164&prj=684&rqi=LLpYJShVRwBHez2lcvfI8pmK6V
RT1ELEC-96-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2A MSB breaker labels from the Hanley submittal do not match the electrical one line diagram. Specifically, breaker Q02 does not exist on the electrical one line diagram which causes all other breaker labels to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621157&prj=684&rqi=yrVCUfei80HvuXfGhLzwTTR0Hi
RT1ELEC-88-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MDSB_H | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_H) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_H_HP (Q06) 1UPS_H3 (Q07) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621161&prj=684&rqi=pPaLl5ACC0Z4yDYN1OuXp8cl0K
RT1MECH-91-005 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (1HP_R2_2) L2A Conduit clamps for the disconnect are impeding removal of the filter and will damage the filter on removal and maintenance. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620454&prj=684&rqi=YV1WXmVva0SghCTcc2NprVUXDe
RT1MECH-82-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A At the 2 # doors on the north side, the pull box back boxes are too close to the adjacent switch for the pull station to be installed/door opened. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620461&prj=684&rqi=3ZGyqYMQJBTkNxPbI5NgD1I3R5
RT1MECH-74-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_R2_13 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_R2_3) L2A Pipework has been damaged/cut and isn't holding pressure - needs to be repaired to allow Therma to progress. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620452&prj=684&rqi=6eoxJ278F34RrmC6yglJIV81xZ
RT1MECH-91-009 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A At the SW doors, the speaker strobe & pull station devices cannot be installed as the back boxes are too close to the adjacent conduit and security JB respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620460&prj=684&rqi=KLGhGjuGMELsfS8SfKzmtoSaee
RT1MECH-91-007 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (WSHP-R2-2) L2A Power wire at the smoke detectors at the Trane WSHPs has not been pulled. Currently they have only pulled the control wiring that shuts the units down. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620457&prj=684&rqi=wiFDJlYYH3ezseVQHOOVeOK3TU
RT1MECH-91-006 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Design correction needed | Design | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (R2, and G HPs) Access to the strainer, balancing valve, isolation valves, is very difficult, due to arrangement of fire alarm and various electrical JBâ€˜s in front of them. Issue is not present on J, H, K skids. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620456&prj=684&rqi=0reogYUBvwLf2c9xPeG6vTcPyi
RT1MECH-91-008 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A Speaker strobe boxes at each of the 4 # doors, require an extension box. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620459&prj=684&rqi=2VCtvOeEJnjyddySxq9YmF96nw
RT1MECH-26-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | General Design Issue | Design | Mechanical â€“ Water | equipment | 1CRAH_G_01 | CRAH - Computer room air handler |  |  | (All Data Hall CRAHs) L2A Discrepancy between 18-1 and 18-2 leak detection set up. At 18-1, leak detection was installed by MC and placed on the unit INTERIOR, to identify leaks in the coil. Photo attached with yellow rope leak detector. At 18-2 It's a point leak detector on a cable which has a plug on the bottom left of the unit EXTERIOR. Please confirm if this was the intended part shipped out and if so, when it will be installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620430&prj=684&rqi=jPSUko2cFCXKQZelEHHhgiUooh
RT1MECH-35-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_10 | CRAH - Computer room air handler |  |  | (1CRAH_G_10) L2A Left side coil holds no pressure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620298&prj=684&rqi=I8pk8hOvPEVi1cMWhRjyzOhoiX
RT1MECH-91-001 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A At the south end of the PH, the drain valve on the CHW supply line, extends laterally over the UPS. Piping should be modified so it drops down vertically so as to eliminate the possibility of water dripping on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620294&prj=684&rqi=je8IZLxzmeFmxYglsho7mdBMZA
RT1MECH-91-003 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (WSHP-R2-2) L2A No CAT 6 cables pulled to WSHP (R-4800 & R-4900 on MPS submitall dwg MPS.522). Associated conduit required as well, see Skid H for example of complete install. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620296&prj=684&rqi=FxCUe7snplo1bgfXGkJ93FFt5o
RT1MECH-45-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_08 | CRAH - Computer room air handler |  |  | (1CRAH_H_08) L2A Left side coil holds no pressure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620283&prj=684&rqi=UwVZvnnHvPUozo1d5FikwgdjXG
RT1MECH-91-004 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A Intake hoods need to be installed on the exterior of the skid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620299&prj=684&rqi=1ypd3sgbNqaqM6A8JhvThqSvkI
RT1MECH-46-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_09 | CRAH - Computer room air handler |  |  | (1CRAH_H_09) L2A Right side coil has no pressure. Needs circuit setter housing gasket and flange weld repair on the return side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620285&prj=684&rqi=tQ5gV5qnI8KIdcngxkPvzcUDDb
RT1MECH-6-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | TRN - Trane | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1ACC_H_13 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_H_13) L2A N5 jumper in control panel is missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620292&prj=684&rqi=eRdqDpyJMgbo4o2UW8CqWkBarx
RT1MECH-82-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A Intake hoods need to be installed on the exterior of the skid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620300&prj=684&rqi=UjIJnbdwBaZhHJfH5astZzmoHg
RT1MECH-57-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_08 | CRAH - Computer room air handler |  |  | (1CRAH_K_08) L2A Left side coil has no pressure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620286&prj=684&rqi=pkSzAVgDTYqoCdVRiZa7qwRyoZ
RT1MECH-91-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A Where insulated CHW lines are supported by unistrut, shields are missing in a couple of locations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620295&prj=684&rqi=zbZQ23GaeHaENJ6OmEd3BvIih4
RT1MECH-3-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1ACC_R2_05 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers (ACC)) Putty inconsistently applied to conduit bushings between the harmonic filter and the ACC power cabinet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620317&prj=684&rqi=pog51hqROMGTJ1Hw7iLNwerVEH
RT1MECH-90-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L2A A number of joints on the ductwork have not been sealed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620297&prj=684&rqi=JKUaBAbNCcnedR7mR7x9JS4Dn6
RT1ELEC-81-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-04-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BTU_G | BTU - Battery Tripping unit |  |  | (1BTU_G) L2A '1BTU_G ground plate 4' connection is not made up correctly. Please refer to attached photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619367&prj=684&rqi=cU9YO7Y2Y5xQdZ98nGaEhYq4Oo
RT1ELEC-91-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-04-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R2_1 | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_R2_1) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_GEN_R2 (Q02) 1PNL_R2_HP (Q05) 1UPS_R2_3 (Q07) 1UMDSB_R2_3 (Q08) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618583&prj=684&rqi=2EC2jYk7XPkatnHCSrb3K2n1d0
RT1ELEC-97-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-04-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB_R2) L2A MSB breaker labels from the Hanley submittal do not match the electrical one line diagram. Specifically, breaker Q02 does not exist on the electrical one line diagram which causes all other breaker labels to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618581&prj=684&rqi=iVohqFCDH7dEa4grjfrxDqfgmT
RT1ELEC-92-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-04-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R2_2 | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_R2_2) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_R2_2_H1 (Q02) 1PNL_R2_2_H2 (Q03) 1PNL_R2_2_H3 (Q04) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618585&prj=684&rqi=RDnjDl9YgJwADb5m75T9QO2Uxz
L2L3 Sun-27-002 | SY05-4 | APAC | Open | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-09-14 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Communications | equipment | SY5-FCMS-9A | FCMS Outstation |  |  | TMD-M-SY5-4 (Ethernet cables and junction box loose inside of FCMS Panel) The DCOS junction box and ethernet cables are untidy inside the FCMS 9A Panel. See image attached. Can these be installed neatly inside the panel. Please provide evidence of work completed before moving to Ready for verification. If not ready, please leave a date on when the works can be completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637856&prj=644&rqi=0ncQ0BoEDjNQwBBsTmuY7piFGz
L2L3 Sun-27-001 | SY05-4 | APAC | Open | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-09-14 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | Communications | equipment | SY5-FCMS-9A | FCMS Outstation |  |  | TMD-M-SY5-4 (Missing gland in FCMS Panel) A hole in the bottom of the FCMS Panel where the temporary power cable is coming through is missing a gland. See image attached. Please upload evidence of gland installed before moving to Ready for Verification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637855&prj=644&rqi=QvJDBanQQsPMcx6LNLxh8aIKkZ
L2L3 Sun-33-001 | SY05-4 | APAC | Open | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-09-08 04:00:00.000 +0400 | General Contractor - BMS |  | Documentation not issued/ Required | Commissioning | Communications | equipment | SY5-FCMS-10A | FCMS Outstation |  |  | TMD-M-SY5-4 (Crossmuller to supply completed panel drawings) Crossmuller have developed red line drawings due field device changes terminated in the panel. Crossmuller to convert red line drawings to complete drawings and supply physical copies in the panels SY5-FCMS-10A & 10B. Same issue applies for panels SY5-FCMS-9A & 9B as they have the same changes made. Please provide evidence of completion of works before pushing to ready for verification. Alternatively leave a comment on when works will be completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637137&prj=644&rqi=cwNCbEIH1toiIybTF4jRvhaNSJ
GI-131 | SY05-4 | APAC | Closed | P3 Low CX | steven.hoang@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | General Contractor |  | DCOS Design Issue | DCOS | [6 empty] | SH-E-SY5-4 (DCOS Graphic Queries) Graphics for STS does not specify where they are receiving supply from EG CB number. It also does not specify which STS is supplying which UDB. Can the template be modified to show text labelling on graphics or is this an approved and agreed graphic design? This issue is raised for the purpose of understanding, tracking and improvements of graphics. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636625&prj=644&rqi=wTJE3ft6UNViVXc0ekrKzIuzuc
GI-125 | SY05-4 | APAC | Open | P3 Low CX | steven.hoang@bureauveritas.com | 2026-08-24 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | SH-E-SY5-4 (A9 UDB FAT Missing) FAT Documents Missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634982&prj=644&rqi=bij34qZxQEHYX0WX8lqIBdauNg
GI-124 | SY05-4 | APAC | Open | P3 Low CX | steven.hoang@bureauveritas.com | 2026-08-24 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | SH-E-SY5-4 (A13 UDB FAT Missing) FAT documents missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634981&prj=644&rqi=W7ON8yk7zXIEIESAV9vJ4mWgoo
GI-120 | SY05-4 | APAC | Open | P3 Low DCOS | steven.hoang@bureauveritas.com | 2026-08-17 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | SH-E-SY5-4 (No Analogue values on GSB08) - DCOS Mapping Incorrect for GSB breaker up stream of A9 MVTB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634009&prj=644&rqi=41bhd1tYz4lm6VDQW8pCVIZz1M
GI-116 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-14 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | ##SY5-4-E-AOB (COLO13-DAZZA PDU LABELLING) Issue to be raised as assets are being energised for tracking, this is part of the L2 scripts. Understanding they have been ordered. Labels (on order ##Push Issue) PDU-7A PDU-32A PDU-48B PDU-47B PDU-46B PDU-46A PDU-47A PDU-48A TEMP label shave been placed to coverer the energisation process. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633732&prj=644&rqi=ZgHAtTLEMuFO1aHto5PPmyjp1x
GI-118 | SY05-4 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-14 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [6 empty] | SY5-4-E-AOB -Earth Grid / Bar Field Test (CxL2A, CxL2B) Raising this for tracking as no clear asset for this on FG, open to add an earthing asset if this works. FIC003 â€“ Earth Grid / Earth Bar Field Testing is currently planned to be completed as a single activity at the end of the project (longest distance testing point) rather than progressively for each room/area prior to energisation. From a commissioning perspective, progressive completion and recording of earth grid/earth bar testing for each room as it is handed over and energised would provide improved traceability and verification throughout the staged energisation process. This comment is recorded to ensure the item remains visible and is not overlooked during the course of the project, particularly given the staged nature of energisations and potential personnel changes prior to project handover including the CxA team. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633734&prj=644&rqi=yHgEm22IvsUxv7Yb2krlVyE58v
GI-115 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-14 04:00:00.000 +0400 | General Contractor |  | Incomplete Connections | Commissioning | [6 empty] | SY5-4-E-AOB COLO13 DAZZA (UDB/PDU Common Issues) Raising for tracking, before EE. PDU-26A - loose CT terminal block HDPM6000 PDU-28A - has a loose cable crimp above the fuse F1 HDPM6000 PDU-29A - paper above the HDPM6000 to be removed & cable crimp on top of power terminals PDU-31A - CT terminal block HDPM6000 disconnected & cable crimp above meter which needs to be removed PDU-32A - isobar cover above the PM and loose CT terminal block HDPM6000 PDU-32A - loose CT terminal block HDPM6000 PDU - 39A - loose CT terminal block HDPM6000 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633731&prj=644&rqi=IqmHqqPRlQKY2TFNLphJsSF6GF
GI-117 | SY05-4 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-14 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [6 empty] | SY5-4-E-AOB (PDU-COLO13-DAZZA Cable Routing Across Unprotected Metal Edge) The cable entering the assembly is routed across a metal cut-out without any grommet, edge trim, or mechanical protection. The cable sheath is in direct proximity to the sharp edge at the cable entry point. The installation presents a risk of cable sheath abrasion and insulation damage due to contact with the metal edge. This condition is not considered good installation practice for cable protection and may impact the long-term integrity of the cable If this arrangement is intentional and forms part of the Schneider Electric design, please provide confirmation that the cable routing has been assessed and that the risk of cable wear against the metal edge over the operational life of the equipment is accepted by the design authority. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633733&prj=644&rqi=XHLUI29nVFi7AYJKBp8mdSMFsr
GI-114 | SY05-4 | APAC | Closed | P3 Low CX | steven.hoang@bureauveritas.com | 2026-08-12 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | SH-E-SY5-4 (A9-STS-01A - 08A & A9-STS-01B - 08B) - Permanent labels indicating Sources 1 & 2 supply not present. Issue raised for tracking purposes | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633386&prj=644&rqi=ibZrgTeVsU6DNVoTBhrCYbAmRD
GI-113 | SY05-4 | APAC | Closed | P3 Low CX | steven.hoang@bureauveritas.com | 2026-08-12 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [6 empty] | SH-E-SY5-4 (R2-OSB-09A & R2-OSB-09B) - R2-OSB-09B STS-05B graphics showing Open close position but does not show trip position - R2-OSB-09A STS-05A graphics showing trip position and unable to be cleared to show open & close positions. - R2-OSB-09A & R2-OSB-09B Missing Comms cable connection from ACB to Comms Outlet. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633382&prj=644&rqi=kIGDFAyTfSMV1lVrWx2gDOIg2p
GI-112 | SY05-4 | APAC | Open | P3 Low CX | steven.hoang@bureauveritas.com | 2026-08-06 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | SH-E-SY5-4 (CALIBRATION CERTIFICATES FOR FAT EQUIPMENT) L1 FAT Documents reference 3 types of testing instruments. The uploaded equipment certificates do not match what was used during FAT. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632686&prj=644&rqi=m43ifRreXU2hfY7qvS7SxE38Is
GI-111 | SY05-4 | APAC | Closed | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-08-05 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | TMD-M-SY5-4 (Fed from labels needed for A9 & A10 MCPs) Power source fed from labels are needed for the MCPs in A9 & A10. Temporary Labels ahave been applied. Issue raised for tarcking. Please provide evidence of completion of wo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632395&prj=644&rqi=nxL5FNJmc1Ckal2o2yUvq82zld
GI-102 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-01 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | AOB-E-SY5-5 (Delivery Documentation Outstanding) Delivery documentation is outstanding. Acceptance dockets and supporting delivery photographs have not been provided/uploaded for review. These records are required to verify equipment receipt, delivery condition, and completion of project documentation requirements. A09-BAT-01-18 A09-MSB/OSB-01 A09-EDB-01 M5-02-BAT-01-03 M5-02-UPS-01 A10-BAT-01-18 A10-MVTB-01 A10-BTU-01 A10-TRX-01 A10-EDB-01 SY5-R2-OSB-10A SY5-R2-OSB-10B A10-MSB/OSB-01 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631970&prj=644&rqi=dYn0WclByzLt62PLsUXkkwChAg
GI-105 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-01 04:00:00.000 +0400 | General Contractor |  | Incomplete Connections | Commissioning | [6 empty] | SY5-4-AOB-E-R2 09A & 09B OSB Busduct Elbow Connections Issue raised to facilitate YT The final elbow connections for the R2 09A & 09B OSB busducts remain outstanding. Once the busduct is connected, the asset will have a direct connection to the R2 lineup redundancy block on live facility, creating the potential for energisation. The OSB's require to be Yellow Tagged prior to the final elbows being installed. This issue has been raised to track the outstanding works and ensure the appropriate controls are in place before connection to the live facility. Issue can be close upon final connection and test result upload. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631975&prj=644&rqi=GdexSlMrZmOOIqqpsHA9p9Tz8Q
GI-097 | SY05-4 | APAC | Open | P3 Low CX | steven.hoang@bureauveritas.com | 2026-07-27 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [6 empty] | AOB-E-SY5-4 (A02 & A09-BTU-01) TAPE Residual on Front Door No Visible Torque Marks on Battery Terminals No Cable Label No Panel Label No Battery Manufacturing Date DC cables not Connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630991&prj=644&rqi=BzbAerJwo6aTeTIs3Hn7OycmGM
GI-098 | SY05-4 | APAC | Closed | P3 Low CX | steven.hoang@bureauveritas.com | 2026-07-27 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | AOB-E-SY5-4 (A09-BTU-01) ##LV FIC001 cable dead test and fed from label AC Cable not connected Raising this for tracking only as EDB is not ready. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630992&prj=644&rqi=79MmMi9NdS3Nny976W8QLi21tr
GI-091 | SY05-4 | APAC | Closed | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-07-05 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | TMD-M-SY5-4 (Variation of DCOS terminations to A9 MCPs) Termination blocks had to be added to the MCPs to facilitate Crossmuller terminations. Crossmuller to add this to their ITPs to show these works have been completed in the A9 MCP & FCMS Panel Upload ITP with comments of work variation to MCP or FCMS Panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627969&prj=644&rqi=nLvXDsDJssy3bSeytV8U2bQSzG
GI-078 | SY05-4 | APAC | Closed | P3 Low CX | raluca.bastucescu@bureauveritas.com | 2026-07-01 04:00:00.000 +0400 | General Contractor |  | Cleaning | Commissioning | [6 empty] | A2 Switchroom to be cleaned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627660&prj=644&rqi=PJ1Vvo31RvXiw1D4Buk9kSUp4R
GI-074 | SY05-4 | APAC | Open | P3 Low CX | raluca.bastucescu@bureauveritas.com | 2026-06-30 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [6 empty] | TRACKING PURPOSES ONLY - VERTIV PURPOSLY REMOVED AP22-X1 cable in UPS Prior to L3 Cx Calibration Activities. Vertiv will put it back once calibration activities are done. Will be closed once Vertiv have completed the tasks. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627482&prj=644&rqi=udXcjme3auY7hS1J4ADEy1d9Yf
GI-067 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-06-25 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [6 empty] | No visibility of the Earth bonding as this is in underfloor containment. BVPI cannot validate the underfloor containment bonding, test results of bonding and earthing to be reviewed for site / area / sub area. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627029&prj=644&rqi=RHW6BMVjnqyeuLHUQatrIALYfa
GI-059 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-06-17 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [6 empty] | AOB-E-SY5-4 (A2-MVTB TEMP POWER APPROVAL) Loop & Good Testing Outstanding. Hi @Satheesh Kumar Natarajan, To allow Cx activities to proceed and keep the program moving are you happy to authorise the temporary supply works on A2-MVTB for testing tomorrow morning? This was the first room where we walked earlier today. o Remaining L2 testing (except Loop), see attached, have been completed & witnessed today by BVMC (awaiting documentation upload to FG) ï‚§ Loop Feeder Testing (##Push issue to be raised to track this 29.06) Team, Moving forward, the first priority and aim is to have tags signed off and in place first, as this is what firstly enables permanent / temp energisation, if this not achievable and as per the MVTB scenario can you please ensure the Cx team are aware and present in the room to ensure the correct chain of approval is being followed to allow an issue to be raised for tracking and to ensure this is pre-approved. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625770&prj=644&rqi=wj9ghh1G1X3VJsZkCPAQCuhoV9
GI-058 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-06-16 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | AOB-E-SY5-4 (A09 & A10 TRX NAME / SERIAL / RATING PLATE) Physical rating plate visibility/access may be limited, or details have not been captured during installation/inspection. Transformer nameplate information (TRX ID, serial number, rating plate details) not installed on the newly delivered assets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625557&prj=644&rqi=QxqZGdkB8HtuHHPVzXR18tHrqb
GI-056 | SY05-4 | APAC | Closed | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-06-14 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [6 empty] | TMD-M-SY5-4 (Ceiling Tiles not modified for CRAH Units) Modification of ceiling tiles above the new 14 CRAH units (7 in COLO1 & 7 in COLO 2) have yet to be completed. L2 Tagging has been pushed back due to incompletion of construction works. Please provide evidence of completion of works. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625255&prj=644&rqi=klloc2S01MoNOUTpZj4fDZEq0g
GI-055 | SY05-4 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | **QC**AOB-E-SY5-4 (M5 & M6-02A ROOMS EXTERNAL LABELING) External Room labeling currently shows storeroom, this needs to be labeled prior to energisation of any power within this room., this clearly identifies the room in the event of a fault or safety issue. Supporting photo to be uploaded. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623853&prj=644&rqi=yuDwmnxkDnQZ2j5gcevSy935yG
GI-054 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | General Design Issue | Design | [6 empty] | AOB-E-SY5-4 STS Panel Openings â€“ Foreign Object & Live Risk This design has been used around the site in all previous phases, Vertiv to comment and acknowledge the risk The Static Transfer Switch (STS) panel has open penetrations on the top of the enclosure (roof). These openings present a risk of foreign objects (e.g., nuts, bolts, tools, debris) falling directly onto internal live electrical components. Operation in bypass mode, where the system is configured to allow maintenance. In this condition, the top (isolated) section of the panel is de-energised, however the bottom section remains live with no physical separation or internal barriers. This creates a risk where tools, fixings, or debris can fall through the top openings and come into contact with energised components below during maintenance activities. During maintenance temp separation will be required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623850&prj=644&rqi=TdfDvik0YEC7VtK3ZT704XELIj
GI-052 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-05-25 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | AOB-E-SY5-4 (A2 STS L1/L2 Documents) â€¢ Equinix â€“ SY05 Phase 4 â€“ STS â€“ GA Drawing â€¢ Equinix â€“ SY05 Phase 4 â€“ STS â€“ Product Description â€¢ Equinix â€“ SY05 Phase 4 â€“ STS â€“ Cross Cabinet â€“ User Manual Screenshot below showing how to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623066&prj=644&rqi=2FtKt7bHSFi4ESmncNOFRe9c0Q
GI-053 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-05-25 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | AOB-E-SY5-4 (A2 STS Calibration Certs) Cal certs required for the below FAT & L2 QA/QC ITP testing. 02A 02B 08A 08B Screenshots below | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623067&prj=644&rqi=uOmlkATCIJnOvTO2BOUTDWRQiY
GI-051 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-05-25 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | AOB-E-SY5-4 (A2-STS IDENTIFICATION LABEL's) - Main Label - Fed From (S1&S2) 02A 02B 08A 08B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623063&prj=644&rqi=NPqn9WSU19ohQ8fR4T2DMl6f9Y
GI-050 | SY05-4 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-04-29 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | **QC**-AOB-E-SY5-4 COLO13 PDU FED From labeling to be addressed and made site location applicable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619986&prj=644&rqi=5CTJdTpNaAUqaxXCKAPx2LxOUr
GI-049 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-04-21 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [6 empty] | AOB-E-SY5-4 (A11 to A12 MVTB VLF CONSTRAINTS) The EC has flagged the risk that the â€œloopâ€ line from A11 to A12 MVTB cannot be re-VLF tested at 80% due to the . Since the cable has been cut and terminated loop in/out of MVTB-A12. Missing the VLF testing provides the risk to verify that the cable will withstand normal operating voltage, will the splice hold up. As of 21.04.2026 BVPI had been informed megger testing can still be performed with the removal of VTs/CTs within A11-MVTB which will prevent the risk of trips. Please provide Comments of next steps to move forward. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618935&prj=644&rqi=74mkwUJ2h8mP6rW4AqJP5OJ6dT
GI-046 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-04-20 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | AOB-E-SY5-4 (UPS DCOS POINT ERROR BCB) Screenshots and photos to be provided to close out this issue Testing Battery Breaker Open, graphic shows Output Breaker Open getting Output breaker Open and should be Battery breaker Open check Alarm - need to be checked again when testing load we need Output breaker Open alarm active to compare Modbus register This point is reversed on the Modbus register Testing Output Breaker Open , graphic shows Battery Breaker Open, getting Output breaker Open and should be Battery breaker Open check Alarm - need to be checked again when testing load we need Output breaker Open alarm active to compare Modbus register | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618796&prj=644&rqi=tK5qEUUq7BjOmpftMu6GNzzAjp
GI-047 | SY05-4 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-04-20 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | **QC**-AOB-E-SY5-4 (A1 & A2 UDB LABELING) Updated Labeling to be printed and applied against the below assets. A1-UDB-02A A1-UDB-02B A2-UDB-02A A2-UDB-02B A2-UDB-08A A2-UDB-08B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618805&prj=644&rqi=KW8428gF7erSAjoQIKwabZKzk6
GI-038 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-04-07 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | AOB-E-SY5-4 (A12-TRX - Documentation Outstanding) Factory Reports - Hitachi to provide Delivary dockets - Hitachi to provide As-Builts (attach as a bulk item to all TRX assets) - Hitachi to provide A12 Equipment layout - WIP - I need to investigate to confirm the status of these submissions. Documents attached to MVTB FIC002 Control Cabling - Uploaded 7/4 FIC012 HV Comms cabling - Uploaded 7/4 FIC-003-Earth Grid-HV- Uploaded 7/4 FIC016 HV Cable Test Cx Reports - Uploaded 7/4 FIC037 : Attached to documents but not visible on the asset (if these can be attached to the asset please) - I need some assistance with linking the documents FIC016 : Attached to documents but not visible on the asset (if these can be attached to the asset please) - I need some assistance with linking the documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617466&prj=644&rqi=K4qifbVLKU9LY46zjFRT1oGBgE
GI-031 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-25 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [6 empty] | AOB-E-SY5-4 (A12 -MVTB LOOP CONNECTION) connection & testing outstanding Raising push issue to allow Red & Yellow Tags to be installed This issue will track the full Cx process and testing of the outstanding MVTB works, pending CR date of 20th April | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616468&prj=644&rqi=4clC1OVaarN9ejzhu74hAwl842
GI-032 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-25 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | ##SY5-HSB & GSB No Asset Identification Labels on new incomer / outgoing GSB and HSB for the new assets installed across the site issue applicable to SY5 site wide | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616469&prj=644&rqi=rkrjQ66Omom96jojnPlCjR1cGq
GI-030 | SY05-4 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-25 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [6 empty] | **QC**-AOB-E-SY5-4 (SCADA / GSB / HSB / ELEC ROOMS SLD) Single Line Diagrams (SLDs) for SCADA, GSB, HSB, and ELEC rooms are outdated and do not reflect recently installed equipment on the SLD. Updated to cover site wide once IFC drawings are approved, Red lines to be completed in the interim . Current diagrams lack new assets, updated electrical connections, circuit configurations. This impacts maintenance procedures, emergency response accuracy, compliance records, and personnel safety. Updated SLDs are required to align with current installations and ensure accurate reference. All HSB / GSB / SCADA ROOMS AND ELEC Rooms to be updated as required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616448&prj=644&rqi=md8CIQPCl1t1YQIdWpU3Tuy07d
GI-027 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning | Commissioning | [6 empty] | SY5-4 GEN17 & 18 Load Testing @ 1.0 PF SY5-4 - Cummins Generator Power Factor Requirements Hi YK Aaron has just been asking me last week about the power factor requirements for the GENs at SY5-4, I know the site based load bank which is unity has been agreed upon but I can't find the correspondence, Are you able to share please? We're now hyper aware of ensuring we have a track of all agreed deviations from the playbook Thanks very much Matthew KERRIGAN Program Manager Wed 18-Mar-26 11:44 AM Hi Matt, We have a FoK 4hrs load test in Sydney factory due to new enclosure manufacturer.. it will be 0.8pf load bank test.. As onsite, we only have 1pf load bank and many onsite units have been done with 0.8pf, thus, we will proceed with using onsite 1pf load bank for site testing.. Cheers Y.K Choong Senior Commissioning Manager More secure, more connected, more sustainable. Learn more about Equinix Australia. EQUINIX PROFESSIONAL SERVICES, DATA CENTER ¦ 578 Lorimer Street, Port Melbourne, VIC 3207, Australia E ychoong@ap.equinix.com ¦ M +61418 614 393 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615925&prj=644&rqi=Jcarl8pd1RfUPdd5SS8Oi9ZTnK
GI-028 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | SY5-4 PDU AS-BUILT Drawings CB reflect 32A EQX & Grog the costumer has upgraded the brakers to 63A for customer requirements | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615950&prj=644&rqi=c55ysSHXpHKlwQI9VfFtcfn5Kr
GI-026 | SY05-4 | APAC | Closed | P3 Low CX | jade.pries@bureauveritas.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [6 empty] | Tiles require cutting so that return air path is clear and free of restriction. All CRAHs to be checked. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615770&prj=644&rqi=EmnqMPMcXHvORQHQL23l0eTO2z
GI-023 | SY05-4 | APAC | Closed | P3 Low CX | jade.pries@bureauveritas.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Installation Damage | Commissioning | [6 empty] | Damage found on CRAH unit locks and scratches found to front covers. CRAH units 29 and 30 - Have damaged locks CRAH unit 34 - Scratch to front panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615756&prj=644&rqi=OSZLz79iT8R3m4w1r6OD1txVww
GI-024 | SY05-4 | APAC | Closed | P3 Low CX | jade.pries@bureauveritas.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Cleaning | Commissioning | [6 empty] | All CRAH units to be properly cleaned on dust and debris prior to energising units. Dust, insulation and footprints present in unit internal chambers and trays. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615761&prj=644&rqi=KNh1nFoGPtnPDQkiYnRIv4xMvV
GI-025 | SY05-4 | APAC | Closed | P3 Low CX | jade.pries@bureauveritas.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Torque required | Commissioning | [6 empty] | Earth terminals to be torqued and marked in all CRAH units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615766&prj=644&rqi=RViWwOlCrXhpKpjfx45CNb31YW
GI-022 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-15 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [6 empty] | ## #STW-MOP-020 - MDB to EMDB Cutover (COLO14 M5-EMDB) Raising push issue to track the energisation of M5-EMDB-01 with SUB circuits outstanding which fall under MOP-020 M6 EMDB Central Feeds Terminated & Energised > Board will then be de-energised and made safe to install CRAH circuits in COLO14. Panel chart/schedule for CBs to be updated once all sub-circuits are installed This push issue will allow L2A & L2B Tags for initial energisation to test submains before MOP works. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615686&prj=644&rqi=52zugNQFbPiJWaibmfEiYZIyhi
GI-016 | SY05-4 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | **QC**-AOB-E-SY5-4 (A12-UDB LABELING) No Asset Identification Labels on PDU's - Issue applicable to all Colo 14 PDU's. PDUs have no fed from or permanent assets tags leaving it unclear to the user if an urgent isolation is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615153&prj=644&rqi=mOgQwL8dwJfLRfs2m2zNHoRB7I
GI-015 | SY05-4 | APAC | Open | P3 Low DCOS | aaron.obrien@bureauveritas.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | **QC**AOB-E-SY5-4 (A12-PDU LABELING) No Asset Identification Labels on PDU's - Issue applicable to all Colo 14 PDU's. PDUs have no fed from or permanent assets tags leaving it unclear to the user if an urgent isolation is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615151&prj=644&rqi=RsFVwVPegPhkRderzSPYUeaQqU
GI-013 | SY05-4 | APAC | Closed | P3 Low CX | luke.kerin@bureauveritas.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | GSB-12 Panel 03 & 04 Permanent feeder labels not affixed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483493&prj=644&rqi=XFtXP3lgxrzn8ZuxSxtvPmmFYL
GI-001 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-01-06 04:00:00.000 +0400 | General Contractor |  | Component/Equipment Failure | Commissioning | [6 empty] | A11 MVTB Relay K06 (Contact Sticking) Latching Cubicle 103 Schneider HV have replaced this K06 contactor and re-tested the new relay. Tracking purpose as a component has been changed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196407&prj=644&rqi=GHUPPj55PbWXQrse6qi5TqQYzq
GI-002 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-01-06 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | SLD (Panel Drawings) RED MARK terminal numbering to be updated on all pages to reflect relay terminal numbering on A11 MVTB Schneider team working on this internally | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196409&prj=644&rqi=XIr5SWcADtANg6LUlzVRobIKCs
GI-043 | SY09x-2 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-18 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | Error | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615923&prj=528&rqi=FiTHN6pytLn9LIHcxfHUhJt1Sd
FPT-269-001 | SY09x-2 | APAC | Closed | P1 High CX | matthew.kerrigan@bureauveritas.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L4 | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | This issue is being raised due to directed works from Equinix to Hanley not yet being performed. Earlier in the project there was a clarification required from Equinix regarding the control wiring of the PQAs in all MSBs across site. This is related to the alarms through the PM8000s where the power meter is used as a gateway to the DCOS Equinix provided clarification and direction to modify wiring. Due to this and the relative simplicity to resolve an issue was not raised however now BVPI has no choice as they are not completed and will delay project progression to L5 Issue is related to L4 activities. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198822&prj=528&rqi=s9k7uiPKsOt1qNqdTEBW4CBUBw
GI-025 | SY09x-2 | APAC | Closed | P3 Low DCOS | sulaiman.khan@bureauveritas.com | 2026-01-28 04:00:00.000 +0400 | Equinix Design Engineer |  | Commissioning Issue | Commissioning | [6 empty] | CHWP-M4 - FT04 has no value mapped to it in DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197697&prj=528&rqi=CBNMHcvd9rHGdBy8XDkxfVc41b
GI-239 | SY09x-2 132kV Substation | APAC | Open | P2 Medium CX | CiaranConlon@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | General Contractor |  | Component/Equipment Failure | Commissioning | [6 empty] | UPS inside comms panel 2-HMTX-2-CP is alarming and needs to be investigated and possibly replaced by Ausconnex. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636231&prj=562&rqi=AiNTWyFjEcoTlAUzPREygkq53R
GI-233 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - 7UT85 Relays - Slight discrepancy seen in settings installed against IFC Grading Study. Settings to be confirmed. See screenshot for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625568&prj=562&rqi=ckYMLYzsbGMmq2hYHCdpgLbLP6
GI-236 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - HMTX TMR/AVR - PT100 Device displays ER2 (Sensor interrupt) error message across all transformers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625574&prj=562&rqi=mGu930aFKL0f8idB0oo730lc9O
GI-232 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2B - 132kV Cabling - Plus ES Calibration Certs to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625244&prj=562&rqi=vuqeYh62t3PjzPxECntTPmlyD3
GI-230 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10 Switchroom & Controlroom - Filters to be installed within vents at access doorways to Switchrooms and Controlrooms. See photo for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623737&prj=562&rqi=2Pnz1yB5HjsX7fAppK76bmEb8w
GI-229 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 Switchroom & Controlroom - Filters to be installed within vents at access doorways to Switchrooms and Controlrooms. See photo for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623736&prj=562&rqi=XQ2POHb5B2fGZoEWFlr8zzZREl
GI-225 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - SY9 Switchrooms - FCU Labelling incorrect / cable supplies installed in incorrect orientation. When isolating specific FCU in switchroom the alternate FCU is isolated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622757&prj=562&rqi=jaF2NpnPFLQJnjEs8Bep1GVVPX
GI-226 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - SY10 Switchrooms - FCU Labelling incorrect / cable supplies installed in incorrect orientation. When isolating specific FCU in switchroom the alternate FCU is isolated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622758&prj=562&rqi=hiU1NkIU7bsBM6qISaJuutXEpK
GI-222 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ LV | equipment | 1-MDSB-1 | MDSB - Mech Distribution Switchboard |  |  | CxL2A - 1-MDSB-1 - Exhaust Fan Label shows incorrect On/Off position. Label shows EF On when it is Off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621532&prj=562&rqi=rUpurkJm08xn3O6FWCMSfXL1h4
GI-224 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL3 - 2-HMTX-1-PP & 2-HMTX-2-PP - Transformer Protection Relay No.2 has intermittent comms losses to DCOS. Causing repeated comms alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621543&prj=562&rqi=cCT2djijQYeF7KLZTKG8ilCf84
GI-223 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL3 - 1-HMTX-1-PP & 1-HMTX-2-PP - Transformer Protection Relay No.2 has intermittent comms losses to DCOS. Causing repeated comms alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621542&prj=562&rqi=KWbv5zSx619AkFE3cetTL1S3Qa
GI-221 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9B - Earth connection cable within the SY9B transformer bund to be securely clamped to the bund wall (GHD Issue) See photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620889&prj=562&rqi=iq3khPGn2RSnY6LuG9gF4lAis6
GI-209 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 132kV Cable screens - Cabling currently secured to supporting structure using plastic cable ties. Correct means of securing cables to be confirmed and updated if required. Potential requirement for cleats or stainless steel. See photos for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620862&prj=562&rqi=863pz1c921aJnpT48S3SuSewiR
GI-208 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10 132kV Cabling Link Box - Links removed for purposes of testing to be reconnected, torqued and marked on completion of CxL2B testing. Some dust found in link box. Link box to be cleaned. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620860&prj=562&rqi=Yy0Y2Ib8RKuWxUf447qqAFTgtX
GI-212 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10 Cable Pits - Cable Pits to be sealed against rainwater accumulation (GHD Issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620879&prj=562&rqi=kPRXw3o7rdh3AsPDQFUP8Xplx0
GI-217 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 - General cleaning required in transformer bund area. Dirt & Debris to be cleared, Rope in cable ducts o be cut back. Stains on the floors of transformer bunds yet to be removed (GHD Issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620885&prj=562&rqi=NsL5GWbwJYxfrbWr6d45n3Huw6
GI-207 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 132kV Cabling Link Box - Links removed for purposes of testing to be reconnected, torqued and marked on completion of CxL2B testing. Some dust found in link box. Link box to be cleaned. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620859&prj=562&rqi=3Hb2svmiqq3o8SYa2o0LvGiFTM
GI-210 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10 132kV Cable screens - Cabling currently secured to supporting structure using plastic cable ties. Correct means of securing cables to be confirmed and updated if required. Potential requirement for cleats or stainless steel. See photos for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620863&prj=562&rqi=ZCeIXhHHMZlfmjTriMy1hXrl7Y
GI-211 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 Cable Pits - Cable Pits to be sealed against rainwater accumulation (GHD Issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620878&prj=562&rqi=jFLrFpViy6n726II11Iwa1MgGq
GI-206 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ MV | equipment | 2-HMTX-1-K2 | HVCABLE - Aerial Flexible Conductor |  |  | CxL2B - 2-HMTX-1-K2 - Ductor Test results missing for C Phase PG Clamp. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620851&prj=562&rqi=2LntxRf4F6K2w2IisUeb5AHXpG
GI-216 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10 - Excess lengths of earth connection bolts in control room yet to be cut off (GHD Issue) See photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620884&prj=562&rqi=59wLy06NW41C4q3ICJKxJbZ3Rv
GI-213 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 - Arc flash labels to be installed as mentioned in SYSS1-1-RPT-EL-691.3S Arc Flash Study Report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620880&prj=562&rqi=tpSzQEDuAVJFukkWlffkLIgdUd
GI-214 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10 - Arc flash labels to be installed as mentioned in SYSS1-1-RPT-EL-691.3S Arc Flash Study Report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620881&prj=562&rqi=2CVxUkIWfjymtVi4oAZelDufE6
GI-219 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 - Sealing of the floor tiles at door entry of the control / switchrooms yet to be completed (GHD Issue) See photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620887&prj=562&rqi=4ISsIBqvCPfSnNcZ6i40WOeVca
GI-220 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10 - Sealing of the floor tiles at door entry of the control / switchrooms yet to be completed (GHD Issue) See photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620888&prj=562&rqi=bt7ydQWz20l9sMrpNTWxqIjKP0
GI-218 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10 - General cleaning required in transformer bund area. Dirt & Debris to be cleared, Rope in cable ducts o be cut back. Stains on the floors of transformer bunds yet to be removed (GHD Issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620886&prj=562&rqi=W8wj4JQR9dSvjLOqOGwJVJrx19
GI-215 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 - Excess lengths of earth connection bolts in control room yet to be cut off (GHD Issue) See photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620883&prj=562&rqi=D8g2jDzzBgLuLQnyuWLpIMgPbZ
GI-205 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-MLTX-1 & 2-MLTX-2 - Various terminations require torque marking. Surge arrestor termination to chassis, Bonding within CT wiring enclosure (at earth bar and to chassis) and bonding within LV compartment. See photos for further reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620477&prj=562&rqi=OUF2ITA9417EPaf8srz2Fuh5Bw
GI-204 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-MLTX-1 & 1-MLTX-2 - Various terminations require torque marking. Surge arrestor termination to chassis, Bonding within CT wiring enclosure (at earth bar and to chassis) and bonding within LV compartment. See photos for further reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620475&prj=562&rqi=qcvKRPhk0OKlL6nu6RjYUexVi7
GI-203 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2B - 1-MLTX-1 & 1-MLTX-2 - Tap to be adjusted to tap 5. Power Transformer output voltage set to 10.5kV. Auxiliary transformers tap settings to be updated to allow for lower supply voltage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620470&prj=562&rqi=pB5x88XPSHId4eJlACUvqdjLyQ
GI-201 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A & CxL2B - 2-MLTX-1 - Report to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620465&prj=562&rqi=zjQPCWrtkh6rmi9Sx7bJ4Z16tn
GI-200 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 Earthing - Earthing to be torqued and marked at all earth bars and cable connections (Switchrooms and Transformer pit) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618953&prj=562&rqi=2CojcqmvTWpDpzXsqEI3qfNwUj
GI-198 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-HMTX-1 & 2-HMTX-2 - Cable end box works to be completed. Silicone sealing between gland plates to be installed. Bonding between gland plates to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618486&prj=562&rqi=jYLmmqBz6X1tonwYG5vupkbuzb
GI-196 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ LV | equipment | 2-DB-1 | ACDB - AC Distribution Board |  |  | CxL2A - 2-DB-1 - Middle cover to be installed and door bonding terminated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618484&prj=562&rqi=nGI4CCbrG8HIsOBnnkxEJnG4ZI
GI-192 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Fire Detection | equipment | 2-FIP-2 | FP - Fire Panel |  |  | CxL2A - 2-FIP-1 & 2-FIP-2 - Cleaning required within panel. Dust and debris present to be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618475&prj=562&rqi=ASHlagqWV7KBaFOMFoa07iNz68
GI-191 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Fire Detection | equipment | 2-FIP-1 | FP - Fire Panel |  |  | CxL2A - 2-FIP-1 - Unable to access panel. Key sheared off inside lock. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618474&prj=562&rqi=us3uleoGDL42CzxmpsJhlAtWTD
GI-193 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Fire Detection | equipment | 2-FIP-2 | FP - Fire Panel |  |  | CxL2A - 2-FIP-1 & 2-FIP-2 - Earthing requires torque marks | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618476&prj=562&rqi=ITb1evS7nMnhvhAMsBdfyBqn3u
GI-186 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ LV | equipment | 2-DB-1 | ACDB - AC Distribution Board |  |  | CxL2B - 2-DB-1 - Report missing cable test reports. Report to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618469&prj=562&rqi=mMFTcHrF7YK0vY97LQw9iyz8Up
GI-183 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-SUSP-1 & 2-SUSP-2 - MIMIC Labelling to be updated. Panel 1 Incomer currently shows incoming cable as a feeder. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618466&prj=562&rqi=bt779e2753AXQb4eq6ti8TKWul
GI-179 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10A Permanent Labelling to be updated for all equipment and cabling. Includes Equipment, HV Cabling, Submains, Subcircuits and Earthing. Note: In addition to the above SUSP, SEP to be updated. Phase indication for Disco. HV Cabling, Earth Cabling and Subcircuits missing labels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618462&prj=562&rqi=t5sNJVUK19V71aUWs5bGhNmq62
GI-197 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-HMTX-1 & 1-HMTX-2 - Cable end box works to be completed. Silicone sealing between gland plates to be installed. Bonding between gland plates to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618485&prj=562&rqi=N0OzmN3kF2QaryMC0WUsYFxhwy
GI-187 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ LV | equipment | 2-BTU-1 | DCDB - DC Distribution Board |  |  | CxL2B - 2-BTU-1 - Report missing cable test reports. Report to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618470&prj=562&rqi=psHyIXNbPu3Yj52NpvMwcXKFFq
GI-180 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10B Permanent Labelling to be updated for all equipment and cabling. Includes Equipment, HV Cabling, Submains, Subcircuits and Earthing. Note: In addition to the above SUSP, SEP to be updated. Phase indication for Disco. HV Cabling, Earth Cabling and Subcircuits missing labels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618463&prj=562&rqi=37fupOdYbHyVSnz3a1NQXxmCS2
GI-181 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-SUSP-1 & 2-SUSP-2 - Thermostats to be set up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618464&prj=562&rqi=h9wfLKduBkagWh4le0kHZTmwkW
GI-182 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - 1-SUSP-1 & 1-SUSP-2 - MIMIC Labelling to be updated. Panel 1 Incomer currently shows incoming cable as a feeder. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618465&prj=562&rqi=5aAHvx8FjbtYMYsLaKiT3nwKNk
GI-178 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - 1-DB-3 & 1-DB-4 - Metering not reading current only voltage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617474&prj=562&rqi=s3LoLcaYiKUVDAhsbsSs1kU4lf
GI-177 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - 1-HMTX-1 & 1-HMTX-2 - TMR/AVR Various Equipment Rating settings incorrect. Time Not set correctly. Time Sync non functioning correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617464&prj=562&rqi=CE4zxYIlZQqurhCWx6Z0hMn9BF
GI-175 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - 1-HMTX-1 & 1-HMTX-2 - TMR/AVR Cx Reports incomplete, missing various info and attachments. To be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616055&prj=562&rqi=8O82Uy3IP5y4ifLGGydvuSQzAo
GI-172 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-20 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Communications | equipment | 2-HMTX-2-NP | HMI - HMI Panel (Network Panel) |  |  | CxL2B - 2-HMTX-2-NP - Missing Network cabling test results in report. Updated report to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616051&prj=562&rqi=ycbN9ZaeI213IeDdtA2ZVkEt6J
GI-173 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-20 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 Substations - WIFI Router to be affixed to agreed location | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616053&prj=562&rqi=widB8uIbfIZBK1DoLY7FErHkEU
GI-166 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-SUMP-1 & 2-SUMP-2 - Enclosure door screws not fixed. Panel door to be secured. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615919&prj=562&rqi=Fh5qF6HmU2LDcstzyV6OcQeQBp
GI-168 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-HMTX-1 & 2-HMTX-2 - Neutral Earthing to be completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615921&prj=562&rqi=JhDrjJobSoME8DqwjNnbFcVMRU
GI-165 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - SY10 Earthing - Earthing to be torqued and marked at all earth bars and cable connections (Switchrooms and Transformer pit) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615918&prj=562&rqi=Hl1GIbsfutuNQkRw723mFrrkrr
GI-171 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-MLTX-1 & 2-MLTX-2 - Neutral earth cable needs to be clearly identified as earth/neutral | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615929&prj=562&rqi=qXjnlnnM8Tukr07vGWkC7MxAAz
GI-169 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2B - 2-HMTX-1 & 2-HMTX-2 - Thermostats to be set up within switchgear. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615922&prj=562&rqi=UP3kkJ8iKfCCt6IJrpoUK4BQ0U
GI-167 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-DB-1 & 2-DB-2 - Heat Shrink to be installed on bare copper at Load side of MTS to DB Section of Switchboard. Top and bottom sections. See picture for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615920&prj=562&rqi=3xyCh3je8p2BCYt3Uiq41jk4nH
GI-170 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-HMTX-1 & 2-HMTX-2 - Dust & Debris present within LCP. Cleaning required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615927&prj=562&rqi=sVIuvzbaFLf31rIl4jHVIry814
GI-159 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - 1-HMTX-1 & 1-HMTX-2 - TMR/AVR LED Mapping not programmed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615912&prj=562&rqi=7gpekqAU6T6Lm3RtSOggCnCsAn
GI-160 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - 1-HMTX-1 & 1-HMTX-2 - TMR/AVR DCOS Points not mapped correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615913&prj=562&rqi=dH0f5TIErqr4Cg30fbo4dq3G5I
GI-161 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-DB-3 & 2-DB-4 - Labelling to be updated. Labelling associated with DB still shows previous naming convention. All small wiring labelling internal to DB and GPO / Light Switches associated with DB to be updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615914&prj=562&rqi=zBdWOwO4AQJsE73hFdy9R0FuGv
GI-162 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-BTU-1 & 2-BTU-2 - Holes in escutcheon on DB to be sealed. 2 x large holes within escutcheon of DB cut out to allow for door to be closed, devices will prevent this presently. Some form of recessed cover to be installed in empty spots to seal up holes. Pole fillers also to be in place where missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615915&prj=562&rqi=VxzD97wekRJuKDtCTPaekTQ6bX
GI-158 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-HMTX-1-NP & 2-HMTX-2-NP - UPS Cabling install incomplete | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615911&prj=562&rqi=VecG02SIiCGEP3sgg4jMaDVvDW
GI-164 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-MLTX-1 & 2-MLTX-2 - Extra External Protection needed for 11kV Cables (UV/Water/Mechanical). Cover to be installed over cables to provide extra protection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615917&prj=562&rqi=f2eHqkBdb6nXMQFr4hmpRv9Vm5
RT1ELEC-1-001 | SY09x-2 132kV Substation | APAC | Closed | P1 High CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Incomplete Connections | Commissioning | Electrical â€“ MV | equipment | 1-HMTX-1-SA3 | HVCABLE - Surge Arrestors |  |  | CxL2A - 2-HMTX-1 & 2-HMTX-2 - Earthing for surge arrestors to be installed. No bonding between arrestors and earth nest. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615916&prj=562&rqi=GdDAac7290tYNyLjzIAXv55Oz9
GI-151 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ LV | equipment | 2-DB-2 | ACDB - AC Distribution Board |  |  | CxL2A - 2-DB-2 - Comms Cabling not terminated. Potentially not required. If not required, it is to be removed and gland blanked off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615776&prj=562&rqi=D20tmqjad2Pjacy6CYSkUCsKQN
GI-153 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-DB-1 & 1-DB-2 - Heat Shrink to be installed on bare copper at Load side of MTS to DB Section of Switchboard. Top and bottom sections. See picture for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615778&prj=562&rqi=5Z18WhFL6bFukFYQzAJiqJw5Hl
GI-152 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ LV | equipment | 2-DB-2 | ACDB - AC Distribution Board |  |  | CxL2A - 2-DB-2 - Pole Fillers missing. To be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615777&prj=562&rqi=rlesNwm2R0pGM3Nm562hpEBKPY
GI-150 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ LV | equipment | 2-DB-2 | ACDB - AC Distribution Board |  |  | CxL2A - 2-DB-2 - Trunking cover misssing interal to Switchboard (Left side) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615775&prj=562&rqi=9LaIS6b52C0AboCi5S6EFNLszk
GI-154 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY910B Permanent Labelling to be updated for all equipment and cabling. Includes Equipment, HV Cabling, Submains, Subcircuits and Earthing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615780&prj=562&rqi=x6blXARYzDcKRf04ZivXs4zBjc
GI-149 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-SUMP-1 & 1-SUMP-2 - Enclosure door screws not fixed. Panel door to be secured. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615168&prj=562&rqi=D5ut4eplQpKAeuMEEWyUBBeF4G
GI-148 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - 1-SUMP-1 & 1-SUMP-2 - Level alarm indication on Pump controller not operating as expected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615166&prj=562&rqi=DR4BzJtK2KoBVQU6XJCexeSF7v
GI-147 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A & CxL2B - SY9 Overhead Conductor - Test reports to be submitted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199810&prj=562&rqi=kWMue18a7XwV2HDIjlZz8XfunS
GI-146 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2B - 1-MLTX-1 & 1-MLTX-2 - Oil Sample / Oil Tests of transformer not completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198975&prj=562&rqi=oysebrSYhkXD3JN3RyMgSforIA
GI-143 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-MLTX-1 & 1-MLTX-2 - Extra External Protection needed for 11kV Cables (UV/Water/Mechanical). Cover to be installed over cables to provide extra protection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198823&prj=562&rqi=c7YpBHGpZQSGecYqnOl7RmRBeD
GI-144 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 132kV Power Transformers - LCP Supplied by vendor allows for two power sources from alternate supplies (9A & 9B). Allowance made for this with both AC & DC Supplies. Currently only 1 Source has been provided to the LCP. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198829&prj=562&rqi=s30X2zu4nUJhMsfc5c9OfIlAh8
GI-145 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - SY9 Earthing - Earthing to be torqued and marked at all earth bars and cable connections (Switchrooms and Transformer pit) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198832&prj=562&rqi=jx6Ye36asVJyMZg5bEinCSO7D8
GI-138 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-FIP-1 & 1-FIP-2 - Bonding to be torque marked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198747&prj=562&rqi=P0pG6zCaUWhm6krV7bZs5eUvgF
GI-136 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | Fire Services Installer - Calibration Certificates to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198745&prj=562&rqi=z3r0vMxJf4xGIeuJEKWwVzI0tK
GI-137 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-FIP-1 & 1-FIP-2 - Dust and Debris present within panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198746&prj=562&rqi=vaxqtoYl9LCsVBwC8qvfdwnWYL
GI-139 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Fire Detection | equipment | 1-FIP-1 | FP - Fire Panel |  |  | CxL2A - 1-FIP-1 - Unused gland on top of panel to be removed and blanked off if not required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198748&prj=562&rqi=mDPugX6dbbeoz0RjNi3SQUGNAh
GI-142 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-HMTX-1 & 1-HMTX-2 - Dust & Debris present within LCP. Cleaning required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198752&prj=562&rqi=fa7eLN1qUepGtmlvu7zZKCDM0F
GI-141 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-HMTX-1 & 2-HMTX-2 - Neutral CT to be installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198751&prj=562&rqi=2zz5bdrGxG7AFWgkTHIZWk8UOt
GI-135 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | Fire Protection System - SOO to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198742&prj=562&rqi=SH8kJQOaQim3NWMqk9LlVBTUOz
GI-134 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9A Switchroom - Cabling not secured. Phase tape used to secure earthing in cable tray. Cable to be secured with cable ties. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198664&prj=562&rqi=3SBiOWl2qItixj9beJSOfZN0SD
GI-133 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9A Switchroom - Light not securely fitted. Held up with cable ties on one side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198663&prj=562&rqi=hfwq2IxrpHHrvaMwwOdXEzMsxz
RT1ELEC-1-002 | SY09x-2 132kV Substation | APAC | Closed | P1 High CX | AmmarKhawaja@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2A | Incomplete Connections | Commissioning | Electrical â€“ MV | equipment | 1-HMTX-1-SA3 | HVCABLE - Surge Arrestors |  |  | CxL2A - 1-HMTX-1 & 1-HMTX-2 - Earthing for surge arrestors to be installed. No bonding between arrestors and earth nest. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198570&prj=562&rqi=6E2nTJcvV1kbajnzqUlcbeRZU4
GI-129 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 132kV Disconnectors and Overheads - Some concern present of tension being on Disconnectors and Surge Arrestors/Bushings. Tension seems to be caused by overhead length and rotating disconnector terminal plates. Potential for damage to equipment when operating disconnectors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198181&prj=562&rqi=7B21e66a0ZiFhUMwPlyc8f0rVR
GI-127 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - MLTX All - Amalgamating tape to be applied at Aux Tx 11kV Cabling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197844&prj=562&rqi=pYDk4k7q9VfnLSkBKtKOIGBleI
GI-122 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - FCU All - Unable to see status of all FCU on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197826&prj=562&rqi=c3XK1sWZKpc9FslcIAgIFKOihM
GI-121 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - 110VDC Battery Chargers - Unable to see DCOS status for various points | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197825&prj=562&rqi=wFSiXWg5Pe4nazZMJ5oz7M3hh7
GI-126 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - ACDB All - Lack of clearance between Main Neutral cabling and MTS secondary outgoing contacts. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197842&prj=562&rqi=kZbRpYuhnFD9tp8OljKq4g9s0H
GI-125 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - Sump Pump All - Unable to see change of state for various DCOS Points. Potential wiring issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197840&prj=562&rqi=d1EtzOCYq1BJ41eB5bmHCC6r2g
GI-123 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ LV | equipment | 1-MDSB-1 | MDSB - Mech Distribution Switchboard |  |  | CxL3 - 1-EF-1 - Exhaust Fan in fault | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197827&prj=562&rqi=6bEEEbvnhWjSoP2IRf2LZAjNWN
GI-120 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2B - 132kV Power Transformers - Siemens Calibration Certificates to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197632&prj=562&rqi=wwYWteWCQDcb8kJGrjcVAxzKy2
GI-116 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - Earthing - Bonding required on various trays within SYA&B. Oil Water Separator, Linkbox & Auxiliary Transformer MV Cable support structure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196933&prj=562&rqi=YEF1ykHOSzROm0fiLjL4cQY2ba
GI-117 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 132kV Transformers - Interface cabling required to be installed between TMR and SUSP for voltage monitoring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196934&prj=562&rqi=nEvHXYUypkOiJEkWPv4TRG6ICS
GI-115 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ MV | equipment | 1-ERTH-1 | ERTH - Earthing |  |  | CxL2A - Earthing - SY9A & SY9B Control Room Door bonding loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196908&prj=562&rqi=saIDmYKZnuOBDfn5hA107bfp2L
GI-119 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - SY9 Auxiliary Transformers - 11kV Cabling earth screens to be sealed with amalgamating tape | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196939&prj=562&rqi=fbwtOraCu73zQZbHefXRCBrEMG
GI-114 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ MV | equipment | 1-ERTH-1 | ERTH - Earthing |  |  | CxL2A - Earthing - 1-BTU-1 Earthing loose at earth bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196907&prj=562&rqi=L7dd3gO0a6t5gy44iHtKges3ta
GI-111 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-DB-1 & 1-DB-2 - Neutral cabling resting on live outgoing terminals. Separation to be created between cabling and terminals. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196835&prj=562&rqi=zG7pRBCi5SsKI8WenkEe9Xn0Kd
GI-110 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - FCU All - No visibility of FCU's on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196833&prj=562&rqi=DvmVWopaid3Nd62mtdtJC5mcm6
GI-108 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9A Permanent Labelling to be updated for all equipment and cabling. Includes Equipment, HV Cabling, Submains, Subcircuits and Earthing Note: In addition to the above SUSP, SEP to be updated. Phase indication for Disco. HV Cabling, Earth Cabling and Subcircuits missing labels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196832&prj=562&rqi=xWzSHjLIFgQtzhIAx0SPUKDfnt
GI-107 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | AmmarKhawaja@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - SY9 Auxiliary transformers - Not bolted down/fixed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196829&prj=562&rqi=VrJPNwx3hVCigDDd1Akcuu9YKl
GI-109 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | AmmarKhawaja@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - SY9 Auxiliary Transformers - Bonding required for MV Cable support structure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196830&prj=562&rqi=M8KfjAoXeG9fB817vdOiowQrGj
GI-112 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | AmmarKhawaja@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-MLTX-1 & 1-MLTX-2 - Neutral earth cable needs to be clearly identified as earth/neutral | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196834&prj=562&rqi=4sVI9SQEAQpyAMEXvfsxpugpR7
GI-106 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 132kV Power Transformers - No presence of earth cabling between LCP Earth Bars and transformer chassis. No continuity seen between various Earth Bars within LCP to Transformer chassis. Potential requirement for adding more bonding. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196541&prj=562&rqi=rIjkmkcOkPzc3X2I7eBTKAaLDx
GI-105 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - 1-SUSP-2 - A04 CB Cover damaged. To be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196405&prj=562&rqi=tAs0axih2omC5LwfBJMfw4EKnt
GI-104 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-HMTX-1-K1 & 1-HMTX-2-K1 - Supports / cable cleats required to be installed for cabling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196365&prj=562&rqi=Pnu0d94mgl6NVBHjOB52xckynG
GI-103 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-05 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - LPS - Lightning Mast Pending installation. Works to be completed & Test report to be submitted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196298&prj=562&rqi=D7cPSjmsUyJgQUJhM6QmCfA2v7
GI-613 | TR06-2 | AMER | Closed | P3 Low CX | Ocean.Kwan@veolia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor |  | Installation | Commissioning | [6 empty] | Main Service gear 1PUSP_1 & 2 sections are missing equipment identifiers/labels, e.g., Interrupter, Protective Relay, Power Quality Meter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623563&prj=358&rqi=GcMdzYz6LUsOmVyOxCCthzjxa8
GI-614 | TR06-2 | AMER | Closed | P3 Low CX | Ocean.Kwan@veolia.com | 2026-06-01 04:00:00.000 +0400 | Vendor- Manufacturer |  | Manufacturing | Commissioning | [6 empty] | TR6-2 (Electrical Block A & R SKID): A few MSB_A breakers were mislabeled (incorrect spelling, incorrect label background color, font size), e.g., UPS_RIB_2, 1UPS-A-2-LBB, 1-CH-A-2, 1LBB_A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623564&prj=358&rqi=xeyzvcZjaAtsjknUKEpDjJAwrR
GI-612 | TR06-2 | AMER | Closed | P3 Low CX | Ocean.Kwan@veolia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Manufacturing | Commissioning | [6 empty] | The posted procedures at the new MSBs is not correct. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623562&prj=358&rqi=fgN5PcQ5LaANi3P2yZpUAvUtBb
GI-116 | TR06-3 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-09-15 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | FWT | Factory Witness Test |  | equipment type |  |  |  |  | AMG NETA Report - Following a preliminary review of the breaker test reports provided for TR6-3, it was noted that the primary injection test of the INS protection for the MSB circuit breakers was not included. AMG to verify with your testing team whether additional reports covering this test are available? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638208&prj=657&rqi=JCdyV4sSHqoQfoy2reas2YXACA
GI-115 | TR06-3 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-09-15 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | FWT | Factory Witness Test |  | equipment type |  |  |  |  | AMG Breaker Test Reports - Upon reviewing the reports, it was identified that certain records include Ground Fault Protection test results for 400A breaker equipment fitted with the MicroLogic 5.3 trip unit. However, the MicroLogic 5.3 unit provides LSI protection only and does not include ground fault protection. AMG is to review and clarify this discrepancy. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638196&prj=657&rqi=ZOKNzY9HCrAkXS4Q9pVWrksRRh
GI-117 | TR06-3 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-09-15 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | FWT | Factory Witness Test |  | equipment type |  |  |  |  | AMG MSBs- While reviewing the FAT documents, it was noticed no torque reports available for the bus. Report is missing this information. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638210&prj=657&rqi=eIgfxDhS2vfbKPn9GBU8nn9atN
RT1MECH-32-001 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-09-11 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CH_A_2 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-A-2: The fitting connecting the pump skid to the chiller evaporator is a different model number comapred to fitting seen on the remaining 6 chillers. Please refer to the attached pictures. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637815&prj=657&rqi=3mLr4PaiHB1T6vEeltwW3fOz8i
GI-114 | TR06-3 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-09-10 04:00:00.000 +0400 | SCH - Schneider Mech |  | Component/ Equipment Failure | Commissioning | [6 empty] | 0.75 in gap in chilled water piping connection between top and bottom mega crah | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637701&prj=657&rqi=c605w3HLN25vm4SGh24ivNNKQm
RT1MECH-87-009 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-09-04 04:00:00.000 +0400 | Consultant | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Applicable to all Skid CRAHs - Secondary source fed from R Block: The max input current mentioned on the CRAH name plate is 13A, the upstream breaker for primary source of the CRAHs installed by MPS are 20 A. However referring to drawing # E715, the upstream breakers for second source on the panel schedule mentions 35 A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636925&prj=657&rqi=5HHxhFU75B51Zp8tRZ7VxDP1cN
RT1MECH-116-001 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-09-03 04:00:00.000 +0400 | Consultant | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1HP_R_05 | HP - Heat Pump |  |  | Common for all MPS skid Trane WSHPs: On the water source heat pump submittal, the "Max Overload protection (A) is given as 15A. On the panel schedule for WHSP fed from R block, The upstream breakers on the panel schedule are 20 A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636780&prj=657&rqi=c9cM7dt6HwAC0djoYDDxFnRftJ
GI-112 | TR06-3 | AMER | Open | P1 High CX | steve.knezevic@veolia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_D | MSB - Main Input Switchboard |  | no | Water ingress through conduit penetrations behind MSB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636750&prj=657&rqi=4LwemzJ7IUehWhfSiL3722GgQa
GI-113 | TR06-3 | AMER | Open | P1 High CX | steve.knezevic@veolia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | Water ingress through conduit penetrations behind MSB and at middle shipping split of skid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636751&prj=657&rqi=oFXBnONNsGhTYs2CW2DqehAUd8
RT1MECH-112-001 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1HP_B_04 | HP - Heat Pump |  |  | Common for all MPS skid Trane WSHPs: On the water source heat pump submittal, the "Max Overload protection (A) is given as 15A. The upstream breakers on the panel schedule are 20 A for the skid WSHPs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636525&prj=657&rqi=6khjQ5gAtQBrbfl8ZzCyKbzv5x
GI-109 | TR06-3 | AMER | Open | P3 Low CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UDPR_C_1 | UDP - UPS Output Switchboard |  |  | UDPR_C_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636559&prj=657&rqi=g0XXotfv3QIXqYlmJtvA2TXjKK
GI-103 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDP_D_1 | UDP - UPS Output Switchboard |  |  | UDP_D_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636548&prj=657&rqi=TgNdAa5HLmSoQ3sFxwHM0xseRT
GI-104 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDP_D_2 | UDP - UPS Output Switchboard |  |  | UDP_D_2 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636554&prj=657&rqi=Ul7cMZNxiakxG3OypPhkWRaWOy
GI-105 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  | no | UPS_C_1_LBB & UPS_C_2_LBB status contacts were not wired to a terminal block to be monitored by the UPS. Three spare EF contacts exist at each breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636555&prj=657&rqi=npqS3o3sQMrIGWBe18XGtCIIDp
GI-111 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UDPR_C_2 | UDP - UPS Output Switchboard |  |  | UDPR_C_2 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636561&prj=657&rqi=pO6oO6SdiInuJg92YuOEu3DCFR
GI-110 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UDP_C_2 | UDP - UPS Output Switchboard |  |  | UDP_C_2 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636560&prj=657&rqi=k8aDoJSlmVmqO4mGdQCpQxGRuA
GI-106 | TR06-3 | AMER | Open | P3 Low CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_D | MSB - Main Input Switchboard |  | no | UPS_D_1_LBB & UPS_D_2_LBB status contacts were not wired to a terminal block to be monitored by the UPS. Three spare EF contacts exist at each breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636556&prj=657&rqi=3uiMxu6NGW5Lyn8QfdpQZpklON
GI-108 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UDP_C_1 | UDP - UPS Output Switchboard |  |  | UDP_C_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636558&prj=657&rqi=QlUfGG74udYzX4MxfUdvmlxn9Q
GI-107 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | UPS_E_1_LBB & UPS_E_2_LBB status contacts were not wired to a terminal block to be monitored by the UPS. Three spare EF contacts exist at each breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636557&prj=657&rqi=IfpsH0qUnYg0zONMVugICt5lwk
GI-102 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDPR_D_1 | UDP - UPS Output Switchboard |  |  | UDPR_D_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636547&prj=657&rqi=CQmorNSvGw7Dd9LHLkKKk9YFjt
RT1MECH-87-005 | TR06-3 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | As per review of the submittal package RMC070, the specification cut sheet individual components are not attached. review Table 2.6 Spare Parts item 12,15,16 -EC Fan -MC-22b -MC-9b -Auxiliar contactor -Step down Transformer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636163&prj=657&rqi=hHGcgiKp4t9afxCTdx3eEw9iiE
RT1MECH-88-006 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | Common for all three CRAH units in Skid E: The panel schedule needs to be revised as per the CRAH asset names inside Skid. It was found that the CRAH names do not match as per drawing M405 (Attached) Also refer to Issue # 152, 155 and 156 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636211&prj=657&rqi=v5Xp1IvfG9G8TMzJRt3ZfZdppd
RT1MECH-87-006 | TR06-3 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | As per review of drawing M405 and on site configuration it was noted that the CRAH labeled 1CRAH_ER_11 is mislabeled as 1CRAH_ER_10. This impacts the following: -BAPI10 - incoming and outcoming EMT labels -wire labels for CB1 and CB2 and main ground. -CRAH Label itself | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636166&prj=657&rqi=sFXU8Y34iTpSAq3kR7Gdnve2zQ
GI-101 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | system | meWall E |  |  |  | Skid E: Rope Leak Detector: Extra Slack on the rope leak detector is not secured neatly in the skid. (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636206&prj=657&rqi=m5dDSGo8pfFiQ5EJzV6Ji8eQ0W | https://equinix.facilitygrid.co.uk/x/project/657/system/13317
RT1MECH-88-003 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | Applicable to all MPS Skid CRAHs: Missing cut sheet of the T sensors on the submittal. (Attaching pictures to indicate the sensors we are referring to) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636089&prj=657&rqi=hhOIfpVj3MKGFMiei639piUIQV
RT1MECH-86-001 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_12 | CRAH - Computer room air handler |  |  | For 1CRAH_ER_12: As per review of drawing M405 and on site configuration it was noted that the CRAH labeled 1CRAH_ER_12 is mislabeled as 1CRAH_ER_11. This impacts the following: -BAPI10 - incoming and outcoming EMT labels -wire labels for CB1 and CB2 and main ground. -CRAH Label itself | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636193&prj=657&rqi=qNEHq0RvBJfqXT5IBPOGH2CPGi
RT1MECH-88-001 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | Applicable to all MPS skids Delta CRAHs: The controls wiring drawing provided in the submittal is not readable, cannot be used for verification of the wiring or the controls components. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636079&prj=657&rqi=lx1WNiMa5DijvPaRGA07mNbY3r
RT1MECH-88-002 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | Applicable for all MPS Skid Delta CRAHs: The T Sensors in the submittal, if the intend of these is to sense the chilled water return and chilled water supply temperature, then these sensor were found not to be thermowells but to touch the copper pipes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636083&prj=657&rqi=AVwwzcRu60ebgMiaVCGmmFEcV6
RT1MECH-88-004 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | For 1CRAH-ER-13: As per review of drawing M405 and on site configuration it was noted that the CRAH labeled 1CRAH_ER_13 is mislabeled as 1CRAH_ER_12. This impacts the following: -BAPI10 - incoming and outcoming EMT labels -wire labels for CB1 and CB2 and main ground. -CRAH Label itself | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636190&prj=657&rqi=YNu1KT7BAo3br3OphKczPjBOCd
RT1MECH-88-005 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | Common for all MPS Skid CRAHs: The safety labels on the CRAH electrical panels need to be in English and French for Skid ESA inspections to pass. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636208&prj=657&rqi=T4UI6gQ9YoeCd6GFHntmyH12CU
RT1MECH-87-004 | TR06-3 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Terminal block labels deviate from the shop drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636162&prj=657&rqi=9pqtMGzoHXWiFmJodHfeHSOcFW
RT1MECH-87-008 | TR06-3 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Construction dust and FOD found inside high-voltage electrical section and on top of the unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636168&prj=657&rqi=ZhG6izroI9AMJtIIUMrVQI1249
RT1MECH-87-007 | TR06-3 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Upon review of submittal OFCI-12 Section 2.1.2.2 Single Line Diagram -it was noted the following fuses have FA Fuses, which deviate from the shop drawing. F3 4Amp fuses found instead of the specified 10Amps F5 10A fuse found instead of a 3Amp fuse. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636167&prj=657&rqi=piyJS8MW1Xq83JwVtl2bh8AvEc
RT1MECH-87-002 | TR06-3 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Ferrule connectors are exposed for terminal 1.1, 1.2, 2.1, 2.2 on component QUINT CAP 4KJ. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636159&prj=657&rqi=SjDcSLaRZXWU7zcdmemKVsVUH8
RT1MECH-87-003 | TR06-3 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | CB1 and CB2 are loosely mounted, there is significant play in the breakers upon inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636161&prj=657&rqi=5LZqnc44uHd4dy7GnoQ5lzm4ci
RT1MECH-87-001 | TR06-3 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Damage cooling coil observed upon inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636158&prj=657&rqi=zq2QsMJXlXj8vjpF1TSIQ74mGa
RT1MECH-37-008 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-08-21 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: Housekeeping PAD has one corner broken. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634620&prj=657&rqi=002OIxXXt8GCjD5DSqp28laMit
GI-093 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDP_B_1 | UDP - UPS Output Switchboard |  |  | UDP_B_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634543&prj=657&rqi=e95AoXzlXuty4UsT6dLHHsNQaP
GI-097 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  | no | SPD bus in section 01C missing cover. Hazard to operators is currently present with exposed busbars | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634547&prj=657&rqi=bexrgi99a973pnYcCmyFMc2twU
GI-099 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1BATT_B_1_1 | LIBATT - UPS Battery |  |  | TB3 1-3 from the BIBR to battery cabinets (MCCB Status) has not been completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634549&prj=657&rqi=VXSiPnnSW3lZQEC1VjLJfmQIYt
GI-095 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDPR_B_1 | UDP - UPS Output Switchboard |  |  | UDPR_B_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634545&prj=657&rqi=7Z5b3YFTUZU4zbgpuxB0Gf42nX
GI-100 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | At UPS_B_1 & UPS_B_2 (XVLDC 21-24) the UPS Charge Limit wiring has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634551&prj=657&rqi=dHJz6ygHtiHSI7gHe6oOQsRSSV
GI-098 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  | no | UPS_B_1_LBB & UPS_B_2_LBB status contacts were not wired to a terminal block to be monitored by the UPS. Three spare EF contacts exist at each breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634548&prj=657&rqi=EKvpZigbKO3A00ZIGojQtXMCX8
GI-096 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDPR_B_2 | UDP - UPS Output Switchboard |  |  | UDPR_B_2 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634546&prj=657&rqi=9Uwn3idj3bMlGO6bKNQnQOypEA
GI-094 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDP_B_2 | UDP - UPS Output Switchboard |  |  | UDP_B_2 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634544&prj=657&rqi=31cjvtsuEcA2QKzski5Jj5dPHJ
GI-092 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-08-07 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | FWT | Factory Witness Test | [6 empty] | Skid D: 1UDP_B_1 and 1UDP_C_1 on the TR6-3 project. The current configuration does not provide sufficient space in the front lug holes to achieve the required wire bend radius, causing the lug to press against the insulator. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632770&prj=657&rqi=EwL1iRJ93uDPFiJlg61XrCD7RL
GI-091 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-28 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Common to all chillers: Model # of the Onicon Flow meter does not match the cut sheet on the submittal. The one received on site Model # is FT-3400-200-1C31 Vs the Submittal which mentions F-3500 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631082&prj=657&rqi=0dQ1HkSaqcSD1vRz69Xdx8GuJg
GI-090 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-28 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Applicable to three Chillers as of now: The Air Vent on the Air Separator was found to be able to rotate by a push. The connection need to be inspected. See on below chillers. (video available on request) 1CH-A-2 1CH-B-2 1CH-B-1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631076&prj=657&rqi=WJJqUhGIniQ2Kt2D8eZ2C0yDIg
RT1MECH-38-016 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-E-1: The FU2 fuse holder label needs to be rectified on the submittal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630898&prj=657&rqi=BclsyaOVGdq0gMAmCAQMLTx6ZJ
RT1MECH-38-015 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | Applicable to TR6-3 Chiller Submittal: On the panel drawing for the pump, the transformer in the panel layout is shown as 460 to 120 V, in the electrical single line drawings it is shown 460 to 24 V and the wiring on site is also as per 460 to 24V. The panel layout drawing needs to be corrected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630895&prj=657&rqi=iINfKa6vw9Iq3yn5b3aJkKnEHc
RT1MECH-38-014 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-E-1, pump skid electrical panel: As per the drawings FU-5 is 8 A fuses but we found 5A fuses installed downstream of 5L1 and 5L2. (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630889&prj=657&rqi=Kw6CiuMVoXYsBMYXoXVtSlHJkE
RT1MECH-38-018 | TR06-3 | AMER | Closed | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-E-1: Missing outdoor air sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630926&prj=657&rqi=D1YD52kgGt2o6zlMimZRLV7Lvg
RT1MECH-38-020 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to TR6-3 chiller submittal: For the MG2 module on the chiller condenser, the drawing shows the termination at P1- and P1 + terminals. The actual terminations on site are on P2- and P2 + terminals. These two terminals are not shown on the drawing. The drawings needs to be updated to match the site installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630932&prj=657&rqi=QzBRH5m5Bc8NcswkI6zlw8S1xl
RT1MECH-38-019 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CU-E-1: The fins are bent on the condenser on the roof. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630930&prj=657&rqi=NUAD6ah7CFUDs9puTy1gG7gR3u
RT1MECH-38-017 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to TR6-3 Chiller Submittal: Missing Cutsheets for the following components: 1.) Evaporator Liquid Level Sensor 2.) Smardt Lift VFD Module 3.) Expansion Valve 4.) Freeze Protection Bypass Valve (BRAY) 5.) Temperature transducers 6.) Pressure transducers 7.)Evaporator Barrel cutsheet provided is a general cutsheet does not provide a model number specific to TR6-3 project. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630899&prj=657&rqi=k5zNS8I0D2wxXaXUDLd20nkPWh
RT1MECH-38-021 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment type |  | ACC - Chiller â€“ Air Cooled |  |  | Common for all chillers: CBTB1 - fusible terminal blocks FU-SIA1 through FU-SIA8 do not denote fuse size. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630934&prj=657&rqi=p986YHt8WMtKvjM7Xj13zNa8IA
RT1MECH-38-013 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-24 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | Applicable to 1CH-E-1 and 1CH-D-1: The model number of the two isolation control valves at the bottom side does not match the cutsheet. Refer to the attached pictures. The Model Number mentioned on the cutsheet is PKRBUP-MFT-T and these two valves the model number is PKXUP-3-T | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630756&prj=657&rqi=IvzwESRvWGN63whBm7u1Q1S1vp
RT1MECH-38-012 | TR06-3 | AMER | Closed | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-24 04:00:00.000 +0400 | SMT - SMARDT | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to 1CH-D-1 & 1CH-E-1: Missing the onicon flow meter on the pump skid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630741&prj=657&rqi=ervw8TqNzWQtR2psKXoH3smmEq
RT1MECH-38-011 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-24 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | Applicable to new chillers 1CH-E-1 and 1CH-D-1: The model number of the freeze protection bypass value does not match the model number of the freeze protection bypass valve installed in the TR6-2 phase. As compared to TR6-2 bypass valve (800 In Lbs.) the torque value is less on the TR6-3 chiller bypass valve (600 In Lbs.) The SMRARDT submittal for TR6-3 phase does not include the cutsheet of the BRAY valve. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630718&prj=657&rqi=A4uRdETCiIdP378txn6OyqG1Uj
RT1MECH-37-007 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-24 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: The conduit connection in the splitter panel entering panel L3 enclosure side is loose and not properly torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630779&prj=657&rqi=mdllxCHMkxrHFALnq0QidUxc9Y
RT1MECH-37-006 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-24 04:00:00.000 +0400 | SMT - SMARDT | L2A | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: ABB breaker SACE Tmax XT4H 250 in L2 enclosure is not resetting, and stuck in the tripped position, preventing door from closing and requires inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630777&prj=657&rqi=ypiVwFXI8P2CcMWf847vrDSSbG
RT1MECH-37-004 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: Seals / Ports missing on the below location on the chiller. - Pump skid and Chiller connection. - Evaporator two ports - Air Separator bottom drain port. Concerns of FOD /Rust . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630604&prj=657&rqi=SS7lgbhUQRF7DP8JUUdIUQvDRj
GI-089 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Applicable to 1CH-E-1 and 1CH-D-1: The location of the flow switch was changed in last phase from its original location (close to the evaporator) to a location on the pump skid. But the new chillers on site still has the flow switch installed close to the evaporator. (Reference picture attached) (Also Refer Issue # 1109 on TR6-2 Facility Grid) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630661&prj=657&rqi=3XRDE96WkGyxyMkc27YGd1AQr2
RT1MECH-38-009 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to 1CH-E-1 & 1-CH-D-1: (As of now these two chillers are on site) The model number of the main disconnect of the chiller does not match the model number mentioned on the submittal. On the submittal the selection is highlighted on Model # OT600U03 and the model # noted on the onsite chiller main disconnect is OT800U03. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630586&prj=657&rqi=EHAix1S1H5nRgHhieB7MzcnyZN
RT1MECH-38-010 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-E-1: Seals / Ports missing on the below location on the chiller. - Pump skid and Chiller connection. - Evaporator two ports - Air Separator bottom drain port. Concerns of FOD /Rust . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630602&prj=657&rqi=cwZagZF13MbivvbXaVXfLEEcvZ
RT1MECH-37-003 | TR06-3 | AMER | Ready for Verification | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | SMT - SMARDT | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: Power Entry Label is incorrect. Shows 480 V but this is a 120V panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630595&prj=657&rqi=5IS2SY8plQI7v3Ait55020mDk0
RT1MECH-37-005 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CHWP-D-1: The chilled water pump electrical panel door is jammed and does not open all the way. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630606&prj=657&rqi=K4O6z1YCZ2v8fyU5yw3kqrv7zv
RT1MECH-38-008 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to the 1CH-E-1 & 1-CH-D-1: (At this point inspection is done only on the chillers received on site) As per the EOR comments on the Pump Skid submittal the fittings on the pump skid connecting to the building chilled water header is supposed to be Victaulic. The fitting seen on the these two chillers is not Victaulic. (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630579&prj=657&rqi=J4LZNrclIIHafBUqeL96UHY0QM
GI-088 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-22 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  | no | Insulation boards are missing at Sections 6 and 10, a recurring issue previously observed on Skid C. An email has been sent to AMG requesting immediate action before MPS closes the back panels; we are awaiting their response. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630459&prj=657&rqi=4k0HUIi7aKxuMyAGgjIrdX4r7K
GI-087 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-22 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  | no | Insulation boards are missing at Sections 6 and 10, a recurring issue previously observed on Skid C. An email has been sent to AMG requesting immediate action before MPS closes the back panels; we are awaiting their response. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630458&prj=657&rqi=iJ5oNaRydPEvIax52gceDR3esB
RT1MECH-38-006 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-E-1: The Equipment label does not match the label on the submittal. The submittal mentions two part numbers one on the main header page and one has a detailed name plate. The header matches the name plate model number on the chiller (Refer to the attached picture) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630201&prj=657&rqi=bR3ZUnpX8HZzfOs9N9DXnDbWcR
RT1MECH-38-005 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to all chillers part of TR6-3 Phase: In order to resolve the ongoing chiller compressor fault on low ambient temperature (Refer to Issue # 1113 from TR6-2 phase) the three discharge isolation valves were to be wired such that they can be controlled individually to open / close from the Kiltech controller. Referring to the new submittal for TR6-3 phase it looks like this correction has not been made. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630198&prj=657&rqi=M9LGVeYPHOzBKNo9x5ZNPEGs3h
RT1MECH-37-001 | TR06-3 | AMER | Ready for Verification | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH_D_1: The pump skid CHWR piping are not aligned, and needs adjustment so that the pump skid can be connected to the chiller. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630177&prj=657&rqi=92I7xgAv9w8TMG6RkQ778NDri4
RT1MECH-38-004 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | Applicable to 1CH-E-1 & 1CH-D-1: Power Entry # 3 drawing on the submittal does not match the panel on site. (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630195&prj=657&rqi=HHtJjZrK5YPi4Av2AMY9Avd27d
RT1MECH-38-007 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - BMS | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to all Chillers : We noticed that the phase monitoring relay is not present in the Compressor panel # 2 as seen on the TR6-2 phase chillers. Upon review of the new submittal for TR6-3 we noted that the phase loss relay is not shown on the single line diagram of the compressor # 2 panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630212&prj=657&rqi=7Kl1dC63it6SB2Qflv0396dBnH
RT1MECH-37-002 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: The Equipment label does not match the label on the submittal. The submittal mentions two part numbers one on the main header page and one has a detailed name plate. (Refer to the attached picture) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630208&prj=657&rqi=bvUnO7hyoWuteP6N8kaFZ3aoa8
RT1MECH-38-001 | TR06-3 | AMER | Ready for Verification | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH_E_1: The pump skid CHWR piping are not aligned, and needs adjustment so that the pump skid can be connected to the chiller. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630178&prj=657&rqi=kYHAHJhBXBIKs8TybSBG3bSm9k
GI-086 | TR06-3 | AMER | Ready for Verification | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Applicable to all Chillers: Issue is for tracking purpose. Smardt to confirm the chiller proof of flow logic and confirm if its as per Equinix standards. (Also tracked on the on going email chain. screenshot attached) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630332&prj=657&rqi=FyVmo1YZVIdwgkqPYCVGeFu1Z7
RT1MECH-38-002 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - BMS | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to all chillers part of TR6-3 phase: The Equinix PLC Control panel is missing on the chiller. On the TR6-2 phase chillers this control panel came from SMARDT Factory with the chiller LCP installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630181&prj=657&rqi=WpufvDpoQ2KFgIX0LAIB4CRgZt
RT1MECH-38-003 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | Applicable to 1CH-E-1 & 1CH-D-1: Power Entry # 3 Panel: As per the Submittal Pg # (13 of 48), the circuit diagram shows one LED or light but the panel on site does not have any LED or Light. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630194&prj=657&rqi=kBe56DdTk9T16lXKq6j9b3ss2O
GI-083 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | For B Skid: Applicable to the control power section of UDP - B1 and UDP -B2: The section should have a protective plastic cover and caution label since a 460 V input is landed in this section. " | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629750&prj=657&rqi=fV1KVm0gPztDdkQGPpMG06Ax1L
GI-082 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | "For D Skid: Applicable to the control power section of UDP - D1 and UDP -D2: The section should have a protective plastic cover and caution label since a 460 V input is landed in this section. " | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629749&prj=657&rqi=zt3jBsH1x57gAv1QZBjqLubNge
GI-081 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | "For C Skid: Applicable to the control power section of UDP - C1 and UDP -C2: The section should have a protective plastic cover and caution label since a 460 V input is landed in this section. " | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629748&prj=657&rqi=2MnoxdygnlWv5wGFcPqYwpIOEv
GI-084 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1UDPR_E_2 | UDP - UPS Output Switchboard |  |  | "Applicable to 1UDPR-E2: The location of the sub feed breaker 5 does not match the location shown on the submittal. (refer to the attached pictures)" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629758&prj=657&rqi=1Lreszmv8CZopbFR8UE5ixAC7P
GI-080 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  | no | For MPS Skid C - Section 06C: Edge guarding for controls cables is missing on the edges as seen on other skids (Highlighted in the attached picture) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629745&prj=657&rqi=Fmktm4uexlqh2Oj2ow7uAeboNV
GI-085 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | Applicable to the all the MPS Skid Equipment: Below lamcoids are needed: - MSB labels for the breaker as mentioned in the MSB submittal. - Fed from labels for all equipment - CRAH - WSHP - UPS - UDPR (subfeed breaker # as well) - Battery cabinets - STS (Some pictures attached for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629766&prj=657&rqi=9p1ne08hiSPv84hBtK6Cza0fho
GI-079 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UDP_C_2 | UDP - UPS Output Switchboard |  |  | For 1UDP-C2: The sub feed breaker # 5, micrologic module is missing is the protective plastic cover which is seen on the dials. (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629743&prj=657&rqi=1r4h03hCJ0xBBoTndsC8oS3xYl
GI-070 | TR06-3 | AMER | Ready for Verification | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1BTU_RMU_D | BTU - Battery Tripping unit |  |  | For MPS Skid D: The BTU rough in work is not completed. As per discussion during the Factory visit on 15th July, it was decided that will be done by MPS before shipping the skid. (Reference pictures attached from E skid) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629478&prj=657&rqi=frMBIaOqm5YTQlVG88fglnAtZT
GI-072 | TR06-3 | AMER | Ready for Verification | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1BTU_RMU_B | BTU - Battery Tripping unit |  |  | For MPS Skid B: The BTU rough in work is not completed. As per discussion during the Factory visit on 15th July, it was decided that will be done by MPS before shipping the skid. (Reference pictures attached from E skid) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629480&prj=657&rqi=ZCgkUL2YLN3isQm1kS473YBtKx
GI-069 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1BTU_RMU_E | BTU - Battery Tripping unit |  |  | For MPS Skid E: The BTU rough in work inside the MPS Skid is not completed. As per discussion during the Factory visit on 15th July, it was decided that will be done by MPS before shipping the skid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629477&prj=657&rqi=kBuIWzkWkmtEJ9IoFYVtnFOPUW
GI-075 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | For MPS Skid C: The CSA / UL Label is currently not present on the Skid Label. (Per discussion on site this will be once the Skid is at TR6 site) (Issue is added for tracking purpose) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629483&prj=657&rqi=xoHP35ujQWGWifEg9iUMP56P9o
GI-074 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | For MPS Skid D: The CSA / UL Label is currently not present on the Skid Label. (Per discussion on site this will be once the Skid is at TR6 site) (Issue is added for tracking purpose) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629482&prj=657&rqi=VhPO0OYW07lF3wx0srKakK5S73
GI-078 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1UDPR_C_2 | UDP - UPS Output Switchboard |  |  | Applicable to 1UDPR-C2: The location of the sub feed breaker 5 does not match the location shown on the submittal. (refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629490&prj=657&rqi=NZVoENnLx3e2Usy4KBSiCRkxWx
GI-071 | TR06-3 | AMER | Ready for Verification | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1BTU_RMU_C | BTU - Battery Tripping unit |  |  | For MPS Skid C: The BTU rough in work is not completed. As per discussion during the Factory visit on 15th July, it was decided that will be done by MPS before shipping the skid. (Reference pictures attached from E skid) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629479&prj=657&rqi=wIUQkQSpP0Rk071ZHxnkWQ9dTR
GI-076 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | For MPS Skid B: The CSA / UL Label is currently not present on the Skid Label. (Per discussion on site this will be once the Skid is at TR6 site) (Issue is added for tracking purpose) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629484&prj=657&rqi=xd4CQSWAliZppiXx8yqxkjQOmB
GI-073 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | For MPS Skid E: The CSA / UL Label is currently not present on the Skid Label. (Per discussion on site this will be once the Skid is at TR6 site) (Issue is added for tracking purpose) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629481&prj=657&rqi=czv8MyROVHlsz9ZyMKAJvqti9f
GI-077 | TR06-3 | AMER | Closed | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDP_D_1 | UDP - UPS Output Switchboard |  |  | Applicable to 1UDP-D-1: As per the submittal the breaker should be LSI, but the sub feed breakers 1,2,3 and 4 installed in this UDP are with micrologic 6.0A (with ground fault) trip units. (Picture attached for one sub feed breaker for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629488&prj=657&rqi=UKOm9o3sG9wrftO7IdrTEpbiTr
GI-057 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | Metallic debris falling into the breaker and busbar compartments. This hazard must be mitigated while drilling and installing the conduit assembly at Section 03A and other Sections. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629272&prj=657&rqi=19PM1yOnCGJUetKEr2R28ucSW2
GI-065 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDPR_E_1 | UDP - UPS Output Switchboard |  |  | UDPR-E-1 &2 : Incorrect LSIG tripping units have been used for 800A LSI breakers in both UDPR-E 1 & 2. Need correction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629283&prj=657&rqi=uMhFE89BddDuIvbMug9HtStYSi
GI-061 | TR06-3 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | Breaker 12B - 1600A LSI breaker is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629278&prj=657&rqi=h2S5ybLqwWT9fAryYZWoeh7XQg
GI-068 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | For E Skid: Applicable to the control power section of UDP - E1 and UDP -E2: The section should have a protective plastic cover and caution label since a 460 V input is landed in this section. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629327&prj=657&rqi=TocjU3v87rhypB5hQLZyF56voS
GI-067 | TR06-3 | AMER | Ready for Verification | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | For MPS Skid E: The CRAH labelling in the skid does not match the labelling provided on the mechanical schedule. On the mechanical skid its 1CRAH-ER-11, 1CRAH-ER-12 and 1CRAH-ER-13. Inside the skid the CRAH labelling is 1CRAH-ER-10, 1CRAH-11 and 1CRAH-12 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629325&prj=657&rqi=CLQkGGDJorIJDBCV2Z7rwAi7jL
GI-058 | TR06-3 | AMER | Closed | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  | no | For Skid C: Missing Kirk Keys on the MSB C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629273&prj=657&rqi=QMxJ475dtMNOGkBiDotI1U4rEQ
GI-060 | TR06-3 | AMER | Open | P3 Low CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | Section 08C - Missing mimic lines | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629276&prj=657&rqi=vDialdNroWHJWko8QIHkaQz4Nl
GI-056 | TR06-3 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | All Skids : K-Kirk devices are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629219&prj=657&rqi=J77RjouoVrSV0KuvSCqUOV7aLe
GI-063 | TR06-3 | AMER | Ready for Verification | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | MSB back cover bolts were not tightened. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629280&prj=657&rqi=F0xD4belhngQ6B5aQBrh7Y69iq
GI-062 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  | no | For MSB C: Noted during Spilt Inspection at MPS Factory: The Mimic representation is missing on the areas highlighted in the attached pictures. This is where a plate is installed by AMG for the ERMS switch . (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629274&prj=657&rqi=iXzTASJRaRFMi2vVT1yrTdC9Dr
GI-059 | TR06-3 | AMER | Open | P3 Low CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | -Sections 07 & 10 UPS Instructions SOO need to update with correct equipment ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629275&prj=657&rqi=JdaBUuNadv0vQVtbUJrG6R9e27
GI-066 | TR06-3 | AMER | Ready for Verification | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_E_3 | EF - Exhaust Fan |  |  | For MPS Skid E, applicable to the Exhaust fan control panel; The auto / Run selector switch is not labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629315&prj=657&rqi=S2pfa9urktCAq86ZB4DXzODrBl
GI-064 | TR06-3 | AMER | Ready for Verification | P3 Low CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | MSB LV panel: Missing circuit directories | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629282&prj=657&rqi=SZaftbWHJdQNlCs0YZU68fSOGS
GI-055 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-12 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Applicable to 7 Harmonic Filters: During the receiving inspection, it was noted that the harmonic filters on site do not match the Motor Size (HP/kW) parameter mentioned on the submittal | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628779&prj=657&rqi=faLQ1TAdHcy8UJGGksTjtIC2Sp
GI-054 | TR06-3 | AMER | Ready for Verification | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | TR6-3 submittal: It looks like the HMI terminals were not shown correctly on the MSB side. I updated the names in the yellow cells. Some of the MSB terminals were not shown correctly for breaker, on gen and on static bypass signals. The corrections are in the yellow highlights. The LBB breaker statuses I could not find in the Anord submittal. Did MPS find this or make an assumption? The items highlighted in blue may have to be added by Anord. The maintenance bypass breaker status is not something that MPS wires. These are installed by Anord internal to the gear. Therefore those cells in red should be removed. Assuming these are the standard Vertiv battery cabinets, these should have the 480V control power to the receptacles and SO cords above the battery cabinets. If this has not yet been discussed with Equinix, please discuss to add in MPS scope. This will also need to corrected in the orange cells. Missing some of the battery controls, which I did not add to the spreadsheet. MPS will wire the major/minor alarm (TB1158) from the BIBR to the top hat terminal block in Cabinet 1 [already shown in spreadsheets but missing detail of point to point shown below]. TB1158 #1 (Critical Alarm COM) = Maj Alarm COM TB1158 #2 (Critical Alarm NC) = Maj Alarm NO [Note Samsung and Vertiv NO and NC terminology are inverted] TB1158 #3 (Critical Alarm NO) = Maj Alarm NC [Note Samsung and Vertiv NO and NC terminology are inverted] TB1158 #4 (Maint Alarm COM) = Min Alarm COM TB1158 #5 (Maint Alarm NC) = Min Alarm NO [Note Samsung and Vertiv NO and NC terminology are inverted) TB1158 #6 (Maint Alarm NO) = Min Alarm NC [Note Samsung and Vertiv NO and NC terminology are inverted) MPS will wire the trip (TB4) field wires from the BIBR to the top hat terminal block in Cabinet 1 [not shown in spreadsheets]. TB4-1 - Ground TB4-3 - Input MPS will wire the Vertiv dry contact wire harness from the battery cabinet module to the top hat in Cabinet 1. MPS will wire the MCCB (breaker status) field wires from the BIBR TB3 to cabinet #1 (2 wires) and cabinet #7 (1 wire). Leave the wires coiled up in front of the battery breaker. MPS will leave the MCCB (breaker status) Vertiv wire harness coiled up in front of the battery breaker. Vertiv will make the connections between the MCCB wire harnesses between cabinets and the TB3 field wires. This is at least what we agreed with the DC21 Vertiv team. Will need to confirm with the TR6 Vertiv team. Perhaps Veolia can assist. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627698&prj=657&rqi=BezjJa7GcxRqeaeszyKK3SU5S8
GI-050 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Design correction needed | Design | [6 empty] | MSB (General) - There is nothing in the submittal that indicates where barriers are to be installed. Is there a drawing that can be provided? In light of the issue above and issues at other sites, we request Anord verify all barriers needed are installed. In particular, we noticed that in Section 6 & Section 11, we don't have barriers on any MSB above the UPS output (IOB). This is the only cable termination section that doesn't have a barrier below. Is this intentional by design? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627693&prj=657&rqi=UN4PSjVwSUedjgYxtfM6ee9FKI
GI-053 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | [6 empty] | UDP/UPR (note that only saw the "E" block) - 800A Breaker lugs appear to only be capable for cables up to 500MCM. Per the site design and the breaker schedule attached, the lugs should be able to accomodate up to 600MCM. Anord to confirm and replace lugs as required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627697&prj=657&rqi=k1YTd3hcUmbgqKjuEURrb4uErN
GI-051 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | [6 empty] | MSB (General) - Section 6 & Section 11 have the voltage present lights for the IOB breakers tapped on the "Critical Bus" output side of the IOB breaker. The voltage present lights by Equinix design should be tapped on the "UPS Output" (cable side) of the IOB breaker. Anord should move the voltage present taps to the same side of the IOB breaker as the PQM voltage sensing leads. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627694&prj=657&rqi=H1flE9XKVgn77hD8Np7cV59CPu
GI-052 | TR06-3 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | [6 empty] | UDP & UPDR were shipped with a random combination of 800A Micrologic 5.0A (without ground fault) and Micrologic 6.0A (with ground fault) trip units. Per Equinix standard, the submittals and the breaker schedule attached, all breakers should be 5.0A (without ground fault). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627696&prj=657&rqi=7A6CapUGkMCbXgT22DEqYUVBF1
RT1ELEC-404-001 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_D | MSB - Main Input Switchboard |  | no | MSB-D - Section 11 is missing the barrier that is installed in the same Section 11 on MSB-D on the critical bus section. Anord to install barrier in MSB-D assuming it is needed and to make consistent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627691&prj=657&rqi=kqGRm2ExL6rb8C9vTItOi8GToQ
RT1ELEC-405-001 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | MSB-E - Main PQM 5000A Phase C CT has a cut on the wire. Wire should be repaired. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627695&prj=657&rqi=7l8ApvMogQw5e7RwslVjpxJ5dm
GI-049 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-06-24 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1CH_E_1 PQF | HF - Harmonic Filter |  |  | For 1-CU-E-1: One condenser fan is clipped was found to be not connected to the fan guard. (Fan 1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626797&prj=657&rqi=M6ts7ewfIp9Yz58uMPafKpVRJL
GI-048 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-06-24 04:00:00.000 +0400 | SMT - SMARDT |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Common for all chiller condensers: Discrepancy in the condenser model number Vs model number noted on the condenser nameplate received on site. On the submittal the model number is "CA150.A020RA.010" On the nameplate of Condensers received on site the model number is "CA150.A020RA.F10" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626708&prj=657&rqi=t53B3jjPlerOhHYJr1nr3qHoIl
GI-025 | TR06-3 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Condenser skid unit: For all 7 units skid Refrigerant line holder too low, do not support refrigerant piping weight.(Pictures attached) After inspecting this for existing chiller condensers it was noted that this issue is also applicable to 1CU-A-1, 1CU-903B-1, 1CU-904-1, 1CU-R-1 and 1CU-R-2. (Pictures Attached) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625799&prj=657&rqi=EcQcnPLhJ8jpxBEFwbFtptaza6
GI-030 | TR06-3 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Component/ Equipment Failure | Commissioning |  | equipment type |  |  |  |  | condenser unit 4032, no tag: com wire out | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625821&prj=657&rqi=n2OWSvm5b3lGpHs8ucp0wgc8yx
GI-031 | TR06-3 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not correct | Commissioning | [6 empty] | unit 4430, 4433: exposed copper wire in disconnect | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625825&prj=657&rqi=xso5UuOjjWSiyMdaJ5CK0kPXTu
GI-029 | TR06-3 | AMER | Closed | P3 Low CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | for all condenser unit submittal drawing and unit don't match contactor showed 20 in drawing, only 10 in unit. Two fans connected to one contactor, vendor to notify if wiring valid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625820&prj=657&rqi=1KcIKA9CY1ssfbgxQGUqwxsBa4
GI-026 | TR06-3 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | condenser units: 2 units missing product tag/serial number | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625806&prj=657&rqi=3mZZiYaM8bvtuGkzZ0blaiz4Qx
GI-028 | TR06-3 | AMER | Open | P3 Low CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | condenser unit 4432, 4030, no tag missing book and spair gasket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625817&prj=657&rqi=u14B8NLm7pNoi66FHMcaQhzd9B
GI-027 | TR06-3 | AMER | Open | P3 Low CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Component/ Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Missing plug for fill in port in condenser | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625808&prj=657&rqi=5OWmtJapbaqNrHff25394c3MjR
GI-024 | TR06-3 | AMER | Closed | P2 Medium CX | vijay.singh@veolia.com | 2026-06-11 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | FWT | Factory Witness Test | [6 empty] | MSB-E: CTs 4 and 6 may be wired or labelled incorrectly. Phase A has wiring for CT6 and phase C has wiring for CT4. This is reversed from the submittals orientation: | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625010&prj=657&rqi=c2KyxEXkAwzZTbi934wJHmdkNu
GI-023 | TR06-3 | AMER | Closed | P3 Low CX | qubert.quintal@veolia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | Main Service entrance switchgear 1PUSP_1 & 2 sections are missing equipment identifiers/labels, e.g., Interrupter, Protective Relay, Power Quality Meter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623971&prj=657&rqi=HkdL7aocaeSxmoAVS1wACmth6I
GI-022 | TR06-3 | AMER | Closed | P3 Low CX | qubert.quintal@veolia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | Electrical Block A & R SKID: A few MSB_A breakers were mislabeled (incorrect spelling, incorrect label background color, font size), e.g., UPS_RIB_2, 1UPS-A-2-LBB, 1-CH-A-2, 1LBB_A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623969&prj=657&rqi=BPnNSYidxIbfMPl9n3EbLhQkuc
GI-021 | TR06-3 | AMER | Open | P3 Low CX | qubert.quintal@veolia.com | 2026-06-04 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Labelling | Commissioning | [6 empty] | The posted SOO procedures at the new MSBs is not correct. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623968&prj=657&rqi=uWKv4RfmCc4VzB8Z2pg7glse3W
GI-020 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Applicable to all the Chillers for TR6-3: It came up part of the GOE inspection that the chillers should include the lamacoid which also matches the name on the BMS along with the lamacoid as per schedule. The chiller panel are missing the labels mentioned on the BMS faceplate associated to the chiller. (refer to the attached picture)(We have used the TR6-2 chillers to demonstrate an example) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623796&prj=657&rqi=jXT51JV0SMcUcVHmFgkClaS22Z
GI-018 | TR06-3 | AMER | Closed | P2 Medium CX | jerome.deschenes@veolia.com | 2026-05-25 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not complete | Commissioning | [6 empty] | Chillers not completed for factory visit Piping cleaned up and joints Missing parts and tie ins for controls and compressors completed. Valves missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623052&prj=657&rqi=ghzIPaEl0oljAcGUDhNiz4EFon
GI-019 | TR06-3 | AMER | Open | P3 Low CX | jerome.deschenes@veolia.com | 2026-05-25 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning | [6 empty] | chillers submittal need to be provided with new updated drawing 57-0161, as new chillers differ in design from the existing one on Equinix Tr6 from project 2. Valves need to have individual tag and number. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623127&prj=657&rqi=MY8xspyg2z6Tuig4JO83ENtlXA
GI-017 | TR06-3 | AMER | Closed | P3 Low CX | jerome.deschenes@veolia.com | 2026-05-22 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning | [6 empty] | Torque report is required for all high voltage, with calibrated tools, date, value. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622831&prj=657&rqi=SaDw38HJdqyQ61K7Ipzr9RcBo4
RT1ELEC-128-001 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-04-23 04:00:00.000 +0400 | AMG - Anord Mardix Group | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_Z | MSB - Main Input Switchboard |  | no | Factory assembly is in progress. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619266&prj=657&rqi=PJjIBHNXBm8uhbj4uBO7fsAJXc
GI-016 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-04-23 04:00:00.000 +0400 | Consultant |  | General Design Issue | Design |  | equipment type |  |  |  |  | For MPS Skid CRAHs in TR6-2 Phase, issue was raised for missing strainers. Based on the discussion with Equinix Design / GOE team this was going to be captured in future designs. Creating issue to track this item or capture feedback on the requirement of strainer on skid crahs. (Refer to attached email chain in the document section of this issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619260&prj=657&rqi=mb22CjGlPdvGIiu2Xh0ECbJLEi
GI-015 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-03-02 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design | [6 empty] | Upon failure of the preferred source, the STS will transfer to the alternate source fed by System R. In the event of multiple UPS failures, the first primary block UPS load will transfer to System R via the STS. However, there is a risk of overloading System R if control signals are not sent to the other primary block STSs to engage a transfer inhibit function. This function is necessary to prevent those STSs from also transferring to the redundant block. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483425&prj=657&rqi=LPC2EmXSbcJgr7cCW6QodqOctk
GI-013 | TR06-3 | AMER | Closed | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-24 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design |  | equipment type |  |  |  |  | The Room # mentioned in the mechanical schedule (dwg # M702) for "B Block Mech UPS & Batt.Room 1613" does not match with room # mentioned for this room on the dwg # M131.F and dwg# A120.F, which is Room 1612.Â Same for D Block, in the mechanical schedule for "D Block Mech UPS & Batt.Room 1613", where as in rest of the drawings its 1614. (Refer to the attached pictures)Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204067&prj=657&rqi=8v7ur7bvIhSRZBdWTxc8XPwDim
GI-012 | TR06-3 | AMER | Closed | P3 Low CX | Ocean.Kwan@veolia.com | 2026-02-24 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design | [6 empty] | Electrical Single Line for Block B, C, D & E - E605 to E608 Logic detail of K-Key interlock betewwn equipment's to be provided. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199962&prj=657&rqi=bC8GHlumdLEVwzG2LRnQyBMciQ
CCD-L0-3-001 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-02-24 04:00:00.000 +0400 | Consultant | DELIVERABLES | Design correction needed | Design | [6 empty] | Electrical drawing E602 MV Single Line diagram has missed RMU shunt trip signal line to RMU protection relay from downstream transformers: - 1RMU_Z -1RMU_901/2 -1RMU_903R -1RMU_903A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199957&prj=657&rqi=XAXoWqs9eZlvfkzyTyZrqRKBY1
GI-011 | TR06-3 | AMER | Closed | P3 Low CX | Ocean.Kwan@veolia.com | 2026-02-24 04:00:00.000 +0400 | Consultant |  | General Design Issue | Design | [6 empty] | Electrical drawing E601 - The key interlock details for K32 and K31 to prevent parallel of two MV sources is not provided. The number of keys be avaliable and captured in the corresponding cylinder to be specified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199960&prj=657&rqi=SZDtBf9TamKoPPWFllRLGeDY8Z
GI-008 | TR06-3 | AMER | Closed | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-22 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design | Mechanical â€“Air | equipment | 1HP_B_03 | HP - Heat Pump |  |  | 1HP_A_01: The asset name has already used by the WSHP in Block R Electrical Skid. (Attaching screenshot from Mechanical Schedule dwg # M701) (Attaching screenshot from TR6-2 phase BMS screen for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199720&prj=657&rqi=N8GaPxl2VExyMGoEWDw9Py4OvO
GI-007 | TR06-3 | AMER | Ready for Verification | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Design correction needed | Design |  | equipment type |  |  |  |  | Referring to the Mechanical Schedule Dwg # M702 (Issue G1) (Issued on 5th Feb 2026) For the Electrical Skid CRAH's, the chilled water entering temperature specified is 70 deg F, whereas the Chiller Plant leaving water temperature for the building is 65 deg F. (Screenshot attached) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199719&prj=657&rqi=o0a9LtuWt9GhN5gqZCHB67Vq3S
GI-006 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-22 04:00:00.000 +0400 | SCH - Schneider Mech |  | Design correction needed | Design |  | equipment type |  |  |  |  | Referring to the Mechanical Schedule Dwg # M702 (Issue G1) (Issued on 5th Feb 2026) The DH 906 and DH 907, the leaving air temperature is shown 76 deg F. Comparing with the TR6-2, phase DH908 CRAH's, the leaving air temperature in schedule was 71 deg F. (Screenshot attached) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199718&prj=657&rqi=1IKLTVOAOB9u0gRzOq2ij6SdTO
GI-009 | TR06-3 | AMER | Closed | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-22 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design | Mechanical â€“Air | equipment | 1HP_R_03 | HP - Heat Pump |  |  | 1HP_R_01: The asset name has already used by the WSHP in Block R Electrical Skid. (Attaching screenshot from Mechanical Schedule dwg # M701) (Attaching screenshot from TR6-2 phase BMS screen for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199722&prj=657&rqi=MOjhjQxoeXS5xdR541YTy4RPa5
GI-010 | TR06-3 | AMER | Closed | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-22 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design | Mechanical â€“Air | equipment | 1HP_R_05 | HP - Heat Pump |  |  | 1HP_R_02: The asset name has already used by the WSHP in Block A Electrical Skid. (Attaching screenshot from Mechanical Schedule dwg # M701) (Attaching screenshot from TR6-2 phase BMS screen for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199723&prj=657&rqi=2gm3GFJ0h9qCijwNCaEvD0rVJd
GI-005 | TR06-3 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-02-21 04:00:00.000 +0400 | Consultant |  | Design not as specified | Design | Electrical â€“ LV | equipment | 1CH_B_1 PQF | HF - Harmonic Filter |  |  | ACCH have recuring issues regarding cold start-up when OAT not available to enable free-cooling. This generate fails to start alarm each time, requiring a service call and unavailability of a redundant chiller during fail period. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199715&prj=657&rqi=JDvTLG7JyJWqOpQW8ztdvNEoCM
GI-004 | TR06-3 | AMER | Closed | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-20 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design | Mechanical â€“ Water | equipment | 1TST_A_2 | TST - Thermal Storage Tank |  |  | For 1-CH-A-2, the associated thermal storage tank asset name is "1TST A-2". In the TR6-2, phase the asset name "1TST A-2" has been used by the Thermal storage tank associated with chiller 1-CH-903B-1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199703&prj=657&rqi=g9IhltElkyiVcY1GCgkjT8VAlv
GI-003 | TR06-3 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-02-18 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design | [6 empty] | Chilled water filtration missing from system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199463&prj=657&rqi=sRkLe1zMZcfmcvsSsGaHBwn39x
CCD-L0-2-001 | TR06-3 | AMER | Open | P3 Low CX | jerome.deschenes@veolia.com | 2026-02-18 04:00:00.000 +0400 | General Contractor - BMS | DELIVERABLES | Design correction needed | Design | [6 empty] | SOO is missing from specification package. A building standard operating sequence will provide clarity of how the system is designed to operate at day1, avoiding cost and changes during cx | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199471&prj=657&rqi=AI7MterMtZuj25M6F5JJO9m86O
GI-002 | TR06-3 | AMER | Closed | P2 Medium CX | jerome.deschenes@veolia.com | 2026-02-17 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design |  | equipment type |  |  |  |  | Outside air temperature for chillers are set at 102.4 F (39.1 C) Last year highest temperature was 36 C, on ground. Chiller capacity shall be selected at a 20 yrs extreme outside temperature, to allow for optimum capacity of remote condenser at peak summer month. Also , chiller remote condensers are now juxtaposed one to one in TR6-3 projects, creating a increased air temperature at condenser intake, plus roof air temperature. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199382&prj=657&rqi=u5Kpz5OpISlIChhPkg36WvrGgw
GI-006 | TY11-P3 | APAC | Closed | P3 Low CX | gerrydevera@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | UPS No. 6 IST On the BMS screen â€œPDU-U46-A1,B1,â€ the assignment for the common spare circuit breaker display for PDU-U46-B1-5C1 was incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626026&prj=649&rqi=wEwE8u84nlAjpAVQcDLLHphEpx
GI-005 | TY11-P3 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Commissioning Authority |  | Component/Equipment Failure | Commissioning | [6 empty] | During an in-house PDU switching test, the thyristor fuse (200A) blew. The cause was identified as the transformer's inrush current. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619208&prj=649&rqi=vKWaqs9fkhMGCeEc4Ov680xhzq
GI-004 | TY11-P3 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT-Elec-Lv2-The breaker labels are not attached to PDU distribution panels for Units 7 and 8. The breakers for PDU No. 1 to 6 also require verification. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618313&prj=649&rqi=dKILMgZTZDlCRfmVc9IDz0g6UH
GI-003 | TY11-P3 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT-Elec-Lv2-Load names (FED FROM) are not affixed to PDU power distribution panels Units 1 to 8. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618183&prj=649&rqi=R3JYV5CO4lmd2gziMEUBumWPf5
GI-002 | TY11-P3 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Installation not complete | Commissioning | [6 empty] | CxLv3-ELEC-UPS No.6-BMS communication test pending due to incomplete wiring from the relay terminal panel to BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199437&prj=649&rqi=irx1oJg0GFa5k4PSOCMEf7ybDU
GI-001 | TY11-P3 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-02-16 04:00:00.000 +0400 | Commissioning Authority |  | Installation Damage | Commissioning | [6 empty] | SAT-ELEC-Lv2-UPS No.6-The side part of output breaker 52P603 was found damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199327&prj=649&rqi=hDGoK0xNX9iQvOs0p6UMKeAbja
GI-018 | TY15-1 | APAC | Closed | P3 Low CX | JezkielDomingo@sygna-apac.com | 2026-04-06 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT: Mechanical L3 During the operation check of the CHW motor valve, condensation occurred on the CHW pipe near 2-1-SWIT-12-4 including the bypass pipeline. The room temperature at the time of the test was 26Â°C, the humidity was 71%, and the CHW supply temperature was 20Â°C. contact Takasago for the cause and solution. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=88453&prj=352&rqi=1qzvRCMnrkb7KZo1y1P3rxMpZH
GI-079 | TY15-2 | APAC | Open | P3 Low CX | MasafumiOkuno@commtechasia.com | 2026-08-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | B-IST No.2 (Generator Failure/Restoration Test) Because the procedures for restoring the generator and DPF system are complex, detailed instructions and sequences should be included in the user manual. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635023&prj=548&rqi=Z6PrLwif3o6QxvOssMeCkMP8X5
GI-082 | TY15-2 | APAC | Open | P3 Low CX | MasafumiOkuno@commtechasia.com | 2026-08-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | B-IST No.1 Regarding the timer setting for the black smoke removal system: although it is currently set to 20 seconds (with a maximum of 24 seconds), black smoke was observed being emitted for several minutes. Discussions are required to reconfigure the timer setting. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635037&prj=548&rqi=IsOORNoNhVpD324cnqHS1YXju3
GI-081 | TY15-2 | APAC | Closed | P3 Low CX | MasafumiOkuno@commtechasia.com | 2026-08-25 04:00:00.000 +0400 | Commissioning Authority |  | improper settings | DCOS | [6 empty] | B-IST No.5 The relationship between the UHV-B power output of 0 kW and the TRB secondary-side power of 107 kW; the reason for measuring power at the TR secondary side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635036&prj=548&rqi=2W2NJScfKP9KXjiheZvOr6oS8n
GI-080 | TY15-2 | APAC | Closed | P3 Low CX | MasafumiOkuno@commtechasia.com | 2026-08-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | B-IST No.1 (Power outage test) After the switch to GEN power, the four exhaust fans in generator rooms No. 6 and No. 7 (1-1-EF-12 18a, 1-1-EF-12 18b, 1-1-EF-12 19a, 1-1-EF-12 19b) were supposed to shut down, but they continued to operate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635030&prj=548&rqi=2NCIeygxhd3RdzltJClhiuaokV
GI-078 | TY15-2 | APAC | Open | P3 Low CX | MasafumiOkuno@commtechasia.com | 2026-08-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | B-IST No.1 After switching to GEN power, a communication error was reported for the following FCU. On-site, it was confirmed that the equipment continued to operate, and the alarm on the BMS automatically reset approximately 5 minutes later. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635015&prj=548&rqi=hB2eyN4wx5nlDgZ0W8Lz2lUzZV
GI-074 | TY15-2 | APAC | Closed | P3 Low CX | SabinBasnet@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | During MIST operation check on chiller (8-1-CH-12-1), it was confirmed that the solenoid valve on drain pipe on Mist panel-1 was broken which caused the flow of water into the drain as soon as the Mist system was started. Although the MIST Control check is done on all the mist systems from BMS side, the MIST system operation confirmation is yet to be checked on (8-1-CH-12-3) as the main breaker for MIST system had to be replaced and yet not replaced. so confirmation on valves and operation of (8-1-CH-12-3) mist is yet to be confirmed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623175&prj=548&rqi=hFBiW4sfpfvHlpZEL7yaCEN5HG
GI-073 | TY15-2 | APAC | Closed | P3 Low CX | SabinBasnet@commtechasia.com | 2026-05-26 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | During MIST operation check on chiller (8-1-CH-12-4) even when the run command was issued on auto mode from BMS side the Mist pump on controller-1 didnot start up causing up a congestionor breakge alarm on BMS side and the MIST-2 started instead. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623092&prj=548&rqi=2qa2padLUvTTqoiNO2v8rH4xRk
GI-072 | TY15-2 | APAC | Closed | P2 Medium CX | SabinBasnet@commtechasia.com | 2026-05-25 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Mist System on Chiller) [NTTF/Carrel - 8-1-CH-1, 8-1-CH-2, 8-1-CH-3 &8-1-CH-4) - Cx3] During Mist operation check on chillers(8-1-CH-1, 8-1-CH-2, 8-1-CH-3 &8-1-CH-4) alarm signal was being received on BMS side for an instant only whenever mist operation was started. Due to which the mist pump was stopping soon afterwards. therefore the mist control operation couldnot be confirmed on time. (refer to issue GI-066) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623022&prj=548&rqi=mMeGi9wcyvQMDl0VjcXfzhl3FC
GI-071 | TY15-2 | APAC | Closed | P3 Low CX | SabinBasnet@commtechasia.com | 2026-05-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | During Mist operation check on chillers, the nozzle head on the sprinklers pipe of mist system of 8-1-CH-12-12 got blown away while the mist system was on operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623017&prj=548&rqi=PXlWCyfAdquN3GDbqTG8RGGnqm
GI-068 | TY15-2 | APAC | Closed | P3 Low DCOS | SabinBasnet@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | During UPS No.5 IST Test6, during the STS automatic switching test, on the BMS side both the primary and redundant side sources were shown as supplying the output for 7-1-STS-12-U5-2-1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622605&prj=548&rqi=ts35aGEdXM4kC9hgqKhlkZgi1C
GI-069 | TY15-2 | APAC | Closed | P3 Low CX | SabinBasnet@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | During UPS No.5 IST (Test9: Fire system test) while deactivating the central fire system control the BMS side control was also disabled mistakely so the fire alarm did not show up on BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622607&prj=548&rqi=gk3JdfrgIr7jj0PBj0G7wb0EzE
GI-066 | TY15-2 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT-Chiller system-regarding the mist system (æ•£æ°´) , NTT-F plans to interchange the Solenoid Valves and Low Switches location on all chillers due to recurring alarms. However, parts must be ordered from Italy (unavailable in Japan), causing procurement delays. They admit this may push completion beyond the end-March deadline, despite their efforts. Requested action: They must submit a report detailing their exact plan and schedule immediately. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615793&prj=548&rqi=QWaPahtU8yoTkpnGw8ux7h7ch8
GI-064 | TY15-2 | APAC | Closed | P3 Low DCOS | SabinBasnet@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | During STS load test, Analog values did not match during communication between the STS and BMS. During testing, when switching communication mapping between the old and new addresses, the old address was considered even when the new address was correct. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614686&prj=548&rqi=T2jayzeCNUtNMqjpzUEOXQLCrh
GI-063 | TY15-2 | APAC | Closed | P3 Low DCOS | SabinBasnet@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | During the alarm verification on STS, the General Alarm on the BMS screen for the STS ((5-1-STS-12-U5-2-2) was not showing up even though the alarm was produced on the equipment side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483414&prj=548&rqi=Ve5q9yVNEAQh0ptxl7B3wSRE8x
GI-062 | TY15-2 | APAC | Closed | P3 Low DCOS | SabinBasnet@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | BMS Graphics Errors: 1.On the Generator (No. 3, 4) BMS screen, the [Synchronizing] setting for DEG No. 4 was not set. The point during synchronization verification was selected incorrectly, so the [Synchronization] indicator did not light up. 2. On the Generator (No. 5, 6) Gen No. 5 screen, [Manual] was displayed even though the mode was automatic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204136&prj=548&rqi=zG3458MOXlQvMyssZUOZzEXGtr
GI-060 | TY15-2 | APAC | Closed | P3 Low CX | SabinBasnet@commtechasia.com | 2026-02-02 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | On the display panel of generator circuit breaker board (1-1GSB-GCBP-4) & (1-1GSB-GCBP-5) of DEG no. 4 &5, the output voltage and current to theã€€DEG control panel (1-1-GSB-CP-4&5) through transformer was displayed as zero although the output on the control panel display was okay. The same problem might be there on other DEG system as well so it is necessary to check the previously commissioned DEG No. 1, 2&3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198089&prj=548&rqi=70B14sNVaqimFkca9Tp2Yp36m7
GI-125 | ZH04-6 | N-EMEA | Open | P3 Low CX | agryszko@global-cxm.com | 2026-09-04 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Permament label with ID name missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636842&prj=555&rqi=ymrylmQopyMQGDh5GvdJqGY37u
GI-124 | ZH04-6 | N-EMEA | Open | P3 Low CX | agryszko@global-cxm.com | 2026-09-04 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Permament label with ID name missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636841&prj=555&rqi=Xk61HkvdpUCXpLPIbqZvUPbwyL
FPT-98-001 | ZH04-6 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Multi-Discipline | system | Migration A |  |  |  | potential issue during switching A5. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636759&prj=555&rqi=uVJYDoGYQlY2AiMzFa19P2CjI3 | https://equinix.facilitygrid.co.uk/x/project/555/system/14760
GI-123 | ZH04-6 | N-EMEA | Open | P3 Low CX | gmcdonough@global-cxm.com | 2026-09-03 04:00:00.000 +0400 | General Contractor |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | During the power failure test, when the alternative power supply was open the alarm info on Vertiv control side stats fire alarm in steady alternative power supply open. Seems like an addressing issue, potentially related to the software upgrade? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636683&prj=555&rqi=AXGjCu9BMmnncwJ7CObSa0LbR8
GI-122 | ZH04-6 | N-EMEA | Open | P3 Low CX | gmcdonough@global-cxm.com | 2026-09-03 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | All test conducted on CRAH-03-13 and only the fan failure test failed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636680&prj=555&rqi=O2AgCqosyOonZ05cR5iTXVxUYf
FPT-98-002 | ZH04-6 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Multi-Discipline | system | Migration A |  |  |  | fuse blown on A2 during switch to put IT load on batteries | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636761&prj=555&rqi=6QxWkl4BmRyJv5YiDfMeSlxpFk | https://equinix.facilitygrid.co.uk/x/project/555/system/14760
GI-121 | ZH04-6 | N-EMEA | Open | P1 High CX | agryszko@global-cxm.com | 2026-08-27 04:00:00.000 +0400 | Equinix Project Manager |  | Component/Equipment Failure | Commissioning | [6 empty] | During RMU testing GEN tripped on overcurrent without any load on it, during investigation, burned spots on Step-up transformer were identified. Equipment on that connection is being investigated by Siemens/Schneider/Avesco, The asset will be updated as soon the root cause of the issue is identified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635579&prj=555&rqi=7zhWMKfD4KIInU3rEfG673j0VC
GI-120 | ZH04-6 | N-EMEA | Open | P2 Medium CX | gmcdonough@global-cxm.com | 2026-08-25 04:00:00.000 +0400 | General Contractor |  | Incomplete Connections | Commissioning |  | equipment type |  |  |  |  | Shielding cable on the CRAH DB not completely sleeved from cable to earth bar. This is an issue on EVERY ground floor CRAH, not on one or 2 but on all. Hardly any ferrules attached to the sleeving either to the earth bar, again need to be rectified before powered on. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635034&prj=555&rqi=ZB1DhtmBJQi4DgorCHRCFFvPnH
GI-108 | ZH04-6 | N-EMEA | Closed | P2 Medium CX | agryszko@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | Trip Lockout not working properly for intertrip. Breaker opens properly, but operator is able to close it immediately, without clearing the lockout. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618823&prj=555&rqi=RUOus3VuMfVqBD0yrVYASwI35Y
GI-104 | ZH04-6 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-03-04 04:00:00.000 +0400 | General Contractor |  | Installation Not Correct | Commissioning | [6 empty] | Cable connections into the 3rd floor CRAH's Glands are lose as the cable is smaller than the gland size | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614684&prj=555&rqi=0IIatXMpiUSZPHcEcZLUzWfIBO
GI-106 | ZH04-6 | N-EMEA | Open | P2 Medium DCOS | Matt.Harker@eu.equinix.com | 2026-02-24 04:00:00.000 +0400 | Equinix Project Manager |  | Commissioning Issue | Commissioning | [6 empty] | Major incident occurred when Siemens attempted to upload additional pieces of Equipment to the live system: Extract of RCA issued by Siemens below: In calendar week 8, the PLC CPU (S7-400) had to be set to "Stop" mode for loading new components as part of project ZH4.6 (project ZH4.6 relevant). After the software download and the restart of the CPU, a MODBUS RTU communication string to several CRAHs could not be put back into operation (existing BMS relevant). This communication strand belongs to the investment part "legacy system" and comes from earlier projects. Siemens started the investigation in coordination with Mr. Milovan Kovacevic (email of 19.02.2026, 15:31). The aim was on the one hand to restart the aforementioned MODBUS RTU string and on the other hand to identify the cause of the fault (existing BMS relevant). In the course of the recommissioning of this mentioned string and the troubleshooting, a firmware update was prepared for the affected legacy part of the BMS. This update was planned for 02/24/2026 and related exclusively to the legacy part of the BMS. The installation of the FW update was carried out exclusively on the PLC level via Profibus (ZH4.6 no longer has Profibus but exclusively Profinet). Further details can be found in the document "Technical Root Cause Analysis Modbus RTU.pdf". Resolution to be added once finalised. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616273&prj=555&rqi=T9u5zPeix1wkBrsJzyn3H9i1ik
GI-100 | ZH04-6 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-02-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Design not as Specified | Design | Fuel | system | Fuel System |  |  |  | In the Fuel system SOO, the day tanks have 5 different Fuel level sensor and values. However, on site only 3 sensors are in the tanks. Clarification needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199659&prj=555&rqi=xXi8qmbJbNlN5kWaIxE8aX9hWX | https://equinix.facilitygrid.co.uk/x/project/555/system/13439