## Issues_FG_2026202609181035_Manu
issue_code | project_name | region | issue_status | priority | reported_by | reported_on | responsibility_name | cx_level | issue_type | issue_category | discipline | asset_type | asset_name | equipment_type_name | manufacturer | model_number | description | issue_url | system_url
GI-017 | AM04-P3 | N-EMEA | Ready for Verification | P2 Medium CX | bjorn.ketelaar@eu.equinix.com | 2026-07-02 04:00:00.000 +0400 | Vendor- Manufacturer |  | Installation Damage | Commissioning | [6 empty] | GSCP has sustained transport damage not clear if internal components are operational, Cummins to verify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627803&prj=620&rqi=aBrXNBoghBbHOaSrXsZdwOOXSo
GI-011 | AM04-P3 | N-EMEA | Closed | Outstanding Paperwork/Documentation | Willem.Zwaagstra@eu.equinix.com | 2026-06-03 04:00:00.000 +0400 | Vendor- Manufacturer |  | General Design Issue | Design | [6 empty] | Following site observations, Equinix would like to clarify the specification and compliance, particularly for the flange connections used in the cooling water piping. It appears that some of the flanges may have been fabricated, rather than standard manufactured flanges. As this system is part of a pressurized installation, we need to confirm that all installed components comply with the relevant pressure equipment standards. Additionally, based on observations in a previous project phase (AM4.P2), similar flange connections in comparable positions also appeared relatively light compared to the mating equipment flanges. However, in the current AM4.P3 installation, this difference appears more pronounced, with visibly thinner flanges being applied. Could you please confirm: - Which standards these flanges are designed and manufactured to (e.g. EN / ASME, pressure class / PN rating, DN designation); - That the flanges are suitable for the operating pressure and conditions of the system; - Whether the required markings (including DN, pressure class, and material/specification) are applied or otherwise traceable. This information is required to ensure compliance and to verify that the installation is suitable for safe and reliable long-term operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623916&prj=620&rqi=3pzDgs6466Xa1OL817WsUKnqGM
GI-007 | AM04-P3 | N-EMEA | Work Completed | P2 Medium CX | christiaan.Gillot@se.com | 2026-04-30 04:00:00.000 +0400 | Vendor- Manufacturer |  | Commissioning Issue | Commissioning | [6 empty] | extra terminals for supply loop XM144 XM145 k205 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620034&prj=620&rqi=FZp9RvBvAuGHC2yMHj8nTEknkL
GI-019 | AT10x-1 | AMER | Open | P3 Low CX | christopher_boyle@fsttechnical.com | 2026-06-30 04:00:00.000 +0400 | VER - Vertiv |  | Installation not complete | Commissioning | [6 empty] | Containment bonding missing throughout Ehouses sparaticly. Please see attached examples of missing bonding throughout multiple Ehouses. Once all bonding is complete please coordinate a walk with Vertiv and FST to verify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627617&prj=601&rqi=8TJWsEZMECQTkXIXGLYCyM9COB
GI-007 | AT10x-1 | AMER | Closed | P3 Low CX | christopher_boyle@fsttechnical.com | 2026-06-29 04:00:00.000 +0400 | Electrical Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | 1GEN Torque report document issues please see attached red lined report. Affected reports -1GEN_R3 -1GEN_P -1GEN_Q -1GEN_S -1GEN_U -1GEN_V -1GEN_R4 -1GEN_W -1GEN_AA -1GEN_BB -1GEN_CC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627257&prj=601&rqi=p7jog07iHJZbFk5lSjkN2YE59m
SOR-57-001 | AT10x-1 | AMER | Open | P3 Low CX | eric_reinhard@fsttechnical.com | 2026-06-11 04:00:00.000 +0400 | Fire Contractor |  | Installation not correct | Commissioning | [6 empty] | Fire Pump Fuel Tank. Fuel line is called out in drawing #FP401-FPH, Detail 10 to have a "1/2 CL BLK nipple and electronically supervised ball valve or potter rbvs tamper switch". Inspection of the tank found that there is not a tamper switch installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635681&prj=601&rqi=NFCQ25n3QEoGZ7JgOu1bYPVbiu
GI-016 | AT10x-1 | AMER | Closed | P3 Low CX | christopher_boyle@fsttechnical.com | 2026-06-10 04:00:00.000 +0400 | VER - Vertiv |  | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MPZ_R2_1 | PP - Power Panel |  |  | ground cables not labeled inside asset or at earth bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624795&prj=601&rqi=8MiRDSct8eFIqyDlwAZiGCzPWo
GI-012 | AT10x-1 | AMER | Closed | P3 Low CX | christopher_boyle@fsttechnical.com | 2026-06-10 04:00:00.000 +0400 | VER - Vertiv |  | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MPZ_L_2 | PP - Power Panel |  |  | Ground cables not labeled inside asset and not labeled at earth bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624782&prj=601&rqi=pSHQ0ayKBOaznhGIfoMlv3jRb2
GI-011 | AT10x-1 | AMER | Closed | P2 Medium CX | christopher_boyle@fsttechnical.com | 2026-06-10 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MPZ_L_2 | PP - Power Panel |  |  | loose strands and broken strand in terminal on main circuit breaker to transformer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624781&prj=601&rqi=DlaU61ferzdWsyP3trM25HGzML
RT1ELEC-2341-001 | AT10x-1 | AMER | Closed | P2 Medium CX | joseph_donnelly@fsttechnical.com | 2026-06-09 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MPZ_L_2 | PP - Power Panel |  |  | cable strands damaged/exposed on main breaker tx side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624593&prj=601&rqi=0j9C1Sd5twW9FwEWrgJu3BiAmH
RT1ELEC-2341-002 | AT10x-1 | AMER | Closed | P3 Low CX | joseph_donnelly@fsttechnical.com | 2026-06-09 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MPZ_L_2 | PP - Power Panel |  |  | latch on door damaged/loose. Will not hold open. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624594&prj=601&rqi=AbAWBqV8E3Mhzkxar6Dc5FZ4mp
RT1ELEC-2341-003 | AT10x-1 | AMER | Closed | P2 Medium CX | joseph_donnelly@fsttechnical.com | 2026-06-09 04:00:00.000 +0400 | Electrical Contractor | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1MPZ_L_2 | PP - Power Panel |  |  | Extension toe for neutral connection to terminal block loose. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624614&prj=601&rqi=JFmwfPYdro72YwlwdntRDXpuVq
GI-005 | AT10x-1 | AMER | Closed | P2 Medium CX | eric_reinhard@fsttechnical.com | 2026-06-02 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | [6 empty] | The underground electrical duct terminations with pulled cable should be provided with temporary closure per spec 26 0543.3.5.I. "Sealing: Provide temporary closure at terminations of duct with pulled cables. Seal spare duct at terminations. Use sealing compound and plugs to withstand at least 15-psig hydrostatic pressure" This should be corrected site wide. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623708&prj=601&rqi=S6VL6UZGOVOBjLiLZXikiSUVOx
GI-004 | AT10x-1 | AMER | Closed | P2 Medium CX | eric_reinhard@fsttechnical.com | 2026-05-26 04:00:00.000 +0400 | VER - Vertiv Electrical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Per Equinix, opening issue for tracking purposes given the following concerns brought up in E-house permitting & Fire Protection meeting on 5/26/26: â€¢ Vertiv to share the Industrial Building Permit documents, and confirm the status of approvals and inspections. o Stamped EoR drawings showing final installation to be confirmed o Once shared, Northstar will coordinate this with the fire marshall | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623166&prj=601&rqi=7NzLdLQPWiqT2uCoDumjpBByMA
RT1ELEC-2374-001 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-22 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1MPZ_AA_2 | PP - Power Panel |  |  | One of the leads heading to the transformer (480v) is not landed correctly, one half of the wire strains were in the breaker and it pulled right out. The other two leads are done very poorly.. The leaving leads (120v) coming from the transformer also have a lot of stray strains. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622810&prj=601&rqi=1SysS1dl84QFHbmBZP50S7qrNV
GI-002 | AT10x-1 | AMER | Closed | P3 Low CX | eric_reinhard@fsttechnical.com | 2026-05-20 04:00:00.000 +0400 | Commissioning Authority |  | CxA Miss | Commissioning | [6 empty] | Facility Grid Training Session - Test Issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622424&prj=601&rqi=OFJSTS1daPh1XtkJM1nJSehzF2
RT1ELEC-2380-001 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-20 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MPZ_CC_2 | PP - Power Panel |  |  | This panel is missing 2 covers, the main dead front to protect the breaker area and the other smaller dead front that protects the 90amp breaker feeding the transformer above. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622478&prj=601&rqi=iq8BJgVCVy0ka726uZbqnHa8yh
GI-001 | AT10x-1 | AMER | Closed | P2 Medium CX | eric_reinhard@fsttechnical.com | 2026-05-14 04:00:00.000 +0400 | General Contractor |  | CxA Miss | Commissioning | [6 empty] | marvair units sitting on pad are not wrapped and are exposed to dust. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621915&prj=601&rqi=jPF86tRf2h7wm0QnC8Gik3z8uZ
RT1ELEC-2365-002 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-12 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MPZ_W_2 | PP - Power Panel |  |  | Missing project required double torque marks on the neutral wire landed on the neutral bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621432&prj=601&rqi=5L7Y82LCKnY47IcfX09MU2HrbQ
RT1ELEC-2365-001 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-12 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MPZ_W_2 | PP - Power Panel |  |  | The transformer wires coming down into the breaker and frayed and wire strands are not secured in the block | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621431&prj=601&rqi=MoWRsHE4kwVyZVH7GHuKJTdld3
RT1ELEC-2383-001 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MPZ_R3_1 | PP - Power Panel |  |  | Missing double torque marks on the transformer line coming down into the lower panel. See attached picture | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620571&prj=601&rqi=ylWGlMR83ZBWefB3Bienln98tS
RT1ELEC-2359-001 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MPZ_U_2 | PP - Power Panel |  |  | This unit is missing the dead front in the panel section of the unit. It is not anywhere in the room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620595&prj=601&rqi=qQs9kTUdVSbJaIeJFqI97iB8Zd
RT1ELEC-2359-002 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MPZ_U_2 | PP - Power Panel |  |  | The small bare ground is not landed on the ground bus | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620596&prj=601&rqi=VBADmdUFGqovRfjwxytTKVEzWP
RT1ELEC-2353-001 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MPZ_S_2 | PP - Power Panel |  |  | Missing the the double torque marks on the 3 transfer leads coming down to the breaker and on the 1 Neutral line heading to the neutral bus bar. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620592&prj=601&rqi=uYmVmvktsa7tOzoFDr8MEHzJlu
RT1ELEC-2350-001 | AT10x-1 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MPZ_Q_2 | PP - Power Panel |  |  | Missing double torque marks on on the neutral line coming from the transformer landed on the neutral bus, see attached picture. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620590&prj=601&rqi=647O2PX71fiGflc6eo2kGOysym
BKT1ELEC-9-006 | AT10x-1 | AMER | Closed | P3 Low CX | Rangsiya_Faihin@fsttechnical.com | 2026-04-16 04:00:00.000 +0400 | VER - Vertiv Electrical | L1 | Installation Damage | Commissioning |  | equipment type |  |  |  |  | MSB_AMCOP Panel has not been received. In the delivery inspection that was submitted by Cleveland repetitive identify that a panel has been missing, and Vertiv is aware that all units is missing a panel, they stated that it will be installed at a later date. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618412&prj=601&rqi=cfuf328UYrP5LZehLsOL7WSRm2
SOR-14-001 | AT10x-1 | AMER | Closed | P3 Low CX | eric_reinhard@fsttechnical.com | 2026-03-30 04:00:00.000 +0400 | Fire Suppression Contractor |  | Installation not correct | Commissioning | [6 empty] | FST inspected one of the Dry Pipe Sprinkler Valve assemblies in Area C and found that the downstream isolation valve w/ tamper switch was not installed. The double-interlock Dry Pipe Valve is identified in detail #2 and #5, located on drawing [FP500-AT10x]. See attached images of details. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616879&prj=601&rqi=VKK8PkZH0oVHvhQ2ChMhBvIUsM
YT1MECH-150-002 | CH05-2 | AMER | Closed | P2 Medium CX | benjamin.mei@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Design not as specified | Design | HVAC | equipment | 1WSHP_D_1 | HP - Heat Pump |  |  | Common to all WSHPs, breaker size off panel are 20A breakers which is correct per equipment submittal and panel schedule. Nameplate on units call for 15A breakers. Submittal for Phase 2 also lists for carrier as manufacturer not trane. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629145&prj=638&rqi=wLQGV7Zyfplv4aXVF3ae53Sh30
GT1MECH-125-001 | CH05-2 | AMER | Closed | P2 Medium CX | marcello.scalise@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Missing Components | Commissioning | HVAC | equipment | 1WSHP_F_2 | HP - Heat Pump |  |  | (1WSHP_F2) On/off switch is missing lockout bracket that is present on D skid WSHPs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628597&prj=638&rqi=ZMKm5AqcV9PMesNlSjQi4SDzbU
GT1MECH-124-001 | CH05-2 | AMER | Closed | P2 Medium CX | marcello.scalise@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Missing Components | Commissioning | HVAC | equipment | 1WSHP_F_1 | HP - Heat Pump |  |  | (1WSHP_F1) On/off switch is missing lockout bracket that is present on D skid WSHPs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628596&prj=638&rqi=cWY2EfhPIHPmMhkdnGM9WxoGmz
GT1MECH-122-001 | CH05-2 | AMER | Closed | P2 Medium CX | marcello.scalise@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Missing Components | Commissioning | HVAC | equipment | 1WSHP_E_1 | HP - Heat Pump |  |  | (1WSHP_E1) On/off switch is missing lockout bracket that is present on D skid WSHPs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628594&prj=638&rqi=XVX4niKQ99fdQXdkfuPskW1zfE
GT1MECH-123-001 | CH05-2 | AMER | Closed | P2 Medium CX | marcello.scalise@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Missing Components | Commissioning | HVAC | equipment | 1WSHP_E_2 | HP - Heat Pump |  |  | (1WSHP_E2) On/off switch is missing lockout bracket that is present on D skid WSHPs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628595&prj=638&rqi=cLnJuncCiEwRb7nEz5iKEUhmWK
YT1MECH-155-002 | CH05-2 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | HVAC | equipment | 1WSHP_F_2 | HP - Heat Pump |  |  | (1WSHP_F_2) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624767&prj=638&rqi=xoKkiTzs0701LirDkzAubIpMTg
YT1MECH-152-001 | CH05-2 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | HVAC | equipment | 1WSHP_E_1 | HP - Heat Pump |  |  | (1WSHP_E_1) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624761&prj=638&rqi=gzNwg5qrftOxDH5yGrBuZuigyI
YT1MECH-154-001 | CH05-2 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | HVAC | equipment | 1WSHP_F_1 | HP - Heat Pump |  |  | (1WSHP_F_1) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624765&prj=638&rqi=qBN2C1IxsUcAbf6IBBrOrY2teP
YT1MECH-153-001 | CH05-2 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | HVAC | equipment | 1WSHP_E_2 | HP - Heat Pump |  |  | (1WSHP_E_2) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624763&prj=638&rqi=P4sHiqjkq28GJ9IMXOHWrY5RXH
YT1MECH-150-001 | CH05-2 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | HVAC | equipment | 1WSHP_D_1 | HP - Heat Pump |  |  | (1WSHP_D_1) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624758&prj=638&rqi=0HAwTy4mbdsJuOyUkVzUSV3ETJ
YT1MECH-151-001 | CH05-2 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | HVAC | equipment | 1WSHP_D_2 | HP - Heat Pump |  |  | (1WSHP_D_2) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624760&prj=638&rqi=Y2nmwzTy2MLWbkQJeAVqn1JIin
RT1MECH-148-001 | CH05-2 | AMER | Open | P3 Low CX | benjamin.mei@veolia.com | 2026-06-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/Required | Commissioning | Mechanical â€“Air | equipment | 1EF_D_1 | EF - Exhaust Fan |  |  | Common to all SKID EFs - Factory Quality Control document has not been received. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623977&prj=638&rqi=BTYz4yBBnu2G5OQhJPVnJkIeFd
YT1MECH-155-001 | CH05-2 | AMER | Closed | P2 Medium CX | benjamin.mei@veolia.com | 2026-06-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Torque Required | Commissioning | HVAC | equipment | 1WSHP_F_2 | HP - Heat Pump |  |  | Common to all WSHPs, there are no factory torque marks on any connections. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623962&prj=638&rqi=LHST0qu9xYUSKyrGJXrfYYSqAu
CCD-L2B-2-001 | CH05-2 | AMER | Closed | P2 Medium CX | ian.tsurumoto@veolia.com | 2026-04-29 04:00:00.000 +0400 | Design Professional | DELIVERABLES | Documentation not issued/Required | Commissioning |  | equipment type |  |  |  |  | STANTEC has not issued a final (SCCS) short circuit coordination study | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619954&prj=638&rqi=kLJg0AEmJiTreZe4kua2hquHw4
RT1ELEC-500-001 | CH05-2 | AMER | Closed | P3 Low CX | karina.leonard@veolia.com | 2026-04-16 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_D_2 | LIBATT - UPS Battery |  |  | (1BATT_D2_2) 1BATT_D2_2 door handle is not secured. The bolt that attaches the locking mechanism to the handle is missing. Door doesnâ€™t stay shut.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618386&prj=638&rqi=lUJo3nHYJTN9CWWF1QYDJCTvtp
GI-016 | CH05-2 | AMER | Closed | P3 Low CX | zachary.riddle@veolia.com | 2026-03-18 04:00:00.000 +0400 | Owner |  | General Design Issue | Design | [6 empty] | PDU Similar for all equipment. Provided hardware for PDU input cable connections is insufficient to complete proper connections. Higher grade hardware was used with approval from Equinix. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616004&prj=638&rqi=fQ5P3grtzJhjV6c8ppHSXPityD
RT1MECH-153-001 | CH05-2 | AMER | Closed | P3 Low CX | mcoday@etechgroup.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | HVAC | equipment | 1WSHP_E_1 | HP - Heat Pump |  |  | There are not CAT6 cables between the Trane WSHPâ€™s and the E Skid DMARK in each skid â€“ (6) total. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199786&prj=638&rqi=NUXH7EEFzrPvZkb1SqDTaOh4ua
GI-013 | CH05-2 | AMER | Closed | P3 Low CX | mcoday@etechgroup.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | There are not CAT6 cables between the Delta BATT3 and the E Skid DMARK in each skid â€“ (3) total. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199785&prj=638&rqi=BUUWMxNy7NfZQ53AdcVTDtig8a
GI-012 | CH05-2 | AMER | Closed | P3 Low CX | mcoday@etechgroup.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Each Delta CRAH remote temperature sensor is not mounted, and cable not ran to the associated UPS in each skid â€“ (6) total. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199783&prj=638&rqi=vPDhR2yGWwuhP5bJ6dJQVVf4vB
GI-017 | CH08x-1 | AMER | Closed | P3 Low CX | dayele@equinix.com | 2026-08-06 04:00:00.000 +0400 | Electrical Contractor |  | FWT Issue | Commissioning | [6 empty] | The local temperature control setpoints configured on the Marvair ACUs do not match the individual unit control setpoints specified by Equinix. This discrepancy may result in unintended or non-standard cooling unit operation during communications loss conditions, as the units may not stage and operate in accordance with the intended control sequence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632648&prj=677&rqi=dMBlZCLyql4tHDXlys5YlXG75X
GI-014 | CH08x-1 | AMER | Ready for Verification | P1 High CX | dayele@equinix.com | 2026-08-06 04:00:00.000 +0400 | Electrical Contractor |  | FWT Issue | Commissioning | [6 empty] | During functional testing, activation of the fire alarm signal resulted in a UPS battery alarm being generated at the UPS system. Investigation indicates that the VESDA fire alarm signal and the UPS battery alarm signal are both terminated on the same input terminal of the MPC10 PLC. As a result, activation of the fire alarm signal backfeeds the UPS battery alarm circuit, causing an unintended battery alarm condition at the UPSs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632632&prj=677&rqi=22oKQXeaqUQfVAquaJSgur7YAU
GI-018 | CH08x-1 | AMER | Closed | P3 Low CX | dayele@equinix.com | 2026-08-06 04:00:00.000 +0400 | Electrical Contractor |  | FWT Issue | Commissioning | [6 empty] | The Marvair ACUs are currently configured to control cooling based on their individual return air temperature sensors rather than the E-House temperature sensors as specified in the design. This configuration does not align with the intended control strategy and may result in non-uniform cooling operation within the E-House. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632652&prj=677&rqi=xRSfEmFoBnrVuTJMSVRWq52dE4
GI-015 | CH08x-1 | AMER | Ready for Verification | P1 High CX | dayele@equinix.com | 2026-08-06 04:00:00.000 +0400 | Electrical Contractor |  | FWT Issue | Commissioning | [6 empty] | The E-House contains three UPS systems and their associated battery cabinets. During testing, activation of a battery alarm from any battery cabinet caused all three UPSs to generate battery alarms. The expected operation is for a battery alarm to be reported only by the UPS associated with the battery cabinet experiencing the alarm condition. CECCo's investigation determined that the battery cabinet alarm input signal to the UPS and the outgoing alarm signal to the Marvair PLC are connected at the same point, allowing the alarm signal to propagate across all UPS systems and generate unintended battery alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632640&prj=677&rqi=m9elw8VNc8V6Q5cpMhSCZb8Gko
GI-016 | CH08x-1 | AMER | Ready for Verification | P3 Low CX | dayele@equinix.com | 2026-08-06 04:00:00.000 +0400 | Electrical Contractor |  | FWT Issue | Commissioning | [6 empty] | The outside air intake openings on the Marvair ACUs are fully exposed to the environment and do not include protective hoods or weather protection. This configuration may allow rainwater ingress into the units during adverse weather conditions, potentially impacting equipment reliability and operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632647&prj=677&rqi=7erZPk0qROzgHscWprhVikJVuK
GI-006 | CH08x-1 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-29 04:00:00.000 +0400 | DEL - Delta Elec |  | FWT Issue | Commissioning |  | equipment type |  |  |  |  | FWT an out of phase alarm triggered | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619906&prj=677&rqi=ZYuLjD8P3cIJPp6DHI4ceD2C62
GI-007 | CH08x-1 | AMER | Closed | P1 High CX | rtyler@equinix.com | 2026-04-29 04:00:00.000 +0400 | Equinix Design Engineer |  | FWT Issue | Commissioning |  | equipment type |  |  |  |  | Logic Controller was not initiating source seek, upon S2 (GEN) supply failure whilst Load was supported by S2 (GEN) and S1 (UTILITY) was already available. Issue found during FWT for logic controller. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619907&prj=677&rqi=LN3GefxjpWxmaYPf3FdsDqSGJb
GI-003 | CH08x-1 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | FWT Issue | Commissioning | [6 empty] | Upon normal S2 > S1 re-transfer (UTILITY RESTORE), as that is manually initiated by the operator, existing delays were insufficient for operator to step away from being in front of the panel. Issue found during FWT Logic Controller Testing. Equinix added a 10s walkaway timer. Delay mitigates risk of arc flash event affecting the operator. The requirement for the operator to step away at a safe distance from the panel board needs to be covered in the SOP. It should be noted that this delay is not present if fail to open/close or trip alarm are being acknowledged. SOP for those activities should require for the operator to disable the ATC first (ATC MODE = DISABLED or MAN) prior acknowledging any latched-on alarms inhibiting transfer/re-transfer sequences. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619597&prj=677&rqi=UCbOGdPRRMMLAOFRB6YL8JSMWx
GI-004 | CH08x-1 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | FWT Issue | Commissioning |  | equipment type |  |  |  |  | Upon normal S2 > S1 re-transfer (UTILITY RESTORE), as that is manually initiated by the operator, existing delays were insufficient for operator to step away from being in front of the panel. Issue found during FWT Logic Controller Testing. Equinix added a 10s walkaway timer. Delay mitigates risk of arc flash event affecting the operator. The requirement for the operator to step away at a safe distance from the panel board needs to be covered in the SOP. It should be noted that this delay is not present if fail to open/close or trip alarm are being acknowledged. SOP for those activities should require for the operator to disable the ATC first (ATC MODE = DISABLED or MAN) prior acknowledging any latched-on alarms inhibiting transfer/re-transfer sequences. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619623&prj=677&rqi=zedm9Jkncjfa8E5OMNIwBjckjH
GI-002 | CH08x-1 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | FWT Issue | Commissioning |  | equipment type |  |  |  |  | Internal buss needs to have more phase stickers applied to more easily identify buss to prevent confusion when working on the buss. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619594&prj=677&rqi=ZaNZHGHaywM3ARdQnULd2H86Tz
GI-001 | CH08x-1 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | FWT Issue | Commissioning |  | equipment type |  |  |  |  | Equinix advised Hanley to separate the RELT and source lamp on/off circuits. In addition, the naming convention for the DC# breakers need to be updated per new circuits. Hanley to verify sources are correct throughout the shop drawings especially for the source for the door mounts. (See attached marked drawings) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619571&prj=677&rqi=SP5xKQTYgtaLPfM3VjucpcoZFV
GI-005 | CH08x-1 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | FWT Issue | Commissioning |  | equipment type |  |  |  |  | Controller was opening UMB or GMB if trip was issued by either breaker as the Service Disconnect state was intended to isolate both S1 and S2. Issue found during FWT Logic Controller testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619624&prj=677&rqi=qtL5zlslHUlahzp5KDll7Gi3WH
GI-078 | CN01-2 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | Arc flash covers interrupt the Communication cable need to be prepare dressing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622627&prj=664&rqi=TZ2DVpxnyMHSFvoPd5Jivg2RvJ
GI-062 | CN01-2 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | BMU Filter to be provided at Back door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622120&prj=664&rqi=OwgAoKrIKhugTwxTQAp42mhC90
GI-050 | CN01-2 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | In module V welded bottom sheet overlaps to foundation holes need to be corrected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622105&prj=664&rqi=sYXiDFZyTPvghbjN375diXtwDh
GI-041 | CN01-2 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | Ronis key not available in the RMU during the FWT, So not able to check Ronis keys interlock ABB has to do perform demonstrate at the site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621944&prj=664&rqi=ihcadGkXPoDfeY3cfA7slcsRjw
GI-047 | CN01-2 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | The bolts provided at the cable clamp are too long. The bolt size should be reduced, as the clearance between the bolt and the earthing connection is very less | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621951&prj=664&rqi=rrxBEUm81mruixQS0ng1SCyBP7
GI-042 | CN01-2 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | Ronis key not available in the RMU during the FWT, So not able to check Ronis keys interlock ABB has to do perform demonstrate at the site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621945&prj=664&rqi=kbtsfq9XhYUR4d7jnn2JlttR8y
GI-048 | CN01-2 | APAC | Closed | P3 Low CX | sivakumar@abluae.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning | [6 empty] | Aluminium gland plate dimensions to be added in the GA drawing. The gland plate thickness is specified as 3 mm in the drawings; however, the actual observed thickness is 2.5 mm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621954&prj=664&rqi=FO45y86FASqDwMZCOtJWWqp38C
GI-043 | CN01-2 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | Ronis key not available in the RMU during the FWT, So not able to check Ronis keys interlock ABB has to do perform demonstrate at the site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621946&prj=664&rqi=0faxx4wvQSxJTQ8cpQKhcx7nfU
GI-200 | DA11-4 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-08-28 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [6 empty] | Door to Electrical Room N is not latching shut. Pulls open freely. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635929&prj=614&rqi=sIx2Tc0i1VB3bIJHZBj5Mf8Wi4
GI-196 | DA11-4 | AMER | Ready for Verification | P3 Low DCOS | jonathan.wright@alphafacilities.com | 2026-08-26 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | [6 empty] | Ground bus EGB-T-4 contains Zinc and Stainless Steel fasteners. Dissimilar metals would likely cause electrolysis and have dissimilar torque values. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635310&prj=614&rqi=7UQQhL1NXnx6mDiirEKWjAJAVM
GI-199 | DA11-4 | AMER | Open | P3 Low CX | bramsay@critical2u.com | 2026-08-26 04:00:00.000 +0400 | Electrical Contractor |  | Cleaning | Commissioning | [6 empty] | T-Block room needs to be cleaned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635416&prj=614&rqi=EL0QPDUH6qWXtKP4ZPcMmnMknp
GI-195 | DA11-4 | AMER | Ready for Verification | P3 Low CX | jonathan.wright@alphafacilities.com | 2026-08-25 04:00:00.000 +0400 | Mechanical Contractor |  | Cleaning | Commissioning | [6 empty] | Listed ACUs contain Material (I.e. brackets, screws) & FOD (I.e. dust, debris, trash) and need to be cleaned: ACU-2-16 ACU-2-17 ACU-2-18 ACU-2-19 ACU-2-20 ACU-2-21 ACU-2-22 ACU-2-23 ACU-2-24 ACU-2-25 ACU-2-30 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635097&prj=614&rqi=Uay2zGz59ZBzUE2w18RzgmunII
FPT-430-002 | DA11-4 | AMER | Closed | P2 Medium CX | pnavarro@critical2u.com | 2026-07-30 04:00:00.000 +0400 | Controls Contractor | L4 | DCIM BCM Issue | DCIM | Electrical â€“ MV | equipment | Existing GEN-4A | Existing Generators |  |  | Gen 4A is not communicating with BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631450&prj=614&rqi=zo1Awjz6ojdtqRqAZx6BtB0Le6
FPT-430-001 | DA11-4 | AMER | Ready for Verification | P2 Medium CX | pnavarro@critical2u.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Component/Equipment Failure | Commissioning | Electrical â€“ MV | equipment | Existing GEN-4A | Existing Generators |  |  | Frequency recovery time do not meet the iso 8528 standards. See attached screenshots of readings and standard. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631330&prj=614&rqi=mmyHzBfGKWTfA6otxvLQXKyNK7
GI-172 | DA11-4 | AMER | Ready for Verification | P3 Low CX | shuyck@morleymoss.com | 2026-07-14 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | DP-GEN-3 | DP-Distribution Panel |  |  | DP-GEN-3 is to have (2) Kirk keyed main breakers that are 800AF/600AT per W-Block SLD sheet E-601.20W but the panel currently has 600AF/600AT main breakers installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629262&prj=614&rqi=QjltQVQDD8SkNFLVRj3G4eshRz
GI-142 | DA11-4 | AMER | Closed | P3 Low CX | cdavis@clunegc.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning | [6 empty] | In CH-14, the 12" condenser water connection to the heat exchanger has 1" difference. Please advise a solution. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623672&prj=614&rqi=aGdL3HOHLQYVFEBSs2aFQZymrv
GI-120 | DA11-4 | AMER | Open | P2 Medium CX | sadkins@critical2u.com | 2026-04-30 04:00:00.000 +0400 | Owner |  | General Design Issue | Design | [6 empty] | USP-A-1, B-1 and C-1 Settings need to be updated. : DA11-2 moved the building to the substation, SCCS was not done correctly to coordinate the move. With DA11-4 being the first to tie directly into the substation, after we got the settings from Oncor it was found that we were not coordinated. Then we worked with Oncor to establish the correct settings, which is what has been implemented into DA11-4. Oncor has since go back and adjusted their side of POD 1, the only remaining item is to have Schneider update our side of the POD 1 to match the functions and settings that were established for DA11-4. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620086&prj=614&rqi=RBY4WKtlYDqHUO80fNnU0iEliO
GI-073 | DA11-4 | AMER | Closed | P3 Low CX | mwarwick@morleymoss.com | 2026-03-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | Mechanical â€“Air | equipment | CRAH-1-47 | CRAH - Computer room air handler |  |  | Pre-installed VA cable is on the wrong terminal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618545&prj=614&rqi=X3DARyuyzEzKyr7kQl5njejFMp
GI-049 | DA11-4 | AMER | Closed | P3 Low CX | mwarwick@morleymoss.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  | equipment | MV Coms Panel Secondary |  |  |  | Cabinet arrived with shipping damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617269&prj=614&rqi=kSViMIWWHkMJnD1WYuKdVZ7W3G
GI-048 | DA11-4 | AMER | Closed | P3 Low CX | mwarwick@morleymoss.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  | equipment | MV Coms Panel Primary |  |  |  | Unit arrived with shipping damage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617268&prj=614&rqi=2iPMjomkj9ukeblOzMFZLLo7Me
L2L3 Sun-151-001 | DA12-1 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-07-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_BR1_2 | CRAH - Computer room air handler |  |  | Fan section - Upper door furthest RH side is misaligned and colliding against frame | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631081&prj=695&rqi=Y4gwuS2sqhUHQtjrkxndyW7xKK
L2L3 Sun-155-001 | DA12-1 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-07-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_BR1_4 | CRAH - Computer room air handler |  |  | ICDM Section - Top latch not aligned and cannot rotate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631083&prj=695&rqi=HACoZ9LFtxkJijicBIXVnsJt0w
L2L3 Sun-185-001 | DA12-1 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-07-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_AR1_4 | CRAH - Computer room air handler |  |  | Electrical Vestibule - Bottom most door latch cannot fully rotate to locked position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631079&prj=695&rqi=rTaYS2WxqqcMoVWNeUIf9QVTaL
L2L3 Sun-184-001 | DA12-1 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-07-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_AR1_3 | CRAH - Computer room air handler |  |  | Fan section - Upper door furthest RH side is misaligned and colliding against frame | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631077&prj=695&rqi=VvRuBh4EtT6Ajw7KzvrYyQNDey
L2L3 Sun-20-001 | DA12-1 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-07-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Labelling | Commissioning | Electrical â€“ MV | equipment | 1MVCB_Z | MVCB - Medium Voltage Circuit Breaker |  |  | Labels on both doors do not match wording from the submittal (page 73) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629267&prj=695&rqi=fLQnLQExS4qUtMg2xhGXE3amsk
GI-030 | DC17-1 | AMER | Open | P2 Medium CX | EMAHLER@ramboll.com | 2026-09-02 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [6 empty] | Communications EMT (Division 27) does not have insulating bushings (Per Division 26) to protect the conductors at terminations with EMT connectors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636535&prj=658&rqi=j4JCgOJmwMqpGH75yOfO4Z1WuL
GI-027 | DC17-1 | AMER | Open | P3 Low CX | SOGOTI@ramboll.com | 2026-08-28 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1RSSB_1 | RSSB - Reserve Spine Switchboard |  |  | Unit has damage to the metallic plate located on top of the unit, please refer to the attached photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635877&prj=658&rqi=i9xZt2kxpbSFdYlAhriN8ejpks
GI-029 | DC17-1 | AMER | Open | P2 Medium CX | Jshaffer@ramboll.com | 2026-08-28 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1RSSB_1 | RSSB - Reserve Spine Switchboard |  |  | K55 and K52 key are both broken off inside the cylinders | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635985&prj=658&rqi=TVYiI3JROMLoBox8UnLVkV5sWx
GI-028 | DC17-1 | AMER | Open | P3 Low CX | SOGOTI@ramboll.com | 2026-08-28 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1RSSB_2 | RSSB - Reserve Spine Switchboard |  |  | Arc flash label on the front panel of the unit is missing, please refer to the photo attached for referece | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635878&prj=658&rqi=3GY5p0s3lWcfhZdvGXiSmd8M32
GI-023 | DC17-1 | AMER | Open | P3 Low CX | jbeall@rosendin.com | 2026-07-31 04:00:00.000 +0400 | SYC â€“ Systecon |  | Component/ Equipment Failure | Commissioning | [6 empty] | SSB-R1 Chiller Breaker failed NETA testing - Long time would not trip | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631863&prj=658&rqi=7nPQc07UcbRjGZHK8aSAVwnJ4q
GI-024 | DC17-1 | AMER | Open | P3 Low CX | jbeall@rosendin.com | 2026-07-31 04:00:00.000 +0400 | SYC â€“ Systecon |  | Component/ Equipment Failure | Commissioning | [6 empty] | SSB-Q Chiller Breaker failed NETA testing - Would not trip on long time | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631868&prj=658&rqi=4RrTB6PlBMjhP6dec6KJFcaYHU
GI-020 | DC17-1 | AMER | Open | P2 Medium CX | gkuczler@rosendin.com | 2026-06-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | UMDSB Termination Points for UPS-3 RBB. Hanley confirmed UPS-3 RBB Points will be 5 & 7 at UMDSB for DC17. Terminal Block in UMDSB only has (5) poles. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627247&prj=658&rqi=IyAhLT2WUMOl1xqZ8satvdEYIj
GI-016 | DC17-1 | AMER | Closed | P2 Medium CX | gkuczler@rosendin.com | 2026-05-20 04:00:00.000 +0400 | Owner |  | General Design Issue | Design |  | equipment type |  |  |  |  | Hanley PDU Transformer Testing Polarization Index testing of PDU's requested by EQX requires isolation of transformer in PDU. Isolation requires removal of factory connection from XO to GND. Hanley has advised factory connections cannot be removed without warranty impact. Need direction on if test is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622633&prj=658&rqi=RFXIX7ykvg9qikqdlKAgsOMcdZ
GI-013 | DC17-1 | AMER | Closed | P3 Low CX | emilyma@dpr.com | 2026-05-11 04:00:00.000 +0400 | SGB-SMIT |  | Design correction needed | Design | [6 empty] | SGB MLTXs relay cut out incorrect size. SGB did not align the SE relay cutout per the dimensions in the submittal. Current dimensions are 8.07x5.12. Required dimensions based off SE relay is 8.07x7.09. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621176&prj=658&rqi=CjiYj6OyfnxvXobYWGtbITUgip
GI-012 | DC17-1 | AMER | Closed | P2 Medium CX | emilyma@dpr.com | 2026-04-29 04:00:00.000 +0400 | JCI - Johnson Control |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Chiller W has a good amount of visible rust inside piping from factory. Other chillers may have the same problem. - Field inspection of Chiller W shows heavy, visible rust scale and oxidation on the internal surfaces of factory-installed piping and nozzle connections. Photographs confirm uniform orange/brown corrosion inside multiple pipe sections, including flanged connections and inlet/outlet barrels. The condition appears pre-installation and is consistent with improper factory preservation, moisture ingress, or lack of nitrogen purge/desiccant protection. Based on identical construction, other chillers are at high risk of the same internal condition. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619949&prj=658&rqi=KNfcQAkJcusPGxmbXCTXU6SsK3
GI-009 | DC17-1 | AMER | Work Completed | P2 Medium CX | gkuczler@rosendin.com | 2026-04-21 04:00:00.000 +0400 | DEL - Delta Elec |  | Component/ Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (3) STS Molded Case Switches were damaged by 3rd tier subcontractor in warehouse. Replacements are needed, DPR has been notified. Need update on replacement order. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619043&prj=658&rqi=1EdhDMbNglHyUBEkhk98dPoC4m
GI-008 | DC17-1 | AMER | Work Completed | P2 Medium CX | gkuczler@rosendin.com | 2026-04-21 04:00:00.000 +0400 | DEL - Delta Elec |  | Component/ Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (2) STS Molded Case Switches arrived with bent pins. Replacements were ordered and expected with March delivery of STS units. No switches were received. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619026&prj=658&rqi=OBgd58QK9gKNl4yvk2tAtbRxj8
GI-007 | DC17-1 | AMER | Closed | P2 Medium CX | emilyma@dpr.com | 2026-04-13 04:00:00.000 +0400 | VER - Vertiv |  | Installation Damage | Commissioning | [6 empty] | Damaged battery cabinet for L3. Vertiv to come out and inspect unit. model PHR3462-001A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617974&prj=658&rqi=ba6n7Bt1PwnA5CWYkaYoIqjN5f
GI-001 | DC17-1 | AMER | Closed | P2 Medium CX | emilyma@dpr.com | 2026-02-09 04:00:00.000 +0400 | VER - Vertiv |  | Installation Damage | Commissioning | [6 empty] | DC17-2 asset - Vertiv Damaged 1200kva UPS at A&A. 1/20/26. SN D25M006518. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198806&prj=658&rqi=LBzvHjkDg8V1nzGw7OeSyYdNWW
GI-108 | DC21-P2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-09-17 04:00:00.000 +0400 | General Contractor |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | ALL G and H Electrical Skid CRAH's: Side doors on unit were left off and the screws are missing to put the doors back in place. We need replacement screws and the doors back on the unit for L4 Testing. Delta HVAC issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638474&prj=678&rqi=GGv32inzHE7Z2eEXJ7itAq1Hrq
GI-110 | DC21-P2 | AMER | Open | P2 Medium CX | francis.callan@veolia.com | 2026-09-17 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | [6 empty] | Common to all Harmonic Filters; The hardware installed for the control circuit inside the harmonic filter is incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638601&prj=678&rqi=KkuK76vm1LOXIaziz1o6fYTEB4
GI-106 | DC21-P2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-09-14 04:00:00.000 +0400 | General Contractor |  | Component/ Equipment Failure | Commissioning |  | equipment type |  |  |  |  | All Electrical Skid CRAH's: G and H. Valve feedback stays at 0 or in "Error" while the valve is commanded open Delta HVAC issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638003&prj=678&rqi=P3uGUOGF8lWK6nOIRQrNiOfCR4
GI-107 | DC21-P2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-09-14 04:00:00.000 +0400 | General Contractor |  | Component/ Equipment Failure | Commissioning |  | equipment type |  |  |  |  | All Electrical Skid CRAH's: Fan feedback (rpm) values are reading 0, even when fans are running. Awaiting PLC upgrade from Delta HVAC for 9/15/26 in the morning. Delta HVAC issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638006&prj=678&rqi=zvTpLPEVDr6WUlHHheVUz5EcQt
GI-105 | DC21-P2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-09-14 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/ Fault | DCOS |  | equipment type |  |  |  |  | All Electrical Skid CRAH's: BMS displays the supply air temperature setpoint at 0 and the differential setpoint as 0. Points do not match between HMI and BMS. The differential temperature setpoint automatically reverts back to displaying 0 after changing this setpoint on the unit HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638002&prj=678&rqi=SHEgMSryFhSanOSGUt78ABO0p6
GI-104 | DC21-P2 | AMER | Open | P3 Low CX | william.park@veolia.com | 2026-09-09 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | Exhaust Fans: Electrical Rooms H and G - Both exhaust fans have UPS wires not terminated and hanging within the exhaust fan controller box. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637534&prj=678&rqi=ZlRgr5t1UtYsfb9uMzyTV7UmnT
GI-103 | DC21-P2 | AMER | Open | P3 Low CX | william.park@veolia.com | 2026-09-09 04:00:00.000 +0400 | Electrical Contractor |  | Missing Components | Commissioning | [6 empty] | Exhaust Fan: Electrical Room H - Ground wire is missing from the exhaust fan controller box. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637530&prj=678&rqi=aymkie1YapYgJgpXhFqJ7VyZF7
GI-100 | DC21-P2 | AMER | Open | P3 Low CX | Aaron.Cross@veolia.com | 2026-09-04 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning | [6 empty] | Water on floor of GEN-H source unknownÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636880&prj=678&rqi=amYW1KbSHSJLYioP9UTtYUnPjT
GI-090 | DC21-P2 | AMER | Open | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-08-20 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | [6 empty] | Some washers appear to be installed on the incorrect side of the ground terminations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634475&prj=678&rqi=w6I0sy88PIWyNFCQ4V1t6C0Lzz
GI-091 | DC21-P2 | AMER | Ready for Verification | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | 1-UPS-G-2: Too much copper is showing between the wire insulation and the crimp at the battery termination. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634482&prj=678&rqi=wqOqWqPbajLm8qoQ0MrQbxbuki
GI-092 | DC21-P2 | AMER | Open | P3 Low CX | samuel.bruce@veolia.com | 2026-08-20 04:00:00.000 +0400 | Electrical Contractor |  | Incomplete Connections | Commissioning | [6 empty] | HVL-G knockout must be removed to route interconnect wires between sections 1 and 2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634512&prj=678&rqi=DY6HJN3V5dfmdeAC7uy5uQZlmn
GI-078 | DC21-P2 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning | [6 empty] | Water appears to be present on the floor outside and around the boardÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630465&prj=678&rqi=L2FtZgG8VvjlExwxRyGmjwCQIf
GI-075 | DC21-P2 | AMER | Ready for Verification | P1 High CX | ayorinde.akinrinlola@veolia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | Skid D - Battery Exhaust Fan Control Box: Â Openings and Cable Protection The fan control box has two unused openings that are not sealed and should be fitted with appropriate hole plugs/covers. Additionally, the conduit entry currently in use is missing a protective collar, leaving the wire exposed where it passes through the conduit opening. Install the appropriate collar to protect the wiring and ensure proper installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630387&prj=678&rqi=0LakXGUt6ngPTFDQHwapspjGdd
GI-074 | DC21-P2 | AMER | Ready for Verification | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/ Equipment Failure | Commissioning | [6 empty] | Skid D: Â Exhaust Fan Not Operational Â The exhaust fan on Skid D is not operational. Initial inspection indicates that the fan motor appears to be faulty, preventing the exhaust fan from running. The fan and motor should be inspected, tested, and replaced if confirmed defective | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630366&prj=678&rqi=HFEAdMLujg3hZpxVKFgh92HhtX
GI-073 | DC21-P2 | AMER | Closed | P2 Medium CX | taquonya.washington@veolia.com | 2026-07-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Design correction needed | Design | [6 empty] | ECB-R-G needs the K2 Kirk key cylinder replaced with the KLB cylinder that matches the site (KLB SN 63374) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630038&prj=678&rqi=KoTcwLNSzymuGljvyqGxYgKWXI
GI-072 | DC21-P2 | AMER | Closed | P1 High CX | william.park@veolia.com | 2026-07-15 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | New Data Hall CRAH's: Main power conduit to the CRAH's was left in place on top of the dampers within the top damper section of the unit. Conduit was found to fall in between the dampers, and dampers will force closed on this conduit resulting in electrical failure and CRAH failure. The conduit must be propped on the side wall or top wall of the inside of the CRAH's with clamps to avoid this conduit from being near the dampers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629456&prj=678&rqi=8GKf42hMZ8jEkb9EJRzVqB1cLD
GI-044 | DC21-P2 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | Skid D&H- Card Reader are higher. The Card Reader is at 56'' to Center. Need to be at 46''. MPS started to rectify these before it shipped out. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627467&prj=678&rqi=1ieOO1Zqd9r2txhzDMBvaLvhev
GI-043 | DC21-P2 | AMER | Ready for Verification | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | Skid G -The fire protection main line is missing the required connection point and has not been properly secured. The fire protection main line is not connected in accordance with the project requirements and must be properly connected and supported. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627464&prj=678&rqi=RR3ubOHSFFk9NCFTKfn39UzXGw
GI-039 | DC21-P2 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | SKID G & H- F/A Box need to be changes: Top F/A box will be removed and changed to an 11B box to provide proper clearance | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627391&prj=678&rqi=cxn8m9HcCWVByJr0Mz6hp4X0tb
GI-038 | DC21-P2 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | SKID G & H- Ground bars not complete: Ground bars are not jumped together inside of skids- 4 Ground Plates do not have jumpers between them. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627383&prj=678&rqi=KU5jpVpBEnHRGhE7VNffP8m8vG
GI-045 | DC21-P2 | AMER | Ready for Verification | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | SKID G- Two sprinklers heads are missing in Skid G as shown in design drawings. Two Sprinkler heads were missing and not installed as shown in drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627468&prj=678&rqi=9ujfmceVLIBsqrB1RtlmGUKAsM
GI-030 | DC21-P2 | AMER | Open | P2 Medium CX | michael.acciaioli@veolia.com | 2026-06-29 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Chilled Water Pump Wiring - The Chilled water pump wiring connection was removed from Chillers D-17 & D-18. The chillers at this site have their chilled water pump getting power from the chiller main circuit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627238&prj=678&rqi=rDgw413ezlBzJhAhSMtVw7Rsdl
GI-029 | DC21-P2 | AMER | Open | P3 Low CX | taquonya.washington@veolia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | Label and placard outside of skid D needs to be updated now that the skid will no longer be tethered. One is made by REI, the other is made by MPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625529&prj=678&rqi=pIUxL9EMoQTV3Xwz3jIRZtDAIj
GI-028 | DC21-P2 | AMER | Closed | P3 Low CX | ron.brackin@veolia.com | 2026-05-26 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | [6 empty] | Flat washer installed is not in accordance with PDU submittal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623158&prj=678&rqi=h6yjciVswFy6KT9vG8j78UsQ14
GI-026 | DC21-P2 | AMER | Open | P3 Low CX | ron.brackin@veolia.com | 2026-05-26 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Change bus labeling on all G and H RPP's incoming feeders (currently says CBA, change to ABC). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623155&prj=678&rqi=kVnJfSJbhr7uYuiSmmI3RhFyiH
GI-027 | DC21-P2 | AMER | Closed | P3 Low CX | ron.brackin@veolia.com | 2026-05-26 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Labelling | Commissioning | [6 empty] | Phase labeling on incoming feeders are labeled incorrectly. In field -CBA, should be changed to ABC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623157&prj=678&rqi=EzFGKhcxj67kcFhLSMvs6OJUhe
GI-025 | DC21-P2 | AMER | Open | P3 Low CX | ron.brackin@veolia.com | 2026-05-20 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | [6 empty] | Exhaust fan receptacle fed from ups-backed source, shoud be non-ups. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622536&prj=678&rqi=4Zrq0cELfcMJPgH7VRtQmwIu4V
GI-023 | DC21-P2 | AMER | Open | P2 Medium DCOS | michael.acciaioli@veolia.com | 2026-05-14 04:00:00.000 +0400 | Owner's Representative |  | DCOS Design Issue | DCOS | [6 empty] | BMS Standard - The DC21 site was originally commissioned in 2020 and used the EBCS3 version 2.6 standard. At the time of DC21-P2&P3 the version for EBCS3 has changed to 4.8. During the Software Factory Acceptance test it was noted that the controls for the new equipment will match the existing standard and not the latest EBCS3 version. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621878&prj=678&rqi=JH99c1R1qTo2DG0OzlXQHCa66q
GI-024 | DC21-P2 | AMER | Open | P3 Low CX | ron.brackin@veolia.com | 2026-05-14 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | [6 empty] | MV Switch D currently has primary and alternate designation swapped in terms of labeling.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621907&prj=678&rqi=cIvfG3zp5AXwsXwXFt29VP73B9
GI-022 | DC21-P2 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | [6 empty] | SKID-D Existing chilled water piping and new chilled water piping in new half skid appear to be at different elevations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617092&prj=678&rqi=WgdAJS9eBc86l9aJXLr6Ba2S0N
GI-546 | DC22-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | Commissioning Authority |  | DCOS Installation not complete | DCOS | [6 empty] | . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623745&prj=475&rqi=fdbc3kpymNpIlvLwpWFsMGthVP
GI-545 | DC22-1 | AMER | Open | P2 Medium DCOS | manuel.gomez@eu.equinix.com | 2026-05-29 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Post RFS --- The Vertiv CRAHs have been wrongly integrated, duplicating 3 Modbus registers : -Return Air Temperature Setpoint -Supply Fan Command -Supply Fan Speed Command | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623469&prj=475&rqi=gjbNToc6dpog3ymsmYvaqxBraY
GI-542 | DC22-1 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-04-16 04:00:00.000 +0400 | SCH - Schneider Electric |  | Installation not complete | Commissioning | [6 empty] | E-house 2 wiring for the one BARD is not complete - this is wiring that should be done by the skid manufacturer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618443&prj=475&rqi=bPi3vmtjRAAMj8h2AoHZPahBCi
GI-537 | DC22-1 | AMER | Open | P3 Low CX | jonas.wudkwych@veolia.com | 2026-03-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | General Design issue | Design | [6 empty] | Kirk Key system for DC22 MV Ring design appears incorrect. ECB_R1_Q1 Final Solution â€“ Replace the K2/K55 cylinder with new K2 cylinder. K2 cylinder is at IAD but need to confirm that you can reuse the housing of the existing cylinder. ECB_R1_Q2 Final Solution â€“ Will swap door with another onsite Will take door from 4th floor (ECB_R1_RS_Q1) and take to 3rd floor (ECB_R1_Q2) once new door arrives. ECB_R1_RS_Q1 Final Solution (not till Tower 2 during DC22-3) â€“ Replace kirk key cylinder and transfer blocks as per design to be determined during DC22-3. New door with transfer blocks shipped from Ireland. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615464&prj=475&rqi=uOWAY7pvu42nG0TJkDfJ8BNBkg
GI-539 | DC22-1 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-03-12 04:00:00.000 +0400 | Equinix Ops |  | Installation not correct | Commissioning | [6 empty] | RPP BCM â€“ Unlcear of setup of Janitiza for RPP BCM. 1/27 â€“ Trevor is currently reconfiguring RPP setup for 415V and single row consecutive at DC22-1. 2/9 â€“ Approximately 10 RPPâ€™s were locked out and not yet complete. Once placed back in service, will complete at DC22-1. 2/23 â€“ Veolia will follow up with DPR/REI on status of RPPâ€™s at DC22-1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615476&prj=475&rqi=Kbtq4QN83ITkvLFiHNjOSBeW61
GI-538 | DC22-1 | AMER | Work Completed | P3 Low CX | jonas.wudkwych@veolia.com | 2026-03-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design correction needed | Design | [6 empty] | Design Change --- No external control power to the ECBâ€™s (If the R-spine is down there is no control power and no communications through the BMS) - Qty: 3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615465&prj=475&rqi=Mmmy5Ux8LWUeeWT6RPX9tSJQ1h
GI-509 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | At the time of commissioning, we were unable to click on the individual compressors on the Chiller Faceplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198504&prj=475&rqi=7kzyEKYhqSsKRP9vPMozhjFvhL
GI-525 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | CRAH Alarm Program: During commissioning, the return air sensor probe failure did not appear on the BMS. It only appeared on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198523&prj=475&rqi=lFTEy7nZCxURFDsHVQbZpBIdqz
GI-494 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Riser designation text did not match actual destination. i.e. "first floor" corresponded to the riser serving the 3rd and 4th floors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198487&prj=475&rqi=uGy2HcmPT1gvEP0IqFdCRV2mtF
GI-489 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | Chilled Water Manager - BMS During commissioning, chilled water bypass valve control wasn't functioning as intended. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198477&prj=475&rqi=Mxg55tlLJ4JMirl4uRvuLtnQCs
GI-488 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | During commissioning, BMS did not have a roof plan showing - All required devices | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198476&prj=475&rqi=rxUzncp5Npuk4GtRKm5EIhwOfD
GI-524 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | CRAH Alarm Faceplate: During commissioning, in the event of a remote sensor fault, it showed a purple box on the CRAH alarm faceplate when it should have been a blue box around the alarm for a remote sensor fault. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198522&prj=475&rqi=ARCZw691oXzCdJlvQVmLKaAITs
GI-516 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | During commissioning, the Isolation Damper Command Mismatch Alarm triggered within 22 seconds of the unit being commanded OFF by the BMS. The alarm cleared after 105 seconds. The Isolation Damper fail time is supposed to be 90 seconds. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198513&prj=475&rqi=mptUq8kh30rYRPBQocUIgQdlT0
GI-503 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | At the time of commissioning, none of the first-floor mechanical was visible on the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198498&prj=475&rqi=0GnrJGEgdeYCXg3nt14gfYRC1s
GI-517 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | At the time of commissioning, an acceptable range of values for the supply air temperature (60-80F) needed to be set. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198514&prj=475&rqi=VsQkWfm90DAlncRYw98Wm2e8hg
GI-484 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | At time of testing, Exhaust Fans were not shown on the BMS graphics. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198468&prj=475&rqi=g1XTymQZaxueI9wjLSFtcx7Pr1
GI-518 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | During commissioning, when we tried to set the minimum fan speed in the setup menu (445), the minimum fan speed changes but did not reflect it on the faceplate Fan Speed Command. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198515&prj=475&rqi=wLMcu4wF1P2Sh5ZmNkRoSHoeya
GI-496 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | At the time of commissioning, chiller data was not being displayed on the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198491&prj=475&rqi=5OUETF3UD4XoLIF0jCLQF6KuHq
GI-531 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Alarm Banner: PLC_IO_Network Alarms were not counted in the full site alarm banner during commissioning. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198536&prj=475&rqi=SuAMlxc88x0Vfc46zSgX06DXJX
GI-506 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | At the time of commissioning, multiple chillers had active faults when a fault at the chiller is not present. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198501&prj=475&rqi=L1Cv7synPkVaxxbvNVdJ0sbBLD
GI-507 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | General Aveva Graphics Issue: At the time of commissioning, there was a hidden box at the name of equipment or type that didn't allow you to navigate to the correct window. It appears to be hidden for every name and if clicked it didn't do anything. These needed to be removed or hidden. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198502&prj=475&rqi=fpwIuX4nELHu5vrrW0Hd5KCDEu
GI-501 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | All Electrical Rooms: At the time of commissioning, Remote temp sensors for ER CRAH's needed their scaling updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198496&prj=475&rqi=ZI2egGFjzxYuzKS6X0msPjBpAR
GI-505 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [6 empty] | A generator yard plan should be provided Equipment in the Generator Yard, such as FCU's and Generator Fuel are not visible on a floor plan. Unable to see on the BMS. Suggest providing a generator yard plan with all devices being communicated to, or a way for end user to see all required control devices. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198500&prj=475&rqi=bdbcjwrt4d0j6rxFjfaQKmaBp0
GI-487 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | FOH/BOH --- At time of testing, BMS was not showing DX equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198475&prj=475&rqi=mNrqQulq2JZVwUiNPSDYmhJp73
GI-530 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | CRAH HMI Program: During commissioning, CRAH's did not break out of grouping mode when not enough sensors are present. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198535&prj=475&rqi=0kg7HGIfHhlNH3n4bHVzd5k9JN
GI-504 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Fuel Fill Station is not shown on the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198499&prj=475&rqi=KrGGwwGnVxG6B1ETpQWHiiYuZ6
GI-508 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | At the time of commissioning, the chilled water pump data was not showing on the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198503&prj=475&rqi=Ggl3D2IBLoyNbg4ejry18ju08f
GI-519 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | CRAH Faceplate - During commissioning, we needed to add the min and max speed command (%) in the setup menu for unitary mode. Minimum fan speed should be 30% per the Equinix Standard | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198517&prj=475&rqi=1TmtP25ARBnt6Qk6Xw4Wfd9QOr
GI-520 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | CRAH Program: During commissioning, the PID ramped up/down too fast when changing remote or supply temperature. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198518&prj=475&rqi=aYxu9PiVY65z5Crp2CQdImqM4e
GI-497 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | Chilled water flow deviation was not responding to range changes C5 and C6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198492&prj=475&rqi=7dTUfOcblLRd7lMYa7DItldvVq
GI-513 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | During commissioning, we were able to write a negative Supply Air Temperature Setpoint on the HMI. We needed to set the range to not allow a value less than 0. Allowable range: 0-100F | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198510&prj=475&rqi=WmKlp002UTOafyWUwClYthf8N6
GI-485 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | At time of testing, BMS was missing all VAV's | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198469&prj=475&rqi=yi68J68bcfqbLIdsfTc5pbVMLs
GI-532 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [6 empty] | Chiller String: During commissioning, Multiple Valves end switches did noy make while valves are fully open. We've seen this issue with Bray Valves due to temperature changes. E-tech verified if valves were configured correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198541&prj=475&rqi=ORgR5vj6FPugKEchqWMeSKIlx2
GI-533 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | CRAH Alarm Faceplate: During commissioning, the chilled water valve mismatch created a mismatch alarm without an alarm rectangle as well as a unit alarm with an alarm rectangle. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198542&prj=475&rqi=bxw3ZThlFIBgHloES5kQa0jA2t
GI-535 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | RTU's: At the time of commissioning, we were losing comms on and off for RTU's. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198545&prj=475&rqi=zV3mnsRkyajXuVgT7GBnHlY9uO
GI-521 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | During commissioning, the System Bypass Valves were hunting and going to 100%, making the pump speed increase to 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198519&prj=475&rqi=wqrsQMyAg7Imd7oJYa6sHl5Ggx
GI-500 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Boilers and Make Up Water are not shown on graphics on both the FOH and MOF | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198495&prj=475&rqi=xnggdnvMZgBGQgnMsg3eqrvYvG
GI-534 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Battery Room WSHP's: At the time of testing, heat pumps had no values that were shown on the faceplate that correspond to the actual units themselves. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198544&prj=475&rqi=7MBDaDxrsHTgLHv4S2rFToYW11
GI-528 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Chiller Cooling Strings: During commissioning, a Wrench was displayed by the chilled water pump on cooling string chiller pages. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198532&prj=475&rqi=TNBRRQj4KIlbjHSLlOn5VubWcx
GI-514 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | During commissioning, a CRAH Summary alarm on the BMS was not triggered when there was an alarm on the CRAH. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198511&prj=475&rqi=BK4EldvlPVeiByBvNWTQ14qBBG
GI-527 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | CRAH Alarm Program: During commissioning, a timer needed to be added to supply fan mismatch. When shutting down, as fans ramp down and command is 0, we shouldn't be in fan mismatch, add 30+ second supply fan mismatch timer. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198531&prj=475&rqi=E3mpBxtzgfZs72ctL26PrjibLL
GI-515 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [6 empty] | BMS Chilled Water Layout: The Weather Station Temperature was not reading accurately. When the ambient air temperature was below 40 degrees, the weather station was reporting 57 degrees on all three sensors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198512&prj=475&rqi=WLUE7FdzHvspmJyGfRAjVgtbWU
GI-529 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | CRAH Program: During commissioning, CRAH's did not pick a new lead unit when the lead unit was not communicating | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198534&prj=475&rqi=XhXhoJsdTj7qBYbgnCNEU4q3LC
GI-486 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | At time of testing, BMS was not showing FCU's | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198473&prj=475&rqi=FGDTsknPcfKqh8WbVyHWkdyZCS
GI-511 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | During commissioning, whenever a CRAH unit lost power, the dirty filter alarm was generated on the BMS. The normally closed contact was changed to normally open | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198506&prj=475&rqi=j6pUe91d3TRRCW97cmKEQAX72o
GI-490 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Multiple Flow Meters and temp sensors are not reading correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198479&prj=475&rqi=9248mXQBRL8qtH759Xhy2tGqFO
GI-522 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | CRAH Program: At the time of commissioning, a power loss event on the CRAH unit didn't trigger a loss of Power alarm. A "Loss of Power" or separate power loss alarm is needed for this event. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198520&prj=475&rqi=wr74kJjDsXXdbUikd7caODsAeH
GI-512 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | During commissioning, the supply and return CFM differed at the unit. Also, the BMS was registering the return CFM and not the Supply CFM on the Faceplate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198508&prj=475&rqi=CwiSYZRvXoOjr1EmVKmPzCmDVS
GI-510 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | At the time of commissioning, the supply fan percentage did not match the unit HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198505&prj=475&rqi=sGnS44lhuQu7KSJjYA7H1zMmwh
GI-523 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | CRAH Program: At the time of commissioning, The Supply Air Setpoint could not be changed manually on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198521&prj=475&rqi=uwDwPLpZBJv4UVqB1hUsIUrDfC
GI-491 | DC22-1 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | MAU valves need to be controlled via temperatures sent by the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198481&prj=475&rqi=LH2UTNo3R9HQfygxgRqFPOVMVc
GI-495 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Chilled Water System BMS graphics: The DP being used on the manager page (to control pump speed) did not match the DP on the system page of the graphics. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198488&prj=475&rqi=yxVJPYP77iYRu30nLo0Vn5WETI
GI-526 | DC22-1 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | CRAH Alarm Program: During commissioning, a "High Air Flow" alarm did not appear on the BMS. Alarm only appeared on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198524&prj=475&rqi=L3QIEWfrMyZEnz7EeVj5paYzDW
GI-105 | DC22-2 | AMER | Open | P2 Medium CX | francis.callan@veolia.com | 2026-09-17 04:00:00.000 +0400 | TRN - Trane |  | Missing Components | Commissioning | [6 empty] | 1-ACC-G-01: Pump VFD housing is missing hardware. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638472&prj=673&rqi=4IYBNPtFR2Un1J9PlcRwJCOaeX
GI-104 | DC22-2 | AMER | Ready for Verification | P3 Low CX | jonas.wudkwych@veolia.com | 2026-09-14 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS the faceplate for the MLTX does not open when the MLTX is clicked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638012&prj=673&rqi=yZK0hcfI6fV9vmjjFeFCRtypm0
GI-102 | DC22-2 | AMER | Ready for Verification | P3 Low CX | jonas.wudkwych@veolia.com | 2026-09-14 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS Both buttons 1UPS_H_1 and 1UPS_H_2 are linked back to the C block onelines not H block | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637987&prj=673&rqi=XB4XRZQWHo6thIr69eewSzmTig
GI-103 | DC22-2 | AMER | Ready for Verification | P3 Low CX | jonas.wudkwych@veolia.com | 2026-09-14 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS the TO DH 3001 button on the H block onelines page is not linked. Please fix | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638009&prj=673&rqi=qhBc01r4tTQtBw9yvz3dE3ztZo
GI-099 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-09-09 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [6 empty] | Onelines are displayed differently for phase 2 compared to phase 1. Please clarify if we are using a different standard throughout the same building. Specifically there is now a second page that the UDPs STSs and PDUs are being shown. See screen shots. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637514&prj=673&rqi=Ng37JtOBbnvsyBjQX7dDw16DFy
GI-098 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-09-09 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | MSB-ALL When one of the LBB breakers is closed the line animation between both the LBBs does not show power going through. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637502&prj=673&rqi=K5XLSLKfZEQl9JfhbPxYqMI1o8
GI-096 | DC22-2 | AMER | Open | P3 Low CX | michael.acciaioli@veolia.com | 2026-09-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | DH CRAHs - Active number of CRAHs in Group on Unit HMI does not update. When removing units from the group or powering off units the number of units in the group does not change. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636872&prj=673&rqi=9bAd8UDBPvXiCXldBA4zu4fbiN
GI-097 | DC22-2 | AMER | Open | P3 Low CX | michael.acciaioli@veolia.com | 2026-09-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS |  | equipment type |  |  |  |  | EF's - Exhaust Fans that have been started and energized are not shown on the BMS. i.e. EF-C | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636877&prj=673&rqi=fmbLGmTmsLSLbc0dkwaHxotIbc
GI-095 | DC22-2 | AMER | Open | P3 Low CX | michael.acciaioli@veolia.com | 2026-09-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | DH CRAHs- CRAH graphics indicate CRAHs are in alarm for "not in Group" when units are in group mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636870&prj=673&rqi=DS7TJqVGD9d3aPh8nyQRSKXIvu
GI-094 | DC22-2 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-09-01 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | Chiller Bypass Valve logic: [Common to all ACC's on previous phase] After stage up to a new chiller, the enabled chiller goes through its normal start-up and starts increasing from 0 GPM to a flow similar to all running chillers. However, the bypass valve immediately reads this start-up as a failing to meet minimum flow state and starts to open. The bypass valve does not need to open during every stage up of a chiller, and should let the new chiller go through its normal ramp-up before being called to open. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636302&prj=673&rqi=Ouzr2XUI2nu3LYMbOQlovd97kc
GI-093 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-08-26 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | [6 empty] | Battery Cabinets - ALL the control power for the battery cabinets has not been labeled showing where power comes from. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635311&prj=673&rqi=4EBCPy4bMI3DkqjpFyxmalNLFn
GI-092 | DC22-2 | AMER | Open | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-08-25 04:00:00.000 +0400 | DEL - Delta Elec |  | Missing Components | Commissioning | [6 empty] | On STSs there is hardware missing from multiple locations on multiple units. See photos. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635100&prj=673&rqi=SBaQy2oVKA7qRaa1IpTkpv4pHW
GI-085 | DC22-2 | AMER | Open | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-08-12 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | [6 empty] | On UPS_A_1, A_2, B_1, B_2, C_1, C_2, D_1, D_2, H_1 and H_2 There is a typo on the control wires labeled 1UPS_A_1-AP30_TB1-1 / 1UPS_A_1-AP30_TB1-2. These labels should read 1UPS_A_1_TB1-1 / 1UPS_A_1_TB1-2. This typo is across the 1 and 2 UPSs in all rooms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633234&prj=673&rqi=0gYLdNx2X0JNZZZPaPRZb86Vp6
GI-073 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 1GSB_2 IO/Control Cabinet - During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633094&prj=673&rqi=DMnuhVouRiQyXoggvh7BjN9Frx
GI-077 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 1GSB_5 IO/Control Cabinet - SE DP discovered a common issue to all GSBs during phase 2 testing and inspection. During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633107&prj=673&rqi=Rc7owLXHkXe2fxpppepQsEbJQ7
GI-079 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 1GSB_7 IO/Control Cabinet - SE DP discovered a common issue to all GSBs during phase 2 testing and inspection. During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633109&prj=673&rqi=ZYsmMYDzpIcmtn9sARZZpXZeJf
GI-074 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 1GSB_1 IO/Control Cabinet - During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633101&prj=673&rqi=7eHmXlkSt8apJQI4CBwSweYjab
GI-072 | DC22-2 | AMER | Closed | P2 Medium CX | francis.callan@veolia.com | 2026-08-11 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [6 empty] | [Common to all ACC's/ Harmonic Filters]: Fuses continue to fail when opening and closing disconnect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633083&prj=673&rqi=MtQDZn43de2T8T6zPrkmiSveBH
GI-078 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 1GSB_6 IO/Control Cabinet - SE DP discovered a common issue to all GSBs during phase 2 testing and inspection. During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633108&prj=673&rqi=vFGYp3nKTBQphzHsESevKwVmlx
GI-075 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 1GSB_3 IO/Control Cabinet - During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633103&prj=673&rqi=PoSG5tvWuc9M3oMOnOJQxuJhSI
GI-076 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 1GSB_4 IO/Control Cabinet - During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633105&prj=673&rqi=lUVanJkxoAASpMZHtwyK69bq5t
GI-080 | DC22-2 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 1GSB_8 IO/Control Cabinet - SE DP discovered a common issue to all GSBs during phase 2 testing and inspection. During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633110&prj=673&rqi=y2H40Qt9mMBKieUanrLrw0g2wS
GI-071 | DC22-2 | AMER | Open | P1 High CX | francis.callan@veolia.com | 2026-08-06 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | [Common to All CRAH's] No torque marks present on all victaulic clamps. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632600&prj=673&rqi=0ZZKgN7UQP8RFMS54SDu3q4cmn
GI-070 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-07-29 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/ Fault | DCOS | [6 empty] | MSB-ALL The PQMs on the MSBs cause comms loss when added onto the switch in the controls section of the MSB. Hanley troubleshooting is ongoing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631211&prj=673&rqi=JCXglhS13SZs6NtAjoy4IRTUlZ
GI-069 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-07-28 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/ Fault | DCOS |  | equipment type |  |  |  |  | MSB-All The Communication Alarm Status is not properly displaying on the faceplate for the breakers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631104&prj=673&rqi=5Dm4alxcmjE2KCJyu5C4erwPOs
GI-067 | DC22-2 | AMER | Closed | P2 Medium CX | william.park@veolia.com | 2026-07-28 04:00:00.000 +0400 | Electrical Contractor |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | ALL NEW DH CRAHS: Metal Shavings have been found all around and on top of the ATS within each electrical section of the Data Hall Mega CRAHS after drilling into the metal frame. Metal shavings need to be vacuumed and wiped away from each ATS and within each electrical box of the new 40 Data Hall CRAHS. Energization cannot occur until this action is completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631069&prj=673&rqi=0iqro6xB1iX09VnHgZlhtHLnbk
GI-068 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-07-28 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | MSB-All The breaker racked out status displays when the breaker is racked out to the test position but the status returns to racked in when racked all the way out. This appears to be an issue with the point being brought in through Modbus. The test position status works correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631103&prj=673&rqi=iUv7R8uG3RfDcUMu6Ulk0qFnTy
GI-062 | DC22-2 | AMER | Closed | P3 Low CX | eric.gremp@veolia.com | 2026-07-10 04:00:00.000 +0400 | Electrical Contractor |  | Torque required | Commissioning |  | equipment type |  |  |  |  | STSs in electrical room H have all had 2 ground lugs torques broken. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628727&prj=673&rqi=HAvVQnzrB0FdKlqLwUOwmMkiCe
GI-056 | DC22-2 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-07-08 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning | [6 empty] | Hanley Gear- MSBs and UDPs ALL are missing the top hat grounding wires | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628386&prj=673&rqi=T2RY9tMNPnqqxyWKzi5iMQBXU2
GI-053 | DC22-2 | AMER | Closed | P3 Low CX | eric.gremp@veolia.com | 2026-06-30 04:00:00.000 +0400 | VER - Vertiv |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | UPSs: All of H-block UPSs are missing kickplates. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627447&prj=673&rqi=kQ00d5w7yIiSK55mYOKsFTipwR
GI-052 | DC22-2 | AMER | Work Completed | P3 Low CX | eric.gremp@veolia.com | 2026-06-25 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | PDUs: This general issue is to track all of the damaged nut inserts in the back of the PDUs so far for this issue damaged inserts have been discovered in 1PDU_C2R1_3, and 1PDUC2R1_2. As mor damaged inserts are found they will be added to this issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627076&prj=673&rqi=RwgQUQaRJgeMGk90jIyEC9Pcdo
GI-050 | DC22-2 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-06-16 04:00:00.000 +0400 | SGB-SMIT |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | MLTX-All We are missing the fiberglass supports for the MV cables on the high side of the transformers. I believe SGB will be shipping these to site to be assembled by Rosendin. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625543&prj=673&rqi=kQO4Yb4RpX27MfdqSFNpn5gAOt
GI-049 | DC22-2 | AMER | Closed | P3 Low CX | jonas.wudkwych@veolia.com | 2026-06-08 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning | [6 empty] | Electrical room CRAH stands came tack welded and are different from the first phase please see photos. Are these stands acceptable and can we get updated submittals showing these stands? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624340&prj=673&rqi=uGJAtfVeCTuugStlTIwnN2psxi
GI-048 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-06-08 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Damage | Commissioning | [6 empty] | One of the stands for the Vertiv electrical room CRAHs is damaged and will need repaired/replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624339&prj=673&rqi=dY2Sagi60R1IJLdyoIVYrWFUVP
GI-047 | DC22-2 | AMER | Open | P3 Low CX | eric.gremp@veolia.com | 2026-06-04 04:00:00.000 +0400 | DEL - Delta Elec |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | STSs(H-Block): 1STS_H1R1_1, 1STS_H1R1_2, 1STS_H1R1_3, 1STS_H2R1_1, 1STS_H2R1_2, and 1STS_H2R1_3 all have been scratched and damaged while pulling MC cabling . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623984&prj=673&rqi=nXBQBRMOtGWKZBBykcEEPkrDr2
GI-045 | DC22-2 | AMER | Open | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-05-18 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | UMDSB-ALL The Spare Breakers in Q08 have a 250A breaker plug but the submittal shows a 150A plug set @ 70A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622211&prj=673&rqi=1iGmk8tjisAyDtfl2jRzeRSE9k
GI-044 | DC22-2 | AMER | Closed | P3 Low CX | eric.gremp@veolia.com | 2026-05-14 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | MSB (ALL): The Hanley Submittal RS-485 communications wiring does not match field installation including location of EOL resistors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621883&prj=673&rqi=2xeI0hsUphQxaUbCRdke4o6Jnw
GI-043 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-05-05 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design correction needed | Design |  | equipment type |  |  |  |  | MSB-ALL the top hat access in the top back of section 09A for chiller power faces the wall and will need to be modified or changed out to face forward to allow the conduit and cables to be installed. On the last phase the top hat was modified. (See photos of both attached) The front top hat is for the MC going to the MDSB (breaker Q10) and the back top hat is for the power to the chillers (breaker Q11). Â Because of the top hats that were included for the MC cables on this phase there still might be issues with access on the install and it might be better to install the chiller cables before the MC on section 09A Talking with Hanley there are 2 options, either the modification of the existing top hats or ordering new ones. Both will need approval from Hanley and ordering new will have a lead time that could push schedules. Â This will need to be done on 1 top hat on all 5 MSB lineups and has potential to cause delays with install and startup. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620450&prj=673&rqi=HuGlmYEALAOE7ZX5T2nghcmIGv
GI-041 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-05-05 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | UMDSB-ALL 2 breakers on each board Q06 and Q07 have the incorrect lug sizes that can only accept 3/0-350 kcmil. The electrical 1 lines call for #1 or 2/0 AWG depending on the length of the run.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620387&prj=673&rqi=EPJ1mwzt6jvPD2Xdtoc6zQCpma
GI-042 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-05-05 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MSB-H B & C a plate on each phase on each shipping split was missed when the bolts were torqued. Everyone on site is aware, old hardware is being removed, new hardware is on the way and the re-torqueing will start tomorrow. Â This issue has been added for tracking purposes.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620449&prj=673&rqi=uEntMuG9mqXDBALWGm1138sx0U
GI-038 | DC22-2 | AMER | Closed | P3 Low CX | jonas.wudkwych@veolia.com | 2026-05-04 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MDSB-ALL Make sure that the equipment meets the minimum clearance of 4 inches from the wall. It appears that MDSB-H as well as other units are less than the required 4 inches. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620248&prj=673&rqi=49D2ebrZBCnHVh8ZLyDuZiPPRF
GI-035 | DC22-2 | AMER | Open | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-05-01 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | MLTX-ALL The control wiring is landed in the control box terminations and not on the transformers. REI has schematics to land the wires in the control box but not on the transformer. Please confirm that this is a task for REI and not SGB as well as obtaining proper documentation to install these wires on the transformer from SGB if this is an REI task. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620132&prj=673&rqi=CLJKFktAdfKaWy4xwgERLwU5po
GI-036 | DC22-2 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-05-01 04:00:00.000 +0400 | SGB-SMIT |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | MLTX-ALL Missing components to land cables run going from the MVTBs to the MLTXs, on the last phase the connections were made on bus bar inside a separate part of the enclosure (see picture) and there were factory cable connections to the actual transformer. I do not see these connections or cabling and support. Will we be connecting the MLTXs the same way as the last phase, if so are we missing parts from SGB? If the cables are being terminated differently can we make sure we have proper documentation and instructions on making the terminations from SGB? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620133&prj=673&rqi=hPNuVEcZmnxYEB2GwJTYx13R9L
GI-033 | DC22-2 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-04-28 04:00:00.000 +0400 | Electrical Contractor |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | MLTX-ALL The bus bar inside the enclosure on MLTX A, B, C, D, and H has been improperly installed and will need corrected. There is a missing insulator that should connect the bus bar to a support bracket. Please see pictures and attached document. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619767&prj=673&rqi=tEqyCPCmouL5Jz40u7D3RU3ksC
GI-032 | DC22-2 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-04-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MSB-ALL The ground bus bar on the back of all MSB sections that was converted to MC bus connections is missing a 1/4" spacer. This was missed during the rework done at the warehouse. This is an issue already known by Hanley and is being added for tracking purposes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619371&prj=673&rqi=x1tfSopQuqc45zg2XTwS4pbD7K
GI-031 | DC22-2 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-04-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MSB-ALL. During the torqueing of the shipping splits between sections 3 and 4 it was found that some of the factory torque connections will need to be broken and associated hardware replaced because of the MC bus bar conversions. This was missed during the warehouse work completed by Hanley and will now need to be done on site. This will This will affect all MSBs This issue was entered for tracking purposes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619370&prj=673&rqi=8ZpU1Lvex71X0icgBODlzvEk7J
GI-028 | DC22-2 | AMER | Open | P3 Low CX | jonas.wudkwych@veolia.com | 2026-04-22 04:00:00.000 +0400 | DEL - Delta Elec |  | Labelling | Commissioning |  | equipment type |  |  |  |  | STSs (common to all) - SOO placards to be replaced with accurate placards showing correct key #s. The SOO placard installed shows references to K1 K2 and K3 keys but the actual keys are A1 B1 and A3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619100&prj=673&rqi=rhQdRVjQ9XLxmGdAfv4mGMqSxr
GI-029 | DC22-2 | AMER | Open | P3 Low CX | jonas.wudkwych@veolia.com | 2026-04-22 04:00:00.000 +0400 | DEL - Delta Elec |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | STSs (common to all) - Neutral kit placards are missing. Please confirm that the neutral kits were installed on the units and provide/ install missing placards. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619101&prj=673&rqi=hoSbXZFecJX6xSXUIui9Ko9koW
GI-027 | DC22-2 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-04-22 04:00:00.000 +0400 | DEL - Delta Elec |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | STSs (common to all) - fuse kits for MSB control power were not installed on the units. The photo with the fuse kit is from an STS on the previous phase.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619092&prj=673&rqi=tNiFRlhPyaIcg1o41qIgVOpi6Q
GI-026 | DC22-2 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-04-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MSB-ALL The ground bus bar between sections 3 and 4 appear to be improperly installed. Leonard from Hanley is already checking with the engineer on proper installation and sourcing the correct hardware. This is an issue across all the MSBs on site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618925&prj=673&rqi=8jMcqtbejyVVea5EHh983LRp7R
GI-018 | DC22-2 | AMER | Closed | P3 Low CX | jonas.wudkwych@veolia.com | 2026-03-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | General Design Issue | Design |  | equipment type |  |  |  |  | MSB - ALL on page 2 of the MSB as-built the Q03 Breaker is shown as having accessory 7 (the 120V Shunt open) but that should be shown on the Q10 Breaker. Also Accessory 8 is not included in the accessories legend. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616568&prj=673&rqi=Kd2NmvyKCMIqr20yeO4bOyYrVF
GI-007 | DC22-2 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-03-20 04:00:00.000 +0400 | SCH - Schneider MV |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MVTB: Edge guard throughout the unit is held in place with painters tape in some places and is not properly fitted/installed to protect wiring from rubbing against metal edges. This issue is in multiple sections of the unit and will need to be addressed and wiring thoroughly checked to make sure the outer insulation on this and other units was not damaged during transport | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616149&prj=673&rqi=7wcB7eJzCekXN8Rxjhb0pVm0C2
GI-005 | DC22-2 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-03-20 04:00:00.000 +0400 | SGB-SMIT |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MLTX: Upside down washers on a bunch of the connections | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616147&prj=673&rqi=jVfjMIYRzQ7iFzWZdorBieiMAk
GI-009 | DC22-2 | AMER | Open | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-03-20 04:00:00.000 +0400 | Electrical Contractor |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | MVTB: The bottom front covers when taken off the unit are easily knocked over in a way that damages the front handles. One of these was accidentally knocked over when inspecting the unit and was damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616151&prj=673&rqi=vYcrUMl5j253rkKnODtTs70cgn
GI-006 | DC22-2 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-03-20 04:00:00.000 +0400 | SCH - Schneider MV |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MVTB: Multiple bolts on the bus bars located in the bottom sections are not long enough to go all the way through the nuts to properly secure the bus bar. These will need to be replaced with longer bolts so at least 2 threads are showing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616148&prj=673&rqi=mmSuIbS9ulqMSzomWMkI5mw3iJ
GI-002 | DC22-2 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-03-20 04:00:00.000 +0400 | SGB-SMIT |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | MLTX: Washers on non-electrical connections are not uniform in size across multiple transformers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616143&prj=673&rqi=9u1G29IhMVXUqGCJz7EapXyP3Z
GI-392 | DX03-2 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-07-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Access Control System (ACS) â€“ Battery monitoring is not available. The system does not provide battery status, battery fault, or low battery indications for monitoring and alarm purposes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629340&prj=603&rqi=nX3iLoivT1Q4fVZMZwIn6NRcG8
GI-391 | DX03-2 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-07-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Access Control System (ACS) â€“ The "Door Not Used/Opened" event shall be configured and programmed in the ACS. During testing, when a valid card was presented and the door was not opened within the configured time period, no corresponding event or notification was generated or recorded in the event log | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629339&prj=603&rqi=faqIYkP7kBnrriD3wyTyXJyMEO
GI-388 | DX03-2 | S-EMEA | Closed | P2 Medium CX | v.baddegama@core-group.me | 2026-07-13 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/ Equipment failure | Commissioning |  | system | Fuel System |  |  |  | Fuel PLC-1 was not communicating with DCOS. Fuel system vendor confirmed PLC-1 is operating correctly on site. DCOS team was not able to ping the PLC from Equinix local server however, it was possible to ping the PLC from the global EQX server. DCOS team advised it could be a network IT issue. UPDATED: DCOS team have confirmed the PLC is communicating to the PLC when connecting directly with the DCOS laptop. Several workshops have been held between the DCOS team, Vendor and Equinix Gen2/Server teams to work through why the PLC is not able to communicate across the network. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628805&prj=603&rqi=DxnZZOPwpaxdoJ7qwdt4Bh55II | https://equinix.facilitygrid.co.uk/x/project/603/system/12118
GI-389 | DX03-2 | S-EMEA | Closed | P2 Medium CX | v.baddegama@core-group.me | 2026-07-13 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/ Equipment failure | Commissioning |  | system | Fuel System |  |  |  | For Fuel storage tanks (FST) No. 3 and No. 4 located in DX3.1 (part of DX3.2 phase), an interstitial leak alarm was active on DCOS system. The fuel system vendor (Green Adaptech / GATSS) stated that the tank leak sensor is connected to the numeracator panel installed in the fuel pump room and the signal originates from numeracator panel and goes to the fuel PLC. GATSS stated the manufacturer of the numeracator panel and leak sensor (in the US) will need to be contacted to troubleshoot and resolve this issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628806&prj=603&rqi=HIV76AlpKQrNgf4WERgqILzprx | https://equinix.facilitygrid.co.uk/x/project/603/system/12118
GI-387 | DX03-2 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-07-02 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Component/ Equipment failure | Commissioning | Electrical â€“ LV | equipment | 1-RPP-F-4 | RPP - Remote Power Panel |  |  | During Thermal scanning of the RPP's it was observed that the temperature with 54kW load connected . During investigation it was found that connection at the incoming MCCB (Factory assembled) was loose. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627711&prj=603&rqi=XQbhRa9NrGRbb4Z3RMEktQ8WQI
FPT-277-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-06-29 04:00:00.000 +0400 | ABEC - DCOS | L4 | Component/ Equipment failure | Commissioning |  | equipment | CHWS L4 FPT & Mech IST |  |  |  | One of 3 flowmeters on one supply flow header going to data hall (RAS-13) was removed to send for calibration. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627287&prj=603&rqi=Qa15L05GyblH9Qva4WdGHkFb45
GI-386 | DX03-2 | S-EMEA | Closed | P2 Medium CX | v.baddegama@core-group.me | 2026-06-27 04:00:00.000 +0400 | VER - Vertiv |  | Component/ Equipment failure | Commissioning |  | equipment type |  |  |  |  | APPLICABLE FOR ALL CRAH's: Vertiv/MDS stated that the CRAH HMI is a new product and that all HMIs need to be replaced. The following issues were observed during various times of testing: 1). When fan speed reaches 100% the HMI goes blank/white and HMI makes a sound. To reset the HMI, the cable connected to the HMI will need to unplugged and plugged in again. MDS engineer was observed to carry out this action multiple times on random CRAHs during various tests (chiller load testing and GF Data Hall load testing). 2). On random data hallCRAH's the HMI freezes preventing any touch input on the display by the user. This was particularly observed in the data hall CRAHs. 3). On random data hall CRAHs it was observed the response to user touch inputs was very slow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627170&prj=603&rqi=iJCYEpaHvysQjJB7blUnnHrpw7
GI-385 | DX03-2 | S-EMEA | Closed | P2 Medium DCOS | v.baddegama@core-group.me | 2026-06-26 04:00:00.000 +0400 | ABEC - DCOS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It was observed on 26th June 2026, the DCOS auto/Manual switch for number of devices in cooling manager manager was not working. Could not be changed from Auto to Manual. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627163&prj=603&rqi=hvJHX75v5gBPncYCxO3GZRFfIG
GI-383 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-19 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | DCIM BCM Issue | DCIM |  | equipment type |  |  |  |  | During RPP checks with operations for DCIM communications it was recorded there were communication issues. ABEC traced the communication issue with the Schneider Gateway. The polarity of the internal connection to the SCU100 was found to be reversed. ABEC connected a separate cable directly from the SCU100 controller to the Schneider Gateway and confirmed that communication with the gateway is working properly. The panel wiring needs to be reverified to ensure proper communication. The cable is currently marked as A(-) and B(+), which appears to be incorrect. It should be A(+) and B(-). The termination should also be checked and verified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626225&prj=603&rqi=TNNyeo2ZkI5nt2wVkZaLxHjLN8
GI-111 | DX03-2 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-06-17 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/ Equipment failure | Commissioning | [6 empty] | Luminaires CMP2-GF-L7-15, CMP2-GF-L7-17, CMP2-GF-L7-19, CMP1-GF-L2-02, and CMP1-GF-L2-04 failed the Battery Autonomy Test (Ground Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625637&prj=603&rqi=vnZL8FGxSIP9FXdHCHRjoYGFTA
GI-110 | DX03-2 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-06-16 04:00:00.000 +0400 | VER - Vertiv |  | Component/ Equipment failure | Commissioning |  | equipment type |  |  |  |  | During STS-F-2 Testing the following was Observed in the ground floor Data Hall CRAH: - low Humidity Summary Alarms present in several CRAH. - Above alarms not resetting on HMI - â several HMI unresponsive - Several HMI were observed to have their â time & date reset to defat (year 2000) - â GC had to switch the CRAH off and on to reset alarms - â Fans not ramping up with return temp reaching 36deg (advised the CRAH were set to 36Deg return air). These were not reamping up individually or as a group. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625525&prj=603&rqi=EkpdkGaXjJD2KvXXmUG32Fvzxx
GI-106 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-11 04:00:00.000 +0400 | TRN - Trane |  | Commissioning Issue | Commissioning | [6 empty] | Trane site technician placed the HMI into STOP mode without notifying anyone. This caused the Chiller to not operate correctly (Compressors failed to start when required). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624896&prj=603&rqi=Eu8amRdEBYv5jcKvTkMHdZ2652
FPT-366-001 | DX03-2 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-06-09 04:00:00.000 +0400 | ABEC - DCOS | L4 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1-STS-E-1 | STS - Static Transfer Switch |  |  | Observed the Kw reading not matching actual output kW on STS graphic. output side of STS and STSSB not energised (white) line. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624634&prj=603&rqi=0pXwHdJjloJUQnijRNbCSNVqu6
GI-105 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-06 04:00:00.000 +0400 | VER - Vertiv |  | Labelling | Commissioning |  | equipment type |  |  |  |  | UPS labels to be corrected. 415V not 400V | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624283&prj=603&rqi=QLhMJGNeBSzKBwKWZzm0Bf5bwF
GI-103 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-05 04:00:00.000 +0400 | CMM - Cummins |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | During UPS level 4 testing, while on Generator source it was observed at both the Generator controller and DCOS the Power factor and the KVAR were reporting 'out of range' at the DCOS. The Power factor was showing a negative power factor. The readings at the Generator ACB on the MSB were found tpo be reading correctly. it is noted that the load bank from DX3.1 is a resistive LB and there is also live loads on the MSB Output board (CRT SMDB). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624126&prj=603&rqi=QoEHeNok60EJvO3hKjgNxEQuLd
GI-098 | DX03-2 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | ABEC - DCOS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | DCOS LCP Templates are BLANK. This is applicable to ALL DCOS LCP panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623891&prj=603&rqi=Mkxb0honPuCRXCA2g4T1kbxYjD
GI-102 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Battery cabinets (D, E & F) Cores 1 & 2 Labels to be corrected after cable orientation swap. ALL UPS battery cable labels to be corrected also. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623896&prj=603&rqi=9JVEoQnPRBF6xNu3qZqGb7vlyg
GI-099 | DX03-2 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | ABEC - DCOS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | DCOS Generator Template 'Deviation from set point'Was shown as Voltage instead as Percentage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623892&prj=603&rqi=p8394l8N9ygFkEUass7VNVVevz
GI-096 | DX03-2 | S-EMEA | Closed | P2 Medium DCOS | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | Chiller Valve (located at the return to the chiller) was closing when the Chiller compressors switched off. this was causing the chiller to shutdown on Evaporator no flow alarm'. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623878&prj=603&rqi=5vGPhvy7TWfzn2n0aUeAaHLLi7
GI-100 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Graphics Issue | DCOS | [6 empty] | UPS High Alarm limit incorrectly calculated on the DCOS Template (80%). Value inputted on the template is 2250, this should be 1780. These were corrected for UPS-D & UPS-E level 4 testing, however it has been observed these have reset to the incorrect values. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623893&prj=603&rqi=qpkhpOw00ZhOSS1uNX2bs2GQu8
GI-101 | DX03-2 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | ABEC - DCOS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | DCOS footer/banner missing Values from DX3.1 weather station including the OAT, OAH, OAWB, DX3.2 PUE value and Fire alarm status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623894&prj=603&rqi=odIrsCE7DastQLDkwctCJSeVBb
GI-097 | DX03-2 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | ABEC - DCOS |  | DCOS Comms Issue/ Fault | DCOS |  | equipment type |  |  |  |  | CHWS no/low flow observed across the system during UPS Level 4 testing (DCOS Cx is ongoing for valves and sensors) after the Data Hall CRAH were started up. In the off positions the CRAG PICV are held in 100% open position. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623883&prj=603&rqi=yE03tPbhe0pmsIl8W9Em6q62ZZ
GI-092 | DX03-2 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-05-22 04:00:00.000 +0400 | Consultant |  | General Design Issue | Design |  | equipment type |  |  |  |  | CHWP supply MCCB at the MSB is furnished with an ELR with trip function. Is this necessary? During the UPS-D level 4 testing we observed that CHWP-D tripped on earth leakage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622809&prj=603&rqi=1ftPLppnsNg4cNqoE86VTAu39u
GI-090 | DX03-2 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/ Equipment failure | Commissioning |  | equipment type |  |  |  |  | During the inspection of Generator D, it was observed that when a low fuel alarm is triggered, fuel is pumped not only to Generator D but also to Generator E&F. This is not compliant with the intended operation, as each unit should function independently. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622466&prj=603&rqi=mfPVurqwYqEqwduAUrQu8rIdh6
GI-089 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/ Equipment failure | Commissioning |  | equipment type |  |  |  |  | When switching the fuel system from Auto to manual the system operates fine. When switching from Manual to Auto Vendor is advising us that the PLC requires a re-boot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622465&prj=603&rqi=wd8J3hRtYezV37BIXq6nxpwnOP
GI-088 | DX03-2 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-05-18 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | The MSB Breaker settings to be secondary tested based on the latest revision LV Coordination study. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622195&prj=603&rqi=bsk9hkQb03jrJ7bkokai8kQJw7
GI-087 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Mimic on the panels for the castell key operation to be corrected (this was observed during L2 testing and has been recorded on the Cx meeting from 5th Februrary. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621769&prj=603&rqi=BUP9IT1paO2BvntPT7FNy4fE3V
GI-086 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-05-12 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | LVBR Specification section #23 'Aux Power supplies'. The sequence upon losing PS1 & PS2 then rebooting to PS3 upon receipt of Generator is not working correctly as the HMI moves to Maintenance Manual mode and locks out (requires manual resetting and no aut transfer can occur. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621252&prj=603&rqi=vRxB4CQUz6a9EGwdAWysTP4faW
GI-084 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-05-09 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Component/ Equipment failure | Commissioning |  | equipment type |  |  |  |  | MSB-LVBR PSU with an inverted signal providing a DC alarm at HMI and to DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621038&prj=603&rqi=cpPAHZSzSUZhVx9yK9X1NmlsmT
GI-081 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-05-05 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning | [6 empty] | FUTURE LIQUID COOLING CHW LINE IN 1st floor Data Hall (1 No.) near CRAH-48: A minor clash was observed between 1 isolation valve handle and the DRV handle. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620388&prj=603&rqi=lVGgv8IXhKSOaYb9zGeb9EnRrD
GI-074 | DX03-2 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Battery cables from UPS to Battery found to have been terminated in the incorrect battery cubical which do not correspond with the correct UPS_Cores. although this does not impact the operation of the UPS, this does not align with the design arrangement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619061&prj=603&rqi=FuetrnKPabv6KahfgV00KYfEHY
GI-073 | DX03-2 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-04-21 04:00:00.000 +0400 | VER - Vertiv |  | Component/ Equipment failure | Commissioning |  | equipment type |  |  |  |  | Advised by the GC & Vertiv during UPS L3 commissioning the UPS PCB requires replacement (applies all 3 UPS).. Vertiv toi confirm to provide a report and advise what the cause of the issue was. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618820&prj=603&rqi=bzQsUKwpgem9Wqt4sw6sJTlhJs
GI-072 | DX03-2 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-04-14 04:00:00.000 +0400 | General Contractor - Commissioning |  | Incomplete Connections | Commissioning |  | equipment type |  |  |  |  | Incoming earth cable is not connected to the outgoing side of the isolator. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618106&prj=603&rqi=JsspH944u9giQuP22Wpqe8CNz6
GI-067 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-03-26 04:00:00.000 +0400 | CMM - Cummins |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Generator enclosure DB labelling in the field for circuits are incorrect and do not provide the circuit reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616551&prj=603&rqi=X2t2Kpg5nYzxI6lGraMc0nkcva
GI-066 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-03-26 04:00:00.000 +0400 | Equinix Design Engineer |  | General Design Issue | Design |  | equipment type |  |  |  |  | During Level 3 STS Start up, during total maintenance bypass (Bypass is energised but the STS including the HMI is shut down) there is no indication on the STS breakers/isolators (other than S2 MCCB LED) that there is LIVE power passing through the busbar, or any interlocks (doors, panel covers etc..The busbar is exposed within the panel as there is no isolation between panel sections of the STS. This is seen as potential safety risk hazard during maintenance activities. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616535&prj=603&rqi=24XWPbjAsgZhwGEN5af5HEomDz
RT1ELEC-586-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-26 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1-GSM-RACK-02 | CAB - ICT Cabinets |  |  | GSM Rack-02: At the top of the GSM rack where the fiber optic cables enter into the rack, there is no brush type cover. There is a risk of dust and debris falling into the rack through this cable penetration hole. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616506&prj=603&rqi=MqPc0eaekATwER1mnQagf7Yxrz
GI-060 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning |  | system | CHW System |  |  |  | It was observed that there was no chilled water flowing through the CRAHs in 1st floor electrical rooms (switchrooms and STS Rooms string D & E). Contractor needs to investigate the issue on site and provide a reason for no chilled water flow based on their observations at site. Please see attached some photos from the CRAH HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616268&prj=603&rqi=JNrvMcPEsAyQDNL3BqDESn0s4e | https://equinix.facilitygrid.co.uk/x/project/603/system/12115
YT1SEC-1-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-03-18 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not complete | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-C | ACU - Access Control |  |  | During ACP-01-NER-C inspections, it is noted the doors on Buffer Vessel Room (1331-B, 1331-C, 1331-D, 1331-E) and Future ETS Room (1351-B) are not aligned, preventing the completion of ACS device installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615932&prj=603&rqi=Ecd2Bp6dkQKDfrUWcjxcVtx7bj
YT1ELEC-557-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | B2-ODF 4 | CAB - ICT Cabinets |  |  | The cable tagging inside B2-ODF-04 rack in DX3.2 FER-C is incorrect. Refer to attached photo for details. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615714&prj=603&rqi=NE3kuyZcXNrNPE7tzV5haBPqWy
YT1ELEC-143-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-03-16 04:00:00.000 +0400 | Low Voltage Electrical Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1-RPP-F-8 | RPP - Remote Power Panel |  |  | 1-RPP-F-8 Drawing pocket missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615708&prj=603&rqi=JbWUntnCn1F8uxKaJj1jg6YIzt
YT1SEC-3-003 | DX03-2 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-03-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not complete | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-E | ACU - Access Control |  |  | Access control panel ACP-01-NER-E: The door between 3.1 and 3.2 has not been installed, resulting in the installation of acs device remain pending. This issue is raised to record this and allow a conditional yellow tag to be applied. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615408&prj=603&rqi=I3GQFfq7u7fT3WFl23gJxlC1Uu
GI-055 | DX03-2 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-03-10 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | DCOS Installation not complete | DCOS |  | equipment type |  |  |  |  | During DCOS P2G testing it was observed that when the ACB on the MSB were racked to the test position then retuned to Service, these remained in the 'test' status showing on the DCOS Graphics. SAS Site team confirm that Modules for the ACB are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615250&prj=603&rqi=RbgkNxdTWhvB8CJ4vmu8Hrpm9H
YT1SEC-3-002 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-E | ACU - Access Control |  |  | ACP-01 NER-E: FF ELECT ROOM has no label on door Motorised lock. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615247&prj=603&rqi=Vzpvk7t25MF0VYphQK3QzRx5JH
YT1SEC-4-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Documentation not issued/ Required | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-F | ACU - Access Control |  |  | FOR ALL Access Control Panels: The related shop drawings (Schematic, Layouts and panel wiring diagrams) need to be updated as per site condition then uploaded officially to ProCore for approval. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615200&prj=603&rqi=1vg7yfNSAxZdTeMbab9P4gf0mo
YT1SEC-3-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-E | ACU - Access Control |  |  | Access control panel ACP-01-NER-E L2B inspection: No continuity observed on cable from ACP-01 NER-E panel to STS Room E motorized lock (EM). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615246&prj=603&rqi=jjx4VxQO2tUzUQ5J6WiC8em66K
GI-057 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-03-10 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | ALL MSB PQMs used for monitoring the Transformer points have not been configured at the factory. this has impacted the Transformer L3 testing, | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615252&prj=603&rqi=dYulJ6SJW1NodRa2CTQTDurrKt
YT1SEC-2-002 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not complete | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-D | ACU - Access Control |  |  | Access control panel ACP-01-NER-D: The junction box cover is missing for the door to STS Room G (1100A). Also ensure junction box cover has the correct tag label. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615117&prj=603&rqi=GDTA7Iwtb9uxl6I6m3zitglNgE
YT1SEC-2-004 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-D | ACU - Access Control |  |  | Access control panel ACP-01-NER-D L2B inspection: One of the door contact devices for the door of MMR-D (1081A) is damaged and needs to be replaced. Cable continuity test to be carried out after new door contact. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615119&prj=603&rqi=VlsEiWKVdePHtLo7QOu3yj6cxy
YT1SEC-2-003 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-D | ACU - Access Control |  |  | ACP-01-NER-D L2B inspection: No cable continuity observed for door contact of GF Data Hall door B (1500 B). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615118&prj=603&rqi=rz9S8gbpoifNvqDWSZmPEOxCbc
GI-049 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-04 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-F | ACU - Access Control |  |  | ACP-01 NER-F: Labelling on junction box above FF Data Hall Door C is pending. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614689&prj=603&rqi=n0KZUs7bm5zNjFiB00raT1IFPN
GI-048 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-03-03 04:00:00.000 +0400 | Equinix Design Engineer |  | General Design Issue | Design |  | equipment type |  |  |  |  | AHU - Air Handling Unit: It is observed there is no Humidity control via a Heater battery or any other physical device within the AFU/MAU's. There us a concern with the high humidity in the region the unit will not provide dehumidification efficiently. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614606&prj=603&rqi=NHpPWwBIErzQFIidWzZbL1eIH0
GI-047 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-02-26 04:00:00.000 +0400 | TRN - Trane |  | Incomplete Connections | Commissioning |  | equipment type |  |  |  |  | Chillers: Although torque marked, manufacturers earth bar connections was found to be loose (checked with hand) and requires tightening. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352229&prj=603&rqi=J6C2puLmRt3aKJ9S8OjUx2Rlsq
YT1SEC-2-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-02-25 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning | Electronic Safety and Security | equipment | ACP-01-NER-D | ACU - Access Control |  |  | Access control panel ACP-01-NER-D: During L2B Cable Point to Point inspection on 25th Feb 2026, it was observed that the cable connecting to the door contact in Battery Room F was damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212851&prj=603&rqi=pHaJRMH3POdFBvQKwGE2KjzjFo
YT1ELEC-540-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | m.louie@core-group.me | 2026-02-20 04:00:00.000 +0400 | Low Voltage Electrical Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1-PFC-E | PFC - Power Factor Correction |  |  | 1-PFC_E isolator rotary handle is missing. PFC cannot be safely energised with this missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199672&prj=603&rqi=idXNH3SygduN5TjvnMDFTipIcG
GI-042 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-02-19 04:00:00.000 +0400 | Consultant |  | General Design Issue | Design |  | equipment type |  |  |  |  | Exhaust fans (EF) are not interfaced with the fire alarm system and therefore do not shut down in fire. This has been confirmed by the desing team and general contractor. Concern that ducts and fans are not fire rated and the risk of transerring smoke through adjacent fire zones and cause fires in adjacent areas. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199546&prj=603&rqi=mW2lomkOM7B9SSvS6HowisEpJE
GI-041 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-02-18 04:00:00.000 +0400 | SOC - Socomec |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | LOTO provisions missing from all STS source 1 isolator. The padlock accessory for the isolator has not been provided or fitted. This does not allow the STS to be fully locked off under the approved GC LOTO procedures. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199456&prj=603&rqi=5qgNfauIIU7ARAvUAvdxd1pMfa
GI-040 | DX03-2 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-02-17 04:00:00.000 +0400 | General Contractor - Commissioning |  | Cleaning | Commissioning |  | equipment type |  |  |  |  | Red rust was observed inside the CRAH on the CHW pipe supports. In addition, white rust was observed on the internal side walls of the CRAH. Refer to attached photos for reference from CRAH-F-E-59 in Switchroom F. This has been discussed with Equinix and Vertiv . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199350&prj=603&rqi=ahfNFfXeCWEjnksteeGuQWSPz5
YT1ELEC-559-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-02-13 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | B2-GF-SEC-RACK-02 | CAB - ICT Cabinets |  |  | B2-GF-SEC-RACK-02 door lock is damaged and unable to close. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199206&prj=603&rqi=UXwIAmLs58VtcFp9cCkyGvTUCD
GI-035 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-02-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Incomplete Connections | Commissioning |  | equipment type |  |  |  |  | All RMU incoming VT's were left in the open position which was picked uop during DEWA energisation. As per Se email dated 10thy februray RMU are safe to energise with the VT in the out of service position. PMU currently not measuring Voltage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199221&prj=603&rqi=b2k389ti0ZIHuLLylaMbppXfsw
YT1ELEC-560-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-02-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | B2-FF-SEC-RACK-01 | CAB - ICT Cabinets |  |  | During white glove inspection for B2-FF-SEC-RACK-01, it is observed the body of the Rack has been sprayed with gray paint to cover scratches/defect. The finish is poor and to be addressed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199146&prj=603&rqi=kFXiSjSln6jbmvJ59Fg0jPlMRM
GI-031 | DX03-2 | S-EMEA | Closed | P2 Medium CX | v.baddegama@core-group.me | 2026-02-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1-RPP-F-4 | RPP - Remote Power Panel |  |  | The earth bar inside all RPP's are missing provision (holes) for terminating earth cables. Refer to attached photo as a reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198852&prj=603&rqi=TAwmdu0zL9dhWWOEvf1GHClJ3O
YT1ELEC-532-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-02-06 04:00:00.000 +0400 | SOC - Socomec | L2B | Component/ Equipment failure | Commissioning | Electrical â€“ LV | equipment | 1-STS-F-2 | STS - Static Transfer Switch |  |  | STS-F-2 top cover showing deflection/damage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198684&prj=603&rqi=fUSdvQpjIrxXRg6mHoz37YlRJG
GI-029 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-01-30 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Component/ Equipment failure | Commissioning | Electrical â€“ LV | equipment | 1-PFC-F | PFC - Power Factor Correction |  |  | PFC-F Blue phase LED cover damaged/missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198054&prj=603&rqi=n2r40GumafFsFFPigWv5yG57WE
YT1ELEC-530-001 | DX03-2 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-01-20 04:00:00.000 +0400 | SOC - Socomec | L2B | Component/ Equipment failure | Commissioning | Electrical â€“ LV | equipment | 1-STS-E-1 | STS - Static Transfer Switch |  |  | STS door lock is faulty (not locking) and requires repair/replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197135&prj=603&rqi=3yb0RrKTAAGw5fhlKSk6GVEvci
GI-018 | DX03-2 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-01-06 04:00:00.000 +0400 | SCH - Schneider MV |  | General Design Issue | Design |  | equipment type |  |  |  |  | RMU Cannot be fully isolated (for LOTO pruposes). A cover has been provided on the mechanical ''On'' button only and not for the 1 - Earth switch (separate issue) 2 - CB on/off, Disconnector on/off by local pushbuttons or 3 - The remote pendant. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196386&prj=603&rqi=UwKzwtRd1hh31HCMYmN8XfgUCw
GI-017 | DX03-2 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-01-06 04:00:00.000 +0400 | SCH - Schneider MV |  | General Design Issue | Design |  | equipment type |  |  |  |  | All RMU's Earth switch are not furnished with Locking devices. This deviates from Equinix design standards for MV Switchgear/RMU. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196385&prj=603&rqi=3GNHJrY3aJnqUCZMemOQB8rlWy
GI-005 | DX03-P1 | S-EMEA | Open | P2 Medium CX | n.forde@core-emirates.com | 2026-09-17 04:00:00.000 +0400 | TRN - Trane |  | Cleaning | Commissioning |  | equipment type |  |  |  |  | During the red Tag inspection it was observed the pipework within both Trane chillers will require flushing (more than back flushing) due to the rust observed. (The same was observed from the Trane chillers for DX031). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638476&prj=699&rqi=CwLBF6kVF60vKWst5qFPKTRf7t
GI-004 | DX03-P1 | S-EMEA | Open | P3 Low CX | n.forde@core-emirates.com | 2026-09-15 04:00:00.000 +0400 | SOC - Socomec |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | STS are missing LOTO provisions on Q41 isolator (Source 1 Primary supply). This issue applies to ALL 4No STS supplied to DX3.P1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638274&prj=699&rqi=4LoMFpyMxb8iZ82GBcSqJaXT3g
RT1ELEC-54-001 | DX03-P1 | S-EMEA | Open | P3 Low CX | c.castro@core-group.me | 2026-09-11 04:00:00.000 +0400 | Low Voltage Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1-MSB-G | MSB - Main Input Switchboard |  |  | 1-MSB-G EKIP power supply modules are missing for 11Q1 and 12Q1 breakers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637733&prj=699&rqi=bhxuWAfFGAPzzVKDexgBIDRvwl
RT1ELEC-35-001 | DX03-P1 | S-EMEA | Open | P3 Low CX | c.castro@core-group.me | 2026-09-09 04:00:00.000 +0400 | SCH - Schneider MV | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1-BTU-RMU-H | BTU - Battery Tripping unit |  |  | 1-BTU-RMU-H panel Door limit switch found damage (switch is bent). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637473&prj=699&rqi=XdsdO19A9WVghTG7DThf7KTcIg
RT1ELEC-76-001 | DX03-P1 | S-EMEA | Open | P3 Low CX | c.castro@core-group.me | 2026-09-09 04:00:00.000 +0400 | Low Voltage Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1-RPP-H-1 | RPP - Remote Power Panel |  |  | 1-RPP-H-1 controller SCU100 is missing / not installed within the RPP. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637474&prj=699&rqi=dZqtHvLCPZXfj18Eep1guuIGcx
RT1ELEC-55-002 | DX03-P1 | S-EMEA | Open | P3 Low CX | c.castro@core-group.me | 2026-08-24 04:00:00.000 +0400 | Low Voltage Electrical Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1-MSB-H | MSB - Main Input Switchboard |  |  | 1-MSB-H: The door of 6.3 Q1 in cubicle 6 is not properly fitted to the breaker. A gap is visible between the door and the breaker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634881&prj=699&rqi=TuswMjEqAqMIhsoh6cKC03o65f
GI-003 | DX03-P1 | S-EMEA | Open | P3 Low CX | l.drake@core-group.me | 2026-08-13 04:00:00.000 +0400 | VER - Vertiv |  | Cleaning | Commissioning |  | equipment type |  |  |  |  | White rust was observed on the internal side walls of the CRAH. Refer to attached photos for reference taken from CRAH's 1-CRAH-G-F-55 1-CRAH-G-F-56 1-CRAH-G-F-57 1-CRAH-G-F-58 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633590&prj=699&rqi=2Ul9jVubgQGJZ2fqtn0LRmXKRG
GI-002 | DX03-P1 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-08-12 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1-MSB-H | MSB - Main Input Switchboard |  |  | MSB-H ACB serving STSSB-H-2 is missing its' ABB EKIP Module (Complete module including Comms and power modules). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633404&prj=699&rqi=L78U62SLVbkMHHDSr5Ea5CDC8C
GI-001 | DX03-P1 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-08-12 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1-MSB-H | MSB - Main Input Switchboard |  |  | MSB-H section 6.3Q MCCB (including handle) is missing. It appears the panel has been delivered to site with this component missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633403&prj=699&rqi=iXxK5Ho5be5DDznMd03K94NcHi
RT1ELEC-55-001 | DX03-P1 | S-EMEA | Open | P3 Low CX | g.madulid@core-group.me | 2026-08-05 04:00:00.000 +0400 | Low Voltage Electrical Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1-MSB-H | MSB - Main Input Switchboard |  |  | MSB-H Cubicle 9 and and 10 plinth damage/deformed. The damage is preventing remove of the panel cover als0. . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632271&prj=699&rqi=JrRVVYsjs6N0dkaxmt6zYhB2ri
GT1ELEC-147-001 | FR08-3 | N-EMEA | Closed | P1 High CX | jyusufi@global-cxm.com | 2026-08-31 04:00:00.000 +0400 | SOC - Socomec | L3 | Installation Not Correct | Commissioning | Electrical â€“ LV | equipment | 1_STS_N_2 | STS - Static Transfer Switch |  |  | During Energisation the bolt losed and had a direct contact with the busbar which caused an ARC Flash incident. The Unit needs to be replaced or all the Parts within mentioned Area needs to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636058&prj=630&rqi=D3KNZFM0YJ0KCBEzno6cMID4rU
GI-091 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-08-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1_STS_N_1 | STS - Static Transfer Switch |  |  | on STS N1 the Lock on the Door handle is defective Broken. needs to be replaced. The Door is bended | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634877&prj=630&rqi=YuCwt4wWwyQkHwR9xrVbgIU3Fa
GI-092 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-08-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1_STS_N_2 | STS - Static Transfer Switch |  |  | plates on Top of STS N2 has been bended / Damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634878&prj=630&rqi=0GVUqaa8P9PTkCt40EwRJ6wGTU
GI-090 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-08-07 04:00:00.000 +0400 | VER - Vertiv |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_UPS_K | UPS - Uninterrupted Power Supply |  |  | Batteries UPS K showing constant charge mode. Core 1 Right | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632694&prj=630&rqi=p6SZ8zieK8xnXCGdjrhUgFcmcQ
GI-089 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-08-07 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_STS_J_1 | STS - Static Transfer Switch |  |  | power factor incorrect on STS J | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632693&prj=630&rqi=MzEyOpYS3e2IyIAZgOAVAVwUEO
GI-087 | FR08-3 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-07-30 04:00:00.000 +0400 | Design Professional |  | Design Correction Needed | Design | [6 empty] | When utilitly failure and generator supply takes over, it takes 20 seconds for generator supply to take over. This generates AFD unhandled fault, comm loss AFD, AFD bump complete alarms on the chiller and shuts it down and they have to be manually reset. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631420&prj=630&rqi=CyuKPmKkC5U9D6LMGkB00NWI9l
GI-086 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-07-27 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1_CWST_10_CWP_J_2 | CWP - Chilled water pump |  |  | Leak on motor shaft going into the impeller on the primary pump in PPR10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630888&prj=630&rqi=YhaA1HCbXeKcStQz6NpX5ZkfDJ
GI-084 | FR08-3 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-07-27 04:00:00.000 +0400 | VER - Vertiv |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1_BATT_M3_01 | LIBATT - UPS Battery |  |  | UPS M3 Battery cabinet 1 needs to be replaced. During snag remediation works on battery cabinet 7 of the UPS M3, a short circuit occurred, which resulted in the need to replace the cabinet, the MCCB, the AC power supply module, internal communication cables and a cable for the fan exhaust | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630839&prj=630&rqi=SVArLscOZrbGCOvUFxbhdUvw2z
GI-085 | FR08-3 | N-EMEA | Closed | P2 Medium CX | drobertshaw@global-cxm.com | 2026-07-27 04:00:00.000 +0400 | VER - Vertiv |  | Installation Damage | Commissioning | [6 empty] | UPS K Battery K - 10 MCCB needs to be replaced. During a site walk, Mercury and Global Cx brought to my attention that there were black soot marks visible on the MCCB breaker in battery cabinet 10 of UPS K. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630880&prj=630&rqi=wJ4DdILvpFRZ5zvd6jgc37AeL8
RT1ELEC-148-001 | FR08-3 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-07-07 04:00:00.000 +0400 | SOC - Socomec | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1_STS_N_1 | STS - Static Transfer Switch |  |  | Damage to door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628147&prj=630&rqi=sY7g880nu0CCyGop8wVNok1g1L
GI-081 | FR08-3 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-07-03 04:00:00.000 +0400 | VER - Vertiv |  | Component/Equipment Failure | Commissioning | [6 empty] | UPS M3 - The issue with M3 occurred during the transient tests on the generator. No hardware faults were detected on the UPS. This behaviour is likely related to the interaction between the UPS and the generator, as the transient tests on the mains supply and all other tests were completed without any abnormalities. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627799&prj=630&rqi=D9cdhmvWkkZ8rXlcAR6Mp6JgmE
GI-080 | FR08-3 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-07-03 04:00:00.000 +0400 | VER - Vertiv |  | Component/Equipment Failure | Commissioning | [6 empty] | UPS H core 2 does not allow to go on battery autonomy. when you isloate the other cores on the UPS to perfom battery autonomy on that one core as soon as load is applied to the core while on battery the core goes offline. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627798&prj=630&rqi=eUyBGZXg4C6SAhqRiH1glRgAmC
GI-079 | FR08-3 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-06-19 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design | [6 empty] | MSB Y x 1 250A breaker with neutral protection to be investigated. Breaker Q13 in panel MSB Y is a 3-pole MCCB and does not include neutral functionality. According to the engineering design by Anord Mardix and approved by RHK and Equinix, Q13 is configured accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626208&prj=630&rqi=PqkF2v1PgjcIPd3TtEADYhDL42
GI-076 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1_STSSB_L_1 | STSSB - Static Transfer Switchboard |  |  | Covers / Plate is missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624755&prj=630&rqi=Nob2Vmp5JujXMWORKi2LOGfKeN
GI-071 | FR08-3 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | SOC - Socomec |  | Component/Equipment Failure | Commissioning | [6 empty] | STS in PPR 12. Went into fault due to back feed alarm causeing the output to open. STS was on S1 bypass, S1 has been seen as an unhealthy source STS has then tried to switch to S2 while S1 bypass is still engaged. Socomec to investigate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624685&prj=630&rqi=OxXjNUYsbZtabAQ5qkFdlGnO54
GI-077 | FR08-3 | N-EMEA | Closed | P2 Medium CX | drobertshaw@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [6 empty] | Transformer for the chiller control panel has failed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624778&prj=630&rqi=B4ZUsXynhrFbe9MaudUIEzj8KV
GI-072 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1_STSSB_L_1 | STSSB - Static Transfer Switchboard |  |  | Covers / Plates are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624724&prj=630&rqi=5WnCNU0Lwz4CBaOjxyeyO6bv3S
GI-070 | FR08-3 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | VER - Vertiv |  | Component/Equipment Failure | Commissioning | [6 empty] | UPS K core 2 Rectifier / Inverter module PH.V failed when load is applied. This needs to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624672&prj=630&rqi=B4x2gG9EIK9MH8E1JKt2kgmqaH
GI-073 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1_STSSB_L_2 | STSSB - Static Transfer Switchboard |  |  | Covers / Plates are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624726&prj=630&rqi=x0APTDXGe3V3e4Lu53c2ItqYLk
GI-075 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1_STSSB_L_4 | STSSB - Static Transfer Switchboard |  |  | Covers / Plates are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624728&prj=630&rqi=XKiTHGMa69PvkyTW0yJeBBOL31
GI-074 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1_STSSB_L_3 | STSSB - Static Transfer Switchboard |  |  | Covers / Plates are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624727&prj=630&rqi=0lSnrhuapJKEhfCaRvKbZYUx6d
GI-068 | FR08-3 | N-EMEA | Closed | P2 Medium CX | drobertshaw@global-cxm.com | 2026-06-09 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Component/Equipment Failure | Commissioning | [6 empty] | MSB R3 Q2 breaker chasis needs to be replaced. The winding mechanism has been turned to far and put stress on the internal gears causing the failure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624449&prj=630&rqi=TRmPsHick5F9Zhhsv6Cz9aAl7c
GI-069 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-09 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1_CWST_12_DC_K_1 | HDAC - Hybrid Dry Air Cooler |  | HTK 3.24/10.9-2S-P4-CU-SLNF | Water distribution over the coils on the HDAC. On PPR 12 if stood facing the HDAC the right side of the unit is performing far better than the opposing side. need confirmation from Jaeggi if balancing has been done and if not, does the water distribution affect the WET mode of the HDAC which also affects performance in WET mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624480&prj=630&rqi=wxPxXufwE5dFuDmM6d6b5W7jLF
GI-051 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | [6 empty] | Glycol sensor on HDAC 10 needs to be replaced. Vortmann advised it will be done next week | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623807&prj=630&rqi=fP423sLAGYu9Le5eCoTCG0kgWF
GI-061 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1_CWST_10_CWP_J_2 | CWP - Chilled water pump |  |  | Leak on primary pump in PPR 10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623822&prj=630&rqi=TF8KNMhB2yfJTBEAm2fHpzrG5Q
GI-053 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | Leak on TT09 in PPR10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623812&prj=630&rqi=c113YC9vQXAmKZvS178a5vO8ee
GI-054 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | PPR 09 Leak on Overpressure valve (near to TT05) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623813&prj=630&rqi=FrfMuUyvRmUQY2N8s4sCUfQBGF
GI-065 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | Leak on Temperature gauge in PPR08 near Primary pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623826&prj=630&rqi=qjoeJBljPlKckKVUEUNitQJvwg
GI-062 | FR08-3 | N-EMEA | Closed | P2 Medium CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | Leak on PPR 08 condenser pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623823&prj=630&rqi=BYtJdaqH7NmdlB6qMY3Hp4ZuXo
GI-066 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | Leak on TT08 in PPR08 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623827&prj=630&rqi=EYBZDPyhV2p2YPMSWofOpsOc72
GI-056 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | PPR 12 leak on PICV 01 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623816&prj=630&rqi=m0Mvkv7y6LtpMjp0VESJYkaJQ1
GI-060 | FR08-3 | N-EMEA | Closed | P2 Medium CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1_CWST_10_CWP_J_1 | CWP - Condensator Water Pump |  |  | Leak on Condenser pumps in PPR10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623820&prj=630&rqi=WtPD4bWOC1y0wYNPHPouSg5sCr
GI-059 | FR08-3 | N-EMEA | Closed | P2 Medium CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1_CWST_15_CWP_H_1 | CWP - Condensator Water Pump |  |  | Leak on condenser pump in PPR15 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623819&prj=630&rqi=fzs3hRROkXbk1BVNb2UiXFp8aH
GI-052 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | PPR 09 TT10 - shows incorrect value when chiller is running. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623809&prj=630&rqi=rwupTKyQtIWlPt7ivrolPeolNA
GI-050 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | [6 empty] | UV lamp defect on Jaegii HDAC PPR 10 HDAC 10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623806&prj=630&rqi=l9ucxhWpax2GLkNZHu8OaVoqHP
GI-058 | FR08-3 | N-EMEA | Closed | P2 Medium CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1_CWST_12_CWP_K_2 | CWP - Chilled water pump |  |  | PPR 15 - Leak on the airvalve on the primary pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623818&prj=630&rqi=CXipgOOPZjLbNGDq1gU738INDV
GI-055 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | PPR 08 Leak on PICV 01 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623814&prj=630&rqi=fNZ8PaQzWd1Hez7pGs1FQb259I
GI-063 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | Leak on TT05 in PPR 15 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623824&prj=630&rqi=aeQEeWIwSPsmco3sGMzmRfXAQ8
GI-057 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | PPR 09 Power socket not live in the CGM | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623817&prj=630&rqi=BKWfR3gvysYyJf6H87fWdAn0IP
GI-049 | FR08-3 | N-EMEA | Closed | P2 Medium CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | [6 empty] | UV lamp defect on Jaegii HDAC PPR 09 HDAC 09 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623805&prj=630&rqi=Wi2j2c9Nx12S4LxNcksMBROFXQ
GI-067 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | Leak on drain off valve below the bypass near the heat exchanger in PPR 09 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623828&prj=630&rqi=IAnMSArYgjJhoa98eyjO6ia1bo
GI-064 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [6 empty] | Leak on Temperature Gauge in PPR15 near to TT07 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623825&prj=630&rqi=kGif4qF7X1zYeLXYNZ8EcLVSZK
GI-048 | FR08-3 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-05-22 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Not Correct | Commissioning | [6 empty] | Data Hall CRAH communication cable had been squeezed too tightly to the tray. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622778&prj=630&rqi=Qw3WRdEWbiNsMdevbYByTtRVQa
GI-045 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Torque required | Commissioning | Electrical â€“ LV | equipment | 1_UPS_Y | UPS - Uninterrupted Power Supply |  |  | DC battery cables are not double torque-marked. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622399&prj=630&rqi=4GUsbLcn7WGAtEvfbT9FTr0pCH
GI-040 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Torque required | Commissioning |  | equipment type |  |  |  |  | Torque marks are not valid, as the cables have not been properly torqued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622394&prj=630&rqi=WHpR9T8Cn1kqGekVBTFjtCxAcl
GI-041 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Cabinet door earthing cables are either missing or damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622395&prj=630&rqi=qyfcSvTjOyEAYSR7oBpUFZUBQW
GI-042 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | On Cabinets 1 and 6, the DC cables are under tension. Please refer to the attached pictures. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622396&prj=630&rqi=spUD8jA6NHQEITYOB3C50oX2hF
GI-039 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | On all battery cabinets, the covers are either damaged or missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622393&prj=630&rqi=upa3yeiJIEMK4ZjoAjWAYkbB0V
GI-044 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1_GCP_Y | CP - Control Panel (Generator) |  |  | End clamps are missing for the complete breaker series, resulting in breaker movement and insufficient securing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622398&prj=630&rqi=Ca4nj9nfyDO1rCmy8qBUfchS3O
GI-047 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1_UPS_Y | UPS - Uninterrupted Power Supply |  |  | Covering plates are missing. The Plates under the MSB / UDP are opened and they needs to be closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622402&prj=630&rqi=rtAr2l78NymVYaDLpDjGVeCKO3
GI-043 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | Electrical â€“ LV | equipment | 1_GCP_Y | CP - Control Panel (Generator) |  |  | Bone tags are missing on several internal and external cables. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622397&prj=630&rqi=PDy3t7dbUXD5sK4zhf9jiVNXsP
GI-046 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Correct | Commissioning | Electrical â€“ LV | equipment | 1_UPS_Y | UPS - Uninterrupted Power Supply |  |  | Cables are under tension. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622400&prj=630&rqi=gXLj0cTfnLC9KjW1w3gH6kzNxR
GT1ELEC-185-001 | FR08-3 | N-EMEA | Closed | P3 Low CX | tgates@global-cxm.com | 2026-05-13 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1_STS_K_5 | STS - Static Transfer Switch |  |  | Asset reference to be changed on DCOS and evidence provided, DCOS states 1_STS_K_10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621728&prj=630&rqi=2YQV4NnzIx5DIkmupUe6sXXMcZ
GT1ELEC-184-001 | FR08-3 | N-EMEA | Closed | P3 Low CX | tgates@global-cxm.com | 2026-05-13 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1_STS_J_5 | STS - Static Transfer Switch |  |  | Asset reference to be changed on DCOS and evidence provided, DCOS states 1_STS_J_10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621713&prj=630&rqi=R3Sy5IKYkcCe6GKKMtg2MpYk01
GI-024 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1_CWST_08_CWP_L_2 | CWP - Chilled water pump |  |  | Armstrong pump - to be checked by Armstrong engineer regarding noise issues potentially with bearings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618830&prj=630&rqi=gxGqkrdvbsoH0Wnqixp7gNA90s
GI-023 | FR08-3 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1_CWST_08_CHWP_L_1 | CWP - Chilled water pump |  |  | Armstrong pump - to be checked by Armstrong engineer regarding noise issues potentially with bearings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618826&prj=630&rqi=jfyBNUGzEpKQWKWzhPhGPa983d
YT1ELEC-228-001 | FR08-3 | N-EMEA | Closed | P3 Low CX | tgates@global-cxm.com | 2026-04-09 04:00:00.000 +0400 | CMM - Cummins | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_GSB_R3 | GSB - Generator Switchboard |  |  | Shutters behind the ACB are faulty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617614&prj=630&rqi=Plbss1YKKCHzO06GMzTsW4kODr
GI-013 | FR08-3 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-04-09 04:00:00.000 +0400 | VER - Vertiv |  | Installation Not Correct | Commissioning | Electrical â€“ LV | equipment | 1_BATT_H_01 | LIBATT - UPS Battery |  |  | DC cableing for UPS batteys needs to be cleated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617606&prj=630&rqi=ISAw7O4ouPIIghAtOibZGsjUFD
YT1ELEC-222-001 | FR08-3 | N-EMEA | Closed | P3 Low CX | tgates@global-cxm.com | 2026-04-09 04:00:00.000 +0400 | Construction Manager | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_GCP_K | CP - Control Panel (Generator) |  |  | Earth bond on door needs to be re terminated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617648&prj=630&rqi=Xres0fqeZAHYr85IJiScRLD7pw
GI-014 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-09 04:00:00.000 +0400 | VER - Vertiv |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_BATT_H_09 | LIBATT - UPS Battery |  |  | Battery Cabinet DC Cable installation covers damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617664&prj=630&rqi=TZgQzrozbbZBInbGXsQmMG8617
GI-010 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_GCP_M3 | CP - Control Panel (Generator) |  |  | no bone tags on the Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617554&prj=630&rqi=zipDuDW9YVtcukDFbHO9xYDecr
GI-008 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_GCP_R3 | CP - Control Panel (Generator) |  |  | Cables are shorts and in tension according to VDE needs to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617550&prj=630&rqi=Z7dk1MYnlrBd5Y2uvQ6jAlGeGU
GI-011 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_GCP_M3 | CP - Control Panel (Generator) |  |  | Cable cover is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617555&prj=630&rqi=L1O45qBrkcrxWaFBpeVhfqpjaW
GI-012 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_GCP_M3 | CP - Control Panel (Generator) |  |  | GCP Door Handel is broken not functional | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617556&prj=630&rqi=m6LkExU42NEEMNztZhvhy5R0kz
GI-009 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_GCP_R3 | CP - Control Panel (Generator) |  |  | no bone Tags on the cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617551&prj=630&rqi=UCrWocLHGd1dSaBHV9FSbj93tY
GI-007 | FR08-3 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-03-26 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1_STSSB_L_2 | STSSB - Static Transfer Switchboard |  |  | 2 MCCB breeaeker handles damaged on site. Need to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616536&prj=630&rqi=9BcLhxcFrBCwQC4ol3HFElp8EL
GI-006 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-03-25 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Commissioning Issue | Commissioning | Controls | equipment | 1_HMI_J | HMI - HMI Panel |  |  | HMI J faulty software & not for the designed Board | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616354&prj=630&rqi=9yURk6DUNGm6Zc64orl8sIFJz1
GI-003 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-03-23 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | ARC Flash protection been broken / Damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616193&prj=630&rqi=kkhWr3vvr4MGCN5ZhNg117kM2z
GI-002 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-03-09 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1_EB_PPR_09 | ERTH - Earthing |  |  | FR8.3 STS L2B Armstong appear to have missed installing the Modbus TCP module ST300 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615124&prj=630&rqi=veANw6yycHv242U5jDe5M7aOXJ
GI-001 | FR08-3 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-03-05 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Commissioning Issue | Commissioning | Controls | equipment | 1_HMI_L | HMI - HMI Panel |  |  | Damaged HMI Display | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614804&prj=630&rqi=zjjnKE1nq50SMw9ALKbHqqxctO
GI-214 | FR10x-1 | N-EMEA | Closed | P2 Medium CX | cjjones@global-cxm.com | 2026-02-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | SUDB_3_Q07 - 1_MVTB_R2 (Q01) Incorrect circuit ref on torque report Torque report not signed Sign off dates incorrect | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=139154&prj=378&rqi=sdPa6qHsruSM3bQNdiTUzfjOLX
GI-001 | FR12-1 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1MVTB_C | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633605&prj=692&rqi=Moq4T0jUaDMal2KkY98Pn2ZWOz
GI-003 | FR12-1 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1MVTB_L | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633610&prj=692&rqi=7mTvgOjGH5btdLRDagnZTA2O9f
GI-005 | FR12-1 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1MVTB_M4 | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633612&prj=692&rqi=bn8LM5AttAybAVKxHM1HFWLhtN
GI-007 | FR12-1 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1MVTB_R1 | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633615&prj=692&rqi=O2KRYCcE1bSTs7uGBdhPSCf7tL
GI-006 | FR12-1 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1MVTB_N | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633613&prj=692&rqi=802Ieq9HEaBYxTUvM0fsTALODh
GI-004 | FR12-1 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1MVTB_M1 | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633611&prj=692&rqi=aWHQIG95lADrbRYEM3768ZSUBN
GI-002 | FR12-1 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1MVTB_D | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633607&prj=692&rqi=Qvfal2SW6Dhmk7EoqLvYLkUGWq
GI-015 | FR13-2 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | General Design issue | Design | [6 empty] | RMU Tx breaker tripping on in rush B, D, A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352280&prj=563&rqi=uyQzaW8W27OY2ycjDL9Pj44wLG
GI-010 | FR13-2 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Graphics Issue | DCOS | [6 empty] | RMU B not visible on DCOS during mains failure test. Port issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352273&prj=563&rqi=5nr26XZVLrlbfxqPOVfnM5LRCL
GI-011 | FR13-2 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Graphics Issue | DCOS | [6 empty] | 2 breakers on UDP B showing tripped when on | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352276&prj=563&rqi=qNwjiSEQQWc735VsPLLKzGeWMg
GI-014 | FR13-2 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Graphics Issue | DCOS | [6 empty] | Generator breaker on MSB C not showing as closed on DCOS graphic | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352279&prj=563&rqi=o3byGjjxacpYmDg9LTeKzQiEKH
GI-013 | FR13-2 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | General Design issue | Design | [6 empty] | When lose of power to fuel pumps you have to restart manually. To be discussed with EQX design and RHK (recommend UPS backed supply) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352278&prj=563&rqi=XY7jEVqdBMxVzmlfnw5j1Vx72W
GI-012 | FR13-2 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning | [6 empty] | Fuel system using low level bulk tank instead of high level bulk tank - Sigma to come and investigate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352277&prj=563&rqi=kqqQsJWfd4UkJn7Q7tvV0Oc60B
GI-009 | FR13-2 | N-EMEA | Closed | P2 Medium DCOS | Alen.Francis@eu.equinix.com | 2026-02-13 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCIM Sync Service Issue | DCIM | [6 empty] | We are unable to verify all expected objects upserted to DCIM. System Integrator/ GC needs to update the DCOS/DCIM delivery time on when this will be completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199201&prj=563&rqi=HcY8UaEInBQlnKkOHpsAkiyXdJ
GI-028 | FR6 - Liquid Cooling | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-08-10 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | TCS/SFN-01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | Opened from a previous IRL. On the SFN some bolts are Carbon Steel and not Stainless Steel. Bolts are to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632976&prj=685&rqi=R1pyQHzRjttPe96xEdzUm5QP66
GI-027 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-05-26 04:00:00.000 +0400 | Owner |  | General Design Issue | Design |  | equipment type |  |  |  |  | Temp sensors on the racks does not show accurate readings, as the sensors are surface mounted and facing the CRAH supply air flow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623135&prj=685&rqi=zONO7GshyOWioj0QUUCJZcvptm
GI-026 | FR6 - Liquid Cooling | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-05-18 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Missing Torque marks on the SFN. Torquing has been done but missing the marks | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622173&prj=685&rqi=Pr2BFhH7rYpj90rjyp3YXwxLCc
GI-025 | FR6 - Liquid Cooling | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-05-18 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Missing Valve Tag Number on the SFN | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622163&prj=685&rqi=zfX4Gx5o2bbvXmmFB6HZL8Uy1N
GI-023 | FR6 - Liquid Cooling | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-05-05 04:00:00.000 +0400 | Owner |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Leak detection schematics are to be updated to include the new SFN area. the alarm is working and has been checked. only schematics to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620487&prj=685&rqi=N0XesTI2i9WeZH5mWVvYUy972X
GI-024 | FR6 - Liquid Cooling | N-EMEA | Closed | P2 Medium CX | sdreik@global-cxm.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/ Equipment Failure | Commissioning | [6 empty] | Control Valve on the CDUs suppose to hold last recorded position after power failure. However, when the controller is starting the control valve is driving back to the lowest % set | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620495&prj=685&rqi=2oGjgpWl3NuSgi9STxXJOXU4wj
GI-022 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | CDU Internal tanks to have a label specifying the PG25 manufacturer sticker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619684&prj=685&rqi=0rWe4vwzN5mVyClpMC5FDoEvQv
GI-018 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | Units to be unified between CDU HMI and DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619533&prj=685&rqi=m5fzy5SnQ0MMcZaRMkxBTyyEfy
GI-015 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | The below alarms are not visible on DCOS graphics: - Secondary DP Setpoint - Critical Alarm - Non-Critical Alarm - High Secondary Supply temp Alarm - Low Secondary supply temp Alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619527&prj=685&rqi=RTgmW3KdGVg317XOaIJe6UtmsK
GI-020 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | on the CDU HMI, Filters 2 and 3 shows reading together not as separate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619536&prj=685&rqi=36lhZs6yZxCsBLvSeYKeS3AS1c
GI-019 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | Leak Detection alarm not available on the CDU graphics | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619534&prj=685&rqi=cPhaaBBWkp88WJR4UF51l5Fihi
GI-021 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | text to be unified when losing a power source on the graphics | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619537&prj=685&rqi=Ec9Zps51LF7VyOrcEUEcGonXTW
GI-017 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Template Issue | DCOS |  | equipment type |  |  |  |  | Text to be fixed not to cover the Graph | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619532&prj=685&rqi=qX8f8VibN44TgzyDlf6CSyy8K4
GI-016 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Template Issue | DCOS |  | equipment type |  |  |  |  | Text to be fixed on the Graphics | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619529&prj=685&rqi=sCufVCNzIJZWn8P5orKEsFLmrp
GI-014 | FR6 - Liquid Cooling | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | General Contractor |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | 2 valves handles are damaged and cannot operate the valves. at the moment the valves are kept open, but cannot be closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618986&prj=685&rqi=Uz7t2eB4NmFJyZtOe3AtJ9jwpY
GI-011 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Comms Issue/ Fault | DCOS |  | equipment type |  |  |  |  | When a comm alarm is generated on the CDU. alarm is showing in the alarm section and incication around the HL point. However, nothing shows on the CDU DH graphics, meaning ops will not be able to see that we lost comm until they go into the CDU graph | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618860&prj=685&rqi=wBoKoRYg74kkWxxwufga24ykKY
GI-013 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Bolts installed on the SFN are short and cannot be fully torqued as the bolts does not even reaching to be flushed with the nut while it should be 3 threads exceeding the nut | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618911&prj=685&rqi=Sr2qsO4f1flkAabfTELZTheqjM
GI-010 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | ATS status showing on the graphics as a text. this should be amended to change or identify when a source is lost with an alarm and which source is still available | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618857&prj=685&rqi=5LLN3IdkfOwJ3V7rdrYb2oI4KM
GI-012 | FR6 - Liquid Cooling | N-EMEA | Closed | P2 Medium CX | sdreik@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | Owner |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Missing Flushing Valves on the SFN pipe work installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618906&prj=685&rqi=hEoFrnGvyxKqZC0YWKjKzj0XVq
GI-005 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-20 04:00:00.000 +0400 | Owner |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Pressure test was achieved on the SFN without installation of the By-pass valve. as discussed with designer, the system will be functioning without it. Once installed a pressure test is to be conducted on that section and closed with a protocol | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618752&prj=685&rqi=KZD7Jw9P8uky87h6gqEh9yFiJO
GI-009 | FR6 - Liquid Cooling | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-04-20 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | Mechanical â€“ Water | equipment | TCS/SFN-01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | SFN missing Pipe identification labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618764&prj=685&rqi=gRrnDBHNNHImXlbwGUdsrvDu5D
GI-007 | FR6 - Liquid Cooling | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-20 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Template Issue | DCOS |  | equipment type |  |  |  |  | The DCOS template shows 10 racks while the latest DWG shows 12. this is to be amended | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618759&prj=685&rqi=UGMS8LcZ4Zwg71CJgsoxwnCAgK
GI-002 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-26 04:00:00.000 +0400 | Equinix Ops |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | Leak Detection | LEAK - Leak Detection |  |  | Leak Detection System installation not complete or L2A/L2B/L3/L4 commissioned. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352230&prj=659&rqi=GysavwIpDTVZYKEJuoEEVx7uaj
GI-001 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-25 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | TCS/SFN hoses supplied by Refcon are designed for steam with pinpricked outer membrane. EQX COE requires the hoses to be changed for hoses specifically designed for PG25. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352227&prj=659&rqi=ZqBQkCPpZCoQ6PVbT85PkTkXUh
RT1MECH-4-005 | HE7: Liquid Cooling | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-19 04:00:00.000 +0400 | Mechanical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Return joint under CDU02 not installed as per manufacturers recommendations as there is not proper "pad to pad" contact on both sides of the joint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199530&prj=659&rqi=lX95OoO1uaViD7i1GKtKRZ4RdO
GT1MECH-4-002 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-19 04:00:00.000 +0400 | Equinix Ops | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Temperature Sensor Low Alarm does not remain red when coming up from a Low Low alarm, but it if you simulate a Low alarm from normal temperature it changes red. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199568&prj=659&rqi=bHLrT7igWFhZ8Re4aL0NXeFot2
GT1MECH-4-001 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-19 04:00:00.000 +0400 | Equinix Ops | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Temperature Sensor High Alarm does not remain red when coming down from a High High alarm, but it if you simulate a High alarm from normal temperature it changes red. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199567&prj=659&rqi=klKzDJaYrQHw15N00N1pR3sdgM
YT1MECH-5-002 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-19 04:00:00.000 +0400 | Equinix Ops | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | No earth bonding on TCS/SFN. EQX to confirm Finnish design requirements on TCS/SFN pipework bonding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199545&prj=659&rqi=yxiYKRRCf6bn1k2xzdpQuoejVh
RT1MECH-4-001 | HE7: Liquid Cooling | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | Mechanical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Some TCS/SFN joints are not installed as per manufacturers recommendations as there is not proper "pad to pad" contact on both sides of some joints. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199351&prj=659&rqi=e8OlvOEvgrSCZX2VgbQmplWve8
RT1MECH-4-002 | HE7: Liquid Cooling | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | Mechanical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Rack 101-105 connections supports are compromised by existing electrical containment. Rack 105 support in particular needs attention/additional supports. Pipework and Valve not level. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199352&prj=659&rqi=tQBfMKW7NJW49rnpGs93XVcn0l
RT1MECH-4-004 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | Equinix Ops | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | All TCS/SFN valves are not labelled with ID tag/label. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199354&prj=659&rqi=UCyWNqYKYHbqJdIVrlraoTIbXI
RT1MECH-4-003 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | Equinix Ops | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | All TCS/SFN temperature sensors are labelled with temporary stickers. Permanent labels to be installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199353&prj=659&rqi=TB3ZUJcTRJ5dTcfAgHIIRfvLti
YT1MECH-5-001 | HE7: Liquid Cooling | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | Mechanical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Rack 101 bypass hose and valve are weeping | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199363&prj=659&rqi=zEz8JYZ0HVTMZAb9qBawj7useA
RT1MECH-4-006 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-05 04:00:00.000 +0400 | Mechanical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Thread tape used on the brass drain valves and gauges installed on the TCS/SFN. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221141&prj=659&rqi=oqkUabwrbhcIEsYGp0chNlFTt4
RT1MECH-4-007 | HE7: Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-05 04:00:00.000 +0400 | Mechanical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Brass drain valves and reg valves installed on the stainless TCS/SFN. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221142&prj=659&rqi=ctZ96fcWamVvOekzONqgrIrEk1
GI-294 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | R/F -Failure of the Battery discharge test for 4 nos. of emergency lighting | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617729&prj=501&rqi=54Qqj3fAqL2RRYShzyY7NTa9QQ
GI-296 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | 13/F LVSB Rm - emergency lighting installation to comply with FSD requirement and within 2m of any FSI installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617731&prj=501&rqi=QgCHK6nbOiNur4G5SKk7QSlHX8
GI-297 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | 15/F LVSB Rm -emergency lighting installation to comply with FSD requirement and within 2m of any FSI installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617733&prj=501&rqi=nqknx8laKvD2qDjNUEixt3QCYj
GI-295 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | 12/F LVSB Rm - emergency lighting installation to comply with FSD requirement and within 2m of any FSI installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617730&prj=501&rqi=uXNfFSTMTJHsjWlpyhi7paYv9u
GI-293 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-04-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Task Uniformity (Min./ Avg. = 0.014) of R/F the Luminaire Schedule by NV5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617128&prj=501&rqi=eaihd8SfUM1M01n0rb84iy7yb2
GI-289 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | CAM 00024 has not been tested because it has not been installed. The installation requires conduit to be run through a CLP-controlled room, and CLP has denied access permission. The matter is currently being discussed by NV5, GEM, and EQX. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616820&prj=501&rqi=WQHJad5ezSU3U9pN0XziRm1tg1
GI-290 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Door 28 (D28) will be replaced from double-acting doors to in-swing door with EM Lock upon completion of BD inspection on Apr 7. EM Lock, Keypad Reader, and Break Glass Unit have been tested without door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616821&prj=501&rqi=UoNPu8P2MR20k0fU9DryUjlBag
GI-291 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Door 20 (D20) have not been installed due to damaged door frame. EM Lock, Keypad Reader, and Break Glass Unit have been tested without door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616822&prj=501&rqi=doRNdxoOmNwrrHCOBp7yagmLde
GI-288 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | CAM 00054 have not been tested as it has not been installed due to requiring conduit installation through CLP-controlled room. CLP did not give permission fpr access. Currently under NV5, GEM and EQX discussion. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616819&prj=501&rqi=GEWkW3cO8GmePbOGu2GeSWeHjJ
GI-292 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | R/F - Emergency lighting discharge lower than 2 lux. (measure from floor) at the beginning of battery discharge. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616860&prj=501&rqi=tp57sBAdhlv140H5jnntgTdV4h
GI-284 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | emergency lighting installation to comply with FSD requirement and within 2m of any FSI installation" & "Emergency Lighting cannot fulfil the FS COP Requirements | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616639&prj=501&rqi=AYMgoIZG52EXmciU2bE8Z90qlB | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-286 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | Avg. Lux Measurement of 17/F Customer Kiosks cannot meet the Luminaire Schedule by NV5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616647&prj=501&rqi=UfvqbgPo2BnF8BVK6vHVEptXyb | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-285 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | Avg. Lux Measurement cannot meet @of 17/F Customer Kiosks, Main conference room, at lounge | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616645&prj=501&rqi=qB3Tg0APxtuQqe54ghO92vDenr | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-287 | HK06-1 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | Task Uniformity (Min./ Avg. = 0.30) of 17/F Lounge cannot meet the Luminaire Schedule by NV5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616648&prj=501&rqi=NvqpFHj5rblmhFnG5WHsoN1wGb | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GT1DCOS-13-001 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-20 04:00:00.000 +0400 | General Contractor | L3 | Component/Equipment failure | Commissioning | Controls | equipment | 1DCOS_LCP_17 | DCOS - Control Panels |  |  | 1041 FER Room TT sensor showing inaccurate from calibrated device. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616065&prj=501&rqi=ONUhbY2QTbOIn1MTFTjNII7ScC
GT1DCOS-13-002 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-20 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning | Controls | equipment | 1DCOS_LCP_17 | DCOS - Control Panels |  |  | Unable to check points for flow (items 5 to 12 on point list / test record) as flow meter installation is pending for Water Department approval. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616067&prj=501&rqi=vuMZEpHiuIEPUgKmCVtU0nHDel
FPT-478-006 | HK06-1 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | system | Fire System |  |  |  | (Typical for 12/F, 13/F, 15/F and 17/F) Genset did not receive "Remote E-stop" after fire signal triggered and therefore genset did not stop and MSFD also did not closed. Fuel supply system PLC did not receive "Fire Signal" to close the valve logically. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615900&prj=501&rqi=tkXNjVS53QyfqK37dD5jwOLB5y | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-005 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | system | Fire System |  |  |  | Missing label for 13F gas suppression system module | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615897&prj=501&rqi=JbdEcumAxQPFsUqRMXayAL5QZC | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-003 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | system | Fire System |  |  |  | Time synchronization issue for FS main panel and repeater panel (Has 1hr and 5mins discrepancy) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615892&prj=501&rqi=W7UAx02c1vDhYK8rQmZPygcuZ3 | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-008 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | system | Fire System |  |  |  | Pre-action panel manual operation function cannot be tested since the base building sprinkler pumps are malfunctioned. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615902&prj=501&rqi=j3vxHiIeaLixail97YZL6exoNc | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-010 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | system | Fire System |  |  |  | 24V power supply to gas suppression system module is not available. Corresponding test for 17F gas suppression system cannot be conducted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615904&prj=501&rqi=rzFHbtL4eGEfNAE1ZMFsm7FfPe | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-009 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Installation not complete | Commissioning | Fire Detection | system | Fire System |  |  |  | "Evacuate" flashing light box inside genset room 12/F & 13/F were not properly fixed. The light boxes were embedded into the promat board wall, and the wall opening was not properly sealed or backfilled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615903&prj=501&rqi=0gH19D5FvvjqT0tRwO00qBwptS | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-002 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | system | Fire System |  |  |  | Gas suppression system signage at 15F to be checked. The flash light effect is different from other signage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615890&prj=501&rqi=F4dvYYyGXoaN4lOeRDGNt9JS0X | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
GI-283 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | Unitary mode for chiller keeps coming on during IST2 on 17 March 26 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615907&prj=501&rqi=Wp7ytzty9YFhczG3x5eKOqGhmX
FPT-478-004 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | system | Fire System |  |  |  | Gas suppression system at 13F module does not receive MFSD feedback status; MFSD is actually closed onsite. After jumping the MFSD feedback signal, the corresponding module was triggered and then NOVEC logical function worked properly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615895&prj=501&rqi=TT85FARvNIMnPBAD624rqdga8R | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | system | Fire System |  |  |  | (ACS)(Typical for 12/F, 13/F & 15/F) Mantrap near passenger lift lobby interlock function malfunctioning ; door release function (by fire signal) works properly in FIST | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615889&prj=501&rqi=NGa2DU6dvPeoZbBC7IiBkMDOGC | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-007 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Labelling | Commissioning | Fire Detection | system | Fire System |  |  |  | Permanent label for damper bypass control panel to be provided (typical) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615901&prj=501&rqi=qLD5nLajO41TeJGRoVGF7N2Z3q | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-479-014 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 10:45AM After failing CHWP-01 at string 1, the DCOS programme still counting for reset after 5 mins | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615751&prj=501&rqi=1TWil87sDGRLNxtH7GpSSOVawX | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-012 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 07:29AM 13040 TER Room, 1TT_01 sensor showing 0C, with a low temperature alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615744&prj=501&rqi=fX0w0wqnZnCK7pbNvj9BiiHYoi | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-013 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 09:10AM UPS_A2 Alarm triggered momentarily. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615748&prj=501&rqi=pxhz1yrKMeFstWx0ihbfNbUxtf | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-004 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | CHWSTR1 DPT-04 loss communication alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615640&prj=501&rqi=thHKlHmAx0Nhy752QxllexBk1i | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
GI-279 | HK06-1 | APAC | Closed | P2 Medium DCOS | ychoong@ap.equinix.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | Fuel Control Panel has no alarm when the panel is down with no power | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615660&prj=501&rqi=yebAQpRpiaYvpVKMQgcIR8Xi2I
FPT-483-022 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS Graphics Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT-1(HLT2) 3/14/2026 11:00PM 13F Tx Room had high temperature alarm triggered. Alarm configuration to be clarified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615675&prj=501&rqi=rCnbBc5fht7T3ygBVDc2VE1kuF | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-024 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | 3/14/2026 HLT-1(HLT2) 11:00PM 17F Lv Switch Room had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615677&prj=501&rqi=p5gQqu1JXFmQ5sn9uwfqXKRdXF | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-485-003 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider MV | L4 | DCOS Graphics Issue | DCOS | Electrical | system | Electrical System |  |  |  | During the IST 2, at 14:35 - During the UPS_M1 is on maintenace bypass mode, the UPS PQM on DCOS is showing -0kW in effect a warning has shown. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615679&prj=501&rqi=cCoLuSZB6b0vW5bPl42X6fACkO | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-479-010 | HK06-1 | APAC | Closed | P2 Medium DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 04:27AM After failing CWP-02 at string 2, WCC & CHWP staged down. String 2 still received command on in D2SD, the cooling tower remained on. 13/F Data Hall 2 CRAH_AR1_14's supply air temperature reached 27C. Data Hall SLA temperature was maintained within SLA range. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615646&prj=501&rqi=dY3VplY2QRTQc7fNp4DCb4goxE | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-009 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 04:07AM When PCP_02 was failed, "Power Supply Common Alarm" alarm did not trigger for PCP_02. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615645&prj=501&rqi=kvwCeCDsqpLflU2EWgFyYpfVFz | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-007 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 03:52AM When PCP_01 was failed, PCP_02 became the primary unit, but "Power Supply Common Alarm" alarm was triggered for PCP_02 instead of PCP_01. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615643&prj=501&rqi=0J3qgPcC9FDWwQVA3XfBw4c2oL | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-008 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 04:07AM When PCP 02 was failed, "Hot Standby Status" and "PCP Status" did not show on DCOS graphics, all greyed out. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615644&prj=501&rqi=oPOdRxQfbfqYraMwK7v7SAFwh0 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-006 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 03:52AM When PCP_01 was failed, PCP_02 became the primary unit, but "PLC Stopped" alarm was triggered for PCP_02 instead of PCP_01. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615642&prj=501&rqi=CqavOwW3PbNyKw1JGCbqch2Img | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-023 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | 3/14/2026 HLT-1(HLT2) 11:00PM 15F Battery Room had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615676&prj=501&rqi=gqLy0foXGcKx32Lt3IykpxU6ZA | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-005 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 03:49AM PCP-02 Module Present Status alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615641&prj=501&rqi=CwSivsNsC1TUfjCJBkAG2iDTzX | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-011 | HK06-1 | APAC | Closed | P2 Medium DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 04:27AM After failing CT-02 at string 2, the WCC, CHWP, CWP all remained running. String 2 was still receiving command on in D2SD. WCC_2 shown off on DCOS but WCC_2 was running normally on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615649&prj=501&rqi=AoAL83ugwLipmUuOqA7KOgnfeS | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-021 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT-1(HLT2) 3/14/2026 11:00:00 PM 1UPS_A1,A2,B1,B2 had high output current, kVA and kW alarm on DCOS. Alarm configuration to be clarified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615674&prj=501&rqi=xMIDDb4z89ZHbMHQhjAuzDPipV | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-485-004 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | Vendor- Manufacturer | L4 | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | During IST 2 EIST-01, when the generator is started because total power failure is applied from the SUDB side, the fuel system on riser B is found to have fuel leakage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615680&prj=501&rqi=GcZg3WOMLBigYSQJ5a9HNXjUzB | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-482-004 | HK06-1 | APAC | Closed | P2 Medium DCOS | ychoong@ap.equinix.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS Graphics Issue | DCOS | Electrical | system | Electrical System |  |  |  | DCOS graphic for MV network. -11kV voltage is shown on SUDB even when the main switch is opened. - Amps is shown even when no load is applied - Energized line and non energized line are wrong | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615658&prj=501&rqi=MiIvYkQKJrCPDbbpr3xqoGAAOk | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-482-032 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | Vendor- Manufacturer | L4 | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | During IST 2 EIST-01, the PLC panel for the fuel system riser is found to have burnt fuse. This affect the riser from changeover when a fault is detected for the riser | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615681&prj=501&rqi=f38AnssgRtlh8l5HcdsuczZk44 | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-483-016 | HK06-1 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 L12 & L13 02:18AM After ATS changeover of 13/F CRAH units, it was observed that CRAH_AR1_01, 03, 08 chilled water valve command went to 0% and fan command went to 50%. 02:19AM 13/F Data Hall SLA temperature sensors exceeded 27C. Pentagon to clarify why power source changeover will cause fan speed command and valve opening command to drop. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615627&prj=501&rqi=Ly882etRVNmExOoXbiYhfVm1pi | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-485-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS Graphics Issue | DCOS | Electrical | system | Electrical System |  |  |  | In EIST-01, during the total power failure scenario where SUDB_1 & SUDB_5 Q01 incoming breaker is opened, the power line logic is wrong. It displays wrong graphic and response. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615634&prj=501&rqi=1eHJszrKzdiHPRsK1spT2lzL6o | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-483-017 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 03:56AM After closing the return and supply valves of Chilled Water Riser B, DCOS was still showing ~4.5L/s of water for Riser B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615628&prj=501&rqi=iR6znjvc6S5X0FPw9JIZHdvrQF | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-018 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 04:16AM For 13/F Data Hall 1, after Chilled Water Riser C was failed, "High Return Air Temperature" alarm was triggered for CRAH_AR1_01, 02, 03, 06, 7, and 17. Data Hall temperature was maintained within SLA. Pentagon to clarify the alarm dead band for "High Return Air Temperature" alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615629&prj=501&rqi=Zfuy662aTvcudqUoEW3K2gPNf4 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-003 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Electrical | equipment | 1ATSMI_M1R1_25 (1ATSMI_M1R1_32) | ATS - Automatic Transfer Switch |  |  | 01:41AM "Emergency Source Not Available" triggered for ATSMI_M1R1_23, 25, 27 Emergency Source. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615639&prj=501&rqi=9n1GPyoRtWtAF9oN7YCfiApsgn
FPT-483-015 | HK06-1 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 L12 & L13 01:56AM After ATS changeover of 12/F CRAH units, data hall temperature sensors exceeded SLA upper limit. It was found that the chilled water valves of the CRAH units closed, causing the supply air temperature to rise. 01:58AM Data Hall temperature dropped back within SLA range | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615626&prj=501&rqi=E9uTZsGWiWXAmZwpTbAgezB4Rp | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-001 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | equipment | 1EF_B_3 | EF - Exhaust Fan |  |  | 1EF_B_3, 1SF_B_2, 1EF_A_2 and 1SF_A_1 communication match alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615637&prj=501&rqi=pmjpWuW9uLw7bevqHO4pbvybr8
FPT-483-019 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | 04:45AM For 13/F Data Hall 1, after Chilled Water Riser C failure reinstate, "High Return Air Temperature" alarm was triggered for CRAH_AR1_04, 05, 08, 09, 10, and 18. Data Hall temperature was maintained within SLA. Pentagon to clarify the alarm dead band for "High Return Air Temperature" alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615630&prj=501&rqi=4JC2KqbmV1BeiYrAXPCWVjLGjf | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-011 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 - Test10 L12 & L13 11:04AM For 13/F Data Hall 01, after failing both CRAH_AR1_08 & 18, SLA sensor 80_TT_04 reached 27C and triggered the SLA upper limit alarm, momentarily. It was floating between 26.9C and 27C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615621&prj=501&rqi=Zi8dH9HQB5x9nezuInJMT1lP0Y | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-007 | HK06-1 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 Test-05 L12 & L13 05:55AM After the data hall load was increased from 75% to 100%, CHWSTR_2 chiller was called to start, but it was not able to stage in. DCOS chiller received an external fault, but no alarm was found at the chiller HMI. Fail to start alarm triggered on CHWSTR2. String 2 then staged in under free cooling mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615617&prj=501&rqi=mPwELwrvgYcpx3RFz26VnPz0KD | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-013 | HK06-1 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-2 (12F & 13F) Test 11: CRAH Failure at Data Hall 1 at L12 and L13. 3/14/2026 12:46 MAU_M3R2_1,2,3 had communication alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615623&prj=501&rqi=Y49TV9Hz3O6ewNUfch4oYAUsPG | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-012 | HK06-1 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 Test-10 L12 & L13 11:40AM For both 12/F and 13/F, it was noticed that for CRAH units that triggered "High Supply Air Temperature" alarm, the alarm is held even when the group temperature has dropped below 25.7C. Pentagon had to power reset the units with the alarm to clear them. Pentagon to clarify why the alarm is unable to clear. Also whether there are any delays, and what is the alarm deadband. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615622&prj=501&rqi=b4XkMeVRm93RBBWezXYgpcBxaF | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-010 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 Test - 05 L12 & L13 10:45AM For 13/F Data Hall 1, after CRAH_AR1_18 was failed, "High Supply Air Temperature" alarm was triggered for CRAH_AR1_04, 05, 08, 09, 10, and 18. Data Hall temperature was maintained within SLA. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615620&prj=501&rqi=uZSXDdCjcOtJ6LfmsL7QcAE7sH | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-002 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 Test-01 L12 & L13 00:17AM When increasing the data hall load from 0% to 25% for 12/F Data Hall 1, "High Supply Air Temperature" alarm was triggered for CRAH_BR1_01 to 10, and 17. Data Hall temperature was maintained within SLA, no pre-alarms triggered for SLA sensors. 00:20AM The "High Supply Air Temperature" alarms auto cleared once the supply air temperature dropped back below the alarm setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615612&prj=501&rqi=yzxL3MNrOik2dwWe3kRvbmFksJ | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-005 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT2 Test-04 L12 & L13 DPT-04 in CHWSTR_1 lost communication | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615615&prj=501&rqi=FqvxKXnHPt2YklhuwNUjQtju6G | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-011 | HK06-1 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-17 (HLT1) 3/8/2026 WCC- Compressor had discharge superheat warning repeatedly triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615590&prj=501&rqi=1N6b3YjfbWy7omiWPtRF7lYUJK | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
GI-275 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | HLT-05 L12 & L13 10:45AM For 13/F Data Hall 1, after CRAH_AR1_18 was failed, "High Supply Air Temperature" alarm was triggered for CRAH_AR1_04, 05, 08, 09, 10, and 18. Data Hall temperature was maintained within SLA. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615550&prj=501&rqi=lw5TRm5PDXxtcVNbq4Pd2du58t
FPT-481-013 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT-10 (HLT1) 3/8/2026 MAU_2 and MAU_3 had incorrect fan speed reading on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615592&prj=501&rqi=OFQiSNP9sFbTJAQLSCNkbSBxWa | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-004 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 1 13F battery room high temperature alarm. Sensor replaced. Observed around 2 degC difference between actual measurement and DCOS reading. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615602&prj=501&rqi=6qbDxYBp9uimX1wGvTN0UbRsm1 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 Test-01 L12 & L13 00:00AM When increasing the data hall load from 0% to 25% for 13/F Data Hall 1, "High Supply Air Temperature" alarm was triggered for CRAH_AR1_01 to 03, 06, 07, and 17. Data Hall temperature was maintained within SLA, no pre-alarms triggered for SLA sensors. 00:12AM The "High Supply Air Temperature" alarms auto cleared once the supply air temperature dropped back below the alarm setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615611&prj=501&rqi=yBGR9nOK212g8JAUQFpjVhJODi | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-004 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS Graphics Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT2 - Test 03 1RPP_B2R1_2_01 graphic mismatch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615614&prj=501&rqi=DBn56ak8Jsoo9D0KwVwA2604WF | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-009 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT3 Test 3 - 09:56 Observe bleed off pump common alarm on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615608&prj=501&rqi=Gl7Jy7zK1jFUQE1tUealjPaYAO | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-009 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 - Test 05 L12 & L13 06:09AM When increasing the data hall load from 75% to 100% for 13/F Data Hall 1, "High Supply Air Temperature" alarm was triggered for CRAH_AR1_04, 05, 08, 09, 10, and 18. Data Hall temperature was maintained within SLA. 06:15AM The "High Supply Air Temperature" alarms auto cleared once the supply air temperature dropped back below the alarm setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615619&prj=501&rqi=84upevfbIMA1NhXIiDVxb5nBKJ | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-003 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 Test-01 L12 & L13 00:30AM When increasing the data hall load from 0% to 25% for 12/F Data Hall 1, "High Supply Air Temperature" alarm was triggered for CRAH_BR1_04, 05, 08, 09, 10, and 18. Data Hall temperature was maintained within SLA, no pre-alarms triggered for SLA sensors. 00:33AM The "High Supply Air Temperature" alarms auto cleared once the supply air temperature dropped back below the alarm setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615613&prj=501&rqi=HrgHTrHQyE4yj8o5s8BIozpq3U | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-010 | HK06-1 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT 3 - Test 22 11:40 Observed CRAH_AR1_13 stop operation during riser failure scenario. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615609&prj=501&rqi=Vj0MyTdWuiQtpBOhckWDErtc8u | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-003 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 1: 0% Data Hall load: 12F Tx Room receives low temperature alarm(25.1degC) at 17:42 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615601&prj=501&rqi=Dhh4H1BJ7CH8utXI1zZvrdvYIG | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-008 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Electrical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 Test - 05 L12 & L13 UPS A2 Alarm triggered. After checking by vendor, it was found phase A was overloaded. After adjusting the loading, the alarm was cleared. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615618&prj=501&rqi=hnxd3VXFZx4VSMCQSd6NCwDAHX | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-006 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT2 - Test 5 05:39AM When increasing the data hall load from 75% to 100% for 13/F Data Hall 1, "High Return Air Temperature" alarm was triggered for CRAH_AR1_01 to 03, 06, 07, and 17. Data Hall temperature was maintained within SLA, no pre-alarms triggered for SLA sensors. 05:42AM The "High Return Air Temperature" alarms auto cleared once the supply air temperature dropped back below the alarm setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615616&prj=501&rqi=0OpcIV6TYKz6afETGKoqaJOCb5 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-012 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT-20 (HLT1) 3/8/2026 CHWBT_4 TCV-03 valve had mismatch alarm triggered. (Typical) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615591&prj=501&rqi=NTDCsxaxnt7sSLiWsxKcv8dLWC | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-006 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | Mechanical Contractor | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT3 - Test4 12/F and 13/F No feedback status for CRAH ATS status | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615605&prj=501&rqi=qpZG7O9q5tr5qT6PbdQpb3TDAt | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-011 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT 3 Test 22 - Mechanical failure scenario. CHWSTR1 changeover to CHWSTR 2. Observe CHWSTR1 fail to start alarm on D2SD. CHWSTR2 operates normally after changeover. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615610&prj=501&rqi=b67KQfvQzJEjctR5WSFgQsRI3N | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-007 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | Mechanical Contractor | L4 | DCOS Graphics Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 13 Pentagon to clarify why after remote air temperature sensor failure, some units will show 0C, but some will hold last status. 12/F: CRAH_BR1_11 sensor 1 shows 0C, CRAH_BR1_14 holds last known. 13/F: CRAH_AR1_11 & 14 sensor 1 holds last known | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615606&prj=501&rqi=8cjkXc6ZkLvjwCU5T7a8IkQPjj | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-008 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 17 SE to clarify 1RAS_06 (Input 3) still having flowrate reading (~4L/s) after shutting off riser B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615607&prj=501&rqi=cctIxcMGlpfX6TU0pdWU3WEP8s | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
GI-266 | HK06-1 | APAC | Closed | P2 Medium DCOS | ShirleyLeong@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning |  | system | DCOS |  |  |  | SE to recheck and troubleshoot the system settings and parameters because SE uploads new software/firmware for the chiller/DCOS when unauthorized software upload is allowed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615518&prj=501&rqi=vo1ne7CQBlTxo9Kzd21d7uBYUr | https://equinix.facilitygrid.co.uk/x/project/501/system/13006
FPT-484-005 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 2 19:10 13/F DH2 exceed SLA during ramp up IT load. Unload to retest. 19:19 start again to ramp up load. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615603&prj=501&rqi=wE0FuBQr1zjvKnZIyo7btE3Ftl | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-002 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 1: 0% Data Hall load: 15F 1EF_R1_6 receives command mismatch alarm at 17:40 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615598&prj=501&rqi=3XkarUo5jpdPgW4OCl0CEx7bBD | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
GI-253 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | 1RPP_B2R1_2-01 graphic mismatch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615378&prj=501&rqi=LW3TEIbJiznakv7A5aNjG1IZwJ
FPT-484-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 1: 0% Data Hall load: 17F Lv Switch Room receives low temperature alarm(24.8degC) at 17:39 17F Tx Room receives low temperature alarm(24.3degC) at 17:39 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615597&prj=501&rqi=w3PpQO1pBlhp0TqduOju1LiWsT | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-482-028 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | Electrical | system | Electrical System |  |  |  | 11:17 - 1MSB_B Q06 is detected with communication alarm during EIST-12 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615346&prj=501&rqi=snt6xVmAtwForEakAB40XgSBJW | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-241 | HK06-1 | APAC | Closed | P2 Medium DCOS | PerryLee@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Pre-HLT L12 12/F Data Hall 1 CRAH_BR1_02 loss of communication alarm, unable to reflect status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615316&prj=501&rqi=kKCt5ovuqiNUCD2kDVvbGG8kwd
GI-239 | HK06-1 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Pre-HLT L12 and L13 13/F Data Hall 2 80_TH_04 exceeded SLA limit, it recorded 27.1C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615313&prj=501&rqi=xoc6t7lFMJBGE6fOhu3ItLXqwn
FPT-482-031 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | SIE- Siemens MV | L4 | DCOS General Issue | DCOS | Electrical | system | Electrical System |  |  |  | 11:34 - During the power changeover for R1 block, MLTX_M1 was triggered with communication alarm. It is confirmed by GEM that the MLTX_M1 is online during the changeover and no M1 equipment undergo changeover. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615351&prj=501&rqi=otMulOikhjmyEsLV7dpj32YbNw | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-243 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | During functional tests of water leak detection system, it is observed that for panels connected to leak detection cables AND point-type sensors, when simulating a specific leak test, the panel and DCOS read distances well above the accepted criteria. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615334&prj=501&rqi=MmElLr4cbUjQep4pvgo1JdtsBx
GI-242 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | During L3 of Water Leak Detection Point-to-graphic test, it is observed that point signals incredibly high value when not detecting any leak. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615323&prj=501&rqi=1N2C0iHDJxMtR5jckgtMtV2vUA
FPT-482-030 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | 11:46 - During the power changeover for R1 block, some ATS that has R1 block as emergency source did not show emergency source not available. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615350&prj=501&rqi=wz9auD59L85fgu0DSiamvtLoaH | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-238 | HK06-1 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Pre-L12 HLT Failure CRAH_BR1_08 and 18 12/F Data Hall 1 76_TT_02 exceeded SLA limit, it recorded 29.1C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615312&prj=501&rqi=iNZSLz6XOrDGNPcYVwR9lzijuq
FPT-482-029 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | SCH - Schneider MV | L4 | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | 11:40 - 1SUDB_5 was triggered with battery tripping unit alarm during block R1 was failed on DCOS. It resumed automatically after block R1 is supplied by generator. GEM team confirmed on site that no alarm were triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615348&prj=501&rqi=mpZ6cR9Nve9OnBeR0lnuKrkDcn | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-240 | HK06-1 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Pre-HLT L12 Test 11 12/F Data Hall 1 80_TH_04 exceeded SLA limit, it recorded 27.7oC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615315&prj=501&rqi=MjmFlfXSWfkaH75Mi8Vrxf7Vlc
GI-207 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | When one outdoor unit was failed (via E-Stop), the standby outdoor unit cannot stage in automatically. It has to be staged in manually. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615192&prj=501&rqi=xkl8mYnmFLBXHOFYAwOhux4bN8
GI-210 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | During unit sensor fail, operating unit will be switched off and other unit will run in 100% to cater the load. Please clarify logic for this scenario for the battery room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615196&prj=501&rqi=TyOHoMJYCVyyo8P6LMXNpN7IcJ
GI-205 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | CRAH_LR1_01 to 14 triggered "High Supply Air Temperature" Alarm, Data Hall SLA sensors were all within SLA range. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615173&prj=501&rqi=e0gedUxsqNgR0TqrYR7EpOUrtA
GI-204 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | After CWP was failed and when STR 2 WCC stages in, the run status of WCC 2 would flicker between On/Off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615172&prj=501&rqi=QOSfikGQQHylMZRsPprI07yrNJ
GI-201 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | MIST-12 When PCP 02 was failed, "Hot Standby Status" and "PCP Status" did not show on DCOS graphics, all greyed out. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615169&prj=501&rqi=Bn0WqDa7AZNNpBio9tsPoTvl0e
GI-237 | HK06-1 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | L12 & L13 Pre-HLT Day 1 Hot spot identified near CRAH-AR1-05 and CRAH-AR1-10, which caused exceed SLA limit on L12 Data Hall 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615299&prj=501&rqi=ziFbYAH7ynK8Td4hV9JLIkeJx6
GI-208 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | When one FCU has power loss, the other FCUs connected to the same outdoor unit will also receive the fault code and trip. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615193&prj=501&rqi=OoBr779CH3aZoscEUGRBZM7aJS
FPT-482-010 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Fire Detection | equipment | MSFD-13-14 | MSFD - Motorised SmokeFire Damper |  |  | 15:10 - MSFD-13-14 located at he generator set in 13/F generator room was found to be closed abnormally due to the flexible link is loose and resume at 15:20 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615276&prj=501&rqi=IYxkf6omjjZOCUfv29ElQQrwa4
FPT-482-020 | HK06-1 | APAC | Closed | P3 Low DCOS | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | Electrical | equipment | 1UDP_B2 | UDP - UPS Output Switchboard |  |  | 16:17 - 1UDP_B2 "communication alarm" is triggered when block B changeover from generator source to main utility source. It is confirmed that the MOXA has UPS power backup. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615286&prj=501&rqi=v9b2m8XLUfwm3CFRYQpPHw2AUm
FPT-482-007 | HK06-1 | APAC | Closed | P3 Low DCOS | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | Electrical | equipment | 1UDP_B2 | UDP - UPS Output Switchboard |  |  | 12:08 - During the load is ramping up to 50%, DCOS recived "Communication alarm". FSL confirmed that the breaker did not triggered any lost communication alarm on site. SE DCOS should rectify this matter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615273&prj=501&rqi=QEJBoCzUgZgzBACX8rxxaJhbQG
FPT-482-021 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | 16:45 - CT occur with vibration fault causing the chiller to change string during the power resume for block M1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615287&prj=501&rqi=B3MnPpIIq42Dgau3ua8XsmhwRN
FPT-482-016 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Electrical Contractor | L4 | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | All "input breaker open" alarm is triggered when the battery is discharged. It is confirmed that the UPS input breaker is not opened on site and on the graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615282&prj=501&rqi=OvBPmo9h49j6CLtBZghD4ycjU4
FPT-482-019 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | 16:11 - When the STS is showing alarm from the event log, the STS icon beneath UDP did not show any alarm or surrounded with any color of border line. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615285&prj=501&rqi=9cgEQAK2hq9bNgEu179NbumiBd
FPT-482-012 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | 15:24 - During the changeover for M1 block, normal power light in 17/F command centre and LOCC room were found and it was not resumed when generator power has kicked in. The power resume after around 5 minutes. GEM EL team claim that there was light work ongoing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615278&prj=501&rqi=rt9h3y6g7pnXmdCd7IOeaCPqU2 | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-482-005 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | 11:27 - Before the EIST start, DCOS received "ATS id no. ATSMI_M1R1_30, 04, 03" Emergency Source Not Available alarm. GEM confirmed that the essential power was healthy on site. GME shall clarify the mismatch between actual status and DCOS status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615271&prj=501&rqi=zJWacaqALKKTsnqGZWL6l4QxzZ
FPT-482-006 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | 11:52 - During the load is ramping up to 25%, DCOS received "summary alarm" with red border line, this indicated as a "high high alarm" were triggered for all the CRAH in 15/F DH1 & DH2. STULZ confirmed it is "high supply air temperature alarm". | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615272&prj=501&rqi=QaRVnpg0Fw1kKJswwo7ns2nb4D
FPT-482-023 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | 17:38 - CRAH in the 13/F LVSB room did not show which source is it on before the power failure started on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615289&prj=501&rqi=kzPZRMMiS8x5R7UToOPD76dSf3
FPT-482-022 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Electrical | system | Electrical System |  |  |  | 17:15 - For SLA sensor 01-07 in the 15/F big data hall, it received communication alarm from 15:31 to 17:38. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615288&prj=501&rqi=eH79miGPMyHZhEBSepq6F6THQm | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-209 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | During non working hours, when the room temperature exceeds 30C, the FCUs would operate. This logic is not available. Please clarify this logic with vendor and NV5 and which room is applicable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615195&prj=501&rqi=ayT9aJJCHBsbEPWK1A9DtiDCtm
GI-203 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | CHWBT_5 Bypass valve mismatch alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615171&prj=501&rqi=HFuMHEfBixxjNQXjdEKHmNHax7
GI-202 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | MIST-12 When PCP 02 was failed, "Hot Standby Status" and "PCP Status" did not show on DCOS graphics, all greyed out. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615170&prj=501&rqi=R2wjJlSLuQQaPAmIX81eH2M2Rj
GI-199 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | L15 MIST MAU 2 Loss of Communication Alarm due to R-Block no power | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615161&prj=501&rqi=hKxQDbf1FX7SZfLXACBLWuQ1ak
GI-200 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | MIST-03 (Failure of CHWP) MAU2 Compressor 1 fault alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615167&prj=501&rqi=wc5SVtwOSgh0quQscAoJTYMUWu
GI-212 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | VRV Alarm priority to be clarified. Gammon to confirm the point schedule with EOR and provide SICD for VRF system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615205&prj=501&rqi=O1pDvzZXHNpWYYYokEjYp451ih
GI-211 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Point to graphic test is conducted on graphic template from SFAT. Gammon to confirm the point schedule with EOR and provide SICD for VRF system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615203&prj=501&rqi=tnfav25Lr7LCmJ74TBvWyUTvIR
GI-213 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | During power failure test for VRF indoor unit, it is observed that there is no alarm on DCOS and it keeps showing last status on the graphic. Gammon to confirm the point schedule with EOR and provide SICD for VRF system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615206&prj=501&rqi=FWXxkvShTaIHaGUCatVB7NQae2
GI-206 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | TCV-03 for CHWBT feedback and common mismatch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615174&prj=501&rqi=LNLLUYc6KiiiPqk9HflaNkUbzF
GI-196 | HK06-1 | APAC | Closed | P3 Low CX | ychoong@ap.equinix.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | During Pre MIST - ChWP changeover/failure, both halls 1&2 exceeded 27degC SLA but return normal within 1 min. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615111&prj=501&rqi=ORjyzc5jlImHQgO7EAhGgv8nQM
GI-154 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | STSSB communication alarm is triggered during Pre-EIST | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615017&prj=501&rqi=Olvv6DYq0B7CIYxVyTVGTqVqN0
GI-166 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | Before the Pre-EIST, for all the SUDB that is not under this phase, MCB common fault is active and triggered on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615045&prj=501&rqi=ygOenvVYpb3m5UTdOMaQ4Hj4BE
GI-171 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | During HLT-13 (CRAH sensor for remote temperature, failure at data hall 1 and data hall 2), data hall 2 exceed SLA temperature high limit of 27 degree. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615056&prj=501&rqi=JuCj0IGmaMHyOokr33aVuER6i1
GI-170 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | During HLT-12 (CRAH sensor failure at data hall 1 and data hall 2), Data hall 2 reached 29.25 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615055&prj=501&rqi=w90HRXRRlW3oTIUgb4d5nVMBJo
GI-179 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | DCOS panels cannot emit fault signal for room temperature sensor for testing ICUs function for temperature sensor fault. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615070&prj=501&rqi=OjaBji1EhjcfrQ5tvwdGmuBUIv
GI-157 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | RMU_R1 is showing red-dotting line on DCOS, however no alarm can be acknowledged on the RMU_R1 side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615021&prj=501&rqi=tTyvYF0chVG12MKjXvYcOu9TB9
GI-152 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Block B receive an overvoltage issue during the Pre-HLT, causing the changeover happen between main utility and generator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615006&prj=501&rqi=3SO8rrdGqnUQY51BoM5UYn8tCS
GI-193 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS | [6 empty] | STSSB_B2R1_1 and STSSB_A1R1_1 communication alarm is triggered | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615084&prj=501&rqi=pfliuBup0NSnFTwqXrjSkR70SP
GI-195 | HK06-1 | APAC | Closed | P2 Medium CX | ychoong@ap.equinix.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | During Pre-MIST, MAU 01 found to be not runing. "SA Dewpoint High" was found on unit HMI | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615110&prj=501&rqi=LXI1yV4T7uukAuwAZlrQ7L0I4w
GI-162 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS | [6 empty] | Before the Pre-EIST started, all MSB are receiving priority 2 alarm and priority 1 alarm on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615037&prj=501&rqi=Xi32PD3EZ7ehipbHzVISujSoCs
GI-189 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | All indoor units supply air temperature lower than temperature set point at controller (set point: 16oC, measured: ~22oC). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615080&prj=501&rqi=kmA0AAXpTrYFfatTFOht0vrzip
GI-190 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | HVAC | equipment | 1FCU_M3_17 | DXID - FCU/DX Indoor Unit |  |  | FCU_M3_17 controller air speed button broken. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615081&prj=501&rqi=HpM5XkO7FNRhraoGIuF3JCssK5
GI-160 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | During the whole Pre-EIST for 15/F, all the CRAH in DH 1 and DH 2 on 15/F, the high supply air alarm is triggered on their control panel and summary alarm is triggered on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615031&prj=501&rqi=hFtimzPugqEDuUYgBaQZ36vClT
GI-168 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS | [6 empty] | During the Pre-HLT, unit individual reading should be shown on DCOS graphic and group control temperature should be | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615053&prj=501&rqi=2mgNwexMyECRyQLxhfvYPyvLtp
GI-197 | HK06-1 | APAC | Closed | P3 Low DCOS | ychoong@ap.equinix.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | During Pre-MIST, PCP 01 was failed, PCP 02 took over but "PLC Stopped" alarm was triggered for PCP 02. Redundancy Fault error alarm and PLC were also triggered for both PCP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615112&prj=501&rqi=ujnoEy9d02qfuraNSGw66hNftM
GI-165 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | [6 empty] | During Pre-EIST day 2, when we are ramping up the load to 75% (16:14), 12/F electrical room room temperature is below low limit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615044&prj=501&rqi=tEGbRBcf2BtNKsuxHPK75d7MBA
GI-164 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | surge protection device failure alarm is still receiving and active on DCOS for all MSB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615042&prj=501&rqi=ZhGAhKsBsjMvtHzAUsek6hPinJ
GI-153 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | Communication alarm for ATS is at MSB-M1 triggered during Pre-EIST when load was at 50% no switching was occuring at that point. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615015&prj=501&rqi=WdqsSG87AfLuyXXzRIUuIkoSTE
GI-158 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | UPS is triggered with high limit alarm on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615024&prj=501&rqi=3bLpJ0h6r6nVCKiuaiQhR7nbcW
GI-161 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | During Pre-EIST (EIST-15), for both of the UPS in 17/F LVSB room, external bypass breaker is closed but both of the UPS did not show it is on external bypass mode on the UPS HMI panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615033&prj=501&rqi=mzi9B2iaf7MmdMwia5vsaWDmDv
GI-188 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | HVAC | equipment | 1VRFOD_M3_5 | VRF - DX Unit Variable Flow System |  |  | 1VRFOD_M3_5 CHW flow speed and return temperature higher than design rating, Calibration cert out/dated for water temperature sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615079&prj=501&rqi=4kJCMbjeZ4Dox7fDB7eYwkxAkR
GI-155 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | [6 empty] | MAU triggered a fault alarm on DCOS but on site the MAU does not have any alarm shown during Pre-EIST | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615018&prj=501&rqi=eUiwSu3Qrnw0pNT16hSfLxF40g
GI-192 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | [6 empty] | The name specified in approved drawings is "FCU_M3_24" but the name of master panel shows "FCU_R2_24". Please clarify and rectify with correct name shown. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615083&prj=501&rqi=AcWiAwnJsefz3ZtXTq3zyb2Kky
GI-191 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | [6 empty] | For all the FCU in 17/F office rooms, E-stop not yet tested. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615082&prj=501&rqi=Z63FpheowT0yxF7IuiYQ2sSJGi
GI-167 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | [6 empty] | During Pre-HLT (HLT-3), when the data hall is on 50% load and maintaining for an 1hr, the 13/F battery room has high temp alarm triggered | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615052&prj=501&rqi=ulIrgZD7jasNJtIVwc8MQMWleR
GI-198 | HK06-1 | APAC | Closed | P3 Low DCOS | ychoong@ap.equinix.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [6 empty] | During Pre-MIST, When PCP 02 was failed, PCP 01 took over but "PLC Stopped" alarm was triggered for PCP 02 Redundancy fault error alarm and PLC were also triggered for both PCP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615113&prj=501&rqi=HQN4R62Bvlmf4taVCkyINNRwkM
GI-169 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | During HLT-10 (CRAH failure at Data hall 1 and Data hall 2), GW88_TT05 and GW94_TT06 reach high temperature after reinstate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615054&prj=501&rqi=Ts3VoYHJT75MyG1OxjLiPHE9A9
GI-159 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | During the EIST-12, when the changeover occur between mains utility and generator, both CRAH in the 17/F LVSB room is showing source 2 unavailable instead of source 1 unavailable (R1M3_1, R1M3_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615028&prj=501&rqi=K3D9NsrT2MccAFdsFuBGMmvkkq
FPT-481-014 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-10 (HLT1) 3/8/2026 GW94_TT06 high temp 27.1 and drop down to 26.9 within sec @05:25 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615593&prj=501&rqi=gIH24rFenoZXTcq8iDLGiMYv8T | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-015 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT-21 (HLT1) 3/8/2026 After Estop the WCC, CHWP can keep running for 2 mins. However after 2 mins, reset estop WCC and reset string 1, but string 1 cannot be reset to resume operation (string 2 was in maintenance mode). SE to clarify whether it fulfills the design intend. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615594&prj=501&rqi=v1aS7CelheeIniiSeaiJlPG1wb | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-010 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT-1 (HLT1) 3/8/2026 1EF_R1_6 had common mismatch alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615589&prj=501&rqi=SijDPhRIwwhI2aIRVit31Cn8zn | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-009 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | HLT-1 (HLT1) 3/8/2026 CRAH_LR1_15 &16 had lo/lo temp alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615588&prj=501&rqi=ephRAXclEytpWKo0VwPxqnyz8J | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-004 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-2 (HLT1) 3/6/2026 13F Batt Rm, Tx Rm, LVSB Rm; 15 Tx Rm; 17F Lv Switch Rm had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615583&prj=501&rqi=iNR649abBZ4J3rbyZETfejoRqN | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-1 (HLT1) 3/6/2026 12F LVSB Rm, Tx Rm; 15F Tx Rm, Batt Rm;17 LVSB Rm had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615574&prj=501&rqi=TVbBVMXL1QnvpqV8KXNd9RDH07 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-003 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | High supply air temperature alarm for DH2 CRAH were triggered at 03:32 and resume at 03:32. Datahall keeps maintaining SLA range. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615582&prj=501&rqi=8R9NUvWprZbJf2TF7x2Sss5FI1 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-002 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS | HVAC | system | Mechanical System |  |  |  | Tuning the bypass valve min flow delay to 20s at 02:38 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615578&prj=501&rqi=jOUvrfJHuH445lpuhm58AedbxL | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-006 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-3 (HLT1) 3/6/2026 12F Tx Rm LVSB Rm; 13F Tx Rm, LVSB Rm; 15F Tx Rm and Batt Rm; 17F LVSB Rm 2 had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615585&prj=501&rqi=bYGGrNRZjibZ4tTArcrPSnH1Mw | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-007 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-4 (HLT1) 3/6/2026 12F Lv switch room had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615586&prj=501&rqi=7vkCY2MeQTZtLAhfuJQPpZP9Jv | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-008 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-5 (HLT1) 3/6/2026 12F Tx Rm, 13F Tx Rm, 15F Batt Rm, Tx Rm and 17/F Tx Rm, LVSB Rm had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615587&prj=501&rqi=tiB3NBojTNkJr5o6V7PNpAZpep | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-005 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | HVAC | system | Mechanical System |  |  |  | HLT-3 (HLT1) 3/6/2026 DH1 CRAH 04,05,08,09,10 had high supply air temp alarm triggered at 04:18 and resume at 04:19 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615584&prj=501&rqi=Gd1r0vUodmzSLvLEFmXbGh9uWQ | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
GI-149 | HK06-1 | APAC | Closed | P3 Low CX | keymanchan@commtechasia.com | 2026-03-05 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | 16/F Chiller Plant - Emergency lighting discharge lower than 2 lux. (measure from floor) at the beginning of battery discharge The possible reason is chiller block the path of light. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614773&prj=501&rqi=6u933WQzf6hUiDx7Mgc37xKxqs
GI-150 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-05 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | During heating mode, 1 outdoor unit will run. If it fails, it does not changeover to the remaining units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614790&prj=501&rqi=Aycn2OJTmMymuEE3WofNny52wd
GI-151 | HK06-1 | APAC | Closed | P3 Low DCOS | JosephHalim@commtechasia.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | MAU overview page showing Static Pressure (Pa) - to change to Fan Flow (l/s). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614792&prj=501&rqi=kbGdigHgQ7GX2LWuPcpAW5pc2C
GI-148 | HK06-1 | APAC | Closed | P3 Low DCOS | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | GEM and SE to coordinate and ensure all setpoints put on DCOS are according to approved settings as alarms were not activated during testing due to incorrect setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483404&prj=501&rqi=oAyOyRBpColSgrKwWxkqT8kDiU
GI-143 | HK06-1 | APAC | Closed | P2 Medium CX | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Gammon to clarify with NV5 the design intent and control logic of outdoor unit activation under different cooling mode temperature. If it is solely controlled by off-coil CHW temperature reading, or if airflow is also considered. To clarify and update SoO. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483399&prj=501&rqi=PmkcX43z0sMnzZvA0mnNMg1m2p
GI-142 | HK06-1 | APAC | Closed | P2 Medium CX | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Gammon to clarify with NV5 the design intent and control logic for CHW Valve under Free-cooling mode. Whether it operates as pre-treatment or not under free cooling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483398&prj=501&rqi=bhSju4zFnb67iJYiS3VOFZ7o1J
GI-145 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | GEM to coordinate with Saiver and SE DCOS to rectify DCOS-autoON function for MAU unable to automatically restart upon power failure resuming. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483401&prj=501&rqi=zMkWCiEtO9BM2NQoxEcZHHeo1l
GI-147 | HK06-1 | APAC | Closed | P3 Low DCOS | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Fan flow not showing correct reading on DCOS for MAU 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483403&prj=501&rqi=EYWpNAXu4ghHGOAtTxhAkTHG0s
GI-144 | HK06-1 | APAC | Closed | P2 Medium CX | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Gammon to clarify with NV5 the design intent and control logic for CHW Valve under heating mode. Whether it operates as pre-treatment or not under Heating. To clarify and update SoO. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483400&prj=501&rqi=oFjRPxqFZucjKX3uHhZ1OJIphY
GI-146 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Compressor #3 icon not showing running / not running status on MAU 1 & MAU 2 DCOS Graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483402&prj=501&rqi=rzwMUxhAG3pBl44kLiKlUSSB9q
GI-141 | HK06-1 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | HVAC | equipment | 1CHWBT_5 | CHWBT - Chilled Water Buffer Tank |  |  | TCV_03 for CHWBT_4 and CHWBT_5 mal-function | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483390&prj=501&rqi=cmXEbOP1KlyJwOGNCRZZklGI2C
GI-140 | HK06-1 | APAC | Closed | P2 Medium CX | JosephHalim@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Control logic deviation from SoO: After 20 minutes (1200s) of exceeding the high SA temperature dewpoint, MAU should raise a high SA temperature alarm and shutdown. However - only alarm appears with no shutdown sequence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483389&prj=501&rqi=38WkhFDWZb7fbPQEOzxVgsfEEB
GT1DCOS-25-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_30 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352268&prj=501&rqi=vIIECqVnEeiLGIeJaLSK2jGopC
GT1DCOS-26-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_31 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352263&prj=501&rqi=yffzSJNGawjkQy2wCCMwkhrigS
GT1DCOS-27-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_32 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352264&prj=501&rqi=T1rbEUdl8Fji0h172AB53poqhz
GT1DCOS-23-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_28 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352266&prj=501&rqi=pDfIT7uuoYs8OMoT5iGiustAon
GT1DCOS-28-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_33 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352265&prj=501&rqi=3IB8Fp4v65TTiFdM8mTYayhNJk
GT1DCOS-24-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_29 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352267&prj=501&rqi=1drDd4V6fA6SqwXp1cozFJGbhA
GT1MECH-2-007 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Humidifier running status to be clarified. Individual running status should be provided on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204111&prj=501&rqi=VisNpRWfXDVhDtjHFtdZSOt2UB
GI-128 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | It is observed that no command point is available on DCOS. Please clarify deviation with point schedule Chilled water valve command Return air temp setpoint Supply Air temp setpoint Supply Fan speed command | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204101&prj=501&rqi=wkHpINUjk0a6nWNe8kSY5IF99u
GI-129 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | It is observed that these points are not available on DCOS. Please clarify deviation with point schedule Entering Water Temp kW Leaving Water Temp Supply fan command | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204102&prj=501&rqi=59TjndF5kERzO9WrUj0XgOgpHD
GT1DCOS-31-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_36 | DCOS - Control Panels |  |  | Full point-graphic report outstanding. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221097&prj=501&rqi=OozOOwvsxRGA3d7uxVdY1pbwD1
GT1MECH-2-015 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | EC fan kW unit to be checked. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204120&prj=501&rqi=B71TUVCf6TvtLlfdZYcRktKPMK
GI-119 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS |  | system | Rblock R |  |  |  | DCOS power line issue - Some power line is not shown with color when it is energised, some is showing with color when it is not energised. In general, the DCOS power line graphic for each equipment has variation to the real-time situation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204085&prj=501&rqi=f6mkPADKqpy6L07Zr5ioOd84ew | https://equinix.facilitygrid.co.uk/x/project/501/system/13010
GI-121 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | ATS alarm log description should be aligned with the graphic description. Normal source available (Rename as normal source not available) Alternative source available (Rename as alternative source not available) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204088&prj=501&rqi=WIGONV8XrWYTRFixxoHSNZjrkU
GI-117 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS |  | system | eWall B |  |  |  | DCOS power line issue - Some power line is not shown with color when it is energised, some is showing with color when it is not energised. In general, the DCOS power line graphic for each equipment has variation to the real-time situation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204083&prj=501&rqi=OticWVFerXTG6tJDA0AGphmk7p | https://equinix.facilitygrid.co.uk/x/project/501/system/13008
GT1MECH-2-010 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Outdoor air damper feedback to be clarified. It shows in 'percentage' on GUI which deviates with point schedule. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204115&prj=501&rqi=n12HbHtU4aD2pntXz9ehg2uqE7
GI-118 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS |  | system | meWall M1 |  |  |  | DCOS power line issue - Some power line is not shown with color when it is energised, some is showing with color when it is not energised. In general, the DCOS power line graphic for each equipment has variation to the real-time situation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204084&prj=501&rqi=jacPOeldcvGHWKfvEPvy4pP0sa | https://equinix.facilitygrid.co.uk/x/project/501/system/13009
GI-123 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that CRAH ATS on alternative status is off when normal source is resumed and ATS is counting down to transfer back to the normal source. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204094&prj=501&rqi=VzDhRU6dWfGyqDBB31nWQXFU4Q
GT1DCOS-29-001 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_34 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221094&prj=501&rqi=h8rj2aJtleIez821nKAilEh3bW
GT1MECH-2-006 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Humidifier control signal to be clarified. It functions as "Read" point which deviates with point schedule | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204110&prj=501&rqi=4oRUA79wDaGILg3njhbYiQkieI
GI-124 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that there is no status update under column "Total" and "Active". Please clarify any status when unit is running or having alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204095&prj=501&rqi=gNfUgz8hXPkW1R0yCB0cERlYLr
GT1MECH-2-008 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Humidity setpoint is not available on DCOS. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204112&prj=501&rqi=jS0gpfacUrO69Oi2w6Vlj6XbmP
GI-125 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that no reading under column kW. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204096&prj=501&rqi=Q8OGpMPrEpwp03BmlTqoms3uaW
GT1MECH-2-012 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Supply air temperature setpoint is not available. MAU is controlled by supply air dewpoint temperature. Please clarify with GC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204117&prj=501&rqi=T3KxNOdZm2puknoHEwOeMsFPs4
GT1MECH-2-009 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Outdoor air damper command to be clarified. It shows in 'percentage' on GUI and functions as "Read" point which deviates with point schedule. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204113&prj=501&rqi=dgPTltYbuTvaO7cmMG7XiLvoQi
GT1MECH-2-005 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Humidifier command to be clarified. It shows in 'percentage' on GUI and functions as "Read" point which deviates with point schedule | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204109&prj=501&rqi=MbJTTkeKtiAnFDHOWFafpxuHnR
GT1MECH-2-001 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Decimal for Supply air fan flow and Air flow sensor range to be checked with GC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204105&prj=501&rqi=iDr07mJlYKd6Yhi5ugcJeTmPXz
GT1MECH-2-003 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Low temperature detector alarm is not available. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204107&prj=501&rqi=KQ2gNpN50QgnszBGoOfCLj8Xy0
GT1MECH-2-011 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Smoke detector alarm mapping mismatch. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204116&prj=501&rqi=PfiX0nZa1ggaskah0uMC41ewdg
GT1DCOS-30-001 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_GWP_35 | DCOS - Control Panels |  |  | Full point-graphic report outstanding. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221095&prj=501&rqi=fR4emmHpOtGnGBJg4GqpR7IyTl
GT1MECH-2-014 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | EC fan DC bus voltage is not available on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204119&prj=501&rqi=UtNOE4Wtl2RtDbnjvkzvjm0AWs
GI-136 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | system | DCOS |  |  |  | It is found that SLA sensor reading have disconnection issue on DCOS. Please double check the configuration. Issue found on SLA sensors at 15/F DH1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221088&prj=501&rqi=mlAImNsIB923DYH73bvbi2vLxD | https://equinix.facilitygrid.co.uk/x/project/501/system/13006
GI-137 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | system | DCOS |  |  |  | It is found that Environment sensor alarm cannot be shown in the alarm log (Area Hierarchy) Issue found on room temperature sensor at floor 6,9 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221089&prj=501&rqi=U7UXOJ4FUHqK7g2woM65srKM8A | https://equinix.facilitygrid.co.uk/x/project/501/system/13006
GI-130 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | system | DCOS |  |  |  | Some SLA sensor faceplates are mal-functioning which is normal during the point-GUI test before. Issue found on SLA sensors at 15/F DH1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204123&prj=501&rqi=ioFO0Bi0aZPFP0lyCcAEkSTmsi | https://equinix.facilitygrid.co.uk/x/project/501/system/13006
GT1MECH-2-013 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment type | AHU - Air Handling Unit | AHU - Air Handling Unit |  |  | All MAU unit / EC fan Auto status not able to be shown as operating on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204118&prj=501&rqi=ahTanoNNMT4eD2k7GMIuvlRm5M
GT1MECH-2-004 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Chilled water valve command to be clarified. It functions as "Read" point which deviates with point schedule | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204108&prj=501&rqi=Eo3NhflnfgzmE4AUrdwYKxTFut
GI-131 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | system | DCOS |  |  |  | It is found that SLA range is incorrectly set. Please confirm the setting and rectify it. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204124&prj=501&rqi=1V7dIwOFYBWOGI62IlZNveR0cp | https://equinix.facilitygrid.co.uk/x/project/501/system/13006
GI-127 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | Mechanical Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that ATS alarm description is different with point schedule. Please clarify deviation with point schedule Normal source available (Rename as normal source not available) Alternative source available (Rename as alternative source not available) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204098&prj=501&rqi=5YIGO98WZenlJteyRuWf5ChEJj
GI-122 | HK06-1 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that CRAH ATS alarm normal source not available alarm stay active even though normal source is resumed. Alarm returns to normal status after ATS transfer back to normal source. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204089&prj=501&rqi=hE40D9XkSyqfr2zJ3eLc8YBB4h
GT1MECH-2-002 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Supply air static pressure is showing supply air flow rate reading. Please clarify the deviation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204106&prj=501&rqi=A4bPqk1VQeBFil7eewz8dNw8Xx
GI-126 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | It is observed site legend shows critical, high, medium, low alarm. In DCOS SICD document for CRAH, alarm severity is shown as urgent, high, low, inform. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204097&prj=501&rqi=bBH8ns1M87JWioK4bAJx7qrWNs
GI-083 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS | [6 empty] | MAU graphic is not ready and self test has not done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199729&prj=501&rqi=841xTYWjrJ9WPIrIS7LfjehNOk
GI-087 | HK06-1 | APAC | Closed | P3 Low DCOS | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | BTMS DCOS communication issue - server is not ready and point is not checked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199734&prj=501&rqi=XWGwC6op5fNk9gMLw9p0LXjHtJ
GI-082 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | It is observed that CRAH ATS alarm cannot be reset by "acknowledge" button after power resume. Please double check the logic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199728&prj=501&rqi=rzXsVgozI2GB7Je6NG0Aojg1ry
GI-085 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | FCU DCOS issue - further clarification required where one point on DCOS is not done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199731&prj=501&rqi=4lylsxe0EVRJDzgtDEh7smBscJ
GI-084 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | VRV point to graphic issue (control card issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199730&prj=501&rqi=ZpCANXB62L5sCnK48ahKpq04rg
GI-086 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | VER - Vertiv Electrical |  | Commissioning Issue | Commissioning | [6 empty] | RPP DCIM point mapping issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199733&prj=501&rqi=Ic2gCFSvWBVaVNRIBdXjo7QvOu
GI-081 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | Electrical Contractor |  | General Design issue | Design | [6 empty] | Fuel pump system SOO issue - during scenario where more than 8 generators sent signal for refilling fuel and a fault occur, pumps were not able to start up or changeover | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199725&prj=501&rqi=tBeRwbNbP5pVhEg3qD8Ef5SPPZ
GI-088 | HK06-1 | APAC | Closed | P3 Low DCOS | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | Chiller logic on DCOS is not ready - some of the logic is not following the SOO even though it can run in auto mode | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199735&prj=501&rqi=htK23ZBOU35MAM3sovffj4UVZn
GI-080 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Fuel pump system Cx L4 - A total of 8 to 15 nos. of Genset hall fill requests, the full system cannot be operated if A1 & B1 of the pumps have a fault. - The full system cannot be operated if Special Changeover scenarios (Already 2 Pump Running, Possible request more than 3 Pump). Because the logic can let both pumps A1 & A2 run or both pumps B1 & B2 run. But it cannot operate any swap combination pattern, both pumps A&B running together. The system will be in â€œHungâ€ Status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199632&prj=501&rqi=uqfFTRC4W1uCpA83vbWdf21uVc
GI-079 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS |  | system | eWall A |  |  |  | DCOS power line issue - Some power line is not shown with color when it is energised, some is showing with color when it is not energised. In general, the DCOS power line graphic for each equipment has variation to the real-time situation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199630&prj=501&rqi=KT03kXJtGOtsafKk5E6NZql7V7 | https://equinix.facilitygrid.co.uk/x/project/501/system/13007
GI-074 | HK06-1 | APAC | Closed | P3 Low CX | leocheng@commtechasia.com | 2026-02-16 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | STSSB test report DCOS cap screen not fully completed. Pending Vertiv to coordinate with Schneider to collect all cap screen to finished test report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199253&prj=501&rqi=i1mXWiAsevx42X4MavYNl4OgYK
GI-075 | HK06-1 | APAC | Closed | P3 Low CX | keymanchan@commtechasia.com | 2026-02-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | BTMS (Busduct temperature monitoring system) 's DCOS part outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199257&prj=501&rqi=zG5vFlroV4XHdz9SpdOPMT8e0y
GI-070 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that there is no status update under column "Total" and "Active". Please clarify any status when unit is running or having alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199235&prj=501&rqi=xX0wZVcEBDCiMNAFHOcxWFy7Vx
GI-068 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that CRAH ATS alarm cannot be reset by "acknowledge" button after power resumption. Please double check the logic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199232&prj=501&rqi=VQkcYUVI7dpe2TbrlhD6H74gTI
GI-071 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that no reading under column kW. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199236&prj=501&rqi=I2NwCvGstrvJ3c6IuakeJHAGEj
RT1MECH-3-001 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | HVAC | equipment | 1MAU_M2R1_3 | AHU - Air Handling Unit |  |  | Nameplate of 1MAU-M2R1-3 is showing different model number to the approved material submission. Approved model: A1(C)1330H-1050W, while onsite model number on nameplate is showing A1(C)1330H-1200W. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199229&prj=501&rqi=T0R3VYgfBU0DItmAXzC9b9w1M4
GI-073 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | Mechanical Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | Entering Water Temperature kW Leaving Water Temperature Supply Fan Command Normal source available (Rename as normal source not available) Alternative source available (Rename as alternative source not available) Please provide clarification and confirmed with EOR for any changes | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199238&prj=501&rqi=wwdyyalp7MqafihZpw0c9yceE2
GI-072 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | It is observed site legend shows critical, high, medium, low alarm. In DCOS SICD document for CRAH, alarm severity is shown as urgent, high, low, inform. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199237&prj=501&rqi=QwnyvbYiBhXlQh3nVi7rswEu42
RT1MECH-2-001 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | 1MAU_M3R2_2 panel affixed with un-updated equipment ID: 1MAU_M2R1_2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199234&prj=501&rqi=NCzO3vRS85WGhk814fVbgSlwQS
GI-069 | HK06-1 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | ATS alarm log description should be aligned with the graphic description. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199233&prj=501&rqi=WTihjzPGoiY8gV6ZKNxOqk9h4J
GI-066 | HK06-1 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-02-13 04:00:00.000 +0400 | General Contractor |  | Component/Equipment failure | Commissioning | [6 empty] | During dummy load test, dummy loader failed to startup. Was first reported that the unit control power shut down during testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199177&prj=501&rqi=NTFSlACHMlN4Wi3urS7bC2UJ3a
GI-067 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-13 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS | [6 empty] | Gen set L3 Fuel pump system point to point test & logic test issue 1. Is the global design graphic for the "Main Tank X lockout" point and alarm show in the pump information? Please clarify. (image 1) 2. In the DCOS graphic during whole fuel pump logic test & point test, all fuel running path are outstanding (image 2, image 3) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199208&prj=501&rqi=X2PJpRpDDvmYHJElTL8pw5mbj7
GI-064 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | BTU 24 hr discharge test were not able to follow as per the playbook intention. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199105&prj=501&rqi=eRzY6S7OebkDQxTBTn7u7YcFpX
GI-065 | HK06-1 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | HVAC | equipment | 1EF_M3_7 | EF - Exhaust Fan |  |  | The exhaust fan type of 1EF_M3_7 in SOO not align with approved fan equipment schedule. In-line fan type approved in equipment schedule, however EC fan type approved in DCOS fan SOO | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199113&prj=501&rqi=XbJWhnglPpcqZ2p9rsRD75gZIG
GI-063 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS | [6 empty] | RMU power path is incorrect. During Cx L4 testing for the RMU, when both of the incoming VCB is open, the power path connecting between both of the RMU is showing to have power floating, whereas the RMU is also shown to be energise to the downstream. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199102&prj=501&rqi=dHYjH29WXf1s5MJx5gXPP6D31K
GI-061 | HK06-1 | APAC | Closed | P2 Medium DCOS | PerryLee@commtechasia.com | 2026-02-11 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | HVAC | equipment | 1CHWSTR_M1R1_1_CWP_1 | CWP - Condenser Water Pump |  | Ebara | WCC and CHWP fail to start but fault alarm not triggered on DCOS due to incorrect set point | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198976&prj=501&rqi=uoGJtkKvzTzro4TiQrLjPYPqlz
GI-060 | HK06-1 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-06 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS General Issue | DCOS | [6 empty] | DCOS graphic for chiller is not ready, immediately fix and solution must take action | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198686&prj=501&rqi=ARmcb6e1u0wgMPROAgm0Fd1ZeY
GI-056 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | DCOS and the network is super slow which it has slowed down the T&C process | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198319&prj=501&rqi=LDbIFAMg59Cgmzmxy4NwzuAww4
GI-059 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS | [6 empty] | RMU point has issue during Cx L4 During the Cx L4 test for RMU, when one of the VCB is opened, the DCOS graphic for the RMU went offline. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198474&prj=501&rqi=7EcFZzolezRuCdm9PbnKmocxxp
GI-057 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | SCH - Schneider MV |  | General Design issue | Design | [6 empty] | BTU for SUDB not able to do 24hr discharge | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198320&prj=501&rqi=o1o5YpUukRosRixfmRs6KKK1Sj
GI-058 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | UPS did not exit ESS mode when it is performing 0% to 50% step load | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198323&prj=501&rqi=AotbuUIq6xiDY01FrdSVys7azK
GI-048 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | As per SOO, fan speed will ramp to meet the setpoint if remote temperature reading is higher than setpoint, vice versa. It is observed that fan speed will ramp when remote temperature is getting closer to setpoint. Please clarify PID / proportional band setting for CRAH fan speed control and update equipment setting table for fan speed control. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198223&prj=501&rqi=53NJiuGc0w5KC1vR67VJjPXrEn
GI-054 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | It is observed that multiple CRAH units supply air grille are damaged and the condition of SAGs are deteriorating. Please provide a schedule for replacement work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198231&prj=501&rqi=niQtlteQHBK75h4Qh4e4Bprb3g
GI-046 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | As per SOO, CRAH equips with in-built return air temperature sensor in Lv Switch Room and in-built return air temperature sensor with humidity in DataHall. It is observed that in-built return air temperature reading is excluded. Please clarify whether it fulfills design intent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198219&prj=501&rqi=CnCdxLpCacAyvozrIGvdsxQhT3
GI-044 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | CRAH fan speed is controlled by return air temperature reading while return air temperature consider highest CRAH unit average remote temperature reading in group for calculation. Please clarify whether it fulfills design intent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198216&prj=501&rqi=TX6voIGV9jRaTww0WtxWrdiOCD
GI-040 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | Missing cover for remote air temperature sensor for CRAH. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197702&prj=501&rqi=ZsJddINlPHcomQHGGQBa7IfZ98
GI-041 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | General Design issue | Design | [6 empty] | When the transformer is de-energized with high temperature trip, power loss to the transformer control power because the incoming control power is coming from one of the DB in MSB which does not have any UPS power back up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198186&prj=501&rqi=zqnIgighOydj3RD8ZN7AkH4CcZ
GI-047 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | It is observed that CRAH unit in group mode consider highest RAT and SAT reading for fan speed and valve control. High / low return air temperature and supply air temperature alarm activation also follow the same logic. Please clarify whether it fulfills design intent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198221&prj=501&rqi=vZgeGGYRCK6ZoxE6RBejwOw1Ai
GI-052 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | As per SOO, CHW valve will be opened to Vmax position. It is observed that CHW valve will close after lost of command signal. Please clarify the deviation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198229&prj=501&rqi=TS3FBG3LgkONeTkeREz5l8n9De
GI-050 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | It is observed that no alarm will be raised on controller under dual power failure condition. It is deviated with SOO. Please clarify the discrepancy. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198227&prj=501&rqi=QHIobVAAuHwIlNOmvBklW3DU7V
GI-051 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | It is observed that CRAH unit requires a close contact for VAC trip while â€œNOâ€ contact is a common practice for fail safe purpose. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198228&prj=501&rqi=nDQpDPkDTkpI672x6r4dBIgWKF
GI-055 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | It is observed that CRAH ATS on alternative status is off when normal source is resumed and ATS is counting down to transfer back to the normal source. (DCOS) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198233&prj=501&rqi=I7HI7grUIXKKwMhNttCLDOU7Bs
GI-042 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Please confirm ATS setting for CRAH in UPS Room that is not supplied by UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198208&prj=501&rqi=26pPDYGTTuVi0FkeMRPTAQB3y6
GI-045 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | It is observed that CRAH supply and return air temperature in group mode is showing the group control temperature on DCOS(All units have the same reading on DCOS). Individual CRAH unit temperature reading cannot be shown on DCOS. Please clarify whether it fulfills design intent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198217&prj=501&rqi=6atzyHTDEneG25A0YyVUz5e3PW
GI-043 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Please confirm remote temperature setpoint in UPS Room. As per SOO, the setpoint is 27degC. It is observed that CRAH in UPS Room is operating at 60% at low load conditions. Return air temperature (from remote temperature reading) is around 25 degC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198215&prj=501&rqi=1UisAc3WlDWXZX9D9Zqg6WlCJi
GI-049 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | As per SOO, remaining fan will ramp up to maximum speed. It is observed that CRAH unit in group control mode will be ramp up to maximum fan speed and stop running afterward when single fan within CRAH is failed. Please clarify the discrepancy. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198224&prj=501&rqi=oHLyprpFpd3n1hQj3vbIV86WoU
GI-039 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-01-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | DCOS network is not stable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197602&prj=501&rqi=OlDABZBFNO6fb5TmbSGDXWCcpT
GI-038 | HK06-1 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-01-26 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | UPS physical damage for UPS L12, L13, L15, L17 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197553&prj=501&rqi=djI5f4TuaGPXioRNZOUEvDZnCx
GT1ELEC-32-001 | HK06-1 | APAC | Closed | P3 Low CX | lawkwokfai@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Construction Manager | L3 | Commissioning Issue | Commissioning | Electrical | equipment | 1ATSMI_M1R1_26 (1ATSMI_M1R1_33) | ATS - Automatic Transfer Switch |  |  | ATS ID number do not match DCOS; B-C & A-C have 54V shown on display and DCOS when power off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197441&prj=501&rqi=mQ8Qg2KKGwzkJd6D8xQ81gfj6A
GT1ELEC-36-001 | HK06-1 | APAC | Closed | P3 Low CX | lawkwokfai@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Construction Manager | L3 | Commissioning Issue | Commissioning | Electrical | equipment | 1ATSMI_M1R1_27 (1ATSMI_M1R1_34) | ATS - Automatic Transfer Switch |  |  | ATS ID number do not match DCOS; B-C & A-C have 54V shown on display and DCOS when power off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197442&prj=501&rqi=2oSk7EA6MDns64EhYRLNMPG89u
GT1ELEC-30-001 | HK06-1 | APAC | Closed | P3 Low CX | lawkwokfai@commtechasia.com | 2026-01-21 04:00:00.000 +0400 | Construction Manager | L3 | Commissioning Issue | Commissioning | Electrical | equipment | 1ATSMI_M1R1_24 (1ATSMI_M1R1_31) | ATS - Automatic Transfer Switch |  |  | Communication alarm test with DCOS fail, device name matched drawing and FG but not match DCOS, B-C and A-C have 54V shown on display and DCOS when power off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197306&prj=501&rqi=woYrOwdF1gr3lbATxqsbfAiKBP
GI-037 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | It is observed that ATS Alarm - Normal source not available and alternative source not available alarm was shown on DCOS graphic which are deviated with point schedule. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197243&prj=501&rqi=VyUy0Whl0nGHjKc8I85vmRZ8ZK
RT1MECH-211-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | HVAC | equipment | 1EF_L_2 | EF - Exhaust Fan |  |  | Installation of motion sensor will be verified at Cx3 after completion of fitting out work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197098&prj=501&rqi=9vUd25UGpZKLYquzIy9w01e8iF
RT1MECH-102-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | HVAC | equipment | 1EF_A_1 | EF - Exhaust Fan |  |  | Installation of motion sensor will be verified at Cx3 after completion of fitting out work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197096&prj=501&rqi=UCqtOFXIkWANpVP7UMDfodattS
RT1MECH-210-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | HVAC | equipment | 1EF_L_1 | EF - Exhaust Fan |  |  | Installation of motion sensor will be verified at Cx3 after completion of fitting out work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197097&prj=501&rqi=84iqyPjBa2z77ey85qIWVDhPzh
GI-036 | HK06-1 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-01-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | 1. ATS equipment ID not aligned between DCOS and on-site layout. 2. Communication alarm only response when both sources is detected with 0V which it should not be the case. 3. When the main source of the ATS is simulate with lose of power, main source still detect with around 50V on phase to phase, this happen same to the alternative source of the ATS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197062&prj=501&rqi=xIiQzAGFEnsM9bQwMprEmJrKLY
GT1ELEC-31-001 | HK06-1 | APAC | Closed | P3 Low CX | lawkwokfai@commtechasia.com | 2026-01-16 04:00:00.000 +0400 | Construction Manager | L3 | Commissioning Issue | Commissioning | Electrical | equipment | 1ATSMI_M1R1_25 (1ATSMI_M1R1_32) | ATS - Automatic Transfer Switch |  |  | Communication alarm test fail, device name match drawing and FG but not match DCOS. B-C & A-C have 54V shown on display and DCOS when power off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197312&prj=501&rqi=9Ba7pR9YO1wlikJW4pUaiWlO3M
YT1MECH-247-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-02 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | HVAC | equipment | 1FCU_M3R2_53 | FCU - Fan Coil Unit |  |  | Scratches were found on LMCP casing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196248&prj=501&rqi=85RJEiY6GBXKUdM3bDBjFkLUW9
YT1MECH-237-001 | HK06-1 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-02 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | HVAC | equipment | 1FCU_R2_54 | FCU - Fan Coil Unit |  |  | Scratches were found on LMCP casing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196249&prj=501&rqi=vGO5h0fQzy6IpHOjZnZIPf72n6
YT1ELEC-419-001 | IL03-1 | S-EMEA | Open | P3 Low CX | o.alemdag@core-group.me | 2026-09-15 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | Trace Heating (Chilled Water) | TRACE - Trace Heating |  |  | L2b_Elec_OA: There are defects on this panel as follows. Pictures are also attached. * Cables routed on earth bar * Two cable lugs connected at a single termination point * Deep cleaning required * Missing bolt connection * Missing cable tray covers * Missing covers at panel bottom * Sealing issue identified * Missing torque marks on connections * Improper cable lug installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638086&prj=609&rqi=XchHfNOMdFa1ChorNfl0103JCy
GT1MECH-378-001 | IL03-1 | S-EMEA | Open | P3 Low CX | s.collier@core-group.me | 2026-09-15 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | General Design Issue | Design | Electrical | equipment | 1HWS_C_1 | HWS - Water Heater |  |  | The access to maintain HWS C1&3 is very limited and may need ceiling removed to replace the Heater if required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638114&prj=609&rqi=snarvPeohAaMWdGwKVw7T81bc9
GT1MECH-136-001 | IL03-1 | S-EMEA | Open | P3 Low CX | k.erbay@core-group.me | 2026-09-03 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_R_01 | CRAH - Technical Room CRAHs |  |  | The ventilation grille's louver is damaged and the mounting screws are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636649&prj=609&rqi=DNTNJV4IH0LCGpWuMGcuFBxchn
L2L3 Sun-159-002 | IL03-1 | S-EMEA | Open | P3 Low CX | o.alemdag@core-group.me | 2026-08-18 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning |  | equipment | PAVA Main Equipment Rack | PAVA Main Equipment Rack |  |  | L2b_Electrical_OA: During L2b inspection, following issues are found the PAVA panel in the security room. * Panel fans, some bolts and covers are rusted. Please check Image 1. * Battery connections are not completed. Check Image 2. * There is still un-terminated cable in the panel. Check Image 3. * There is high dust, foreing objects inside and around the panel. * Cable entry from above is not sealed. Covers in bottom side of the panel is not completed. Check Image 4. * Panel humidifier or thermostat setting must be set as per required value. Check Image 5. * It is not clearly visible which cable connection is done each zone. There is no label on the panel racks etc. Check Image 5. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634095&prj=609&rqi=Tmzf0brrLnfAbrPllHDv4khHDG
GT1FS-222-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | o.alemdag@core-group.me | 2026-08-18 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Component/Equipment Failure | Commissioning | Fire Suppression | equipment | 1MFD_C_62 | FD - Fire Damper |  |  | L3_Electrical_OA: There is an issue during L3 test, C _62 damper open-close status could not be completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634100&prj=609&rqi=lhWk2t58h6ez9tjxRMFwFNEuWd
YT1SEC-37-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | o.alemdag@core-group.me | 2026-08-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Electrical | equipment | NIRB.0101 | ICT Racks |  |  | L2B_Electrical_OA: Missing equipment ID tags especially AV sockets etc. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632728&prj=609&rqi=DSWpThgeOYWr1vtn25ZEMDPxgj
GT1MECH-44-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-08-03 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_17 | CRAH - Technical Room CRAHs |  |  | The equipment label on the CRAH unit is damaged and partially illegible. It needs to be replaced. This applies to the CRAH units listed below. -1CRAH_A_17 -1CRAH_A_18 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631994&prj=609&rqi=uOMTN24pzaee44SIGERetrLtJ2
YT1ELEC-34-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | a.tuysuz@core-group.me | 2026-07-20 04:00:00.000 +0400 | CMM - Cummins | L2B | Component/Equipment Failure | Commissioning | Electrical â€“ MV | equipment | 1-GEN-B | GEN - Generator (MV) |  |  | During the MV route checks from 1-GRMU-C to 1ZZTRMU_A, cracks were observed on the MV termination kits (Euromold type) installed at the incomer connection from the Gen-B alternator to 1-1GRMU-B. The MV cable connection between the generator alternator and the GRMU incomer shall be thoroughly inspected. The cracked termination kit shall be replaced with a new approved termination kit and the cable shall be tested following the replacement. A cable test report shall be prepared and submitted for all generator-to-GRMU incomer cables. The report shall include, at a minimum, two clear photographs demonstrating that the cable termination kits are installed correctly and are free from defects. This comment is applicable to all Generator sets and their respective GRMU incomers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630007&prj=609&rqi=7m2FMWULicYoX5VFZwsQfBI3cd
RT1ELEC-32-006 | IL03-1 | S-EMEA | Open | P3 Low CX | a.tuysuz@core-group.me | 2026-07-08 04:00:00.000 +0400 | CMM - Cummins | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1-GEN-A | GEN - Generator (MV) |  |  | Regarding the ARUP exit signage and emergency lighting fixtures used in the GEN-SET area, and with reference to the correspondence below dated Thursday, 21 May 2026, at 3:47 PM, please note that the lighting fixtures inside the containers shall be fully replaced with self-contained emergency luminaires,And external lights to be provided over all acces doors. This requirement is applicable to all GEN-SET containers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628431&prj=609&rqi=yDyizvdw9v0XdU0fuf5z0CL6L7
RT1ELEC-32-005 | IL03-1 | S-EMEA | Closed | P3 Low CX | a.tuysuz@core-group.me | 2026-07-08 04:00:00.000 +0400 | CMM - Cummins | L2A | Design not as specified | Design | Electrical â€“ MV | equipment | 1-GEN-A | GEN - Generator (MV) |  |  | Regarding the ARUP / Generator Earth Bar technical submittal and the design correspondence below dated 07/07/2026 at 10:17 AM, the earth bar inside each genset container shall be rectified in accordance with the approved technical submittal and the requirements outlined in the email. This requirement is applicable to all Gensets. "The removable link shall be incorporated into the generator earth bar arrangement as indicated in the approved Cummins shop drawings. This requirement was raised during the QA/QCâ€“FAT visit, formally noted, and subsequently reminded. To remain fully aligned with the design intent, the incomer connections originating from the transformer room, local earth rods, and the serial bonding conductors between generator earth bars shall be terminated on the opposite side of the removable link, as shown in the shop drawings. This arrangement is necessary to maintain compliance with the approved design." | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628430&prj=609&rqi=IBvNLmQHFpFND7DajZwpbjCucW
L2L3 Sun-159-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | w.tavares@core-group.me | 2026-06-26 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning |  | equipment | PAVA Main Equipment Rack | PAVA Main Equipment Rack |  |  | During the L2B inspection it was found that same PAVA speakers need to be replaced, and the Cleaning has not been Completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627061&prj=609&rqi=cTlTJWBU9MAguKshdbk7ZUApEr
GI-027 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-19 04:00:00.000 +0400 | SCH - Schneider MV |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Closing interlock logic in C264: mismatch between software and wiring. There seems to have been a wiring change in the C264 interlock output contact (change from NC to NO). These wires have different labels than factory wiring. Now the latest software update in 264 matches the original wiring Even the drawings are confusing. On one page there is NC contact, on another page is NO contact. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626239&prj=609&rqi=3NTUCICNX49zR1YttlmxdBSvh6
GI-024 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-17 04:00:00.000 +0400 | General Contractor |  | General Design Issue | Design | [6 empty] | Personel cannot be evacuated safely in case of an urgent, rapid evacuation. if someone goes out rapidly from the gemerator enclosure it would find itself trapped on the plantform, on the side without ladder | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625750&prj=609&rqi=MH7AMHXRafEg2Cyn6ErUfKAdkI
GI-022 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-17 04:00:00.000 +0400 | SOC - Socomec |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Internal STSSB power connection found not torqued during ispection. (section right after the bus bar flange - see attached picture). This was torqued and marked during the inspection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625585&prj=609&rqi=s7itCgdc9qW6UnWOiOQ6pSfjM4
GI-023 | IL03-1 | S-EMEA | Open | P3 Low CX | i.vasilescu@core-group.me | 2026-06-17 04:00:00.000 +0400 | CMM - Cummins |  | Installation not correct | Commissioning | [6 empty] | MV cable tray is not secured against seismic risks. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625749&prj=609&rqi=K3EjHNLyyfikyZML8zNCeumlIm
GT1ELEC-15-005 | IL03-1 | S-EMEA | Closed | P1 High CX | m.yerkoylu@core-group.me | 2026-06-16 04:00:00.000 +0400 | SCH - Schneider MV | L3 | Component/Equipment Failure | Commissioning | Electrical â€“ MV | equipment | 1PUSP_2 | PUSP - Primary Utility Supply Panel |  |  | The L3 phase connection to the Voltage Transformer (VT) experienced an arc flash event. The VTs appear to remain structurally intact; however, arc flash marks were observed on the top surface of the L3 VT and around the L3 cable boot. The protective top cover at the L3 cable termination on the VT side was found dislodged following the incident. The VT enclosure sustained mechanical damage, with localized outward bending of the panel, but no internal components were exposed. Inspection of the L3 VT secondary wiring revealed no apparent damage to the cables themselves; only the protective sleeving showed signs of arc flash damage. It should be noted that the L3 VT and its associated cabling were factory-installed, terminated, and tested by the MCE vendor, and were delivered to site as a complete assembled package. No personnel were present in the room at the time of the incident, and no injuries were reported. Photos are attached. MCE/GC to provide RCA accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625471&prj=609&rqi=2v0dtuC6zkWkpnUYSOA3mGB63i
GI-021 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-11 04:00:00.000 +0400 | SCH - Schneider MV |  | General Design Issue | Design |  | equipment type |  |  |  |  | MV commissionability: trip signals should be made available through the test block. otherwise, with each maintenance these wires will be tampered with | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625308&prj=609&rqi=wi2lZr9BDSDQaAZMvOgycAdnYt
GT1ELEC-15-003 | IL03-1 | S-EMEA | Closed | P3 Low DCOS | i.vasilescu@core-group.me | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS Design Issue | DCOS | Electrical â€“ MV | equipment | 1PUSP_2 | PUSP - Primary Utility Supply Panel |  |  | this "alarm" needs to be properly defined. at the moment, with cb open, the alarm changes its status just by changing the disconnector | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623665&prj=609&rqi=fpQDcTbnWJXSPmcRrXauxd49UV
GT1ELEC-15-004 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider MV | L3 | Design correction needed | Design | Electrical â€“ MV | equipment | 1PUSP_2 | PUSP - Primary Utility Supply Panel |  |  | spare contact for trip lockout is wired to a NC contact. this should be wired to NO contact. change in PUSP1 as well | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623666&prj=609&rqi=vIjRhL8rnEZenwu3QISE6aL9Qc
YT1MECH-412-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-06-02 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Design correction needed | Design | Fuel | equipment | Fuel -Oil System-GEN-R | FFIL - Fuel Fill System |  |  | Access to the daily fuel tank is inadequate. The piping/valves structures installed in front of the access area restrict maintenance access and should be reviewed against the clearance requirements specified in the approved drawings. In addition, sufficient access is not available to fully open the louvre doors on the generator enclosure. A permanent access platform shall be provided to ensure safe operation, inspection, and maintenance activities in accordance with HSE requirements and the manufacturer's recommended clearance requirements. Applicable to all GEN Sets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623642&prj=609&rqi=FDbwR9AfbaWbVoJ3Emwy0kK3tJ
GI-016 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  | equipment type |  |  |  |  | this contact needs to be NO. to be modified in PUSP1 as well. attach picture with evidence to close it | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623667&prj=609&rqi=IMHOHPSR3OC01fKkJH020meW0w
GI-018 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider MV |  | Incomplete Connections | Commissioning |  | equipment type |  |  |  |  | trip circuit supervision inputs are both active when according to schematics only one should be active (return path through CB position) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623669&prj=609&rqi=Z5SyBciCS08NJFGvIKZM8gHpBY
GI-017 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  | equipment type |  |  |  |  | TRIP OUTPUT needs to LATCHED! | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623668&prj=609&rqi=Cf0wI3zhBel8WpKXuq474XGfQr
GI-014 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-21 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | system | MV System |  |  |  | Cables from Control circuits need the have their screen earthed on one end. attached, in the picture, are current measurements from SUDB. to PUSP. its screen is not earthed on any side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622687&prj=609&rqi=B4lKOihjShpgcHu4EZBL9QNZSP | https://equinix.facilitygrid.co.uk/x/project/609/system/12241
GI-013 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-21 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  | equipment type |  |  |  |  | Current measurement circuits need to have one point of earthing on star point. currently, the circuits coming from SUDB to PUSP is not earthed. a temp link has been made in PUSP1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622686&prj=609&rqi=kpN4QTp2BvsN8he3DgLAshcvIW
GI-012 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-21 04:00:00.000 +0400 | SCH - Schneider MV |  | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1PUSP_1 | PUSP - Primary Utility Supply Panel |  |  | current measurement cable cannot be of a colour identical to grounding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622675&prj=609&rqi=LgSHFZ9FxWc7DESJrxwRm2QkVI
YT1MECH-48-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_17 | CRAH - Technical Room CRAHs |  |  | The grilles of the CRAH unit was damaged (see attached photo) and needs to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622541&prj=609&rqi=uqN9KjHoJuJDOOqt1AAXcns3Ev
YT1MECH-49-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_18 | CRAH - Technical Room CRAHs |  |  | The left panel/cover of the CRAH unit was damaged (see attached photo) and needs to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622539&prj=609&rqi=MlXs1AQZrXdgxikz4lXV7WiBdN
YT1ELEC-35-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | a.tuysuz@core-group.me | 2026-05-18 04:00:00.000 +0400 | CMM - Cummins | L2B | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1-GEN-C | GEN - Generator (MV) |  |  | During the L2B inspection of 1-GEN-C comments are listed below. 1- GEN SETs pressure test reports for pipework and day tank shall be added to the L2B documentation. (Previous phase test document is attached.) 2- Pressure gauge calibration certificates shall be added to the L2B test documentation. 3- Sleeves shall be installed at the each MV cable tray joints, and the sections which is contact on MV cables shall be cut/trimmed accordingly. 4- The gap between the deck ladder and the walking platform shall be closed. 5- The GRMU MV cable glands shall be tightened at the bottom. 6- Floor openings shall be closed. ( General comment ) 7- It was observed that particles are present inside The batteries and alternator.Cleaning is done not enough. 8- Rusted IMC conduits shall be cleaned in accordance with the applicable procedure/standard. 9-Emergency lighting fixtures and signage have not been installed on the doors.( Please provide tech submittal ) 10-LV and ELV cables shall be properly rectified, as the current installation is not sufficient. 11-General and detailed cleaning of all equipment parts shall be completed. 12-Equipment (lighting switches, power outlets, etc.) shall be labeled according to the DBL circuits, not according to the cable schedule. The items listed above are applicable to both 1-GEN-C and 1-GEN-B. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622152&prj=609&rqi=iKAYWiEWHThyAuRjFHPcH5cmqB
GI-003 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Three wires are are not permitted in the same terminal. RON should get in contact with SCH and ARUP to check the two options: - add extra terminals in PUSP control panel (preferred method) - use a 4wire measurement circuit. A ready for verification status from RON should be set once an answer from ARUP is obtained | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621790&prj=609&rqi=IKZJB1spoX9uBAMkc3X2FUtd6f
GI-007 | IL03-1 | S-EMEA | Closed | P3 Low DCOS | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | PUSP - "Alarm" The tag of this signal should be changed to be self explanatory. It is supposed to be voltage presence. Both alarms are active if the Voltage Transformer is not energized - Bus without voltage. As a minimum, the "Alarm" should be changed to "Bus voltage absent". Need to clarify the actual function of this button | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621859&prj=609&rqi=UfB9NbZTU4loH0xY9JmMjkVuDB
GI-009 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | Electrical â€“ MV | equipment | 1PUSP_1 | PUSP - Primary Utility Supply Panel |  |  | PUSP - Feeder - current measurement cables don't have labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621865&prj=609&rqi=GLxPgD4Dzye3e78yQ1tYcR7Pj0
GI-004 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  | equipment type |  |  |  |  | P643 Current circuits: 34kV outgoing cable Core Balance CT is not wired as per relay manual. NER CT not present in the design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621792&prj=609&rqi=PKF7DO57QgqHLGO7d9DNdAuxAi
GI-006 | IL03-1 | S-EMEA | Closed | P3 Low DCOS | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS | Electrical â€“ MV | equipment | 1PUSP_1 | PUSP - Primary Utility Supply Panel |  |  | PUSP Bay numbers (Q01, Q02) don't match the ones from DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621857&prj=609&rqi=SnRn7edd0PR2gOgxCw7tlmT0iE
GI-008 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Design correction needed | Design |  | equipment type |  |  |  |  | PUSP - Tx Feeder- Isolator Switch Position is not present in DOCS Every HV equipment position needs to be present in DCOS one way or another | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621864&prj=609&rqi=AW2UZYFu0I61bPYRl3l8ZhTzqp
GI-011 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | PUSP - Trip Lockout signal is not latched in the relay. DCOS status won't show if a relay tripped the Circuit Breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621870&prj=609&rqi=G5JVQLiARIiTBzTknZ9gwRKsdS
GI-010 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  | equipment type |  |  |  |  | PUSP - TX Feeder - Local/Remote button not wired into relay, can't be made available in DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621867&prj=609&rqi=oSmuZJym4H25h89RWsmoGHKFt3
GI-002 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | The wires connecting the Current Transformers from SUDB to PUSP have a cross section of 2.5sqmm and they might be too thin (but as per design IL031-RON-ZZ-ZZ-SH-E-POWR-6103). Schneider to confirm that the used wire on site is the correct one by updating the IL31 - MV Network CT/VT Calculation document (IL031-SCH-ZZ-ZZ-CA-IC-MVSWGR-7009.pdf). At the moment this situation is not covered in the design. Add a calculation chapter for the CT connecting SUDB to PUSP., prove calculation with a 2.5sqmm and the length from SUDB to PUSP is within limits | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621786&prj=609&rqi=AESHGmkC8nJMnwXGXeRNXc01lh
GT1ELEC-14-002 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ MV | equipment type | PUSP - Primary Utility Supply Panel | PUSP - Primary Utility Supply Panel |  |  | PUSP Power Meter shows a frequency alarm when the line is simply disconnected. Alarm should be filtered if it's out of range during operation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621854&prj=609&rqi=Vj9TwraKLzQYWX98HUijLiqcWp
GT1ELEC-14-001 | IL03-1 | S-EMEA | Open | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV | L3 | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1PUSP_1 | PUSP - Primary Utility Supply Panel |  |  | Pendant CB status not working (light bulbs are missing) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621853&prj=609&rqi=01aoPVPWbvBQuCasjZzrZpbkGA
GI-005 | IL03-1 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  | equipment type |  |  |  |  | Breaker failure protection functionality in PUSP is reversed. Incomer sends trip to Feeder, when it was supposed to be the other way around. (executed as per drawing) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621852&prj=609&rqi=7UB5A72l2dAMHromL3MecwtFMb
YT1MECH-405-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-05-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Design correction needed | Design | Mechanical â€“ Water | equipment | 1TST_1 | CHWBT - Chilled water buffer tank |  |  | It was observed on the buffer tank recharge line that a sudden reduction from DN200 to DN80 may create an excessive increase in velocity and pressure loss. In common site practice, a maximum reduction of two nominal pipe sizes is considered acceptable. For larger reductions, a staged reduction is recommended. Confirmation by the EOR is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620694&prj=609&rqi=Y4mloel5hNOURq1q6O0OE8yzP6
YT1FS-94-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-05-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Fire Suppression | equipment | 1MFD_C_1 | FD - Fire Damper |  |  | Permanent asset label is missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620354&prj=609&rqi=wXIdiYIqEbdlNg6MdaCDzdYETS
RT1ELEC-332-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-04-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | LD-FO-GEN-B | LEAK - Leak Detection (Fuel) |  |  | Carry out full visual inspection of panel and found that metal gland shall be installed prior to the final connections of the tubes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618376&prj=609&rqi=VXfI79TUT08MvaicCNB5RoyPSW
RT1FS-259-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-04-15 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Fire Suppression | equipment | 1MFD_LB_04.3 | FD - Fire Damper |  |  | The duct connections of the fire dampers do not comply with QA/QC standards and are applicable to all transformer room dampers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618194&prj=609&rqi=9QjFG1LzDfFvBXpvlQ82JKLppb
RT1FS-260-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-04-15 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Component/Equipment Failure | Commissioning | Fire Suppression | equipment | 1MFD_LB_04.4 | FD - Fire Damper |  |  | It has been observed that the fire damper cannot be opened manually. This must be rectified prior to the L2B inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618196&prj=609&rqi=WBusZK0BcHdAngvn4bOMyf2zUG
RT1FS-180-002 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-04-02 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning | Fire Suppression | equipment | 1MFD_R_8 | FD - Fire Damper |  |  | The open/closed position labeling on the fire damper actuator is missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617135&prj=609&rqi=HjCjqFMwahuhy9vWVyqKYkpBaG
RT1FS-180-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-04-02 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Fire Suppression | equipment | 1MFD_R_8 | FD - Fire Damper |  |  | The damper does not open due to a clash between the duct elbow and the damper blade. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617134&prj=609&rqi=8TKjHOUxc6Wtqw1SKk95691jeK
RT1FS-257-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-03-31 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Design correction needed | Design | Fire Suppression | equipment | 1MFD_LB_04.1 | FD - Fire Damper |  |  | Inadequate maintenance access in LB-Transformer room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616923&prj=609&rqi=0JQcjr999gwmzv4IlqgMWPfSd8
RT1FS-255-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-03-31 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Missing Components | Commissioning | Fire Suppression | equipment | 1MFD_LB_02 | FD - Fire Damper |  |  | Missing component. Kit WE has not yet been installed yet. Applicable to all LB fire dampers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616922&prj=609&rqi=mG3xjrfLhpiBb5aQOz4yCM9F2i
RT1MECH-385-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-03-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Incomplete Connections | Commissioning | Electrical | equipment | 1HWS_C_5 | HWS - Water Heater |  |  | Equipment should be installed complete with reinforced flexible connections. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615223&prj=609&rqi=Z2E5xZ8XmiYMdjR6CVZbxPCRN4
RT1FS-53-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-02-25 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Fire Suppression | equipment | 1MFD_A_62 | FD - Fire Damper |  |  | Fire damper installed has not been supported in accordance with the approved benchmark details and project requirements. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204131&prj=609&rqi=5htq9IH2XxeBkrItZF0lgnapOu
RT1FS-4-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Fire Suppression | equipment | 1MFD_A_5 | FD - Fire Damper |  |  | This installation of the following MFDs: 1MFD_A_5, 1MFD_A_62, 1MFD_A_75, 1MFD_A_76, 1MFD_A_77, 1MFD_C_30, 1MFD_C_42 and 1MFD_E_02 are not as per the approved BENCHMARK. The installation of these MFDs shall be rectified to proceed for the L2A inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204130&prj=609&rqi=fJ8XagEoS0EOKcMximayeebTaz
YT1FS-119-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-16 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Fire Suppression | equipment | 1MFD_C_28 | FD - Fire Damper |  |  | Earthing cable is connected the MFD support system. However, bonding between the support system and the MFD body is not yet done. GC to complete the installation of the missing bonds. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199270&prj=609&rqi=AbflAqDWsDCC3rUjQ7v2FGuUcY
RT1FS-81-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-16 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Fire Suppression | equipment | 1MFD_B_27 | FD - Fire Damper |  |  | 1MFD_B_27 is not accessible due to its installation above the busbars (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199264&prj=609&rqi=hUgVhNgofwBhS6YtzaKLeUblJC
YT1FS-29-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-06 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Fire Suppression | equipment | 1MFD_A_31 | FD - Fire Damper |  |  | Body bonding is not installed. This case has been identified in many of the MFDs installed. GC to re-inspect all the MFDs and make sure that bonding is installed as project specs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198687&prj=609&rqi=tijkszVWbAbOD33CSA24cY7IVP
RT1MECH-122-002 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_18 | CRAH - Technical Room CRAHs |  |  | One of the bottom covers of the CRAH unit is damaged and must be repaired or replaced by the GC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198222&prj=609&rqi=VIoNc1M7aBblMVl6m7wzwbd5Xn
RT1MECH-122-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_18 | CRAH - Technical Room CRAHs |  |  | One seismic cable is in direct contact with the C channel support of the cable tray installed above the CRAH unit. The C channel support shall be relocated by the GC team to ensure proper clearance for the seismic cable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198220&prj=609&rqi=s4f6USXH0npyGpXfFv35FJSRPN
RT1MECH-121-002 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-03 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_17 | CRAH - Technical Room CRAHs |  |  | 1CRAH_C_17 has a visible gap between the structural frame and the black protective sheet attached to it. This defect requires correction or replacement by Vertiv. (Please refer to the attached photo for additional clarification.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198212&prj=609&rqi=s7TZMbaWxl8Bh7zT3QFraIDEDx
RT1MECH-121-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-03 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_17 | CRAH - Technical Room CRAHs |  |  | The seismic bracing cables installed on 1CRAH_C_17 at four corners do not conform to any single one of the four installation alternatives provided by the seismic design supplier. Instead, the current installation is a hybrid configuration combining elements from both Alternative 1 and Alternative 2. Vertiv is requested to provide official confirmation on whether this mixed installation is acceptable and approved by the seismic designer. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198209&prj=609&rqi=WduES0BRlrGJP9EDntgE7pQdkU
RT1ELEC-15-008 | IL03-1 | S-EMEA | Closed | P2 Medium CX | m.yerkoylu@core-group.me | 2026-01-28 04:00:00.000 +0400 | SCH - Schneider Electric |  | Missing Components | Commissioning | Electrical â€“ MV | equipment | 1PUSP_2 | PUSP - Primary Utility Supply Panel |  |  | SF gas level is found low. Close to critical level as per gauge. To be rectified prior to power on. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197726&prj=609&rqi=kkpnhTx65OlGQExj8QHLQXCSbF
RT1FS-176-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-01-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning | Fire Suppression | equipment | 1MFD_R_4 | FD - Fire Damper |  |  | The firestop label should be applied to both sides. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197246&prj=609&rqi=tpwBp5xRbw4gGG5y7MTxuC8ASx
GI-001 | IL03-1 | S-EMEA | Closed | P3 Low CX | m.yerkoylu@core-group.me | 2026-01-12 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning | [6 empty] | Damaged MV Cables (2 nos) observed at PUSP-2. GC to investigate further and propose the way forward. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196679&prj=609&rqi=AUEQVIKQLBgPog2qzvZ2SKA9IU
RT1ELEC-32-004 | IL03-1 | S-EMEA | Closed | P3 Low CX | t.marculet@core-group.me | 2026-01-05 04:00:00.000 +0400 | CMM - Cummins | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1-GEN-A | GEN - Generator (MV) |  |  | General issue for all Gensets - Earthing cables missing from the starpoin connection to the local earth bar. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196317&prj=609&rqi=NXZFTAgseMZnC7DzWH92hCGHaU
RT1ELEC-35-005 | IL03-1 | S-EMEA | Closed | P3 Low CX | t.marculet@core-group.me | 2026-01-05 04:00:00.000 +0400 | CMM - Cummins | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1-GEN-R | GEN - Generator (MV) |  |  | Generator container has a dent by the door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196318&prj=609&rqi=LP0NSCFM6HI3xbz1ufoGIHKSjn
YT1MECH-40-001 | IL03-P1 | S-EMEA | Open | P3 Low CX | k.erbay@core-group.me | 2026-09-01 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Design correction needed | Design | Fuel | equipment | Fuel -Oil System-GEN-E | FFIL - Fuel Fill System |  |  | Access to the daily fuel tank is inadequate. The piping/valves structures installed in front of the access area restrict maintenance access and should be reviewed against the clearance requirements specified in the approved drawings. In addition, sufficient access is not available to fully open the louvre doors on the generator enclosure. A permanent access platform shall be provided to ensure safe operation, inspection, and maintenance activities in accordance with HSE requirements and the manufacturer's recommended clearance requirements. Applicable to all GEN Sets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636414&prj=625&rqi=EUsa8xlP0iJnHHRplahad29bwh
YT1MECH-40-002 | IL03-P1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-09-01 04:00:00.000 +0400 | CMM - Cummins | L2B | Installation not correct | Commissioning | Fuel | equipment | Fuel -Oil System-GEN-E | FFIL - Fuel Fill System |  |  | During inspection, it was observed that the tension cable of the fire safety fusible link valve system is in direct physical contact with an adjacent metal support bracket (as highlighted in the attached image). The bracket is obstructing the free movement and direct path of the cable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636415&prj=625&rqi=c4Ow84xXurvcSMGRYvzEfpNCZq
GI-001 | IL03-P1 | S-EMEA | Open | P3 Low CX | j.shaw@core-group.me | 2026-08-24 04:00:00.000 +0400 | TRN - Trane |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Cap ends missing from pipework on Chillers. This could lead to accidental drainage of the system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634889&prj=625&rqi=9h7SQxIR6PEBpf4AVyKKHMnNP0
RT1MECH-34-001 | IL03-P1 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-06-28 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1EF_E_03.2 | EF - Exhaust Fan |  |  | The fan panel door mechanism is damaged and must be repaired. Scratches and paint defects on the panel door shall also be rectified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627220&prj=625&rqi=BbAQbec4XcDJeOQaKgMmcj2rPF
GI-279 | JH02-1/2 | APAC | Open | P2 Medium CX | junkaichan@commtechasia.com | 2026-09-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | Calculation for Riser kW is wrong - pending confirmation of correctness of TT sensors. - this affect Total Cooling Load capacity summation value. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638639&prj=632&rqi=RchjJDTss2gHoIKmlktWhQDKFu
GT1MECH-465-001 | JH02-1/2 | APAC | Open | P2 Medium CX | KaiJetSim@commtechasia.com | 2026-09-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Incomplete Connections | Commissioning | Fuel | equipment | FPPUMP1 | FPMP - Fuel Pump |  |  | FPPUMP1 While polishing process with selected FBulk_1 as supply, neither of the pump (Pump_1 / Pump_2) trip, another pump (Pump_2 / Pump_1) able to takeover. However, while polishing process with selected FBulk_2 as supply, the changeover does not happen. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638456&prj=632&rqi=Fd1cmjIbntehMVxIJnMyApjQ13
GT1ELEC-177-002 | JH02-1/2 | APAC | Open | P2 Medium CX | charitysamar@commtechasia.com | 2026-09-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | Pending DCOS point-to-graphic verification for Q16. DCOS is unable to monitor Q16 voltage (AB, BC, CA, AN, BN, CN), current (A, B, C, N), power (kW, kVA, kVAR, kWh), and power factor due to a communication/connection issue. Power meter communication interface/components require replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638077&prj=632&rqi=zuKYSORD8niIJHjF25em99qWp1
GI-278 | JH02-1/2 | APAC | Open | P2 Medium CX | junkaichan@commtechasia.com | 2026-09-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Doubtful Input power reading on JCI Chiller Control Panel. Observed WCC is reading 40kW input power at 30% motor amp on JCI chiller controller. This value is illogical and different to FWT result of 110kW input power at 31% motor ampere. Action: Please correct the reading on all JCI controller. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638065&prj=632&rqi=4bmbvibFWAvyj2LflheDfTmOys
YT1MECH-533-001 | JH02-1/2 | APAC | Open | P3 Low CX | KaiJetSim@commtechasia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Fuel | equipment | FPPUMP2 | FPMP - Fuel Pump |  |  | FPPUMP2 No pump labeling and rotation direction on pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637873&prj=632&rqi=STMECbESN4EBrNBylQpUs9svyB
YT1MECH-532-001 | JH02-1/2 | APAC | Open | P3 Low CX | KaiJetSim@commtechasia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Fuel | equipment | FPPUMP1 | FPMP - Fuel Pump |  |  | FPPUMP1 No pump labeling and rotation direction on pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637871&prj=632&rqi=ZAgtFrGdpWmZ270o9Oa30UzI0x
YT1ELEC-225-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-09-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1RPP_F1R1_2_1 | RPP - Remote Power Panel |  |  | 1RPP_F1R1_2_1 Incoming cable and earth cable not attached with label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637562&prj=632&rqi=x0S2swTqPHwDPrPxyzO8SnvBaS
GT1DCOS-10-002 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Controls | equipment | 1DCOS_RIO_1 | DCOS - Control Panels |  |  | DPT mapping for ewall riser 01 and 04 is wrong. onsite the dpt is connected to different riser not as per mapping. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637411&prj=632&rqi=zouBG2F9vOhppRMUZWtGdFj7dq
YT1ELEC-116-001 | JH02-1/2 | APAC | Closed | P3 Low CX | charitysamar@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STS_D1R1_2 | STS - Static Transfer Switch |  |  | Remove white paint splashes from the STS panel door and clean the affected surface. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637432&prj=632&rqi=eydqUlPfjCk6GS3VwnaJSndKSL
GT1DCOS-10-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Controls | equipment | 1DCOS_RIO_1 | DCOS - Control Panels |  |  | TT sensor mapping on graphic is wrong. when plug out sensor 1, both sensors 1 and 3 give out alarm. this is identical for other sensor inside the chw loop. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637410&prj=632&rqi=B9CqwIcpsT2VEXpviaBmtHCKcS
YT1MECH-257-001 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_10 | EF - Exhaust Fan |  |  | 1EF_M1_10 calibration certificate serial number for cable test on Accesstech side is not tally with the one mentioned inside checklist. Please take a necessary action. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637440&prj=632&rqi=S8dMirH3QoT60y0Ordb7R0U2t2
GT1ELEC-127-006 | JH02-1/2 | APAC | Open | P3 Low DCOS | AliHazmeerHamdan@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | UPS_A1 - Line animation still not fully configured correctly. Honeywell to rectify and ensure the animation accurately reflects the actual system status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637142&prj=632&rqi=83c1Jc5xVpR9vuDRy7jnWhrzWy
GT1ELEC-127-004 | JH02-1/2 | APAC | Open | P2 Medium DCOS | AliHazmeerHamdan@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | UPS_A1 - Refer to DCOS graphic, some item / equipment not fully configured or still shows undefined value. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637139&prj=632&rqi=xVp6GkdfjbXNmFs9ktlMsLOz0w
GT1ELEC-104-001 | JH02-1/2 | APAC | Ready for Verification | P2 Medium CX | charitysamar@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STS_E2R1_1 | STS - Static Transfer Switch |  |  | During the STS (Static Transfer Switch) Functional and Burn-in Test, a significant load discrepancy of approximately 60 kW was observed following the transfer from Source S1 (E Block) to the alternate Source S2 (R Block). The observed discrepancy is considered abnormal and requires further investigation. Contractor shall investigate and identify the root cause, verify the accuracy of the load measurement/metering and associated power distribution, and implement the necessary corrective actions to rectify the issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637145&prj=632&rqi=IRnbMz32PUIeTe8DQwktdfxshF
GT1ELEC-127-005 | JH02-1/2 | APAC | Ready for Verification | P3 Low DCOS | AliHazmeerHamdan@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | UPS_A1- Eaton shall provide the applicable threshold or range values to Honeywell to ensure that the displayed values are correctly configured and identifies any out - of range conditions or abnormal status indications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637140&prj=632&rqi=xQqiSwGOqgH0lmgkt6lbfLCTB0
GT1ELEC-5-001 | JH02-1/2 | APAC | Open | P2 Medium CX | charitysamar@commtechasia.com | 2026-09-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_R | RMU - Ring Main Unit |  |  | The RMU ring circuit breaker position is currently not indicated on the DCOS monitoring interface. Honeywell shall configure and integrate the circuit breaker position (Open/Closed) into the DCOS for remote monitoring. (This applies to MV Overview, see attached photo for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637057&prj=632&rqi=NvQPgmJraS96R7RJmM4MDjXaYo
GT1DCOS-3-006 | JH02-1/2 | APAC | Open | P2 Medium DCOS | MuhammadHaziqZakaria@commtechasia.com | 2026-09-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/Equipment Failure | Commissioning | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | DCOS graphic for FCV_03 keep flicking On and Off when the feedback is at 0%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637066&prj=632&rqi=jwiEttCEzJTE9aCpyUAl4u6W1c
GI-268 | JH02-1/2 | APAC | Ready for Verification | P2 Medium CX | junkaichan@commtechasia.com | 2026-09-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_F1 | UPS - Uninterrupted Power Supply |  |  | During Cx3 Testing for UPS F1 for 10. UPS OVERLOAD - (SINGLE) - LB ramped up to 1400kW for 10 mins to trigger Static Bypass transfer (L2 overload alarm), after Static Bypass transfer immediately L3 overload alarm triggered and offloaded the UPS. Action Required: To preform investigation and submit RCA. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636944&prj=632&rqi=F0Ia421k5g4vkdTxB3gRoW1RvM
GI-270 | JH02-1/2 | APAC | Open | P3 Low DCOS | junkaichan@commtechasia.com | 2026-09-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_A | MSB - Main Input Switchboard |  |  | Phase-N signal of voltage and current show on graphic as per required in SPL, but designed breaker is TPN. Action required: HW please confirm with EOR to remove these unnecessary items on graphic. and attach final screenshot to proof this is removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636949&prj=632&rqi=T9vCgU8Ru3DYnMnHMsLg07g0k2
GT1MECH-165-001 | JH02-1/2 | APAC | Open | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-09-04 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_06 | EF - Exhaust Fan |  |  | During Cx3 Temperature Validation, found the temperature sensor for 1EF_M1_06 show (27.7Â°C) which is a different reading (29.3Â°C) from a calibrated temperature meter. The different is higher than the acceptance tolerance (Â±0.5Â°C). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636801&prj=632&rqi=YVfEpBq7fhFfwqc458OYcKmR65
GT1MECH-172-001 | JH02-1/2 | APAC | Open | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-09-04 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_05 | EF - Exhaust Fan |  |  | During Cx3 Temperature Validation, found the temperature sensor for 1EF_M1_05 show (37.1Â°C) which is a different reading (31.3Â°C) from a calibrated temperature meter. The different is higher than the acceptance tolerance (Â±0.5Â°C). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636798&prj=632&rqi=5IA77r0notFxgKEzLi6ikZ7MpT
DCIML2B-1-001 | JH02-1/2 | APAC | Open | P2 Medium DCOS | sganeshmahadik@ap.equinix.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L2B | DCIM Maximo Issue | DCIM | Controls | system | DCIM |  |  |  | Maximo and Location Vectors list is not ready as Cx activities are going on. It's essential to DCOS/DCIM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636679&prj=632&rqi=UVIYCJKQ0ToR8Hm8zPyCA1d2Ya | https://equinix.facilitygrid.co.uk/x/project/632/system/12791
GT1MECH-137-006 | JH02-1/2 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | All CRAH units fire cable yet to be terminated to the units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636677&prj=632&rqi=ASuKcvhhmi3fNMlijoXI7rvTBR
GT1MECH-137-005 | JH02-1/2 | APAC | Open | P2 Medium DCOS | samintarajarujunan@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | Supply Fan Command Mismatch alarm unable to simulate. SE does not have fan feedback data provided to DCOS. This point is DCOS calculated and based on the onsite testing it was found that this point unable to be simulated for testing. Please recheck the logic and get the point tested to close this issue. Applies to all CRAH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636675&prj=632&rqi=PIlgf54e67CiNSDNgU2CadEw2x
GI-266 | JH02-1/2 | APAC | Ready for Verification | P2 Medium CX | junkaichan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS | Electrical â€“ LV | equipment | 1STS_A1R1_1 | STS - Static Transfer Switch |  |  | There is a list of boolean points informed by CSPM cannot be tested at P2G due to Socomec controller do not have simulation function. Please confirm with manufacturer with official letter confirmation on which point unable to be simulated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636427&prj=632&rqi=O1SIL18vC2tNQqO6WbxeO9nNW7
GT1MECH-137-002 | JH02-1/2 | APAC | Ready for Verification | P2 Medium DCOS | samintarajarujunan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | Valve Mismatch is a DCOS calculated Alarm. 30s delay has been added however during testing it was identified that the mismatch still be triggered on multiple occasion. To recheck the programming on the implementation. Applicable for all CRAH Units | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636388&prj=632&rqi=XvZlxBJKpAi13zUkcBGYlYGP6C
GT1DCOS-3-005 | JH02-1/2 | APAC | Open | P2 Medium CX | imanuddinhamdan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | Line animation and buffer tank mode is wrong when the open the FCV 03, the buffer tank mode is not changing. Line animation also | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636483&prj=632&rqi=gIxOqQSMcDOsowPPOsqgpkzkyO
YT1ELEC-108-001 | JH02-1/2 | APAC | Closed | P3 Low CX | charitysamar@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STS_F2R1_2 | STS - Static Transfer Switch |  |  | Damaged STS ventilation/insect mesh at roof support. CSPM to rectify and reinstate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636393&prj=632&rqi=jS9xvWYUN7hwwnH45Ly8H1Ul6e
GT1MECH-137-004 | JH02-1/2 | APAC | Open | P3 Low DCOS | samintarajarujunan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | The Command screen has 2 submit buttons. Apply to All CRAH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636392&prj=632&rqi=JjZ0AIVxwyFrSPRfqt7Blqino9
GT1MECH-137-003 | JH02-1/2 | APAC | Open | P2 Medium DCOS | samintarajarujunan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | Num of Units in Group is still computed based on the configuration point. This means the number is based on how many units has been configured in a group rather than a live value. During testing one of the grouping cables has been removed to observe the change in number units in group. However, found that it does not reduce. The only way to reduce the number of units in group is to configure a different value from the CRAH HMI. Applies to all CRAH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636389&prj=632&rqi=p5UBogleIrmf44R9cNAMQPwReI
GT1MECH-137-001 | JH02-1/2 | APAC | Open | P2 Medium DCOS | samintarajarujunan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | Resilient and Resiliency Vote Calculation to recheck. Once 1 of the Units from the group receive summary alarm, all the units in the group loses its resiliency vote. however, based on the approved calculation, resiliency vote is calculated individually for each unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636386&prj=632&rqi=7yf2tWuZzkDDiCOxBcPV3xHql2
GT1DCOS-3-002 | JH02-1/2 | APAC | Open | P2 Medium DCOS | junkaichan@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | CPR1- AI - FT-01 on site not performed flowrate verification and P2G - no flowmeter ready by HW. (P2-HW) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636223&prj=632&rqi=dnMjuUxQVtum7e1j45TFMnyR8c
GT1DCOS-3-001 | JH02-1/2 | APAC | Open | P2 Medium DCOS | junkaichan@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | CPR1 - DO - CT1 and CT2 share same start/stop command from DCOS graphic - whichever faceplate of CT1/CT2 give command start/stop, both CT1 and CT2 will run/stop together - confirm with HW EOR if this is intended design (P2-HW) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636218&prj=632&rqi=2U92cwMOtqEuS8ihhFGJhqbesP
GT1DCOS-3-004 | JH02-1/2 | APAC | Open | P3 Low CX | junkaichan@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | CPR1 - All Belimo valves in chiller plant no proper tagging, and some with wrong tagging. ACT to rectify based on approved schematic. (P3-ACT) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636225&prj=632&rqi=qadAbN8pkjHdpKDGFt5SCm0G9C
GT1ELEC-95-001 | JH02-1/2 | APAC | Open | P2 Medium CX | charitysamar@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STS_A1R1_2 | STS - Static Transfer Switch |  |  | During the STS Point-to-Graphic Test/Functional Test, no DCOS line animation (energized/white indication) was observed on the STS Source 2 Bypass path while the system was in S2 Bypass Mode and STS Q42 breaker was in the Open position. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636216&prj=632&rqi=0DRw6WdlQFEybCX0YhEyAhfPwi
GT1DCOS-3-003 | JH02-1/2 | APAC | Closed | P2 Medium DCOS | junkaichan@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | CPR1 - AO - CT VFD speed command not working - DCOS can't send out command signal to VFD to control pump speed (P2-HW) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636224&prj=632&rqi=i5Fx2K4IlhJ4oDFqwWYlOvmFqR
GI-265 | JH02-1/2 | APAC | Closed | P2 Medium DCOS | junkaichan@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS | Electrical â€“ LV | equipment | 1MSB_A | MSB - Main Input Switchboard |  |  | MSB_A DCOS PQM unable to communicate during official P2G witness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636171&prj=632&rqi=fHoB27edtEJXT38chBiLmzfVrh
GT1ELEC-215-001 | JH02-1/2 | APAC | Closed | P1 High CX | charitysamar@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LBSB_1 | LBSB - Loadbank Switchboard |  |  | Water ingress into the Load Bank Switchboard occurred due to incomplete cable installation associated with the Mobile Generator. Contractor shall provide an Incident Report identifying the root cause, extent of water ingress, and corrective actions taken. Contractor shall also assess and confirm which electrical tests are required to be repeated prior to re-energization of the switchboard and resumption of load bank testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635215&prj=632&rqi=lIAdfu1t9qj1z13LVPBCj2ELOT
YT1MECH-308-001 | JH02-1/2 | APAC | Open | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_5 | FPMP - Fuel Pump |  |  | The cable from 1FP_M1_5 to Overflow Pump connected to the single phase circuit has been installed 3 phase color identification (RYB). the cable color arrangement does not comply with the required single phase identification, which should be Red (L), Black (N), and Green (PE) . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635231&prj=632&rqi=LgtC9V6QtEfwo98ERcwlhsWpm8
GI-263 | JH02-1/2 | APAC | Ready for Verification | P2 Medium DCOS | AliHazmeerHamdan@commtechasia.com | 2026-08-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | The trend logging for the electrical system, particularly for the UPS systems, has not been fully configured in DCOS. The trend logs for the UPS and overall electrical system parameters are still incomplete. This limitation prevents DCOS from properly recording and trending the electrical parameters during the UPS Burn In Test. Honeywell required to complete configured and setup the trend logs for all UPS system and the overall system in DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634559&prj=632&rqi=dhZAsM8UtEYWyVlqKPH6C36WFl
GT1ELEC-128-001 | JH02-1/2 | APAC | Ready for Verification | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-08-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UPS_A2 | UPS - Uninterrupted Power Supply |  |  | During the load slowly increase until 100% (1200kVA) for UPS_A2, the UPS generated phase C Overload alarm at HMI. The overload event was triggered phase C (Blue Phase) only, while the overall UPS load remained below the configured overload threshold. the configured overload setpoint is 106%, however, the Phase C Overload alarm was triggered when measured load was still below 106% setpoint, this event occurs shows the phase is unbalanced. In addition, the DCOS did not receive or display any overload of phase unbalanced alarm from UPS_A2 when the alarm was active on the UPS HMI. The DCOS alarm indication is critical for operational operation. Any abnormal or protection event detected by the UPS should be correctly transmitted and displayed on the DCOS to alert the Operations team. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634558&prj=632&rqi=ZmVsNLqMTn3RKTVF6ABPwbeCnK
YT1MECH-216-001 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_D_1 | EF - Exhaust Fan |  |  | Found the tagging for DCOS cable is not tally between its own pair and the cable name inside checklist. Please do the necessary rectification to close the issue. Please check on all EF before close issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634571&prj=632&rqi=CD8MaO1Kl2Z4xfxaUgAyvmdQcK
GT1ELEC-135-004 | JH02-1/2 | APAC | Ready for Verification | P2 Medium DCOS | AliHazmeerHamdan@commtechasia.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_E2 | UPS - Uninterrupted Power Supply |  |  | During UPS_E2 Burn in Static Bypass, DCOS graphic just remain at Double Conversion (online mode). The graphic does not reflect with UPS status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634164&prj=632&rqi=q3Ym9gMoKck0lGVtPaPlrW6QNL
GT1MECH-193-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-08-18 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M2_2 | EF - Exhaust Fan |  |  | Fan running time and time taken to trigger is not tally for all the fans. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634045&prj=632&rqi=k6Xj2R1L9ShVYqrlHrFGQYTXzF
GT1MECH-194-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-08-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M2_1 | EF - Exhaust Fan |  |  | When fire alarm is triggered at the M2_1 , M1_1 also triggered the fire alarm. Same goes to the refrigerant leak simulation same fan triggered as well. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634021&prj=632&rqi=IbyVFxgt4Xq9QIPHhphsTspqgQ
GT1ELEC-135-003 | JH02-1/2 | APAC | Ready for Verification | P3 Low DCOS | AliHazmeerHamdan@commtechasia.com | 2026-08-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_E2 | UPS - Uninterrupted Power Supply |  |  | The breaker status Q01, Q08 and MSB_E_PQM displayed on the DCOS is incorrect. The status indication needs to be checked and rectified before proceeding with the Gen Source transfer testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634115&prj=632&rqi=cPilZHsrkkXRps8qbhCdWm5h2p
GT1ELEC-133-001 | JH02-1/2 | APAC | Open | P2 Medium DCOS | AliHazmeerHamdan@commtechasia.com | 2026-08-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_M1 | UPS - Uninterrupted Power Supply |  |  | The DCOS is displaying an incorrect value for Gen_M1, and the breaker status is also not being reflected correctly in DCOS. Please verify all the points at MSB Graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633914&prj=632&rqi=SSYrBbXgh9PzZpplTthcYfSSx6
YT1MECH-237-002 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_03 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found there is missing terminal block inside panel for 24 VDC and possible missing cable termination since SLD and GA drawing mention for 24 VDC. Please clarify the issue and close the issue immediately. ISSUE APPLIED TO ALL EF | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633869&prj=632&rqi=KzA6fni6vg8ODxNh1EyrPcViNk
YT1MECH-237-003 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_03 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the cable tagging for DCOS is not tally as per checklist. Please refer photo attached for the discrepancy. Understand the one from checklist is the correct one. If so, please change accordingly. Please do check for other cable as well. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633871&prj=632&rqi=OuYqfeGX3OfzXTnuJuNHdhpJ2K
YT1MECH-229-002 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_R_1 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found there is missing terminal block inside panel for 24 VDC and possible missing cable termination since SLD and GA drawing mention for 24 VDC. Please clarify the issue and close the issue immediately. ISSUE APPLIED TO ALL EF | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633868&prj=632&rqi=gFmrhIQB0AQsJyJJatKmFkRLFB
GI-261 | JH02-1/2 | APAC | Ready for Verification | P1 High DCOS | AliHazmeerHamdan@commtechasia.com | 2026-08-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS | [6 empty] | Issue: DCOS/CPOS graphics development, deployment, and validation are significantly behind schedule. SFAT-validated graphics and database evidence are no longer valid, requiring substantial rework. Multiple graphics remain incomplete or contain errors, trending configuration is not fully implemented, equipment integration and handshaking activities are outstanding, and no consolidated tracker exists to monitor completed versus pending works. These deficiencies are preventing chiller plant testing, sensor validation, TAB verification, burn-in testing, and other commissioning activities from progressing as planned, creating a significant risk to the project RFS milestone. Honeywell is required to provide a comprehensive recovery plan, resource allocation strategy, outstanding works register, and milestone-based schedule recovery actions. Impact: Delay to Cx activities, inability to complete planned testing, risk of repeated testing effort, and potential RFS schedule slippage. Required Action: Honeywell to submit RCA and execute a detailed recovery plan with clear ownership, resource augmentation, daily progress tracking, and prioritized completion of critical DCOS/CPOS graphics and integration activities. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633763&prj=632&rqi=KeAHC4VjBfZ4Yc8EkCyk1UmuLd
GT1ELEC-132-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-08-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_R12 | UPS - Uninterrupted Power Supply |  |  | The line animation on the DCOS graphic is not fully aligned with the actual system status. Please verify and rectify the animation accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633760&prj=632&rqi=pm1vEo84k2lm0G3foidNSORZR2
GT1ELEC-132-002 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-08-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_R12 | UPS - Uninterrupted Power Supply |  |  | The reading shows at MSB_R_Q_04 for KW and PF are still incorrect. The Value required tally with DPM MSB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633761&prj=632&rqi=mfHShFI7vNqVM8RBxAoYGD76G1
YT1ELEC-606-001 | JH02-1/2 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_C_1_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q04 to "SPARE". Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633191&prj=632&rqi=QlnzqNAFXDYLY9O2liQyFlErMl
YT1ELEC-607-002 | JH02-1/2 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_D_1_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q04 to "SPARE". Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633189&prj=632&rqi=5E4zIcZLqMmw9fzW48F084NTeX
YT1ELEC-607-001 | JH02-1/2 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_D_1_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q04 to "SPARE". Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633188&prj=632&rqi=xgBtYOWzkv3RogcXUcon74QfPx
YT1ELEC-152-001 | JH02-1/2 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_C_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q09, Q10, Q11 and Q12 to "SPARE". Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633192&prj=632&rqi=csNGF6pLxuHxh4uRo9WKz5sriR
YT1ELEC-608-001 | JH02-1/2 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_F_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q02 and Q03 from "SPARE" and Q11 from "SPACE". Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633194&prj=632&rqi=eHVBaaRytG9HcLpQt8kzL7H0fC
YT1ELEC-389-001 | JH02-1/2 | APAC | Closed | P3 Low CX | charitysamar@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_C_06 | LVSB - Low Voltage Switchboard |  | i-Box | Update the as-built drawing to incorporate the changes and place the approved revised drawing in the designated document pocket of the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632994&prj=632&rqi=TTdn8xkLiXq72xO6l7SBZoYEiH
YT1ELEC-367-001 | JH02-1/2 | APAC | Closed | P3 Low CX | charitysamar@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1_27 | LVSB - Low Voltage Switchboard |  | i-Box | Update the as-built drawing to incorporate the changes and place the approved revised drawing in the designated document pocket of the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632989&prj=632&rqi=xDlKP6HpK6iB3SssSw0cmnGGBj
GT1ELEC-177-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | MSB_R. During simulate utilities failure (Open Breaker). The Gen_R breaker at MSB not automatic close and the genset not kick in to start. The UPS_R1 in discharge Mode (Battery Discharge). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632831&prj=632&rqi=FfkVWEQ8nGh6sML7Rs5kJTC15i
GI-258 | JH02-1/2 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-08-07 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | HMI panel aready install by GC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632696&prj=632&rqi=WPJXtikKFKE9SRJGbw6qi09Fwe
GI-259 | JH02-1/2 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-08-07 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_D | MSB - Main Input Switchboard |  |  | HMI panel already install by GC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632701&prj=632&rqi=nkIbZRzM60ESLGBmXhTKEJpgac
GT1ELEC-135-002 | JH02-1/2 | APAC | Open | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_E2 | UPS - Uninterrupted Power Supply |  |  | During the Burn In test UPS_E2 (Double Conversion), UPM 2 and UPM 3 experienced an overtemperature trip due to the elevated supply air temperature from CRAH system. The high CRAH supply air temperature resulted in an increase in the ambient temperature around the UPS, causing the UPM operating temperature to exceed the allowable limit. Please verify and confirm the condition of UPM 2 and UPM 3 following the overtemperature trip event. Kindly check whether the event has caused any abnormality, derating or impact the UPM efficiency and output capacity. I believe this UPM can operate 0â€“40-degree Celsius without derating based on technical specifications. it would be appreciated if Eaton could provide the UPM temperature history or trend prior to the overtemperature trip, including the final temperature recorded before the trip. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632709&prj=632&rqi=0brgUHXE4pWCKv7catAn1mICfT
GI-260 | JH02-1/2 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-08-07 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_F | MSB - Main Input Switchboard |  |  | HMI panel already install by GC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632704&prj=632&rqi=DyT0roViSLtA8i4yAV9kooKwUU
GI-257 | JH02-1/2 | APAC | Closed | P2 Medium CX | junkaichan@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_R11 | UPS - Uninterrupted Power Supply |  |  | - load up UPS to 35%~420kw - â engineer check for meter verification between PQA and UPs HMI - â found imbalance current at UPS HMI (output meter -blue phase) while PQA showing healthy reading Please submit RCA report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632500&prj=632&rqi=8aXEDTL8cN7iEbctAXri5mFNIu
GT1ELEC-135-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-08-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_E2 | UPS - Uninterrupted Power Supply |  |  | The UPS_E2 HMI current indication is abnormal. The blue phase current reading is significantly lower than the red & yellow phase. R = 175A, Y=172A and Blue=86A. Please verify the current measurement and CT wiring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632265&prj=632&rqi=p4OI5JojYHMkrmymm05vEj9LDF
YT1MECH-199-001 | JH02-1/2 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-08-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | To complete installation of field sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632070&prj=632&rqi=hXvXgnmrNdLz2jlo4rAbNQ1fDw
GT1ELEC-180-001 | JH02-1/2 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-08-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_M2 | MSB - Main Input Switchboard |  |  | Test 27- Flex initiated transfer to Fixed Generator (Closed Transition). The Generator started and the utilities breaker were in closed position. However, the system did not receive the Sync Ready status signal. As a result, the synchronization sequence could not proceed, and the transfer to the Generator source was inhibited. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632082&prj=632&rqi=tc8MPuAwXZEX4wo8jGRKOx9g9z
YT1MECH-227-002 | JH02-1/2 | APAC | Closed | P2 Medium CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_06 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the end of fire cable is left hanging from the junction box. Please complete the fire cable installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631963&prj=632&rqi=0kxBQja5vwwWAvulLz5sN9Boqd
YT1MECH-227-003 | JH02-1/2 | APAC | Open | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-02 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_06 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the TS glass cover is broken. Please rectify to close the issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631964&prj=632&rqi=1FOHGuxfGkEmctP1njW9vB5Zsk
YT1MECH-227-001 | JH02-1/2 | APAC | Open | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_06 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the cable for DCOS is missing however the DCOS is mentioned inside the SLD. PIC claims the drawing is wrong. Please attached any relevance document to show proof DCOS cable is not to be terminated on this panel. Please amend the drawing if necessary. APPLIED TO ALL EF | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631962&prj=632&rqi=3v23CnElKTVJJhsqGeOMELEPlc
YT1MECH-260-001 | JH02-1/2 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1TEF_M1_1 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, noticed fire cable is missing from the drawing attached inside the pocket drawing. Please discuss with relevance party to clarify the fire cable termination. Issue for panel LCP_1TEF_M1_1&2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631716&prj=632&rqi=fFl47B8VHGkMrZFcE9sy6xNlSt
YT1MECH-229-001 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_R_1 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the breaker size is larger than SLD and GA Drawing. On site breaker install 20A while in all drawing mention breaker size is 10A. Please verify and amend as necessary. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631361&prj=632&rqi=hN0QTEXbNkoHJTYxrPAPbNguJP
YT1MECH-237-001 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_03 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the breaker size is larger than SLD and GA Drawing. On site breaker install 20A while in all drawing mention breaker size is 10A. Please verify and amend as necessary. APPLIED TO ALL EF | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631357&prj=632&rqi=BvZa2AEjS7RyL80eZdP0mLLUgi
YT1MECH-230-001 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_B_1 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the breaker size is larger than SLD and GA Drawing. On site breaker install 20A while in all drawing mention breaker size is 10A. Please verify and amend as necessary. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631359&prj=632&rqi=1Rmcl30ocwYl5OOAs4iN7SvVxQ
YT1MECH-236-001 | JH02-1/2 | APAC | Open | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-30 04:00:00.000 +0400 |  | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_A_1 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the breaker size is larger than SLD and GA Drawing. On site breaker install 20A while in all drawing mention breaker size is 10A. Please verify and amend as necessary. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631349&prj=632&rqi=0joriA3BRBH3U5fp9oaoZRy0V1
YT1MECH-223-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | junkaichan@commtechasia.com | 2026-07-29 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_E_1 | EF - Exhaust Fan |  |  | Signal cable from fan control to LiB Block E (E_ 1-7) and (E2_1-7) is not installed, tested thus termination at LiB is incomplete. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631123&prj=632&rqi=wbyghNhW9mmSHYKwopbmx9ptO8
YT1MECH-177-001 | JH02-1/2 | APAC | Open | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_E_1 | CRAH - Computer room air handler |  |  | Pressure Testing and flushing documents are approved on Project Portal and attached to the correct section of Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630831&prj=632&rqi=GHmtUY46bH6NGs23T7sSMVy9Mx
YT1MECH-183-001 | JH02-1/2 | APAC | Open | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_1 | CRAH - Computer room air handler |  |  | Pressure Testing and flushing documents are approved on Project Portal and attached to the correct section of Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630833&prj=632&rqi=2GefyG2yQkWOR8034eqr45G0vG
YT1ELEC-154-001 | JH02-1/2 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_F_1_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q04 from "SPARE" to the correct load. Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630655&prj=632&rqi=nT9kxCL69WFNmMlgXNs5LoT1t5
YT1ELEC-107-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | charitysamar@commtechasia.com | 2026-07-23 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STS_F2R1_1 | STS - Static Transfer Switch |  |  | The tagging at the busduct connection point to the STS does not correspond to the tagging on the busduct body. If the discrepancy is limited to the busduct body tagging, a continuity test should be conducted to verify the connection, and the tagging shall be corrected afterward. However, if the discrepancy is at the connection point, the busduct will need to be modified to ensure the correct connection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630513&prj=632&rqi=Bu3kwDEr9dZksP4AcDIttbmDJW
YT1ELEC-370-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1R_38 | LVSB - Low Voltage Switchboard |  | i-Box | 1LVDB_M1R_38 RCCB for each phase, to be swapped out for 2 pole MCB as confirmed by NV5 to avoid nuisance tripping. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630218&prj=632&rqi=CosrurjRIZ1NQjLT4pvYi0a8Gn
YT1ELEC-106-001 | JH02-1/2 | APAC | Closed | P3 Low CX | iau@cspm.com.my | 2026-07-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STS_E2R1_2 | STS - Static Transfer Switch |  |  | White Glove Report is approved on Project Portal and appended to the document section of this checklist | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629708&prj=632&rqi=pFupCdjZRgnhVQL3V1CoHJVrrg
YT1ELEC-103-001 | JH02-1/2 | APAC | Closed | P3 Low CX | iau@cspm.com.my | 2026-07-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STS_E1R1_1 | STS - Static Transfer Switch |  |  | White Glove Report is approved on Project Portal and appended to the document section of this checklist | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629712&prj=632&rqi=YeOGVuQbO1rHasYe4WZXphiFHB
GT1ELEC-129-001 | JH02-1/2 | APAC | Open | P2 Medium CX | charitysamar@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_B1 | UPS - Uninterrupted Power Supply |  |  | UPS DCOS SPL not in Honeywell Points List during Cx3 Testing: -DC Ground Fault -DC Over Voltage Shutdown -Input Current Unbalance -Maintenance Bypass Breaker Closed -Maintenance Bypass Breaker Open -Output Breaker Closed -Output Breaker Open -Over Temperature Shutdown -Overload Shutdown -Resiliency Vote -Resilient -Static Switch Disable -Synch Enable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629341&prj=632&rqi=LTslgFGhFGsHoh5WkNbF2jNI63
YT1ELEC-365-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | charitysamar@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1_25 | LVSB - Low Voltage Switchboard |  | i-Box | Please attach/provide the calibration certificates for the exact test instrument used. The Cable Insulation Resistance Test conducted on the cables on July 13, 2026, was performed using a Kyoritsu test instrument with Serial Number E8528764. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628833&prj=632&rqi=hjGIHcA3tCEAAcWkq0ckEqxwkT
YT1ELEC-364-001 | JH02-1/2 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1_24 | LVSB - Low Voltage Switchboard |  | i-Box | During YT inspection, found 1 of the timers that located beside the contactor inside panel is not turn on. All the timers T2 and T3 is turn on while T1 beside the contactor C1 is turn off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628640&prj=632&rqi=tKBH3SOtpsqiv1JsxoSP5PLk8B
GT1ELEC-178-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_M1 | MSB - Main Input Switchboard |  |  | During the UPS_M1 Failure Mode Test Under Utilities Supply (Failure of UPS Batteries for 5min). The LiBattery breaker was switched OFF. Initially, the UPS transferred to Static Bypass mode. After the LiBattery breaker was isolated, the UPS transferred to Double Conversion mode. During testing 50% load. Approximately 1-2 mins later, the following breakers tripped due to Ground Fault Protection: 1) Incoming from Tx (Q_01) : Tripping A (1200A) : time (0.00sec) 2) Incoming for UPS_M1 (Q_10) : Tripping A (600A) : time (0.00sec) Additionally, the time and date settings in the micrologic protection units were not configured correctly, preventing accurate identification of the trip sequence and confirmation of which breaker operated first. The vendor shall carry out the detailed troubleshooting to the determine the cause of the Ground Fault Trips. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628638&prj=632&rqi=g1Qux0tAhP5XE0DsesmjWaSu9V
YT1ELEC-603-002 | JH02-1/2 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_28 | LVSB - Low Voltage Switchboard |  | i-Box | During YT inspection with GC and vendor, found the termination for contact is not as per drawing. Drawing show termination from only 2 MCB (Y3 & Y4) while on site termination is connecting from 3 outgoing MCB to contactor C2 (1L2-21, 1L2-22, 1L2-23). Please advise. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628641&prj=632&rqi=gR3VURsoDjbF64KbtXX7cr6Oka
YT1ELEC-555-001 | JH02-1/2 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1ATSM_M1R_27 | ATS - Automatic Transfer Switch |  |  | During YT inspection, noticed the quantity for fuse inside the panel is not the same as in the drawing. Total quantity for fuse inside drawing is 9 nos while the total quantity inside the panel is 10 nos. Please confirm the nos of fuse and do some amendment if necessary. This issue is applied to all unit 1ATSM panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628642&prj=632&rqi=1E6K8MdI3BJJm7xfbjesJjkoZ1
RT1MECH-625-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAK_C_1 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628687&prj=632&rqi=9d6ic3tkL5dCcH046Af6Op1ubt
RT1MECH-277-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_07 | EF - Exhaust Fan |  |  | Permanent equipment labels affixed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628634&prj=632&rqi=BK0C2BNxC5gTMzL2x8goO9YBBa
YT1ELEC-603-001 | JH02-1/2 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_28 | LVSB - Low Voltage Switchboard |  | i-Box | During YT inspection with GC and vendor, found the termination for contact is not as per drawing. Drawing show termination from only 2 MCB (R3 & R4) while on site termination is connecting from 3 outgoing MCB to contactor C1 (1L1-21, 1L1-22, 1L1-23. Please advise. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628637&prj=632&rqi=2QZUaasLK56juHpY6AUZmMZy0i
YT1ELEC-5-002 | JH02-1/2 | APAC | Closed | P3 Low CX | charitysamar@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_E | RMU - Ring Main Unit |  |  | The shielding cable has been cut and rejoined using a bolted connection (bolts and nuts). Confirmation from ABB is required to verify whether this repair method is acceptable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628515&prj=632&rqi=gANTzqeHCFLMH2sYgVNc74aGzK
RT1MECH-620-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_D_4A | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628506&prj=632&rqi=MulhhlHFx6epnEegSo6DtICEwj
RT1MECH-608-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_A_3 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628470&prj=632&rqi=SlL4s8ZHSMIdmvhECI6USeZ5TH
RT1MECH-611-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_B_3 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628493&prj=632&rqi=2u2zG71791vkUHPze8f42EvwVq
RT1MECH-619-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_D_1 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628503&prj=632&rqi=T7ZRhsnyu7I6LvtuEqPE4HrmOF
RT1MECH-616-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_C_4 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628502&prj=632&rqi=rqELqE9gliTQOlWO1Dt67zlkuw
RT1MECH-607-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_A_4A | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628467&prj=632&rqi=nyrUKdj6OAg1F2ZtTZx3q9NdxY
RT1MECH-615-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_C_1 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628495&prj=632&rqi=fHI89uwPoTbQaCyjoNs0JocGyY
RT1MECH-623-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_D_4 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628505&prj=632&rqi=FJ8nO5LecJRDem6uK79OWhXRjT
RT1MECH-613-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_B_2 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628492&prj=632&rqi=NwKcMnavwVzrrjTr9CwfURJT6Y
RT1MECH-621-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_D_3 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628509&prj=632&rqi=goGWL5nrSqk0YXH4ZDgy6Oni9a
RT1MECH-614-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_B_4 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628494&prj=632&rqi=hlgTsarLngiUWs6kfAj7e3J969
RT1MECH-624-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_M1_1 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628507&prj=632&rqi=jrJFYXwicLae1rji0lGZ4aKHA3
RT1MECH-622-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_D_2 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628504&prj=632&rqi=IuvGnrlSOimmDXkFG3qjsRbV01
RT1MECH-612-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_B_1A | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628267&prj=632&rqi=VKBdcud8GKgFPDnPGlxpYoMGnE
RT1MECH-610-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_B_1 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628266&prj=632&rqi=EHp24FRdwySFqAWL4pOBr9hBle
RT1MECH-605-001 | JH02-1/2 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1LEAKZ_A_2A | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628269&prj=632&rqi=isYC47wGkKlqpM1H5B4x0uJFyH
YT1MECH-306-003 | JH02-1/2 | APAC | Closed | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | The wall penetration is still not fire sealed. This outstanding work is preventing us from issuing yellow tag for PUMP ROOM 1 & PUMP ROOM 2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628166&prj=632&rqi=ih8lO2eySVLUyFFmVX0MVBaEg5
YT1MECH-306-004 | JH02-1/2 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | The earth chamber still not tested yet & kindly place the labelling or tagging at Earth Chamber follow the Earthing Main Schematic labelling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628167&prj=632&rqi=0SkmdZnbFq5eQHJlhhpvrKxrZM
YT1ELEC-130-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_B1 | UPS - Uninterrupted Power Supply |  |  | GC need provide Photo Evidence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628112&prj=632&rqi=axwZwvKMf6KbWM9MdoOMqQX9dT
YT1DCOS-12-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Controls | equipment | 1DCOS_RIO_3 | DCOS - Control Panels |  |  | Wrong power source tagging. supposed me 38-B6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628264&prj=632&rqi=P7GpjTdz8W2zKPfPqk46UDAeDp
YT1DCOS-10-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Controls | equipment | 1DCOS_RIO_1 | DCOS - Control Panels |  |  | Wrong tagging for power supply. Supposed to be B1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628263&prj=632&rqi=zMBjmsXs1Mw2SVSj55VPYTCAqV
YT1MECH-307-004 | JH02-1/2 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_2 | FPMP - Fuel Pump |  |  | All permanent earthing not complete installed & labelling in PUMP ROOM 1 & PUMP ROOM 2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627957&prj=632&rqi=HOdP90EobHrvzHwg0hqo6YNd2T
GT1ELEC-127-003 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | UPS has been verified with latest new firmware version CSB : 5.12.342. Eaton to ensure the latest version update is incorporated in new setting revision and submit to design consultant for approval. Please attached new approved setting document for record purpose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627493&prj=632&rqi=CXwfVD5x25vhQpD8o1zsyQAYxq
GT1ELEC-127-001 | JH02-1/2 | APAC | Closed | P3 Low DCOS | ahmadfuad@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | Battery time remaining status on DCOS to recheck formula as it does not indicate correct time as per UPS HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627490&prj=632&rqi=x7VdVGlNFRiPacHKya9EZlfGpd
GT1ELEC-127-002 | JH02-1/2 | APAC | Open | P3 Low CX | ahmadfuad@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | UPS is showing kWh/day status on HMI, however DCOS is using kWh as per approved SICD. Eaton to verify if the correct HMI status with per day status should be there or to be revise to kWh | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627491&prj=632&rqi=iydR7VFkq6RPGlYKawKKBflE1L
YT1ELEC-7-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_A | RMU - Ring Main Unit |  |  | During preparation of UPS_A1 load, test it was observed that RMU_A1 trip due to earth fault trip to Q_03 outgoing breaker to MLTX_A1. Further investigation, it was found cable shield for the 3C phase cables were found to be outside of ZCT. RYB to seek clarification via email from ABB. As for the solution to bring the cable shield inside the ZCT is acceptable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627190&prj=632&rqi=LlWcghDlvoLBQEC6KgGhn0WDYR
GI-253 | JH02-1/2 | APAC | Closed | P3 Low CX | junkaichan@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | CRAY Isolator installed right below water flexible hose connection - risk of damage/safety during maintenance/accidental water leakage. Suggest checking with design team if the isolator design is acceptable or any modification required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626444&prj=632&rqi=X42i3AxecW1HaObAwYYKSLEWV0
YT1MECH-210-002 | JH02-1/2 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_M2_2 | CRAH - Computer room air handler |  |  | Pressure Testing and flushing documents are approved on Project Portal and attached to the correct section of Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626307&prj=632&rqi=KZlpYlAO0ICwAPaei6ldnI6z21
YT1MECH-209-001 | JH02-1/2 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_M2_1 | CRAH - Computer room air handler |  |  | Confirm that Chilled Water has been pre-commissioned, flushed and treated to approved Method Statement and witnessed by GC/CxA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626304&prj=632&rqi=3nXKgWpAbMRZiYuMp561zkCK9M
YT1MECH-209-002 | JH02-1/2 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_M2_1 | CRAH - Computer room air handler |  |  | Pressure Testing and flushing documents are approved on Project Portal and attached to the correct section of Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626305&prj=632&rqi=WiJAhIh81YsuYCF7ARaVp2PEOg
YT1MECH-210-001 | JH02-1/2 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_M2_2 | CRAH - Computer room air handler |  |  | Confirm that Chilled Water has been pre-commissioned, flushed and treated to approved Method Statement and witnessed by GC/CxA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626306&prj=632&rqi=OwiiJB326ePttnYfo72Gd3ejBx
RT1ELEC-246-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_D_1 | LEAK - Leak Detection |  |  | The panel no permanent tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626286&prj=632&rqi=f687DWCaccxt5SLpFgeaoi5VT3
RT1ELEC-248-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_B_2 | LEAK - Leak Detection |  |  | The panel no permanent tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626290&prj=632&rqi=TPOazOAHdyblxXkljTXxCcg7Oq
RT1ELEC-244-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_D_2 | LEAK - Leak Detection |  |  | the panel no permanent tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626284&prj=632&rqi=VuYTdHRNJe9MwRgYLZ5OnHdoXd
RT1ELEC-247-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_A_2 | LEAK - Leak Detection |  |  | The panel no permanent tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626289&prj=632&rqi=xkeU6g667C2CKAFrO2CwpabT34
RT1ELEC-241-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_M1_3 | LEAK - Leak Detection |  |  | The panel no permanent tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626281&prj=632&rqi=HXfaQDo8SjS3XNRepoMaVkJKy2
RT1ELEC-242-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_M1_4 | LEAK - Leak Detection |  |  | The panel no permanent tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626282&prj=632&rqi=s9RuIe6xM5IMHljnXoMKwuMHIl
RT1ELEC-239-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_M1_1 | LEAK - Leak Detection |  |  | The permanent labelling not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626278&prj=632&rqi=duPGlchw5Nl9aX7U9HfOZRvCjz
RT1ELEC-240-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_M1_2 | LEAK - Leak Detection |  |  | The panel no permanent tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626280&prj=632&rqi=YX1GNTmanfwL7ZQIIxGlssMo8S
RT1ELEC-245-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_C_1 (L1 near DG) | LEAK - Leak Detection |  |  | The panel no permanent tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626285&prj=632&rqi=0Vej8vhoRAFH5JgmYpE9QZTOYY
RT1ELEC-243-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_C_2 | LEAK - Leak Detection |  |  | The panel no permanent tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626283&prj=632&rqi=PNu9ovVPv7nbPTUG0rhBpyFKyv
RT1ELEC-246-002 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1FOLDZ_D_1 | LEAK - Leak Detection |  |  | The panel alignment requires adjustment as it is slightly slanted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626288&prj=632&rqi=aH3v8kbvvgT29ndXGR9wdKcYTw
GI-249 | JH02-1/2 | APAC | Open | P1 High CX | pauljohnson@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_M2 | RMU - Ring Main Unit |  |  | 1BTU_M2 side of the unit is damaged and the door now not aligned to close. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625740&prj=632&rqi=S4jf9evfFQRzG3DJAiuATIeVnj
GI-250 | JH02-1/2 | APAC | Open | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M1R_03 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_M1R_03 bottom cover of the busbar section dented. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625741&prj=632&rqi=ifsowpjaqPBnPP2uPS65oGFojJ
GI-248 | JH02-1/2 | APAC | Open | P3 Low CX | junkaichan@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1MWP_M1_1 | DOMW - Domestic Water Set |  |  | coiled up cable in MCC cabinet not terminated - to be clarified the purpose. if unused to be wrapped up the exposed termination. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625589&prj=632&rqi=TB506NuxyzHaEVLnkpO97fo8BM
GI-247 | JH02-1/2 | APAC | Open | P3 Low CX | junkaichan@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1MWP_M1_1 | DOMW - Domestic Water Set |  |  | Pressure switch control cable no label. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625588&prj=632&rqi=vmgmljQWWrA4OKpGBbnuT0qwAl
RT1ELEC-201-001 | JH02-1/2 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-06-16 04:00:00.000 +0400 | Commissioning Authority | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R_4 | MDSB - Mech Distribution Switchboard |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625413&prj=632&rqi=Zak6Oh5HJ3FAtkLvdpTJtYnhot
RT1ELEC-201-002 | JH02-1/2 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-06-16 04:00:00.000 +0400 | Commissioning Authority | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R_4 | MDSB - Mech Distribution Switchboard |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625415&prj=632&rqi=2f2Z02KQrPJXA4KAfQe8q9CF6b
YT1MECH-310-002 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_4 | FPMP - Fuel Pump |  |  | the cable missing tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625431&prj=632&rqi=5nJMmRxedGkWccNWjkaVNOshiN
YT1MECH-307-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_2 | FPMP - Fuel Pump |  |  | Cable entry at the Fuel Pump Panel (bottom) of the panel is not properly gland and the cable need flexible conduit before entering the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625417&prj=632&rqi=LUGk3SPd6fsaAwCwIWEZS01Lol
YT1MECH-309-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_3 | FPMP - Fuel Pump |  |  | Cable entry at the Fuel Pump Panel (bottom) of the panel is not properly gland and the cable need flexible conduit before entering the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625427&prj=632&rqi=IzlgWQyY6zEyrZesmfceGS7YGf
YT1MECH-307-002 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_2 | FPMP - Fuel Pump |  |  | The cabling missing tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625418&prj=632&rqi=OBnHAe4IFPKJGrQq9NxOXCTYi4
YT1MECH-310-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_4 | FPMP - Fuel Pump |  |  | Cable entry at the Fuel Pump Panel (bottom) of the panel is not properly gland and the cable need flexible conduit before entering the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625430&prj=632&rqi=iywZQASu2GXakj7N000HICWUiB
YT1MECH-306-002 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | Cable missing the tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625420&prj=632&rqi=dRCCo2ziSVi8nODfq7jLj3NsJW
YT1MECH-309-002 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_3 | FPMP - Fuel Pump |  |  | The cable missing tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625428&prj=632&rqi=S9j5tNivgjcx2fSsjOJZUzTWD7
YT1MECH-306-001 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | Cable entry at the Fuel Pump Panel (bottom) of the panel is not properly gland and the cable need flexible conduit before entering the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625412&prj=632&rqi=ru5ZvADeMZAzqdsUpd4LmVpZRO
YT1MECH-309-003 | JH02-1/2 | APAC | Open | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_3 | FPMP - Fuel Pump |  |  | Cable dressing is not acceptable. Cable ties have been at the cable bend, causing excessive bending. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625429&prj=632&rqi=grHkeVIVt5XuJt9vFg5DNqtVoY
YT1MECH-307-003 | JH02-1/2 | APAC | Open | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_2 | FPMP - Fuel Pump |  |  | Cable dressing is not acceptable. Cable ties have been at the cable bend, causing excessive bending. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625419&prj=632&rqi=GqP0tr8pHkGWmACXbVHnMKD160
YT1MECH-200-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_2 | CRAH - Computer room air handler |  |  | isolator for power source to be label to differentiate power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626192&prj=632&rqi=88F6KVecQ880luqcRX0dTjLecS
YT1MECH-200-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_2 | CRAH - Computer room air handler |  |  | Conduit for fire is tear | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626191&prj=632&rqi=L0RqAyzNHkO1D9KpR5QdL5gO8w
YT1MECH-200-003 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_2 | CRAH - Computer room air handler |  |  | Conduit to be labelled serving whats trade/service | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626193&prj=632&rqi=jOM34TN8rxPUoEmGS31QaKg2OS
GI-242 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_3 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624914&prj=632&rqi=ztQCxgV1rBYVgp6SkzqjAigJCK
GI-246 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_8 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624920&prj=632&rqi=Rli5dUxxOLHiJ6o2QXflBKEAFc
GI-243 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_5 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624916&prj=632&rqi=vjyiOcN5nvgRJaNqEGIV5xLAkc
GI-245 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_7 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624918&prj=632&rqi=gGmnn1wRldsHzNFNmBkD19JHei
GI-244 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_6 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624917&prj=632&rqi=VesPh3fZqVP1G7BAu5cEidoQ4o
GI-241 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_2 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624912&prj=632&rqi=jqWa1WbwGyDfNmeZoERUplnbn1
YT1MECH-203-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_5 | CRAH - Computer room air handler |  |  | Conduit to be done properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624821&prj=632&rqi=FpUlGBlz4RtT0839gqhkplV8dI
GI-240 | JH02-1/2 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-06-10 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_15 | LVSB - Low Voltage Switchboard |  | i-Box | Closed issue panel warning sign sticker refer photo attachment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624632&prj=632&rqi=OWF8BZg2GI7prk2n7fQDAwah18
YT1MECH-202-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_4 | CRAH - Computer room air handler |  |  | tear conduit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624819&prj=632&rqi=r7FsQb1wmOLuVUE1ZG5BwXyh32
GI-239 | JH02-1/2 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-06-10 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1_15 HVAC DB | LVSB - Low Voltage Switchboard |  | i-Box | Closed issue Panel warning sign sticker refer photo attachment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624631&prj=632&rqi=zg3diCgLjt3U8iHyUtsvBq5eBW
YT1MECH-201-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_A_3 | CRAH - Computer room air handler |  |  | isolator to be label at A and B source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624820&prj=632&rqi=7Sp03RksjjQwW3OMC8z1ISmTss
YT1MECH-295-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_2_CHWBT | CHWBT - Chilled water buffer tank |  |  | Valve clashing with tank | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624293&prj=632&rqi=pm2p3AnSXIMmzKod91xDzJcblQ
YT1MECH-299-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_6_CHWBT | CHWBT - Chilled water buffer tank |  |  | Valve clashing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624289&prj=632&rqi=6dLBAZUd9VCzHjgECYi6dU9J1o
YT1MECH-294-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_1_CHWBT | CHWBT - Chilled water buffer tank |  |  | valve clashing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624294&prj=632&rqi=GsIAte3YTdh0BK9BJ1uDSRw6G3
YT1MECH-299-003 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_6_CHWBT | CHWBT - Chilled water buffer tank |  |  | flow direction label to be install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624291&prj=632&rqi=wbvx8XsQ4mqOKlWnvN8CeRo6A4
YT1MECH-300-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_7_CHWBT | CHWBT - Chilled water buffer tank |  |  | Accesories not intalled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624292&prj=632&rqi=BQdDwDYIeGiIPaMPxEckx7HOD5
YT1MECH-299-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_6_CHWBT | CHWBT - Chilled water buffer tank |  |  | insulation to redo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624290&prj=632&rqi=G6ukbIGBpICsiFPQXsgQm0GvHX
YT1ELEC-450-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-06-06 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_03 | LVSB - Low Voltage Switchboard |  | i-Box | Circuit tagging missing on plastic cover. To install circuit tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624229&prj=632&rqi=rXWS69tAhL9vN83tUCu6uBN807
YT1ELEC-214-001 | JH02-1/2 | APAC | Closed | P1 High CX | ahmadfuad@commtechasia.com | 2026-06-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_9 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_M2R_9 was energised prior obtaining Conditional Yellow Tag (CYT) or Yellow Tag (YT) given to the panel which deviate from the established Cx process and EQIX playbook. GC to submit RCA detailing the sequence of event and the corrective action plan to prevent same issue occurring again in future. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624228&prj=632&rqi=I9cuLxtGcMWwyzEUVENaIcGdnC
YT1MECH-192-005 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_R_4 | CRAH - Computer room air handler |  |  | Tear conduit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624277&prj=632&rqi=xTPEypFkBfXsF1Hxoii67FkmBR
RT1ELEC-472-001 | JH02-1/2 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_15 | LVSB - Low Voltage Switchboard |  | i-Box | Panel warning sign stickers are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624104&prj=632&rqi=Rg0m4tsZTepcvXkg53bFB088wR
RT1ELEC-378-001 | JH02-1/2 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1_15 HVAC DB | LVSB - Low Voltage Switchboard |  | i-Box | Panel warning sign stickers are missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624101&prj=632&rqi=1MfcYsH4XHoEUOb2iUnQIJFjHr
YT1MECH-192-002 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_R_4 | CRAH - Computer room air handler |  |  | Comm cable is not properly tagged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624274&prj=632&rqi=BTQRLLoJjJSQ4G2Xc0sIJov5Np
YT1MECH-192-003 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_R_4 | CRAH - Computer room air handler |  |  | Isolator to be labelled power source And B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624275&prj=632&rqi=6rtAYNcfkaNpi49uZYG0P8EMX6
YT1MECH-192-004 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_R_4 | CRAH - Computer room air handler |  |  | equipment is coated with dust and cleaning to be done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624276&prj=632&rqi=VxGyJr53v1AtSFU1jwX8dopzC9
YT1MECH-192-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_R_4 | CRAH - Computer room air handler |  |  | Fire cable not terminated per standard and unlabelled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624273&prj=632&rqi=H3toV8xHamzph8RBeX70nnrFLi
YT1MECH-276-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_4_CWP | CWP - Condenser Water Pump |  |  | isolator cover missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624030&prj=632&rqi=DsOxXFQbAToECZfeqhE9uv8OrJ
YT1MECH-271-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_6_CHWP | CHWP - Chilled water pump |  |  | DCOS and Xinnetwork conduit not labelled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624014&prj=632&rqi=cmJb4GzNJSHECSBEum4rJ4DFUj
YT1MECH-268-003 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_3_CHWP | CHWP - Chilled water pump |  |  | cable tagging missing xinnetwork | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624013&prj=632&rqi=RtHDZut0UpGXgly1I9SbKk24zd
YT1MECH-272-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_7_CHWP | CHWP - Chilled water pump |  |  | torque mark misaligned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624021&prj=632&rqi=6z2fSIh6vIbxJjxC5hD4bmbBPL
YT1MECH-272-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_7_CHWP | CHWP - Chilled water pump |  |  | conduit to be labelled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624020&prj=632&rqi=hyGsTlpwtSBaUoFFVVOOEoeWnL
YT1MECH-268-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_3_CHWP | CHWP - Chilled water pump |  |  | labelling for trunking and conduit to be done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624011&prj=632&rqi=6IeieT8muoMb4tt3jwT2xrRz4n
YT1MECH-269-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_4_CHWP | CHWP - Chilled water pump |  |  | cable tagging not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624031&prj=632&rqi=PA743M0KW1zLVJkud2vyYG8OW1
YT1MECH-268-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_3_CHWP | CHWP - Chilled water pump |  |  | Torque marking not done properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624012&prj=632&rqi=Sgzs4je8ogC1vH1KYbpSjQTWAf
YT1MECH-272-003 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_7_CHWP | CHWP - Chilled water pump |  |  | missing cable gland | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624023&prj=632&rqi=sv5r3beq6SKmx0oTPehnHoL4Fa
YT1MECH-279-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_7_CWP | CWP - Condenser Water Pump |  |  | missing cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624024&prj=632&rqi=OTOvoq3fu84IV7rGKVT85OMQxM
YT1MECH-271-002 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_6_CHWP | CHWP - Chilled water pump |  |  | cabel tag missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624015&prj=632&rqi=kbU72bPBUbK1fGAMrWevJhNiwR
YT1MECH-271-003 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_6_CHWP | CHWP - Chilled water pump |  |  | no cable gland | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624017&prj=632&rqi=wlaWY3IuKqi633AuIpN5NNXoJB
YT1MECH-243-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1PF_M1_3 | EF - Exhaust Fan |  |  | Isolator IP rating compromise | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623879&prj=632&rqi=pTUVBdX0AtKNsOuaCKClDxWoKJ
YT1MECH-246-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1PF_M1_7 | EF - Exhaust Fan |  |  | Ip rating compromise since coring on isolator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623880&prj=632&rqi=QfM2AkpfzZl1mXNYuJ39CqHoBV
YT1MECH-246-003 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1PF_M1_7 | EF - Exhaust Fan |  |  | cable labelling is wrong and swapped over damper and mv fan | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623882&prj=632&rqi=CZltoVnuAImIegtkUzFrACDd1N
YT1MECH-246-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1PF_M1_7 | EF - Exhaust Fan |  |  | Isolator not labelled serving to which panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623881&prj=632&rqi=y3VU5pmWRYbnrL9lVmnRPe8nYw
YT1MECH-244-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1PF_M1_4 | EF - Exhaust Fan |  |  | isolator IP rating compromise | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623874&prj=632&rqi=gVko989qyR1Rnp0JnmZg1ET3RA
RT1MECH-317-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1TEF_M1_1 | EF - Exhaust Fan |  |  | GA and SLD not tally onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623756&prj=632&rqi=EzxFTr1W89GfeltBOE1zqjgQ7A
RT1ELEC-488-001 | JH02-1/2 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVSB_M1R_5 | LVSB - Low Voltage Switchboard |  | i-Box | The outgoing breaker tagging (Q_04, Q_06, Q_07) at 1LVSB_M1R_5 panel on site is not tally with the latest revision (Rev 02) of the SLD drawing. Please check and amend the drawing based on site condition. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622579&prj=632&rqi=GT8kX0OpapbYSNwaVkKPINjdGy
YT1MECH-296-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_3_CHWBT | CHWBT - Chilled water buffer tank |  |  | Valve clashing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622619&prj=632&rqi=GAt0M5kVSudfwzQlSk5H9YB4xP
YT1ELEC-392-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_CR_09 | LVSB - Low Voltage Switchboard |  | i-Box | Electrical wiring drawing does not tally with FCU layout drawing. Electrical drawing has CCT R1 to FCU_A_30, but FCU layout has this as FCU_A_25. (All other circuits are the same as this) Electrical drawing & LVDB SLD to be red-lined (updated) as per the FCU layout drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622358&prj=632&rqi=MB6rC03kdDsrerbV06whiSzRuY
YT1ELEC-461-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_AR_09 | LVSB - Low Voltage Switchboard |  | i-Box | Electrical wiring drawing does not tally with FCU layout drawing. Electrical drawing has CCT R1 to FCU_A_02, but FCU layout has this as FCU_A_04. (All other circuits are the same as this) Electrical drawing & LVDB SLD to be red-lined (updated) as per the FCU layout drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622213&prj=632&rqi=yWquRooFKp0EiVVmYY6tIFmzsN
RT1ELEC-213-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-05-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_4 | MDSB - Mech Distribution Switchboard |  |  | Outgoing breaker tagging Q_02 (To 1CHWSTR_M2_9_CWP) and Q_03 (To 1CHWSTR_M2_9_WCC) need to be revise to follow CWP (To 1CHWSTR_M2_3_CWP) and WCC number (To 1CHWSTR_M2_3_WCC). Typical to all 1MDSB_M2R_2 to 8 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621923&prj=632&rqi=UiCqZ2BGfwnH87RmyrtyrrLDSt
YT1MECH-275-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_3_CWP | CWP - Condenser Water Pump |  |  | isolator box to change and label. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621773&prj=632&rqi=FNmFa1ugNzgvtjXVeiXV2lEvho
YT1MECH-278-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_6_CWP | CWP - Condenser Water Pump |  |  | no cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621778&prj=632&rqi=ALklMZuhPML5POy3JicB65gfS6
YT1MECH-275-001 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_3_CWP | CWP - Condenser Water Pump |  |  | no tagging at cat6 cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621772&prj=632&rqi=CDepA4iELuRkuQqITOXy9SGwRg
GI-231 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | All bolted connections are not torque tightened and some pipe support brackets are not completely installed. Applied to HSD Yard, Pump Room 1 and Pump Room 2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620184&prj=632&rqi=ND8Mfl3EuW3XgVeusaZqGuo3Ex
GI-230 | JH02-1/2 | APAC | Ready for Verification | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | it was observed that all pipes in Pump Room 1 & Pump Room 2 are not labeled, identified and painted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620183&prj=632&rqi=l1KMYw995sLmRBtXhlJ33HRsTn
GI-233 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Fuel | equipment | FPPUMP1 | FPMP - Fuel Pump |  |  | it was observed all pipes are no labeled, torque tightened, identified and painted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620188&prj=632&rqi=tOXeRkifZIem7CIk60Yd367KtD
GI-232 | JH02-1/2 | APAC | Open | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | it was observed Check Valve (FR_CV2 & FR_CV3) are installed in the wrong direction. Applied in Pump Room 2 & Pump Room 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620186&prj=632&rqi=xoGi1iswPN0MXiyGRS45zzeDi9
GI-229 | JH02-1/2 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-05-04 04:00:00.000 +0400 |  |  | Commissioning Issue | Commissioning | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | The pressure gauge, test point and flow switch are missing at Pump Room 2 & Pump Room 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620182&prj=632&rqi=vsWIJiGodzvCCvNMJcDJsMIw6V
YT1ELEC-65-001 | JH02-1/2 | APAC | Open | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1ATSM_M1R_02 | ATS - Automatic Transfer Switch |  |  | It was observed that there were no DCOS monitoring to 1ATSM_M1R_01 till 07 (supplying to CHW pumps). Honeywell to recheck with EoR and confirm if these ATSM panels supplying to CHWP require to be monitored or not in DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619676&prj=632&rqi=5fCoc5CqPwKhilVbBTcqDyaQio
RT1MECH-186-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-24 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1AS_B_11 | FFU - Air Scrubber |  |  | isolator blocked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619443&prj=632&rqi=02eyjaQAcJU4e04uZvwfUxsCdW
RT1MECH-182-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1AS_B_09 | FFU - Air Scrubber |  |  | fan clashing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619444&prj=632&rqi=U8MmVWOkcxd0GWIbsqjvlkJmMj
YT1ELEC-212-001 | JH02-1/2 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_4 | MDSB - Mech Distribution Switchboard |  |  | Outgoing compartment Q_03 nameplate shows to 1CHWSTR_M2_9_WCC. Actual on-site outgoing goes to 1CHWSTR_M2_03_WCC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619159&prj=632&rqi=JGGXBaarq6AJqFGfsT262XkMaN
RT1ELEC-372-001 | JH02-1/2 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1R_33 | LVSB - Low Voltage Switchboard |  | i-Box | Permanent equipment labels missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619162&prj=632&rqi=Qf9wWnsfB3bINsU1Kkfs0LBBVc
RT1MECH-200-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1AS_A_04 | FFU - Air Scrubber |  |  | power isolator blocked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619441&prj=632&rqi=zpR5uGMgMdTFibZ9NUnOopzkrF
RT1MECH-210-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1AS_B_02 | FFU - Air Scrubber |  |  | Cement marks on unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619439&prj=632&rqi=G45XuNmRnzkVxW6ivRBzXdWnLs
RT1MECH-208-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1AS_B_01 | FFU - Air Scrubber |  |  | faulty isolator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619438&prj=632&rqi=1ap51sHjSnSut5DAavs3rgrPao
RT1MECH-212-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1AS_B_03 | FFU - Air Scrubber |  |  | cable management to be done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619440&prj=632&rqi=Edv4wemaeQUECD8voJzRX9Kitg
RT1MECH-243-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | imanuddinhamdan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_4 | CRAH - Computer room air handler |  |  | Valve bracket damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619168&prj=632&rqi=n9qp5TMzVaZJtyvwcu5zaU9HdZ
RT1MECH-232-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_5 | CRAH - Computer room air handler |  |  | Confirm clear access is available to all CRAH components and that sufficient withdrawal space has been allowed for maintenance, removal and replacement of parts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619166&prj=632&rqi=NDOZ7aAdISY1XtPwnQGfcLJOl9
RT1DCOS-42-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Controls | equipment | 1DCOS_CP_1 | DCOS - Control Panels |  |  | Neutral bar only provided for protected earth ( power earth bar). No functional earth (signal earth bar) provided for the panel. Other panels PCP, SCP, RIO, LCP has both functional. HNY to get confirmation from EoR. Aoolicable to all CP panels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618967&prj=632&rqi=Xz51xZWi5RKfbIjbIDmNCm1zcl
RT1MECH-228-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_1 | CRAH - Computer room air handler |  |  | Confirm clear access is available to all CRAH components and that sufficient withdrawal space has been allowed for maintenance, removal and replacement of parts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619164&prj=632&rqi=KmgtbPoYrz8df63VLC3fRp4sfs
RT1MECH-229-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_2 | CRAH - Computer room air handler |  |  | Confirm clear access is available to all CRAH components and that sufficient withdrawal space has been allowed for maintenance, removal and replacement of parts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619163&prj=632&rqi=0O2ggoB9e5bJ274vcgX0o7hgnK
RT1MECH-230-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_3 | CRAH - Computer room air handler |  |  | Confirm clear access is available to all CRAH components and that sufficient withdrawal space has been allowed for maintenance, removal and replacement of parts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619165&prj=632&rqi=y5DzGCQZt5KMXV0jpavMz3UDYq
RT1MECH-320-002 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1MAU_M1_1 | AHU - Air handling unit |  |  | The equipment labelling has not been fixed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618004&prj=632&rqi=Fk6wFcKZKxA06jXA0B76UWU2Ki
RT1MECH-320-003 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1MAU_M1_1 | AHU - Air handling unit |  |  | To provide relevant project piping specifications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618005&prj=632&rqi=Nmj7gq7O8x1OajSuuMpfKmIuOv
RT1MECH-320-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1MAU_M1_1 | AHU - Air handling unit |  |  | Observed dents and scratches on the bottom plate of the MAU. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618001&prj=632&rqi=V4MnF2SJ3gyzkY9RzhdA3rxrwB
YT1ELEC-122-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | As per understanding from Siemens, the earthing from the TX to earth system, it should be 2 earths from the TX room earth bar to the TX LV side and 2 earths from the TX room earth bar to the TX MV side. Current onsite installation has all 4 earths from TX room earth bar to TX LV side. GC to confirm with vendor (Siemens) and NV5 that this is an acceptable installation method | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617768&prj=632&rqi=CvHLcutbt9lxZ2q3KxZQ0PY7B9
RT1MECH-374-003 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1DWBP_M1_1 | DOMW - Domestic Water Set |  |  | No Tagging for Pump and Panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617613&prj=632&rqi=PSBFYEkrlgaKuSudQt91jDFRAm
RT1ELEC-382-001 | JH02-1/2 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_27 | LVSB - Low Voltage Switchboard |  | i-Box | Missing permanent nameplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617598&prj=632&rqi=ZCX9Zi2bcOBsr14VJapWuRR6Xj
RT1MECH-368-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1MWP_M1_1 | DOMW - Domestic Water Set |  |  | IP Rating for Panel to be updated with supporting letter from Supplier | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617290&prj=632&rqi=mhP1eVGuWmHsZ6sH0vnEuD1PLL
RT1MECH-255-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_6 | CRAH - Computer room air handler |  |  | Internal Tagging for equipment to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617287&prj=632&rqi=DuH8zhuYR43tjJevlQWTBDQbhX
RT1MECH-374-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1DWBP_M1_1 | DOMW - Domestic Water Set |  |  | Panel IP Rating to be clarified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617337&prj=632&rqi=zDvDCuNspzHX7blU6XZKYo3Owy
RT1MECH-374-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1DWBP_M1_1 | DOMW - Domestic Water Set |  |  | SLD Drawing to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617338&prj=632&rqi=qYpS7BoSEnIgHZrcMLQMaNnMsG
YT1ELEC-93-003 | JH02-1/2 | APAC | Closed | P1 High CX | ahmadfuad@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1SUDB_1 | SUDB - Secondary Utility Distribution Board |  |  | During energisation site walk conducted on Friday (3/4/2026), it was observed that there is a potential SF06 gas pressure issue at K01 Outgoing Feeder of 1SUDB_1. The SF06 pressure gauge indicates the reading is outside of the acceptable (green) range. ABB to investigate and determine the root cause of the issue whether it is due to gas leakage or instrument faulty. ABB to submit RCA for the issue to outline the findings corrective actions and preventive measure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617355&prj=632&rqi=hbYFlcpFfJcMAvTcw44V6T6KuO
RT1MECH-368-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1MWP_M1_1 | DOMW - Domestic Water Set |  |  | MCB Rating to be clarify. Drawing shows 40A while however onsite shows 32A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617291&prj=632&rqi=NLXRIC9jLaZH9m6PLHVsFeaJwc
RT1MECH-368-003 | JH02-1/2 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1MWP_M1_1 | DOMW - Domestic Water Set |  |  | Missing Labelling for equipment and warning sign | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617294&prj=632&rqi=Cv3C8h1OnfzzWAIlWUyy5mASwx
RT1MECH-376-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1TWSP_M1_1 | DOMW - Domestic Water Set |  |  | Panel tagging and Pump Tagging to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617336&prj=632&rqi=cdIPug46Us20lLqAWKM1kTYkZp
RT1MECH-376-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1TWSP_M1_1 | DOMW - Domestic Water Set |  |  | Single Line Drawing to be updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617335&prj=632&rqi=FQa8CcrKhqBql8FRLPE1j0McRt
RT1MECH-378-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1RWFP_M1_1 | DOMW - Domestic Water Set |  |  | Panel naming and pump tagging to be updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617334&prj=632&rqi=d3KHiJSRpLFpNjyPAmJLF0PRqY
RT1MECH-378-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1RWFP_M1_1 | DOMW - Domestic Water Set |  |  | Panel IP Rating to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617332&prj=632&rqi=lRBqd6K36vVVd1T6lbM3f9w2za
RT1MECH-294-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_03 | EF - Exhaust Fan |  |  | Exhaust fan duct support bracket is installed in a slanted and improper alignment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617303&prj=632&rqi=uo2yW4Z3zj1JXddqZBthydG5aB
RT1MECH-255-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_6 | CRAH - Computer room air handler |  |  | No Permanent Tagging Installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617288&prj=632&rqi=Yjpo9TfCxbW2F8PqvImQ1odFnJ
RT1MECH-251-001 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_2 | CRAH - Computer room air handler |  |  | Internal tagging for the sensor to be updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617285&prj=632&rqi=CsOdTw5CHlfdpIziiiQULtCtiB
RT1MECH-251-002 | JH02-1/2 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_2 | CRAH - Computer room air handler |  |  | Tagging for equipment is not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617289&prj=632&rqi=XxTwnHsHwbM919hFcwO8VJQJtm
RT1MECH-296-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_04 | EF - Exhaust Fan |  |  | Exhaust fan support bracket is in contact with the cable tray. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617214&prj=632&rqi=rpdgdOE1TGcpFjkcA9LGRnwDQT
RT1MECH-292-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_B_3 | EF - Exhaust Fan |  |  | Equipment layout drawing needs to be updated as the panel name shown is incorrect compared to the onsite panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617217&prj=632&rqi=i9cRPZNlYwxgRNwcQ9m3JI1XaX
RT1MECH-292-002 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_B_3 | EF - Exhaust Fan |  |  | Drawings missing from the panel. Applicable for all exhaust fan at Pre Action rooms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617218&prj=632&rqi=TsAU52ND91e0JIuYmUleoszjKm
RT1ELEC-495-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVSB_M1_1 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign is not affixed to the panel. Applicable to all panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617000&prj=632&rqi=l3GAewnNMBtrsxith7fk1hWqer
RT1ELEC-486-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M2_06 | LVSB - Low Voltage Switchboard |  | i-Box | General arrangement and schematic Drawings not in the panel. Applicable to 1LVDB_M2_06 and 1LVDB_M2_07 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616783&prj=632&rqi=bWbQrLDlS8VQldOnjmNFkxG4yD
RT1ELEC-486-002 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M2_06 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign is not affixed to the panels. Applicable to all panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616784&prj=632&rqi=yjYjoeFjkqqmBnI2d54lE8doXS
RT1ELEC-592-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M2_10 | LVSB - Low Voltage Switchboard |  | i-Box | Panel nameplate is damaged. Applicable to 1LVDB_M2_10 and 1LVDB_M2_12 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616785&prj=632&rqi=6FWSmSyEP5bVQmsgRaLZjKblTY
RT1ELEC-593-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M2_11 | LVSB - Low Voltage Switchboard |  | i-Box | Panel door knob is broken. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616786&prj=632&rqi=ZzGMq8XS7pgFiZUFGhSG9FcuRm
RT1MECH-351-004 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_1_CHWBT | CHWBT - Chilled water buffer tank |  |  | Permanent equipment labels not fixed. Apply to all Buffer Tanks. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615931&prj=632&rqi=RGGZoDoU2hHrJSZ2ULKopw1UTp
RT1ELEC-37-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1ATS_FR_02 | ATS - Automatic Transfer Switch |  |  | Panel door is unable to close properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615498&prj=632&rqi=S0cb5mcpUzBjfzC3dmMvz4MT7v
RT1ELEC-33-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1ATS_DR_01 | ATS - Automatic Transfer Switch |  |  | Dual power supply sign is not affixed to the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615494&prj=632&rqi=N3PcIEljwAQLG2nxAs3LVsbSKB
RT1ELEC-146-001 | JH02-1/2 | APAC | Open | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_F | MSB - Main Input Switchboard |  |  | HMI not yet positioned and installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615499&prj=632&rqi=jzmRCLGPrkSdfPruo3U6WzXzA5
RT1ELEC-144-001 | JH02-1/2 | APAC | Open | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | HMI not yet positioned and installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615493&prj=632&rqi=tVWdh4nZ4ci29SWANQd9aueWwZ
RT1ELEC-145-001 | JH02-1/2 | APAC | Open | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_D | MSB - Main Input Switchboard |  |  | HMI not yet positioned and installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615495&prj=632&rqi=AhZZWMOC1Q2sjQUUgRnJNPjJQn
YT1ELEC-13-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | pauljohnson@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | CT for L3 phase is to be replaced and to be tested once installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615490&prj=632&rqi=hHms2n2K4jNVq1FsyPtT7hgQkU
RT1ELEC-366-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1_25 | LVSB - Low Voltage Switchboard |  | i-Box | Latest revisions of both the General arrangement and schematic Drawings missing . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615497&prj=632&rqi=hp9N6bFX6HVQnQTMwtsZL5L946
YT1ELEC-11-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | pauljohnson@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | CT for L3 phase is to be replaced and to be tested once installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615491&prj=632&rqi=T32qSICfHbb0bkG8zUCM3pacCZ
YT1ELEC-128-001 | JH02-1/2 | APAC | Closed | P1 High CX | ahmadfuad@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | During busduct Cx2A was conducted between 1MSB_A to 1UPS_A1, it was observed the earth bar on UPS compartment and busduct N bar is too near to each other. It was observed that the spacing is less than 5mm spacing. GC to evaluate and make adjustment to ensure the safe gap of more than 25mm in between. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615338&prj=632&rqi=WAL8GpcMRztKz9Nzwjyw9JZh8V
RT1ELEC-13-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615090&prj=632&rqi=YlL7R0mG0OvW5CjiurU7doP4Xp
RT1ELEC-5-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_E | RMU - Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615091&prj=632&rqi=53cnJmWVkyX4iJuAVQnp69Y0Ct
RT1ELEC-11-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615089&prj=632&rqi=KcYONP7ahdkOf2hY2UwPUEyVyu
RT1ELEC-12-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615093&prj=632&rqi=EsEMqaROQccNZbKrjEi1X4jocr
RT1MECH-330-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_1_CWP | CWP - Condenser Water Pump |  |  | Danger warning sign is not installed on panel. Apply for all CWP panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614869&prj=632&rqi=YNSxNGdlhfM2mOKRLD99v3yQUv
RT1MECH-351-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_1_CHWBT | CHWBT - Chilled water buffer tank |  |  | Tank painting micron indicated 50 micron for external layer and 150 micron for internal layer as per document specification. GC to provide prove on painting micron. FAT document didnt shown the information. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614745&prj=632&rqi=Br2eLxTujVgrWI86ZZ7C6gzsn2
RT1MECH-323-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_M1_1_CHWP | CHWP - Chilled water pump |  |  | Danger warning sign is not installed on panel. Apply for all CHWP panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614787&prj=632&rqi=A0EEsCY1v6RpIlDBiKuqGhkePD
RT1MECH-351-003 | JH02-1/2 | APAC | Open | P3 Low CX | ahmadfuad@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_1_CHWBT | CHWBT - Chilled water buffer tank |  |  | maintenance ladder to buffer tank stop short at plinth. However no access provided from ground to plinth. Suggest to extend the ladder to the ground. GC/ACT to confirm maintenance feasibility. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614748&prj=632&rqi=C9YaPSKYCc1GdCen4W2v2jQQld
RT1MECH-351-002 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_1_CHWBT | CHWBT - Chilled water buffer tank |  |  | Bolting at the floor and end connection did not indicate torque mark. To ensure all bolting have torque mark and demonstrate to CTA on site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614747&prj=632&rqi=IDB5PdJqTskdjvWnz1ADdZOmaS
RT1ELEC-404-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_DR_8 | LVSB - Low Voltage Switchboard |  | i-Box | Proper circuit number tagging to install. Current installation is not acceptable. Refer to the sample as per attached. Typical for all LVDB panels. Please do one sample for review before proceed for other panels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614680&prj=632&rqi=5IS2R3pUvyTW1l5peOcuerRj42
RT1ELEC-129-004 | JH02-1/2 | APAC | Closed | P3 Low CX | fazdliabdulmubin@eaton.com | 2026-03-02 04:00:00.000 +0400 | Commissioning Authority | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483517&prj=632&rqi=XTCueKoQIVXg5I2z2etLzoPDgV
RT1ELEC-129-005 | JH02-1/2 | APAC | Closed | P3 Low CX | fazdliabdulmubin@eaton.com | 2026-03-02 04:00:00.000 +0400 | Commissioning Authority | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | Installation checklist from MCE completed (signed off) and attached to this checklist as a document (where Applicable) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483520&prj=632&rqi=UQl0rjX9Zw5AuEEdwq3G2kqJHC
RT1ELEC-96-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STS_A1R1_1 | STS - Static Transfer Switch |  |  | FAT report provided is without the Primary Injection test on ACB breaker. As per Cx playbook, PI test is require to be conducted on site for breaker >250A. CSPM to arrange manpower to complete the testing on site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483514&prj=632&rqi=o2CwBUBFhEWHLla9vd210hgFYS
YT1ELEC-179-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-26 04:00:00.000 +0400 | Consultant | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_M1 | MSB - Main Input Switchboard |  |  | Q14 incorrect settings for the short time. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352255&prj=632&rqi=KPA6SC4i790wWPQc0TodknGsEt
RT1ELEC-181-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  |  | HMI not yet in position and wall mounted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204140&prj=632&rqi=j7EZlxdchcc8eEfhTNZjRurHXa
RT1ELEC-178-002 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  |  | HMI not yet positioned and installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204138&prj=632&rqi=DiZuklP0GrVGPzBqGHYA4YgixR
RT1ELEC-177-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_A | MSB - Main Input Switchboard |  |  | HMI not yet in position and wall mounted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204141&prj=632&rqi=DLZ7zFSTNFR9cWhMOLJ616I6sG
RT1ELEC-180-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_M1 | MSB - Main Input Switchboard |  |  | HMI not yet positioned and wall mounted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204143&prj=632&rqi=ITUqzjbXfKTiCYYSVr0UcTRPjN
RT1ELEC-129-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | DC+ and DC- busbar to tag '+' in red color and '-' in black color. Current on site missing color tag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199812&prj=632&rqi=1lVBgHoctvjFT7VaKmkuUeJ85h
RT1ELEC-129-003 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | Missing equipment tag for UPS to install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199815&prj=632&rqi=iy5piM3ZFqSMDL8Hp0AAxNL50U
RT1ELEC-129-002 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | Missing drawing pocket to install infront of cover plate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199814&prj=632&rqi=pJlCRsqkhg21VHEjXIO9tj25Xe
RT1ELEC-158-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_8 | MDSB - Mech Distribution Switchboard |  |  | Control drawing missing in the pocket drawing. Control Cable tagging for control unable to check. Typical for all 1MDSB_M2R_2 to 8. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198963&prj=632&rqi=QQlYI0tiLB0HDB5NlpNbIuuwiV
YT1ELEC-177-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | pauljohnson@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  |  | For the eWall Earthing Schematic, the schematic shows MSB, Transformer Room & Generator As a TNC (should be TNC-S) with a Neutral Earthlink shown inside the MSB. Also the schematic shows the LV cables from the TX & Genset as a PEN (Protective Earth & Neutral Combined) conductor. Current onsite LV cabling doesn't tally with the schematic and TNC set up, as cables installed have 14 earth cables from the TX to the MSB. GC to confirm with design. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198962&prj=632&rqi=qTZpxBSfJBfPxnlk7QJ5jMPweE
RT1ELEC-60-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1ATSM_DR_02 | ATS - Automatic Transfer Switch |  |  | Danger warning sign and dual supply warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198582&prj=632&rqi=maa8Ig5tbor6ZqMeIw1BK3teO8
RT1ELEC-56-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1ATSM_CR_02 | ATS - Automatic Transfer Switch |  |  | Danger warning sign and dual supply warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198583&prj=632&rqi=oeg48tNVbGv10APhzVpLha1Ndt
RT1ELEC-393-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_CR_09 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning is not installed on panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198575&prj=632&rqi=nJzevXGSYqcl090txkW885l9mb
RT1ELEC-397-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_C_13 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198578&prj=632&rqi=NQKh53FNP9mdCQDz01ounmIeJ9
RT1ELEC-178-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  |  | MSB_B HMI panel not yet installed as part of MSB Cx2A. Arrange with GC to expedite installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198576&prj=632&rqi=GA1J4K8OE2fjMLsMMnUA4QigLe
RT1ELEC-405-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_DR_9 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign is not installed on panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198571&prj=632&rqi=L3TFv5g7yeByXdFincTUHqzLZg
RT1ELEC-409-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_D_13 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign is not installed on panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198562&prj=632&rqi=tDAhiEbSmgcBbHR4Bc0Y0MzBBu
RT1ELEC-521-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_12 (40A) | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198581&prj=632&rqi=8hrms6LYXlbr3B32OiUYaHlskT
RT1ELEC-519-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_07 (40A) | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198579&prj=632&rqi=zSwcltYWZUr47LhyKLbn0uKjfw
RT1ELEC-179-003 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | MSB_R HMI panel not yet installed as part of MSB Cx2A. Arrange with GC to expedite this installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198573&prj=632&rqi=QavxI4aT72mBjrDs1FkCW0NuBl
RT1ELEC-520-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_11 (40A) | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign is not installed on panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198567&prj=632&rqi=nX6bbxShqdgTYZaJcHWZEAme0W
RT1ELEC-518-001 | JH02-1/2 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_06 (40A) | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198577&prj=632&rqi=70nRLRrzIVkWW1pNIiWT8mSipH
RT1ELEC-30-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1ATS_AR_02 | ATS - Automatic Transfer Switch |  |  | Permanent equipment labels are affixed and are as per approved colour scheme. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198288&prj=632&rqi=N8kFF5gQoBB9Gs7phGhl2ZYbnx
RT1ELEC-473-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_R_09 | LVSB - Low Voltage Switchboard |  | i-Box | Verify Permanent equipment labels affixed and are as per approved colour scheme. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198289&prj=632&rqi=WJMKas2t0bfI7CkJwKivRFhakJ
GI-228 | JH02-1/2 | APAC | Closed | P1 High DCOS | ahmadfuad@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Controls | equipment | 1DCOS_PCP_1 | DCOS - Control Panels |  |  | (FWT) During DCOS and CPOS SFAT, it was observed that minimum testing readiness was prepared by Honeywell. The test was deemed Not Acceptable and re-SFAT required. Line animation and basic graphics requirement were not presented due to unreadiness. These items are mandatory and required to be tested during SFAT. The configuration is not based on signed off SICD. The DCOS HMI graphics were only presented for one typical set of equipment, which does not comply with the MOS requirement that 100% of graphics must be ready and tested. Finally, no proper Internal test report and QA/QC report with graphic screenshot were not provided before the SFAT date. Honeywell to submit RCA for detailed failure root cause and corrective action plan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197901&prj=632&rqi=az01WNRLzOAu58KD05vj171sVK
YT1ELEC-93-002 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1SUDB_1 | SUDB - Secondary Utility Distribution Board |  |  | 1BTU_1 Battery Charger have two charger namely Charger 1 and Charger 2. Incoming power for Charger 1 identified is from LVSB_M1_35 R2. However, no incoming cable identified for Charger 2. Please recheck with design EOR to confirm power source for Charge 2. Typical comments for 1BTU_2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197324&prj=632&rqi=YO1i8S34Ih9wSZ4ZV4PcfWDa5f
YT1ELEC-488-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVSB_M1R_2 | LVSB - Low Voltage Switchboard |  | i-Box | LV cables connection to isolator for LCP-1EF-M1-13 and LCP-EF-M1-12 to redo cables termination due to bending radius not acceptable. As per PB 5.1 Equinix allow a min bend radius of 12-15 times the cable diameter | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197322&prj=632&rqi=ghn0qazo7yoNINrvOND43wZ8fq
YT1ELEC-199-002 | JH02-1/2 | APAC | Closed | P2 Medium CX | pauljohnson@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R_3 | MDSB - Mech Distribution Switchboard |  |  | For MCCB's Q02, Q03, Q04 & Q05 Discrimination study for instantaneous and ground faulty doesn't align with the Breaker Frame Size (In) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197154&prj=632&rqi=XAT82qKFbWJuVvIOj1CUhdHRuF
RT1ELEC-182-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_M2 | MSB - Main Input Switchboard |  |  | MSB_M2 HMI panel not yet installed as part of MSB Cx2A. Arrange with GC to expedite installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197175&prj=632&rqi=Hc94wkyTunCSSkV6EjGUG8v6DV
RT1ELEC-216-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_10 | MDSB - Mech Distribution Switchboard |  |  | Discrimination setting. Refer marked in yellow changes from R4. To finalise setting with design consultant and update sticker where required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197172&prj=632&rqi=wbSM1QTpwFSHwmRivz8T57fQRr
YT1ELEC-204-001 | JH02-1/2 | APAC | Open | P3 Low CX | pauljohnson@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M1_04 | MDSB - Mech Distribution Switchboard |  |  | Confirm all labels and safety labels are present | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197141&prj=632&rqi=SDV7NwyRxYql3K3BqkB03fTEqr
YT1ELEC-204-002 | JH02-1/2 | APAC | Closed | P2 Medium CX | pauljohnson@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M1_04 | MDSB - Mech Distribution Switchboard |  |  | For MCCB's Q02, Q03, Q04 & Q05 Discrimination study for instantaneous and ground faulty doesn't align with the Breaker Frame Size (In) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197146&prj=632&rqi=kIxrkSPRuoDZS5dreeBe2SKr96
RT1ELEC-215-001 | JH02-1/2 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_M2R_9 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_M2R_9 Q_06 breaker size onsite is 160AF/40AT. Discrimination Study for Q_06 show 100AF/40AT. Breaker size installed on site correct as per SLD. To reconfirm with design consultant which to follow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197163&prj=632&rqi=61Nm2h8Rc05tC9dzw74RUorRpS
YT1ELEC-199-001 | JH02-1/2 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R_3 | MDSB - Mech Distribution Switchboard |  |  | Confirm all labels and safety labels are present | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197153&prj=632&rqi=H12Quljw5IpeQB9C1HaMAU5O72
RT1ELEC-182-002 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_M2 | MSB - Main Input Switchboard |  |  | Tagging for switches K01 to K05 pending installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197178&prj=632&rqi=Bv5JsllJQzdB42trMD2HVYyK2u
RT1ELEC-10-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | 1RMU_B panel tagging pending installation. Typical for 1RMU_M1, 1RMU_M2, 1RMU_R and 1RMU_A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197100&prj=632&rqi=8OYap0mZM70Mnj7pznn939YNBs
RT1ELEC-10-003 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Permanent ladder or movable ladder or platform are required to be position inside the RMU. Current testing was conducted using temporary ladder. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197102&prj=632&rqi=A3c41jRoVHSKf6zR5OKqRciO2o
RT1ELEC-10-002 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | ZCT and Moxa BMS card pending installation inside RMU. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197101&prj=632&rqi=GPVqEoWCE4jYnSvmbT9eTkNowC
YT1ELEC-94-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1SUDB_2 | SUDB - Secondary Utility Distribution Board |  |  | Current Setting for below was tested on site without actual setting. However, to confirm if setting require to be set on site and If required please confirm the setting with design consultant. Typical comments for SUDB1 and SUDB2. 27- undervoltage 59- Overvoltage 81U - underfrequency 81O - over frequency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196867&prj=632&rqi=2rYpMWaBInxDX8X4nqgYfUt9Ue
YT1ELEC-93-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1SUDB_1 | SUDB - Secondary Utility Distribution Board |  |  | Current Setting for below was tested on site without actual setting. However, to confirm if setting require to be set on site and If required please confirm the setting with design consultant. Typical comments for SUDB1 and SUDB2. 27- undervoltage 59- Overvoltage 81U - underfrequency 81O - over frequency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196866&prj=632&rqi=9X5ZEvsuw9HOXkMUT9ekCLAf0o
RT1ELEC-94-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1SUDB_1 | SUDB - Secondary Utility Distribution Board |  |  | Approved Schematic drawing SLD yet to place inside SUDB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196759&prj=632&rqi=g2BJzPwwh1ulhHysu6q6TicUTw
YT1ELEC-372-002 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1_34 | LVSB - Low Voltage Switchboard |  | i-Box | Pending incoming cable test Cx2B. To expedite cable installation and testing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196557&prj=632&rqi=gyJBQnpRTsEVDRnl3ofIAtdZXP
YT1ELEC-178-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | HMI_R is yet to position and start Cx activity. To expedite wall mount installation and start Cx2A and Cx2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196555&prj=632&rqi=rFVgIw6aFHkujS8tpUMPCCTwZe
YT1ELEC-372-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LVDB_M1_34 | LVSB - Low Voltage Switchboard |  | i-Box | Incoming cable test pending installation and Cx2 document signed off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196544&prj=632&rqi=Z8EgQhGFN9OYduVjK2cPtNJT5W
YT1ELEC-198-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R_2 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_R_2 discrimination setting not tally with PDC report 1) Q_02 Please confirm I Instantaneous should be (6.0 x 100A (breaker frame size) = 600A) instead of 240A from discrimination studies. 2) Q_02 to 05, 07 to 12, 16 to 20 setting Ground fault at 0.4 x 100A = 40A which typical to trip setting? Otherwise, should this be typical to Q_01 which is 0.2 x 100 = 20A setting? 3) Q_14 I instantaneous 6.0 x 160A = 960A however setting shown is 600A. Please confirm Once NV5 revert, to update and retest accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196556&prj=632&rqi=ZvZ7A0ZMdXEWFi46msTYFvJ1HD
RT1ELEC-179-002 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | HMI R have yet to position and start Cx2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196416&prj=632&rqi=cXg7N1tpqYGL2IwNmCUNMH3LYS
RT1ELEC-179-001 | JH02-1/2 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | Key switches tagging missing on panel to install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196305&prj=632&rqi=nRQULAjfvXpptjpqtHHm0FSRpk
RT1ELEC-1-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-11-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Nameplate found rusty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615404&prj=626&rqi=ScqT0CLTybrgkJIbaI8UHYao1k
BT1FD-6-001 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-09-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | During the 1st alarm simulation, there was a delay in alarm signal detection/indication at the DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638410&prj=626&rqi=ZUNznXitUIPuUlGFOaQtmdgH0V
BT1FD-4-002 | JK01-2 | APAC | Open | P2 Medium CX | wellyjulian@commtechasia.com | 2026-09-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | During General Alarm, the motorized fire damper at the fire riser did not open. MFD FOH B panel indicated Floor 6, whereas it should indicate 4 dampers. LCP indication showed Floor 4 MFD ON. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638416&prj=626&rqi=rU9q1Z5hOBktAH58ibgdnbtBlH
BT1ELEC-4-001 | JK01-2 | APAC | Open | P1 High CX | fauzanfikri@commtechasia.com | 2026-09-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | During test generator under 100% load condition, abnormal noise and vibration were observed at the generator exhaust. On second start-up attempt, the generator was found hunting condition Testing could not be continued and further investigation from Altrak is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637827&prj=626&rqi=bphcaeP9uvmT1zwSt4CHARi872
BT1FD-5-001 | JK01-2 | APAC | Open | P1 High CX | wellyjulian@commtechasia.com | 2026-09-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_5.01 | PAV - Pre-Action Valve |  |  | During 1st Alarm simulation, SAP Fire Panel L5 indicated â€œCARD 3 LOOP 2 â€“ CARD MISSING/FAILED,â€ resulting in failure of the required interlocks, including CRAY ramp-down and other systems, following the General Alarm sequence. Orient to provide RCA and confirm whether card replacement or troubleshooting is required, followed by full re-testing of the interlock sequence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638412&prj=626&rqi=k9dN5yVpUR2Rhfe2NQ8nXO25Db
GT1FD-39-001 | JK01-2 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-09-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Fire Detection | equipment | ASDSP-7.10 | VES - Vesda |  |  | During P2G with DCOS, Description in alarm shows ASDSP-7.09 instead of ASDSP-7.10. DCOS team to fix this issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637728&prj=626&rqi=kfaQX4qQy5bvG5ud87pGTQItGX
BT1ELEC-38-001 | JK01-2 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-09-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | CxL4 â€“ 1MLTX_F can't be performed due to an issue with temperature control component. In addition, the communication cable to DCOS is still showing communication loss (commloss) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637790&prj=626&rqi=LBfFA2r06u25d4oewWX4NzQeNd
BT1ELEC-5-001 | JK01-2 | APAC | Open | P1 High CX | fauzanfikri@commtechasia.com | 2026-09-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | During CxL4 testing for scenario â€œEarthing Switch State Checking for Maintenance 1RMU,â€ the earthing switch coil on 1RMU_B was not working. This is second time the same issue has occurred. The same issue also happened previously when 1RMU_B was energized | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637764&prj=626&rqi=ESXFou3KLjofcY7yNSrXUis3aW
GT1ELEC-155-003 | JK01-2 | APAC | Open | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Controls | equipment | 1PANEL_I/O_Motorized Damper | CP - Control Panel |  |  | GC need to perform Air TAB for MAU and provide report Air TAB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637453&prj=626&rqi=UjBmnpO5K1ywj4PQisbUefZu5Q
GT1ELEC-155-002 | JK01-2 | APAC | Open | P2 Medium DCOS | DimasKurniawan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Controls | equipment | 1PANEL_I/O_Motorized Damper | CP - Control Panel |  |  | DCOS have to provide additional register (regarding new SoO of MAU Motorize Damper) that need to integrate to DCOS monitoring: - High Temperature Alarm - Bypass Damper Fault - Room Damper Fault Level 2-7 (Cool Spine) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637448&prj=626&rqi=EL52L53EL1yuDrjD5oVPNDRehs
GT1MECH-81-001 | JK01-2 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_6.01 (Existing) | PAV - Pre-Action Valve |  |  | Seismic Bracing not yet installed and will be planned to install asap by GC. (This issue for all floor) Ensure that when installing those, there will be not affect piping and support pipe. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637418&prj=626&rqi=V0uD3o6WrpurIRJIVAUhKYD1WP
BT1MECH-60-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | There is a discrepancy in the Hâ‚‚ sensor reading. The value displayed on the HMI-LCP is 1, whereas the sensor indicates 0. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637251&prj=626&rqi=gPrRcT5UBPqxjWOA0qGaaXXCnf
BT1MECH-57-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | During the Fire Alarm Signal Test, the fire alarm status on the LCP HMI remained "False." | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637250&prj=626&rqi=qRaot1VG4LIZx7RVh9seJHPSW5
BT1MECH-60-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | During the Fire Alarm Signal Test, the fire alarm status on the LCP HMI remained "False." | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637249&prj=626&rqi=wO7YbbtF7AOquLNf3Y7DaRwwG2
BT1MECH-64-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-04 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | During the manual ON/OFF on HMI operation, when the selector switch is moved to Manual, the unit immediately starts running. However, according to the SOO flow for Manual Mode, the selector switch should first be moved to Manual, followed by pressing the Start button on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636785&prj=626&rqi=gIS0ZGdejsnTyfbJXrKu8UFaXJ
BT1MECH-67-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-04 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | During the manual ON/OFF on HMI operation, when the selector switch is moved to Manual, the unit immediately starts running. However, according to the SOO flow for Manual Mode, the selector switch should first be moved to Manual, followed by pressing the Start button on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636797&prj=626&rqi=devqIW20yB924cyLkRFfkrJCf4
BT1MECH-67-001 | JK01-2 | APAC | Closed | P2 Medium DCOS | MulyaSitanggang@commtechasia.com | 2026-09-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | There is a discrepancy between the room temperature sensor reading and the temperature displayed on the DCOS graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636795&prj=626&rqi=TFQXmKy4jE0fUgOEHFMeo50i84
BT1MECH-62-003 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_C_54 | EF - Exhaust Fan |  |  | During the manual ON/OFF on HMI operation, when the selector switch is moved to Manual, the unit immediately starts running. However, according to the SOO flow for Manual Mode, the selector switch should first be moved to Manual, followed by pressing the Start button on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636655&prj=626&rqi=yH4n7wzbgLaeyBGGfgt2KlpVuD
BT1MECH-62-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_C_54 | EF - Exhaust Fan |  |  | The room temperature reading on the HMI LCP not fluctuating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636654&prj=626&rqi=IPMk0sziVraWweIqVFle0MNEzL
BT1MECH-58-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_B_31 | EF - Exhaust Fan |  |  | During the manual ON/OFF on HMI operation, when the selector switch is moved to Manual, the unit immediately starts running. However, according to the SOO flow for Manual Mode, the selector switch should first be moved to Manual, followed by pressing the Start button on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636668&prj=626&rqi=YurlJ5G4YNSXvbYnNIfvQ1HHpY
BT1MECH-61-001 | JK01-2 | APAC | Closed | P2 Medium DCOS | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_C_53 | EF - Exhaust Fan |  |  | There is a discrepancy between the room temperature sensor reading and the temperature displayed on the DCOS graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636651&prj=626&rqi=YCCMqY0N0ivUxyREcFxfY7lOZz
BT1MECH-58-001 | JK01-2 | APAC | Closed | P2 Medium DCOS | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_B_31 | EF - Exhaust Fan |  |  | There is a discrepancy between the room temperature sensor reading and the temperature displayed on the DCOS graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636667&prj=626&rqi=VpRgGyB1xlRkpyYHlD3RSSdwDx
BT1MECH-62-001 | JK01-2 | APAC | Closed | P2 Medium DCOS | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_C_54 | EF - Exhaust Fan |  |  | There is a discrepancy between the room temperature sensor reading and the temperature displayed on the DCOS graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636652&prj=626&rqi=olHhFV81LI9RMqwHF7bDwOYIYm
BT1MECH-50-003 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_22 | DXID - FCU/DX Indoor Unit |  |  | During Dx FCU Functional Test, when Simulate the space/room temperature Higher than current set point by changing the Setpoint at Centralize LCP, set point temperature does not trigger to thermostat | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636426&prj=626&rqi=i9pSwnESXy5aTeEYBWmAh4UeHF
BT1MECH-50-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_22 | DXID - FCU/DX Indoor Unit |  |  | There was no change in the set temperature on the LCP and DCOS when the set temperature was changed on the thermostat. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636421&prj=626&rqi=NsnGfVb95C35RceLOl0PUKor93
GT1ELEC-48-004 | JK01-2 | APAC | Closed | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Please revise the graphic for STSSB_C_1 refer to STSSB_B_1, as they are one integrated equipment, not separate equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636447&prj=626&rqi=TlIwS9GO8G75e3YoYeyaOax1KK
BT1MECH-50-004 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_22 | DXID - FCU/DX Indoor Unit |  |  | During Dx FCU Functional Test, when Simulate the space/room temperature Lower than current set point by changing the Setpoint at Thermostat, set point temperature does not trigger to Centralize LCP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636430&prj=626&rqi=1GNAYLl70PWIGhF5Ru0705XMnk
BT1MECH-50-005 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_22 | DXID - FCU/DX Indoor Unit |  |  | When Start Hot Standby Sequence test, Second FCU units in the same room are not operating normally (B_22) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636443&prj=626&rqi=SMmgH6l1wcO4cmL2oPiEbDNb6j
GT1ELEC-50-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | Please revise the graphic for STSSB_D_1 refer to STSSB_B_1, as they are one integrated equipment, not separate equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636453&prj=626&rqi=5F8Yr5GuElaQE0fh6D440MQ9L2
GT1ELEC-49-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Please revise the graphic for STSSB_C_2 refer to STSSB_B_1, as they are one integrated equipment, not separate equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636452&prj=626&rqi=3ZRIfUEDZly4mNUjr8WcPoDhfY
GT1ELEC-52-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Please revise the graphic for STSSB_F_1 & F_2 refer to STSSB_B_1, as they are one integrated equipment, not separate equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636454&prj=626&rqi=mBLqiF3g1GFeBOtvH39WPtjIcn
BT1MECH-50-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_22 | DXID - FCU/DX Indoor Unit |  |  | During the compressor failure test, the compressor power was intentionally switched off. After the power was reinstated, the VRFOD did not immediately resume automatic operation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636409&prj=626&rqi=NA5ZVN2tGFS9I31w4dUD2t2pqr
BT1MECH-54-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | During alarm test, upon DXFCU power loss the alarm appeared for approximately 8 minutes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635489&prj=626&rqi=GTvcp2zTmSN1WhkSPy01fKDcE2
BT1MECH-52-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_42 | DXID - FCU/DX Indoor Unit |  |  | During alarm test, upon DXFCU power loss the alarm appeared for approximately 8 minutes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635580&prj=626&rqi=dLsOL2rEK5DMcV2Ppf6M6sgsYz
BT1MECH-54-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | There is a discrepancy in the room temperature readings between the thermostat and the LCP/DCOS (The readings on the LCP and DCOS are the same) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635569&prj=626&rqi=RpWAKd9R2OUl9o6MvKgeJx30Xw
BT1MECH-53-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_B_41 | DXID - FCU/DX Indoor Unit |  |  | During alarm test, upon DXFCU power loss the alarm appeared for approximately 8 minutes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635488&prj=626&rqi=xr7EEDzxymirgAc7uU0AupTjdN
BT1MECH-53-003 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_B_41 | DXID - FCU/DX Indoor Unit |  |  | During Simulate power failure for PICV actuator by disconnect power supply to the PICV actuator from control panel. After re-connect power supply, PICV closed first then open again to last position. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635490&prj=626&rqi=l2AXx148C94qEjDSguknbINLLd
BT1MECH-52-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_42 | DXID - FCU/DX Indoor Unit |  |  | During Start Stop Sequence (Auto Mode) LCP unit cannot be switched to Auto Mode (Need To Confirm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635586&prj=626&rqi=mL3hLGurxmSGJkF6cKFpclMZNI
BT1MECH-52-003 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_42 | DXID - FCU/DX Indoor Unit |  |  | There is a discrepancy in the room temperature readings between the thermostat and the LCP/DCOS (The readings on the LCP and DCOS are the same) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635587&prj=626&rqi=g1lNFtCKKA1O3C6CnOxrlWFbTp
GT1MECH-87-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Fuel | equipment | 1LCP_FPUMP_B2 | FT - Fuel Tanks |  |  | Actual test regarding existing Pump function cannot perform due to incomplete PRV setting. Once it already done and can be test, please invite CTA to witness | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635230&prj=626&rqi=g0iSG9Gz6CNv7veJrd22u36BLb
GT1MECH-86-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Fuel | equipment | 1LCP_FPUMP_A2 | FT - Fuel Tanks |  |  | Actual test regarding existing Pump function cannot perform due to incomplete PRV setting. Once it already done and can be test, please invite CTA to witness | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635227&prj=626&rqi=AHt3pUxrHDwk3FbLlle2xJwR7z
BT1MECH-53-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_B_41 | DXID - FCU/DX Indoor Unit |  |  | During Start Stop Sequence (Auto Mode) LCP unit cannot be switched to Auto Mode In SOO mention can Auto Mode Operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635234&prj=626&rqi=roBRvp9Mtcz0V2mzrdMgqYXx2H
BT1ELEC-41-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | During CxL4 1RMU_D, Power meter at 1MSB_D_1 shows an inaccurate kW reading compared to the actual load | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634714&prj=626&rqi=wHRQmVc19Rko0EPanwQRfN5ECE
GT1FD-1-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Fire Detection | equipment | 1FAS_2 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634252&prj=626&rqi=Wum1X5C1hMsnJr6rzFMLmdEPs6
GT1MECH-26-003 | JK01-2 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634308&prj=626&rqi=CwP5DurHFi5UDAKRwUebiH9Onk
BT1MECH-51-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | During Fail compressor by failing power to compressor. Verify Loss Communication alarm at DCOS. FCU remain running on site is off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634360&prj=626&rqi=zQRC1fAPq5qdCHdM7ovDRW46Ds
GT1FD-5-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Fire Detection | equipment | 1FAS_6 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634255&prj=626&rqi=9dsWukbRvygQ9e11ReX1px7qlT
GT1MECH-26-002 | JK01-2 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634307&prj=626&rqi=AJXpZSv7fBNnHXkixJyCKxj2Gm
BT1MECH-51-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | During indoor trip alarms no alarm verified at DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634345&prj=626&rqi=10F0qwBXaDYWYRGvjdwl5AQ6UU
GT1MECH-25-002 | JK01-2 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634311&prj=626&rqi=e7zF8Mie1Iv9XWj9G7eCwhYEyU
GT1FD-3-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Fire Detection | equipment | 1FAS_4 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634253&prj=626&rqi=wZgDVaKuix21sJgihX8MhuxmgS
BT1MECH-51-003 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | During Start Stop Sequence (Auto Mode) LCP unit cannot be switched to Auto Mode In SOO mention can Auto Mode Operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634361&prj=626&rqi=am7LY77Zt0yTw6zFobgql4HZaH
GT1MECH-25-003 | JK01-2 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634312&prj=626&rqi=qJEVIqgsibWSBEP5hiSuktm9lJ
GT1MECH-27-003 | JK01-2 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634306&prj=626&rqi=zDpaWMd8v35SL9OBip2h7qK0v9
GT1MECH-27-002 | JK01-2 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634305&prj=626&rqi=tZK5fM4Bt3dUsqp5Yc2v3veK2e
GT1MECH-24-004 | JK01-2 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634310&prj=626&rqi=TKkSJJQih2icFfFHxF4uzkUV43
GT1FD-4-001 | JK01-2 | APAC | Open | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Fire Detection | equipment | 1FAS_5 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634254&prj=626&rqi=NU5OPmYUAt4o5F6msHmHUc8lAx
GT1FD-6-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Fire Detection | equipment | 1FAS_7 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634256&prj=626&rqi=yDxXlJo1RYF2ubOon9es4zGsnv
GT1MECH-79-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_2.01 (Existing) | PAV - Pre-Action Valve |  |  | Integrated testing with CRAY has not been performed when the 1st alarm, CRAY will ramp down. Orient to perform this test with Vertiv and make a report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634257&prj=626&rqi=NGTpAk4dqI617p3IdUvxrVMKuM
GT1MECH-24-003 | JK01-2 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634309&prj=626&rqi=8QVqcDw9wrCA0TfHibBU1bvXx7
BT1MECH-51-004 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | During Start Stop Sequence (Manual Mode) PICV water flow 1.5 (PICV water flow available (â‰¥1.6 lps)) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634362&prj=626&rqi=OPAbyifYzOxhXnCpytY3vpwd9T
GT1MECH-75-002 | JK01-2 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634165&prj=626&rqi=tpcH0Wtr5dW3B3JeSgyeUtzmdn
GT1MECH-77-004 | JK01-2 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634166&prj=626&rqi=dCNO1CoQCdquupoRVUFpmein2V
GT1MECH-78-002 | JK01-2 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634167&prj=626&rqi=J81s8THpJDNcIzrf1K3B5hUSLf
GT1MECH-76-006 | JK01-2 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634080&prj=626&rqi=3oAvWckFDyg6tFBT2ZHM1Xfpje
GT1MECH-35-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-08-18 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | During airflow measurement test, blanking panel beside Cool Array unit are bend / curved when running 100% fan speed of Cool Array test | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634048&prj=626&rqi=3eOPX57I63j6pSUWtPLOvqcJDA
BT1FD-5-002 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_5.01 | PAV - Pre-Action Valve |  |  | During CxL4 (Water Discharge Test) some issues are discovered; - The LED indicator floor mimic panel doesn't ON during 1st & 2nd alarm (DONE) - There's a water leak/splash on water gong (DONE) - Need to add support for drain pipe at sprinkler Control Valve Room (DONE) - install flow direction sticker for fire pipe at some point (DONE) - Seismic Bracing not installed yet (DONE) - Wire burn in HAC & CAC will be test during IST (FYI) - Need to add installation isolation valve after flow switch (suggestion from FMG) --> for future maintenance (FYI) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638414&prj=626&rqi=jgdSbL0wwJUnW0s9NOw7fRnKPh
BT1FD-4-001 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | During CxL4 (Water Discharge Test) some issues are discovered; - Need to add support for drainpipe at the Sprinkle Control Valve Room (DONE) - install flow direction sticker for fire pipe at some point (DONE) - Seismic Bracing not installed yet (DONE) - After the test, leakage was found in 1st floor piping that makes Jockey Pump starts running continuously (DONE) - Wire burn in HAC & CAC will be test during IST (FYI) - Need to add installation isolation valve after flow switch (suggestion from FMG) --> for future maintenance (FYI) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638415&prj=626&rqi=IihmlgSdOF7dmojKlu2zZqiTGW
BT1FD-6-002 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | During CxL4 (Water Discharge Test) some issues are discovered; - There's a water leak/splash on water gong 7th floor (DONE) - Need to add support for drain pipe at sprinkler Control Valve Room (DONE) - Install flow direction sticker for fire pipe at some point (DONE) - Seismic Bracing not installed yet (DONE, can check on RFI reports) - Wire burn in HAC & CAC will be test during IST (FYI) - Need to add installation isolation valve after flow switch (suggestion from FMG) --> for future maintenance (FYI) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638411&prj=626&rqi=9uKjJ1wVH105kEc7x6WzANHBvy
GT1FD-2-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Fire Detection | equipment | 1FAS_3 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633417&prj=626&rqi=CahnmHwEEx1kA6swh6pKOjni5B
BT1ELEC-30-005 | JK01-2 | APAC | Open | P1 High CX | fauzanfikri@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Based on discussion between Aurecon, CTA, TnT, Altrak & GC regarding the phase unbalance issue during CxL4 1UPS_D_1, Altrak is required to investigate the issue and provide an RCA (Root Cause Analysis) for the phase unbalance observed when step load using generator source Issue related: During load step-up to 75% with Generator source, MSB panel detected a phase unbalance, causing power source automatically transfer from Generator to Utility. The same 75% load step-up was repeated using Utility source, and no phase unbalance was detected and remained stable at 75% load | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633390&prj=626&rqi=lD2UrRIr7PiaSdtdVj51vPLI29
GT1MECH-76-005 | JK01-2 | APAC | Open | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633408&prj=626&rqi=rtiwZ07foZ6QyRjrlkJsbpZAXG
GT1MECH-77-003 | JK01-2 | APAC | Open | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633412&prj=626&rqi=wRiLvwFvTK9Q2rSfbLImfRTs2D
GT1MECH-78-001 | JK01-2 | APAC | Open | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633410&prj=626&rqi=DW8TdfAwLlNA6H62jfKD4xH4Om
GT1MECH-75-001 | JK01-2 | APAC | Open | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633411&prj=626&rqi=pOTfBasLYQxv7RLrwtoeozROPG
YT1ELEC-155-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | ( Issue CxL2A Laying cable from DB_FOH_7_L to DB_DALI_L7) Need install labelling at FOH side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633151&prj=626&rqi=k2U2pFlOueL5QTJ18tF339jjMQ
YT1ELEC-152-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L4 | DB - Distribution Boards |  |  | ( Issue CxL2A Laying cable from DB_FOHA_4_L to DB_DALI_L4) Need install vinyl netral and grounding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633150&prj=626&rqi=EFKWaF0akOl1uESXw70v1PfTuf
GT1ELEC-155-001 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Controls | equipment | 1PANEL_I/O_Motorized Damper | CP - Control Panel |  |  | During the HRA activity for the MAU motorized damper programming and commissioning activity, the following items were identified: 1. Update the SoO flowchart to reflect the actual operating condition and obtain approval from the AE. 2. During a power failure, the actual motorized damper remains closed, rather than returning to the last position as currently stated in the SoO. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633221&prj=626&rqi=kj7WPMrvez59s3IovBFGRyfoD9
GT1ELEC-8-001 | JK01-2 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | For (FDAY) DCOS P2G verification related to Valve Command and Valve Feedback, GC need to coordinate with related parties to perform those tests. And after test already perform, Orise need to revise their report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633010&prj=626&rqi=bsyBckVw848CG6SAR3TY9GIvBb
GT1ELEC-9-001 | JK01-2 | APAC | Closed | P2 Medium DCOS | DimasKurniawan@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | For (FDAY) DCOS P2G verification related to Valve Command and Valve Feedback, GC need to coordinate with related parties to perform those tests. And after test already perform, Orise need to revise their report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633011&prj=626&rqi=X45g96956Q5XuLLXZLSE7ZpzOH
BT1ELEC-40-001 | JK01-2 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Key "K3" on Solenoid box can't take out during process reinstate the maintenance bypass for UPS, because UPS OFF conditions and thereâ€™s no power on HMI, so that can't send the signal to Solenoid box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633008&prj=626&rqi=4a2dwyWJNfPlRScHBK3p9N8l4d
GT1ELEC-7-003 | JK01-2 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | For (FDAY) DCOS P2G verification related to Valve Command and Valve Feedback, GC need to coordinate with related parties to perform those tests. And after test already perform, Orise need to revise their report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633006&prj=626&rqi=mxttWzUgyIXUPdnajyaN2ZPWMG
GT1ELEC-6-001 | JK01-2 | APAC | Closed | P2 Medium DCOS | DimasKurniawan@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | For (FDAY) DCOS P2G verification related to Valve Command and Valve Feedback, GC need to coordinate with related parties to perform those tests. And after test already perform, Orise need to revise their report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633009&prj=626&rqi=Vd8iHxh4nnvoF9x1FuSvkGg3oP
GT1FD-7-002 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-2.04 | VES - Vesda |  |  | Based on the current ASDSP point list, new loop-3 integration to DCOS points have not yet been configured and programmed. See the HLI Modbus List for reference. Be sure to retest after configuration. (Responsibility Orient and Orise, with escort by GC) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632821&prj=626&rqi=AJJezs0vGBpNMFhhFCFwfLectO
GT1MECH-73-002 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_5.01 | PAV - Pre-Action Valve |  |  | (Only for Record) During the PASCV C&E Matrix testing, a smoke detector was triggered in the data hall. At that time, the CRAY team had not yet confirmed whether the CRAY unit would ramp down as expected. Therefore, Orient and Vertiv conducted an internal test and invited CTA to witness the test and close this issue. (Orient already installed the cable and module). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632818&prj=626&rqi=MGgnLJnRQnzNAVAaFkfUo610xy
GT1MECH-72-002 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | (Only for Record) During the PASCV C&E Matrix testing, a smoke detector was triggered in the data hall. At that time, the CRAY team had not yet confirmed whether the CRAY unit would ramp down as expected. Therefore, Orient and Vertiv conducted an internal test and invited CTA to witness the test and close this issue. (Orient already installed the cable and module). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632817&prj=626&rqi=vFKbhJhRKqfHd70a4mncdTgTcD
GT1MECH-74-003 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | (Only for Record) During the PASCV C&E Matrix testing, a smoke detector was triggered in the data hall. At that time, the CRAY team had not yet confirmed whether the CRAY unit would ramp down as expected. Therefore, Orient and Vertiv conducted an internal test and invited CTA to witness the test and close this issue. (Orient already installed the cable and module). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632819&prj=626&rqi=nc51xdP33rKWULUC4xul0GH0ec
BT1ELEC-39-001 | JK01-2 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Key "K3" on Solenoid box can't take out during process reinstate the maintenance bypass for UPS, because UPS OFF conditions and thereâ€™s no power on HMI, so that can't send the signal to Solenoid box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632779&prj=626&rqi=zd4gcAGRE7vwHp08gYQhgj6TvE
BT1ELEC-32-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | During CxL4 1UDP_F_2 testing, abnormal sound/noise was observed from UPS unit during operation at 100% load on inverter mode | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632777&prj=626&rqi=lirAdRRcUdhMBJGRKvgMbJ70v5
GT1MECH-73-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_5.01 | PAV - Pre-Action Valve |  |  | Need to touch-up painting pipe and install flow direction. Manual Call Point (Z3-MP-10) need to install ID tag. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632655&prj=626&rqi=1KbYNOx9GMW161jGFM3somGwMH
GT1MECH-72-001 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | When the solenoid valve and PASCV are activated, the flow switch is active but the monitoring on the MIMIC and panel does not match with C&E Matrix. Need to check and retest and invite CTA for closing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632730&prj=626&rqi=R5cbVZhZ39hWXiDFb82ip9G83Z
BT1MECH-6-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | During Fan Speed Control (Group Control) Unit CRAH not response (Simulate the Return Temperature sensor set point lower than the current Return Temperature Sensor Value (Average sensor value) Fan speed does not increase | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632690&prj=626&rqi=SVTy5VpYBS7aprZxknxH4njpi8
BT1MECH-6-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | During Fan Speed Control (Group Control) Unit CRAH not respone (Simulate the Return Temperature sensor set point higer than the current Return Temperature Sensor Value (Average sensor value) Fan speed not decrease (STULZ) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632691&prj=626&rqi=VJ0hq43T0JKJDy0mpbiBpIVlJx
BT1ELEC-26-002 | JK01-2 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Key "K3" on Solenoid box can't take out during process reinstate the maintenance bypass for UPS, because UPS OFF conditions and thereâ€™s no power on HMI, so that can't send the signal to Solenoid box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632752&prj=626&rqi=iiJt8DNIAWLcg5MNeYA12QXJHS
GT1MECH-2-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | Please provide report cable for sensor CH4, H2 and CO. And revise acceptance criteria (on the MoS) of these 3 tests according to Approve SoO. Attach photo once it done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632735&prj=626&rqi=iUTdDxfsPu3b37P4KDcrz8U5ht
BT1MECH-6-003 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | During Grouping Failure / Lost Communicationâ€ alarm not appears DCOS, and on CRAH display not have sign alarm, only sound alarm on CRAH Unit (STULZ) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632692&prj=626&rqi=EVJLyt8PMEU2BPEbIUscUQ7kIx
BT1MECH-1-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | During Fan Speed Control (Group Control) Unit CRAH not respone (Simulate the Return Temperature sensor set point higer than the current Return Temperature Sensor Value (Average sensor value) Fan speed not decrease (STULZ) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632492&prj=626&rqi=U0KTkOxCsLIwDJSkRoxTkmxCrb
BT1MECH-11-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | During Water Leak Alarm test, the module sensor did not respond (usually the indicator lamp is on, but this off) Stulz to rectify this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632499&prj=626&rqi=gYSHSLwqjYIWWZ1Q3b08heoXhI
BT1MECH-1-003 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | During Grouping Failure / Lost Communicationâ€ alarm not appears DCOS, and on CRAH display not have sign alarm, only sound alarm on CRAH Unit (STULZ) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632493&prj=626&rqi=kygBRQ1RBA1i3e0d7X3dbcpotQ
BT1MECH-1-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | During Fan Speed Control (Group Control) Unit CRAH not response (Simulate the Return Temperature sensor set point lower than the current Return Temperature Sensor Value (Average sensor value) Fan speed does not increase | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632277&prj=626&rqi=B4Q6LcZCmsJkqlaGZQTAErNJdG
BT1MECH-12-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-08-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | During simulate of supply air temperature sensor failure, CHW Valve cannot modulate open to Vmax | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632102&prj=626&rqi=Do1CPGVf2rSI4XoKW4xUZQwLL6
GT1MECH-72-003 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | During the low-pressure simulation, a discrepancy was identified between the actual panel status and the C&E Matrix Rev. 04. The actual panel status is shown as Supervisory, while the C&E Matrix indicates an Alarm. Please clarify the intended status and confirm the correct sequence. If the C&E Matrix requires revision, the updated C&E Matrix shall be reviewed and approved by the Design Team. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633020&prj=626&rqi=639x4pwb3LlLKfqm8P6OM7roWO
GT1FD-7-001 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-2.04 | VES - Vesda |  |  | (For All ASDSP issues) During the L3 ASDSP testing, the ASD workstation was not ready, as an additional VHX 1200 module was required for configuration and programming. After the installation is completed, the vendor and GC shall retest the ASDSP functionality. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632820&prj=626&rqi=LkUVbUnIKvEpLWI1SrspcqFupE
BT1ELEC-29-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | On DCOS & HMI UPS input phase-to-phase voltage displayed phase-to-neutral voltage values | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631945&prj=626&rqi=wzhbQzOPyVyAIEdE43mOHelxyM
BT1ELEC-30-004 | JK01-2 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Key "K3" on Solenoid box can't take out during process reinstate the maintenance bypass for UPS, because UPS OFF conditions and thereâ€™s no power on HMI, so that can't send the signal to Solenoid box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631944&prj=626&rqi=pA5uDzseJcRhSy0HsaQNndRy21
YT1ELEC-123-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Discrepancy between drawing and actual labelling, need update drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631736&prj=626&rqi=5KhPAmayDGzBS6jdftRLw1JrgF
YT1ELEC-123-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | elevation socket outlet not align with shop drawing (refer attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631737&prj=626&rqi=8LkB24OYhmsTHVSvHrKXAtqZ6R
YT1ELEC-120-004 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Elevation socket outlet not align with shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631731&prj=626&rqi=woEXh7HZS6V5zhKfRQsyFgUQPQ
YT1ELEC-14-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_A_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A 1UPS_A_2 to Libattsys_A_2) Labelling cable is incorrect, please change from 1UPS_A_2 to Libattsys_A_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631741&prj=626&rqi=job6QYZxyMOi6MR4QEKJu6GZGD
YT1ELEC-14-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_A_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A 1UPS_A_2 to Libattsys_A_2) Vinyl install for cable (+) is incorrect . Please replace it with the black color | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631739&prj=626&rqi=lUYDRwAq4ibV5s7G6Xwgj8SrXl
YT1ELEC-120-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Discrepancy between drawing and actual labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631728&prj=626&rqi=VOXvuzxbSOxLHmLXvNvfuVVOSr
BT1ELEC-30-003 | JK01-2 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | During load step-up to 75% with Generator source, MSB panel detected a phase unbalance, causing power source automatically transfer from Generator to Utility. The same 75% load step-up was repeated using Utility source, and no phase unbalance was detected and remained stable at 75% load | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631943&prj=626&rqi=2GduWvIaeUP4qwFKqWhqLjD0MM
YT1ELEC-23-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_G_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A 1UPS_G_2 to Libattsys_G_2) Vinyl install for cable (+) is incorrect . Please replace it with the black color | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631751&prj=626&rqi=10TThip3UEbynsZqUeX1Fd9IRK
YT1MECH-39-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | During Cx activity, found that one of support for return pipe (near PICV) are loose and not securely tight. Attach photo from same angle once already rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631727&prj=626&rqi=abgvpIHVXWaWYb240bHq7Mtf7d
YT1ELEC-23-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_G_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A 1UPS_G_2 to Libattsys_G_2) Labelling cable is incorrect, please change from 1UPS_G_2 to Libattsys_G_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631753&prj=626&rqi=O5hoVoFKXNv0TPwO13COlq1cQl
GT1MECH-64-002 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_41 | CRAH - Computer room air handler |  |  | During Waterflow Verification (PICV VMax) the HMI cannot show the value of Opening Chilled Water Valve, while in DCOS it appears. Stulz needs to rectify, attach photo once it already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631444&prj=626&rqi=ZbqWRUbjB5IciXkT40090E5aXx
GT1MECH-74-002 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | During Low Air Pressure Switch Function + 1st Alarm Test, Solenoid and Flow switch is not triggered, need to check and re-programming with latest Cause and Effect Matrix | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631443&prj=626&rqi=C42GlwYVb5wXkTdokPMhEKg3Bt
GT1MECH-74-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | During CxL3 activity, ID tagging valve for PASCV 7.01 are not installed yet. Pipe direction sticker also not installed yet, please provide. Once all been done, please attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631429&prj=626&rqi=HNLglqc80yCHJbe13GW5Vc2qvh
BT1ELEC-33-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Inconsistent overload alarm threshold was observed between UPS units. UPS F2 (Mechanical UPS) triggered the overload alarm at 107% load (above 100% load), while UPS D2 (Mechanical UPS) triggered the alarm at 112% load (above 110% load). The overload alarm setting shall be standardized across all UPS unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631724&prj=626&rqi=aYkuWumnoen8UceCtOq9bMZB7D
GI-031 | JK01-2 | APAC | Open | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | The gaps between CA need to be sealed off (for all floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631105&prj=626&rqi=KWAtwp6FCHDiNc8lanBuOuBWuC
GT1ELEC-51-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631012&prj=626&rqi=VWzMAuFzEQcWTVsyl2U3gwOyOg
GT1ELEC-46-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631002&prj=626&rqi=4L4BnNuSuk9ElsjUY0D5pwLO0g
GT1ELEC-52-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631014&prj=626&rqi=bi8fqogtIoBEypu8pYaKg3Ww2E
BT1ELEC-30-002 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | During UPS overload test, DCOS indicated "Battery Discharge" alarm even though the UPS was not operating on battery mode (ORISE) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630999&prj=626&rqi=DH6fojeSmL9pLYceqDYCVI0UFB
YT1ELEC-170-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630874&prj=626&rqi=SzVYHZ7Or0EU6ciNijtXcHKfkk
YT1ELEC-165-004 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630866&prj=626&rqi=OyPCW1vAOoHHuyojL4oiYNA2fy
YT1ELEC-164-007 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630864&prj=626&rqi=u6KSQbuGeZlUavjwMjm4TL49d1
GT1ELEC-47-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631004&prj=626&rqi=FbeMf0mhcWbA7rFVHqxDusim15
GT1ELEC-46-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631003&prj=626&rqi=6YDJRDaRlmwaRR2ryD6hf9HZH4
BT1ELEC-33-001 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Status of operation mode UPS after Overload Test, UPS status is Static bypass (Load on Bypass in DCOS), but in DCOS shows Load on Inverter | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630835&prj=626&rqi=zxRMJ4wCNIBLvyz5gteJtWscs7
BT1ELEC-30-001 | JK01-2 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | During 50% load step-up on Generator source, 1MSB_D_1 panel unexpectedly switched back to Utility. When trying to transfer the power source back to Generator, Breaker QE (Generator incomer) failed to close even though the Generator was running | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630998&prj=626&rqi=pfLGWS406jCW2r7uTJjekIl2tc
GT1ELEC-47-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631005&prj=626&rqi=KlBDQoWwXsU5kGR0ziVJ2jUdaD
GT1ELEC-48-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631007&prj=626&rqi=GLOWhyJhBe3AKcjdXCh4CsiOTA
GT1ELEC-48-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631006&prj=626&rqi=dekFIHGifsO8qZD2WL6sYtrhje
GT1ELEC-50-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631174&prj=626&rqi=BIqbIj5VqJgap2nibPhczQ8A6R
YT1ELEC-168-005 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630868&prj=626&rqi=CulEoJmYNmNn6aoP07HM5JYPLC
GT1ELEC-51-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631011&prj=626&rqi=JDweJ6pvgsAjeG2yS6JutEUUDP
YT1ELEC-169-008 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Rrom readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630873&prj=626&rqi=sqVms6UhpjLoF0AOgmX3VmEGsO
YT1ELEC-167-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630863&prj=626&rqi=O0HX3CfL5ipbsITW8tGbiXgYJc
GT1ELEC-50-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631010&prj=626&rqi=ciANR9UN2kahQogzTgr68k3fQk
GT1ELEC-49-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631008&prj=626&rqi=MkPXYqQOOgnqN50MWmV8dezMOR
GT1ELEC-53-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631176&prj=626&rqi=f6TR8VhFZEF6zC9VechUVslqzU
YT1ELEC-171-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630875&prj=626&rqi=9qSe9PfYfeBEfqbg9aY7dudZfg
GT1ELEC-49-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631009&prj=626&rqi=IHIpu6jpuGCDvZHstoYi5On48a
GT1ELEC-53-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631177&prj=626&rqi=EgEObJlXhBD9JTPqTJNyYZOiUB
GT1ELEC-52-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631013&prj=626&rqi=iadGQM8nYZGwAPvQ50MCmh3jqo
YT1ELEC-166-007 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630869&prj=626&rqi=2VuykcWdD73U1Q1karLcVX9cwk
GT1ELEC-7-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Voltage Dip during Block Load Test 0%-100%-0% out of tolerance. 418 to 280 Volt (above 20%) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630674&prj=626&rqi=q9nfLqVsBkbYR3m6gKBtn8WQHi
BT1ELEC-28-002 | JK01-2 | APAC | Open | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | During UPS transition from Normal Mode to Dynamic Mode, the DCOS graphic did not update. The operating mode remained displayed as "Load on Inverter" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630608&prj=626&rqi=cW6ewpy6xdhHg1BX2fW6MXJcG2
BT1ELEC-28-004 | JK01-2 | APAC | Open | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | During the Maintenance Bypass test, Key K3 at MSB solenoid box could not be released after switching sequence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630610&prj=626&rqi=iJrzuPJCDktmK4g2f6s5na1aDg
GI-030 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | All the sharp edges (which is in contact with the cable) need to be protected with rubber protection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630627&prj=626&rqi=dA5rZKtCe1TiDkzHUMKOZBKFZU
GT1ELEC-7-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Frequency Dip during Block Load Test 0%-100%-0% out of tolerance. 50Hz to 41.88 Hz (above 10%) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630675&prj=626&rqi=YR6kfvGfDzOhg1DAoOXIM9SPZa
BT1ELEC-28-003 | JK01-2 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | During UPS overload test, Overload Alarm was not triggered even though the UPS load reached 110% of rated capacity | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630609&prj=626&rqi=vgcXIgRzhStRnomd4DF9mEouYT
BT1ELEC-28-001 | JK01-2 | APAC | Open | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-07-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | DCOS Graphics Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | During UPS transition from Normal Mode to Eco Mode, the DCOS graphic did not update. The operating mode remained displayed as "Load on Inverter" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630607&prj=626&rqi=4qfsY2i9kWx6VKTjGv3OTPqiab
YT1MECH-62-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630236&prj=626&rqi=Pm3zPhhhxHjqt3YncvB5vNWfXS
YT1MECH-61-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630229&prj=626&rqi=WwM7DfIoIpKsE7sU2VWMKSfpE1
YT1MECH-59-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630221&prj=626&rqi=C6LW9djWEfh8uFKbj3qOi8kJWs
YT1MECH-59-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | Tidy Up Fire Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630224&prj=626&rqi=KOJuOt9oPxMgs2RHtAet0huEpn
YT1MECH-60-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | Tidy Up Fire Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630228&prj=626&rqi=ze96R8Xybsms6Gt0axMG9eCpC5
YT1MECH-60-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | Completed Termination Cable PICV | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630226&prj=626&rqi=0FgDXfPxHAvhvwDT8fepdLrDky
YT1MECH-60-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630225&prj=626&rqi=zE2b1iW4605H4gDB9v1RE2IK4k
YT1ELEC-6-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630310&prj=626&rqi=jsfErSF9CECTwFOJIf27HaWs4o
YT1MECH-61-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | Tidy Up Fire Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630232&prj=626&rqi=DVSnPLo4JLUTsEKHGQQ6DGZLtJ
YT1MECH-61-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | Take Out Material Not Use | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630231&prj=626&rqi=VUsWLspuhNj2OwsxylQ04yicpE
YT1MECH-60-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | Take Out Material Not Use | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630227&prj=626&rqi=Yti7MXgAPEPnW6DiTknhjwAQB4
YT1MECH-61-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | Completed Termination Cable PICV | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630230&prj=626&rqi=ESIeBFQEq2w3H8xPIFWCwaI6zQ
YT1MECH-59-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | Take Out Material Not Use | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630223&prj=626&rqi=MhAq7E6lVKaELXvgHkptWieuDc
YT1MECH-61-005 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | Tidy Up Flexible Installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630233&prj=626&rqi=9m4jP7YjEuJYH13yOhkxKHjVAt
YT1MECH-62-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | Completed Termination Cable PICV | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630237&prj=626&rqi=Mo7TSaotI6QhmmDlDoUIMsYvvI
YT1MECH-62-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | Tidy Up Fire Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630239&prj=626&rqi=ZjKJu0a51ocri8EsXNC80mYkB5
YT1MECH-62-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | Take Out Material Not Use | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630238&prj=626&rqi=Z0BFPU80nJclPKyhqcnAeovLSu
YT1MECH-59-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | Completed Termination Cable PICV | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630222&prj=626&rqi=Hi2RVg2GQiJZBgPytvunvNTues
GT1MECH-76-004 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | During the verification of the flow reading between FM and the handheld tools, witnessed by CTA. The flow readings from FM and Pump HMI are consistent. However, the handheld measurement at the orifice balancing point does not match and shows fluctuating results, indicating a potential issue with the orifice. GC is required to obtain a formal statement letter from the orifice manufacturer/principal to clarify and justify the discrepancy. Compare with CHWP 2: with the same tools (the results are good and not much different) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630095&prj=626&rqi=PmI8cViTydkxolZ4BMLar3b3Dv
GT1MECH-77-002 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | During the verification of the flow reading between FM and the handheld tools, witnessed by CTA and attended by the Orifice Balancing principal, an anomaly was identified between the FM and handheld readings. GC shall investigate the discrepancy and provide clarification/ statement letter with principle regarding the observed measurement results. CHWP 4: FM: 43 l/s ¦ Handheld: -0.1 kPA (appx. 7 l/s) Compare with CHWP 2: with the same tools (the results are good and not much different) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630074&prj=626&rqi=swX5mKUuvAZY2YUbP0cmgZ84IS
GT1ELEC-17-002 | JK01-2 | APAC | Open | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Several points have not been tested: This includes all UPS units. - Output Overload - Output Alarm - Overload Shutdown - Rectifier Fuse - Total Output kW - Input Breaker Open - Low Battery Alarm - Battery Amps - Battery Time Remaining Status | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630169&prj=626&rqi=nkCDhr3eI5gY0FE1rpUR4mYmuj
YT1MECH-57-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | Completed Termination Cable PICV Valve | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629981&prj=626&rqi=mXtQcO0mG6Y0YJcLNXeG7jQimN
BT1ELEC-26-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | During the preparation for the UPS B_1 L4 (Burn-In) test, a cable was found to be in contact with the busbar. Once finish burn-in, install additional rubber protection on the cable, as over time the cable may come into contact with the busbar again. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629978&prj=626&rqi=BGmdehl5oE4CnaPCkITzOjSbgo
YT1MECH-57-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | Tidy Up Fire Cable at CA unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629982&prj=626&rqi=QgzKDftjBQS9VoXJHUqAQUuhrx
YT1MECH-57-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629980&prj=626&rqi=9FFmrcU1uqJhphF6mJMeQvH9jB
YT1MECH-58-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | Take Out Material Not Use | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629985&prj=626&rqi=3FJo0ZksB9aGqj6GxPBZBrKhrV
YT1MECH-58-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | Completed Termination Cable PICV | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629984&prj=626&rqi=72xsvcJC8jkH5hVwNP60Fg8K6W
YT1MECH-58-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629983&prj=626&rqi=kIpDOnZPuuIl7b5pCVi6EiwGvV
YT1MECH-58-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | Tidy Up Fire Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629986&prj=626&rqi=KBL76dSkyyP9QmtpqOrK30omNu
GT1MECH-76-003 | JK01-2 | APAC | Closed | P1 High CX | MulyaSitanggang@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | A leakage has been identified on the CHWP-03 pipeline. Please provide an explanation of how this issue could have occurred, including a detailed Root Cause Analysis (RCA). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629352&prj=626&rqi=NnZKMyWAxxP4jTHmkFzdpPp1U7
YT1ELEC-162-002 | JK01-2 | APAC | Closed | P2 Medium DCOS | DimasKurniawan@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | General Contractor | L2B | DCOS Installation not complete | DCOS | Electrical â€“ LV | equipment | 1Fuel Leak_L3 | LEAK - Leak Detection |  |  | The DCOS cable hasn't been pulled to the panel, even though the drawing shows a DCOS connected to the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629412&prj=626&rqi=LphCk92LvydoMVFsVCo5Cl6KdB
YT1MECH-43-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Completed Termination Cable Sensor_CA Response in issue must take evidence each of equipment in Block D (5th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629356&prj=626&rqi=xnSjIxED7cFxjcLDJxjkzYipdD
YT1MECH-43-006 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Tidy Up Flexible Installation_CA Response in issue must take evidence (report) each of equipment in Block D (5th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629359&prj=626&rqi=lG3cxyhsmiZowbJBe7kGOB6DHF
YT1MECH-43-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Completed Install PICV Cable_CA Response in issue must take evidence each of equipment in Block D (5th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629354&prj=626&rqi=Duc3ICIfPr38DqwNXLBv52Ovzr
YT1MECH-43-005 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Take out material not Use_CA Response in issue must take evidence each of equipment in Block D (5th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629357&prj=626&rqi=DjO91dVD7bdoaAEdaExqA7UlpD
YT1ELEC-9-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628852&prj=626&rqi=wCB4SHLV3pudbSDCdR3b3AaOHu
GT1ELEC-50-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L3 | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | Key interlock on ACB is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630618&prj=626&rqi=Sq1G6VWcRW5ombGYicBDiYZYgO
GT1ELEC-48-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L3 | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Key interlock on ACB is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630617&prj=626&rqi=xdyTaSu55pk8pqVcMMzy4v6ybq
GT1ELEC-53-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L3 | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Key interlock on ACB is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630619&prj=626&rqi=JR67iv5tyJzvMO8kLI4WVbAwPk
GT1MECH-77-001 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | During CxL3 Running Pump, leakage in connection pipeline | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628846&prj=626&rqi=UQOK76HGL6soRepZ6RSIhgt2GM
YT1MECH-50-004 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_C_01 | CA - Cool Array |  |  | Kindly Provide Report for Installation Flexible pipe (completed sign off TNT and CTA) Response in issue must take evidence/report each of equipment in Block C (4th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628858&prj=626&rqi=j4X6ZrrytLwD8hktyd3yWgI3ET
GT1MECH-76-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | During CxL3 Running Pump, leakage in flange connection pipeline | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628844&prj=626&rqi=pYUdeaBbijcFcCCSdNzZ23aU2o
YT1MECH-50-003 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_C_01 | CA - Cool Array |  |  | Kindly Termination All Cable Installation at Sensor unit Response in issue must take evidence each of equipment in Block C (4th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628855&prj=626&rqi=fyrQqrdRePzqnJ36fn8uytIZdR
YT1MECH-50-002 | JK01-2 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_C_01 | CA - Cool Array |  |  | Kindly Tidy Up All Cable Installation (Cable Sensor) Response in issue must take evidence each of equipment in Block C (4th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628854&prj=626&rqi=FrSXByHDUAskBJMQtgOy1icERr
GT1ELEC-17-001 | JK01-2 | APAC | Open | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Based on UPS Point-to-Graphic (P2G) test results, several DCOS points have not yet been tested. Please complete the testing for the following points: (will be verify during CxL4 ) 1. Battery Amps 2. Battery Discharge 3. Blower Fan 4. Alarm 5. DC Cap Fuse 6. Output Overload 7. Overload Alarm 8. Overload Shutdown 9. Rectifier Fuse 10. Total Output kW | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628675&prj=626&rqi=QBIP0nOgDwEgg1P2yTlq1EEZK4
YT1ELEC-46-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628735&prj=626&rqi=SdmsPMJiwIUZXA1eK4b4ZDPkyr
YT1ELEC-168-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Wrong cable termination location. The cable from 1MDSB_R1_2 to 1TOU_F_2 has been terminated at the wrong breaker Q1-3 at 1MDSB_R1_2 side. The correct termination point is breaker Q1-6. Please rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628708&prj=626&rqi=BKoiT67JvsmCXPScvFj0m9iIkq
YT1ELEC-165-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Wrong cable termination location. The cable from 1MDSB_R1_2 to 1TOU_C_2 has been terminated at the wrong breaker Q1-6 at 1MDSB_R1_2 side. The correct termination point is breaker Q1-3. Please rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628706&prj=626&rqi=kfKYQvamSvfbqppVNhi2ZJAMES
YT1ELEC-7-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628725&prj=626&rqi=mqjp8AYcXMfdU3NyAhSgn9DL8T
YT1ELEC-47-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628736&prj=626&rqi=AbFuMNLR5tm9IsgjAiRNc3gBCF
YT1MECH-41-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628557&prj=626&rqi=5J7Cta8AtEaMRaveJfAO9iOotE
YT1MECH-41-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628570&prj=626&rqi=JnPGVSttSfWYIlBB2OUjXzuBpR
YT1ELEC-49-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628550&prj=626&rqi=RPsDtU4cyPtApZFGu9XdtXC7hc
YT1MECH-41-004 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH are not yet pulled. When the cable already pulled, please do the installation properly and attach photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628560&prj=626&rqi=P3xsSVyMX0kMCF8Hc7EHLDiwFG
YT1MECH-39-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628555&prj=626&rqi=9HyTGZbfNRVWQ5tZ23P7wdYAtT
YT1MECH-39-005 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628577&prj=626&rqi=EZSYfMXG9kIdAqPJawxwCwy0yB
YT1MECH-39-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628568&prj=626&rqi=dj4GrML4iFs8xMulnHX0UjVYdb
YT1MECH-39-003 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH already pulled but need to tidy up and installed properly. Cable test also not perform yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628563&prj=626&rqi=3aEdE7oSP4DLBCi7hXa4FUMGmA
YT1MECH-36-004 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH already pulled but need to tidy up and installed properly. Cable test also not perform yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628543&prj=626&rqi=tJhUth0oxtBO00YoRBB2oYHluH
YT1MECH-36-006 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628549&prj=626&rqi=GuLNKwVXHs3uAEFRvVzGcVmtve
YT1MECH-36-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628528&prj=626&rqi=0oRt7bMJehGAV4cgNum48swqU9
YT1MECH-36-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628544&prj=626&rqi=lGwpUXBIWKkibYS300NRghQMIR
YT1ELEC-8-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628548&prj=626&rqi=gSbGnuDhsTMGHFU6fXAbzYmvyo
YT1MECH-38-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_03 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628567&prj=626&rqi=1xnAmLD4Vx8UOKFSUK3nxn5XMz
YT1MECH-38-003 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_03 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH already pulled but need to tidy up and installed properly. Cable test also not perform yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628564&prj=626&rqi=KHD7LzCWsu2ANkYdVexIp8NNyx
YT1MECH-38-005 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_03 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628579&prj=626&rqi=flLN7wkzHIdnRTa2zCabDkSN05
YT1MECH-40-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_06 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628569&prj=626&rqi=q1MKDWcszImwnskqomOHBqq70P
YT1MECH-40-003 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_06 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH already pulled but need to tidy up and installed properly. Cable test also not perform yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628562&prj=626&rqi=j7PFPtV7YjhBiGK0NeX3Qdgr0m
YT1MECH-38-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_B_03 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628554&prj=626&rqi=DgEWZscjYUTU7N1zITEPWEkakA
YT1MECH-40-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_B_06 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628556&prj=626&rqi=q8VhvI5Tge1qU9ibf9n4s9A3Y9
YT1ELEC-18-010 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | kattyrachmawati@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | White glove inspection/FOD report not yet submitted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628491&prj=626&rqi=oiqeJXzIYUhPH2zACKq0ymAgfy
YT1MECH-40-005 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_06 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628576&prj=626&rqi=0ieVvedwEnNmfKblssHEuFRWcG
YT1MECH-79-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_1 | FFU - Air Scrubber |  |  | Completed Cable Installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628533&prj=626&rqi=BINam0tEBnFAkEJnQ3IE4mnOaO
RT1ELEC-169-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Controls | equipment | 1PANEL_I/O_Motorized Damper | CP - Control Panel |  |  | equipment name / labelling onsite does not match with name on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628512&prj=626&rqi=JJAGYdtuYA1M3yJLnI43q4xYJo
YT1ELEC-50-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628551&prj=626&rqi=nMTX0yaIvvpdOd9CgXzyPGubqV
YT1MECH-79-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_1 | FFU - Air Scrubber |  |  | Label Equipment Not Straight | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628534&prj=626&rqi=qNIUuYPDwHi4W14TewTsHC4cGN
YT1ELEC-51-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628553&prj=626&rqi=JxFwrpVUjRXMkB5YxtXmT5CjKE
YT1MECH-42-004 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH are not yet pulled. When the cable already pulled, please do the installation properly and attach photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628559&prj=626&rqi=wFfWKONSeBU8X4wiZo5JRc0wsK
YT1MECH-42-006 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628574&prj=626&rqi=jUnxrKCnoyct05ianxvYtyXlTK
YT1MECH-79-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_1 | FFU - Air Scrubber |  |  | Cable Straight Not Straiht | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628531&prj=626&rqi=hdWhZI5FEHcMC4wob2w742EF6S
YT1MECH-42-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628571&prj=626&rqi=BzxstWVnEbMo0iFZC9PR7PhMMk
YT1MECH-37-005 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_02 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628580&prj=626&rqi=4uJbwNjzyu7pUlyGNVndkUVFhv
YT1MECH-37-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_02 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628566&prj=626&rqi=e525CT91mZHjyihKMvEGyHYEyD
YT1MECH-37-003 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_02 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH already pulled but need to tidy up and installed properly. Cable test also not perform yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628565&prj=626&rqi=386Y3Yu76rfBFUcKHv6iAkbzqv
YT1MECH-37-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_B_02 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628552&prj=626&rqi=rs55LUM3zTa2PiArabgYBQ8cA1
YT1MECH-42-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628558&prj=626&rqi=fO02KH5VbAoB9CHvvxhaZ7D7EZ
YT1MECH-41-006 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628575&prj=626&rqi=oIK7oSUNU1VJUuA1gKqoWk1liy
YT1MECH-76-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | Remove Silica From FFU Unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628308&prj=626&rqi=br9KTF4pCOsC6kmwY0pLQlmEUC
RT1ELEC-29-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1UPS_G_2 | UPS - Uninterrupted Power Supply |  |  | Please upload following documents: 1. RFIT documents 2. Certificate calibration of Torque Wrench | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628300&prj=626&rqi=rG0hY0urf7hJtvI7a39Gv6j2PE
YT1ELEC-30-007 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Please upload Torque Report Earthing Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628411&prj=626&rqi=OJaEd96IjBhhquo7vOUQHiTNm7
YT1MECH-78-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | Clean the dirt from the FFU unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628307&prj=626&rqi=qnJbr9KagkplxAenUB5o8yhMui
GT1ELEC-1-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L3 | Cleaning | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Top of panel found dusty. Please re-clean to minimize dust ingress into panel and busbar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628306&prj=626&rqi=Uc4nlO8Ybiuxa52hVaxT4YatXi
YT1MECH-69-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | Adjust Door FFU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628309&prj=626&rqi=6jalEs3qXEz0GRTo1pERX2Cicj
YT1ELEC-29-011 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Please upload Torque Report Earthing Cable (not include on CxL2B earthing cable report) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628402&prj=626&rqi=01t6tgzXdhJLzjnUMyBAQpEhUW
YT1MECH-65-004 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_2 | FFU - Air Scrubber |  |  | The FFU door does not close smoothly. Kindly adjust the door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628163&prj=626&rqi=OHtwWjq9oU1grIXV6cxLDlfWP6
YT1ELEC-25-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628182&prj=626&rqi=Tx4uxIZE3pEyRcd1BPiz5ccUhB
YT1ELEC-32-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628185&prj=626&rqi=UNnudb2gNx048m8mCvmqidwWHH
YT1ELEC-31-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628184&prj=626&rqi=VePYBGxvxMr7oi4phliNhWF9aL
YT1MECH-67-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_4 | FFU - Air Scrubber |  |  | The FFU door is not closing tightly. Please adjust the door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628165&prj=626&rqi=QqpUwM06JZqAzXd4XV0uVp1i6X
YT1MECH-66-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_3 | FFU - Air Scrubber |  |  | The FFU door does not close smoothly. Kindly adjust the door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628164&prj=626&rqi=wL0JjTz3s6SRfWTOnjHN14iD2f
GT1MECH-76-001 | JK01-2 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | During the Internal CxL3 Pump Performance Test witnessed by CTA, a discrepancy was observed between the flow rate reading displayed on the Flow Meter/SCP Panel and the Pump HMI. (SCP Display: 46 Hz --> 64 L/s and HMI Pump: 46 Hz --> 11.43 L/s) Further investigation is required to verify which reading accurately represents the actual flow rate and to ensure the displayed values are correct and consistent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628111&prj=626&rqi=6v6CRVru78Lrp9X0nzTubTTdV3
YT1ELEC-26-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628183&prj=626&rqi=DjDiCAg50cJweo8Ez6hoQ6F087
YT1ELEC-48-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628181&prj=626&rqi=HJDXK3O7NZ3rX1dgwFGGJdyjzY
GT1MECH-62-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | During Air TAB inspection, some of grille section on the unit was loose and cannot remain steady when the airflow CRAH blows. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628033&prj=626&rqi=iZJb7nHJ1leh60VQAXMMJeJj1E
YT1ELEC-171-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628178&prj=626&rqi=gpUR7Fc35CgpCB9xT0ZSpJaOOc
YT1ELEC-170-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628177&prj=626&rqi=mu0vyWJo2lPtHKrug9M6AcnhUM
RT1ELEC-125-010 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | The uploaded drawing of panel is an old version. Please replace it with the latest updated drawing, old version must be unlink/removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627964&prj=626&rqi=DcemCOJcfnS3Yhe6N4wCwy8vc7
YT1ELEC-165-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628173&prj=626&rqi=Qb4hOKyMkGfFLu6sW4ZNr0yoX6
GT1MECH-60-003 | JK01-2 | APAC | Closed | P2 Medium DCOS | DimasKurniawan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | Discrepancy between SICD and actual measurement (SICD = airflow , actual = waterflow) Orise needs to change the parameter and approval. This for all CRAH units | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627984&prj=626&rqi=6w6sMSVx6YKiWVd3zSVoA0nFWn
YT1ELEC-164-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628172&prj=626&rqi=OqPonStOuW5AxUDrud8h35RTw2
RT1ELEC-122-007 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | The uploaded drawing of panel is an old version. Please replace it with the latest updated drawing, old version must be unlink/removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627961&prj=626&rqi=SdYyor6ddo1Eb6yvOwRCTBKROC
YT1ELEC-166-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to attached images | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628171&prj=626&rqi=tR2JFcJ01F0nVFKJRQQ5dzpz1U
GT1ELEC-122-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Unused hole must be close | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627971&prj=626&rqi=gJ5KUb9kTSF3nVawWaMEiGIJP1
YT1ELEC-167-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628174&prj=626&rqi=U3EweV3Ou2DixKugIs0ggmMb2g
RT1ELEC-131-006 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | The uploaded drawing of panel is an old version. Please replace it with the latest updated drawing, old version must be unlink/removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627967&prj=626&rqi=UvzBIAznKvEwZjviRuKIkrpjiT
YT1ELEC-168-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628175&prj=626&rqi=CNhDx4KF6jADerrqKv10Aoxgbo
RT1ELEC-128-013 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | The uploaded drawing of panel is an old version. Please replace it with the latest updated drawing, old version must be unlink/removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627966&prj=626&rqi=F8S4akAwMGnTSaqUFTYXkXvFwc
YT1ELEC-169-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628176&prj=626&rqi=QQ1M1P2vNAoveU6V1ebGZhfrFr
GT1MECH-60-004 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | When conduct P2G CRAH, parameter "Waterflow" cannot be simulated (STULZ need to be check and clarify) This issue is for ALL CRAH UNIT | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627986&prj=626&rqi=FP2W1l8kdGTuztHVoCvvxgSAGz
GT1MECH-26-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | The DS sticker has not been installed. JCI must implement a DS-approved sticker on the chiller's DB panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627851&prj=626&rqi=pLwFbOaII0XlNG2zGNHNaUypMN
GT1ELEC-10-002 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Based on the MSB Point-to-Graphic (P2G) test results, several DCOS points for breakers QE, QN, Q1-1, Q1-3, Q1-4, Q1-5, and Q1-6 are not available. This issue is applicable to all MSB units. Please refer to the attached picture for details. The unavailable points are as follows: 1. Current N 2. Voltage AN 3. Voltage BN 4. Voltage CN | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627856&prj=626&rqi=vMXYMvNWmaldox9mPTBeHNbpiC
GT1ELEC-11-002 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Based on the MSB Point-to-Graphic (P2G) test results, several DCOS points for breakers QE, QN, Q1-1, Q1-3, Q1-4, Q1-5, and Q1-6 are not available. Please refer to the attached picture for details. The unavailable points are as follows: 1. Current N 2. Voltage AN 3. Voltage BN 4. Voltage CN | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627869&prj=626&rqi=rgd1PQbEP1Mi4JJT2ZbS39EStY
YT1ELEC-125-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Issue White Glove Inspection, please close all issues on WGI form and provide photo evidence for all issues already closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627968&prj=626&rqi=QRJYiI6pHfmbPsqimUTRC7L9p0
GT1MECH-27-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | The DS sticker has not been installed. JCI must implement a DS-approved sticker on the chiller's DB panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627852&prj=626&rqi=Z0VsfR26dJODHC22Txc2dyWHm9
GT1MECH-24-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | The DS sticker has not been installed. JCI must implement a DS-approved sticker on the chiller's DB panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627849&prj=626&rqi=vexlkA0IcUPVdfa46V0LEFXQOO
GT1MECH-25-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | The DS sticker has not been installed. JCI must implement a DS-approved sticker on the chiller's DB panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627850&prj=626&rqi=EWTJM19leh2Y8RRKiREYm5TVmc
GT1MECH-24-002 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Lesson learned from phase 1) The evaporator leaving temperature setpoint can only be adjusted when the HOA is in Hand Mode. JCI shall implement the software update in Phase 2 to enable remote setpoint control in Auto Mode, then notify CTA for verification onsite. Implement for all chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627853&prj=626&rqi=YVIJVxydzsmgCZUEge2pzGVyfx
YT1ELEC-30-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Issue White Glove Inspection, please check the attached images. Make sure issue already closed and please provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627810&prj=626&rqi=J7bd9IT7i8PYfJpThCcmbkfJ6F
YT1ELEC-29-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Issue White Glove Inspection: Please refer to attached image and provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627809&prj=626&rqi=Mz9xfHeLhVDvrQyUJjT5VGhJMg
RT1ELEC-14-028 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Factory Test Data including Calibration certificates not uploaded to FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628020&prj=626&rqi=k9lrb3AWzcKsGm5piHV231OG8d
YT1ELEC-28-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_2 | LIBATT - UPS Battery |  |  | Issue White Glove Inspection, please check the attached images. Make sure issue already closed and please provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627812&prj=626&rqi=lHLnU23jyG7dEbahDfVym8pawu
YT1ELEC-16-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Issue White Glove Inspection, please check the attached images. Make sure issue already closed and please provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627814&prj=626&rqi=pPhLOfm7QZ4sBMEaguYQPkejhW
YT1ELEC-122-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Issue White Gloves Inspection, please check the attached images. Make sure all issues already closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627761&prj=626&rqi=YmhQu85HiVfXs1utycq2LpZopQ
YT1ELEC-15-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Issue White Glove Inspection, please check the attached images. Make sure issue already closed and please provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627813&prj=626&rqi=y5mriAscpeHw9QmUlyrofD3CSj
YT1ELEC-27-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | Issue White Glove Inspection, please check the attached images. Make sure issue already closed and please provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627811&prj=626&rqi=nA1oL97l8x3dyNETuR0FFKwnSj
RT1ELEC-15-028 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Factory Test Data including Calibration certificates not uploaded to FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628021&prj=626&rqi=1oFg0miTMIgy4vfdegw7FTm7Da
GT1MECH-22-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | issue from CxL2B. Cable communication not connected yet to existing unit (VRFOD A_21) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627778&prj=626&rqi=aQBsGTM1SYMKgthg8emX4Y5Bu1
YT1MECH-26-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | Cable communication not connected yet to existing unit (VRFOD A_21) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627776&prj=626&rqi=daE3ZnLvviJhUPu6bxNfOrOl6E
YT1MECH-27-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | Cable communication not connected yet to existing unit (VRFOD G_61) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627774&prj=626&rqi=c6fWV69xcna8lS40F4JUmHCgXH
YT1ELEC-22-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Issue White Gloves Inspection, please check the attached images. Make sure all issues already closed and please submit photo evidence after closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627770&prj=626&rqi=wbAZNdRfobYl4Y3hWOp1OOp3ks
GT1MECH-23-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | issue from CxL2B. Cable communication not connected yet to existing unit (VRFOD G_61) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627775&prj=626&rqi=0uIlwBTDCLHMoxVCjfn1werrBB
YT1ELEC-21-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Issue White Gloves Inspection, please check the attached images. Make sure all issues already closed and please submit photo evidence after closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627760&prj=626&rqi=TVvpFjXQY0HRBUEy9XnTTq6CmV
YT1MECH-20-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_B_22 | DXID - FCU/DX Indoor Unit |  |  | Cable communication not yet connected to existing unit (VRFOD A_21) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627771&prj=626&rqi=80mavvBQJcfCOMWr8qv6tFLDm2
GT1MECH-16-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_B_22 | DXID - FCU/DX Indoor Unit |  |  | issue from CxL2B. cable communication not yet connected to existing unit (VRFOD A_21) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627773&prj=626&rqi=9oJacErnExdaj9YDu5VSRH2Udk
RT1ELEC-13-028 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Factory Test Data including Calibration certificates not uploaded to FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628018&prj=626&rqi=ieJYFZEuTSTR1G01w9CPnSzsUh
GT1ELEC-1-005 | JK01-2 | APAC | Closed | P2 Medium DCOS | dickyhermawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Re-assigned to Orise) Need to update latest SICD approved. Based on the RMU Point-to-Graphic (P2G) results, several mandatory DCOS points from the Outgoing RMU MVBCM are not available: See attached picture 1. IED Test Mode 2. Voltage AB 3. Voltage BC 4. Voltage CA 5. Power Factor 6. MW 7. MVA 8. MVAR 9. Frequency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627772&prj=626&rqi=xaF8Hg2GJmenU2qivtepiyPejp
YT1ELEC-119-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Issue White Gloves Inspection, please check the attached images. Make sure all issues already closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627763&prj=626&rqi=LMOnMpZvTFuNRkvu3fd0iT8Blm
RT1ELEC-12-011 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | Factory Test Data including Calibration certificates not yet uploaded to FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628017&prj=626&rqi=j05yV25La9WbklxwCqVcRNa3Ka
YT1ELEC-13-014 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of all panel is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627514&prj=626&rqi=a27eiczR5idlAuyOiGMsKOtq1m
YT1MECH-24-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_B_41 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627506&prj=626&rqi=C1SbrUrE0tp0iVomzMdCc09gto
YT1MECH-23-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_42 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top all of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627507&prj=626&rqi=fpId8KzblUhWIHcAI1hXv3ZLiN
YT1ELEC-20-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Please close issue White Glove Inspection (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627541&prj=626&rqi=aarc2btXugKr3hvPuqe6GqLUOr
RT1ELEC-36-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Temp. sensor not installed at cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627532&prj=626&rqi=mZ9rgi7z1704Ku2U4lYsg5E6IT
YT1MECH-2-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of Daily Tack is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627522&prj=626&rqi=fceFxMNoXBUPqcMIm9J5txgjXr
YT1MECH-25-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627505&prj=626&rqi=LLOyY7dsaZLQXR4d8oELevWgba
YT1MECH-27-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627496&prj=626&rqi=yiIbCdmqXjJMeWmJBjwK0WxEjr
YT1MECH-4-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of Daily Tack is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627521&prj=626&rqi=NqQeOl2G1H6BIJwrbEenV57wCs
YT1MECH-26-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top all of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627508&prj=626&rqi=2PyQoqgibDYg4SXpCq9zwzjdXo
YT1MECH-5-001 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of Daily Tack is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627518&prj=626&rqi=Tz23QAPBhSjMR0j2hBO14RfgSD
GT1ELEC-10-001 | JK01-2 | APAC | Closed | P2 Medium CX | JoshuaPrasatyaGani@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Incoming and outgoing single-core cables to Panels MSB_B and MDSB_B are not installed in trefoil arrangement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627551&prj=626&rqi=F1AiPZUtJqZBF6VR9CEOQ0dUjW
YT1ELEC-17-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Please close the issue white glove (refer to attached photo): 1. Busbar still dusty 2. Need re-torque & double mark to all bolts 3. Missing bolt (9 pcs) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627537&prj=626&rqi=tWryPwV5zLW4z8jXWP1dTrTTGk
YT1ELEC-18-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Please close issue white glove inspection (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627540&prj=626&rqi=kFjc2IqP6ebLXWXDufCBtaSLUn
RT1ELEC-33-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | Temp. sensor not installed at cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627533&prj=626&rqi=XLAt8yTAtG2k7Rj7SBIdpCI3f7
YT1MECH-19-003 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of Out Door is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627498&prj=626&rqi=V770065VZmFYAPm1BdCzQcM3GC
YT1MECH-22-002 | JK01-2 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top all of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627553&prj=626&rqi=WQEmFRXba7ifwvIeqf8pQBFCQ3
GT1MECH-60-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | (Issue move to CxL3) External pipe arrow/ direction not installed yet. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627273&prj=626&rqi=92ZdQWErKeqiF4q0UEKvpplpLt
GT1MECH-60-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627412&prj=626&rqi=ebITKJKvWlpCbHKwGzQLsDcgkH
GT1MECH-64-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_41 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627424&prj=626&rqi=K3fSTGU9Ois3ejQ83jWMvfvLPs
GT1MECH-61-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627414&prj=626&rqi=vOAtUgKKP0ERUzEavcgkxFBHaW
GT1MECH-59-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627410&prj=626&rqi=w8Z5AgZ3fownGw4qvtj5oUBGhU
GT1MECH-68-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627430&prj=626&rqi=A0HMe4YTkaLkvuZPes0jilyWCr
GT1MECH-67-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627428&prj=626&rqi=wlNlk3KcLntOQorEJdEqxqhXA2
GT1MECH-58-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627406&prj=626&rqi=4Dpo9QUXAo2DlFD0sEUdFJQgUY
GT1MECH-57-002 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_21 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627274&prj=626&rqi=UaqU4Rt2THigEtbeCfLvDGJqj1
GT1MECH-62-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627417&prj=626&rqi=fen1v2K65nPbnQkk0D9hbNgDuS
GT1MECH-69-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_62 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627431&prj=626&rqi=FAjxaLcRZNrB5J64x2db6sU9fv
GT1MECH-56-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627405&prj=626&rqi=WDxZPiXUVuLL7W5pE7wXIGhjg2
GT1MECH-71-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627434&prj=626&rqi=I4SI26bjhoE6l3WUHalziQakCP
RT1ELEC-30-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_A_2 | LIBATT - UPS Battery |  |  | Please upload following documents: 1. RFIT Report 2. Approved Layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627326&prj=626&rqi=xoFjiWw8tr8KVc7jltDKhJUaUz
GT1MECH-70-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627432&prj=626&rqi=1RtpMH4MnAlzgCqxvHyXw7x0A5
GT1MECH-65-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_41 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627425&prj=626&rqi=7ToXvCBiCpm27hdyNSsb1ESJeZ
GT1MECH-66-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627427&prj=626&rqi=FBQxld2pav4OnqaIGITXqbgs38
GT1MECH-63-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627418&prj=626&rqi=qYJTlHnu8eMj3WhhqGZeK3KbUw
GT1MECH-57-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_21 | CRAH - Computer room air handler |  |  | (Issue move to CxL3) External pipe arrow/ direction not installed yet. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627216&prj=626&rqi=cjSadJ8VJozBThdDzetS7sPTPp
YT1ELEC-125-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Please note that the CxL2B LV Cable Report for 1MDSB_F_2 to 1DB_F_CRITICAL (photo on DB panel side) is still based on a temporary cable installation. Please update the report once the permanent cable has been installed and re-upload the revised report to this checklist. Kindly remove/unlink the previous report that contains the temporary cable installation evidence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627854&prj=626&rqi=9VAtx644BQuXaJY8YqYsvk9uzM
YT1ELEC-22-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Grounding busbar is not sufficient for all grounding cable terminations. Please extend the busbar to avoid cable stacking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627331&prj=626&rqi=uf52ZfcNI6UUiZLrms4GAK8jB4
YT1ELEC-22-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627332&prj=626&rqi=HGk7dOnCQvXKG4lk72pqboQYwu
YT1ELEC-22-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627333&prj=626&rqi=OCyjP28i6PJIG1xoX2xL2Ecn5O
YT1ELEC-119-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Please note that the CxL2B LV Cable Report for 1MDSB_D_2 to 1DB_D_CRITICAL (photo on DB panel side) is still based on a temporary cable installation. Please update the report once the permanent cable has been installed and re-upload the revised report to this checklist. Kindly remove/unlink the previous report that contains the temporary cable installation evidence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627855&prj=626&rqi=9IbGl7JvXaVxY4Yiko6f6FuEnB
GI-024 | JK01-2 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | Lev 2. MV Riser 2. Grounding tray size does not accommodate all the grounding cables in the riser, so the cables pile up and cannot be tied up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627022&prj=626&rqi=fW3RWgyXxSIl8Pa8mblJKGLomh
YT1ELEC-15-001 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | DCOS cable has not been terminated at the UPS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627101&prj=626&rqi=EWOgS1uDM9bocdqjhacB3H1ORZ
YT1ELEC-16-007 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | DCOS cable has not been terminated at the UPS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627106&prj=626&rqi=ZbS3ftPmi9J3aEqkzDw1cQ7R17
YT1ELEC-20-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627112&prj=626&rqi=IlMDrEQVIk8fFTh0XBChbQnX7d
YT1ELEC-16-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Minimum 3 threads shall be visible beyond the nut | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627103&prj=626&rqi=l0iVdXuFcQyk3BXnGeTWNaTgsq
GI-027 | JK01-2 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | Lev 2. MV Riser 2. Grounding tray size does not accommodate all the grounding cables in the riser, so the cables pile up and cannot be tied up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627027&prj=626&rqi=yI5iTbzUVMFgOIJMaeTc4sAKSK
YT1ELEC-10-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Earthing Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627049&prj=626&rqi=bkPQfPguP2j6QbqueSncd0xGLv
RT1ELEC-153-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue EWALL Room D) Need to install cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627142&prj=626&rqi=pScMN99h8l99crU4au707s9XDi
RT1ELEC-153-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue STS Room D) Need to add flat & belleville/spring washer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627146&prj=626&rqi=OxEP8xPXJ3RC64fNzoAFzt0AUk
RT1ELEC-153-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue EWALL Room D) Minimum 3 threads shall be visible beyond the nut and need to install spring washer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627141&prj=626&rqi=ciUAzcEjgQAfeBZrd76Rv0CGxK
GI-026 | JK01-2 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | Lev 2. MV Riser 2. Grounding tray size does not accommodate all the grounding cables in the riser, so the cables pile up and cannot be tied up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627026&prj=626&rqi=3oADwKMdnbsPbR1ojXUxR64l0V
RT1ELEC-153-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue Battery Room C) Minimum 3 threads shall be visible beyond the nut and need to install spring washer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627143&prj=626&rqi=YqAtkdd3A27Ph96mGYGQE9SnHI
YT1ELEC-19-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627113&prj=626&rqi=NMTbC0FJGyTxXn6jxKQr2AmQhT
YT1ELEC-16-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627105&prj=626&rqi=KBOVtJElr5nrBLC6pfgQUKmHNo
RT1ELEC-152-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue STS Room B) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627144&prj=626&rqi=h22Y5QA0yv6JzaR0ju1LS4PryZ
RT1ELEC-152-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue Battery Room B) Vinyl cable loose & cable tagging not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627145&prj=626&rqi=0UMdldlHKfHTAo0xnNoXOhHaDc
GI-029 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | The existing water leak cable is trapped between the Li-Batt racks. Based on site walk with Aurecon, the cable must be pulled and re-laid to cover the new Li-Batt racks | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627030&prj=626&rqi=P1XqVIaPfp6YP0mSbenqyajvds
RT1ELEC-153-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue STS Room D) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627147&prj=626&rqi=DA1kXt3BCaWBL94GWwk2rD8W9F
YT1ELEC-16-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Control/Auxiliary cables are not connected and need proper cable dressing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627107&prj=626&rqi=7MzCUwZhStqTtSNOQrWlwLvBKn
YT1ELEC-15-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627102&prj=626&rqi=auASZuSuLFrJV4QPsDeh5sIO5H
YT1ELEC-47-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Earthing Cable) Cable Tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627050&prj=626&rqi=lztRq3CgIjxs7vmasebvqyUiPF
YT1ELEC-18-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Grounding busbar is not sufficient for all grounding cable terminations. Please extend the busbar to avoid cable stacking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627109&prj=626&rqi=1mDRMoE3jlrJjjVpmlYuruWgMA
YT1ELEC-20-002 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | DCOS cable has not been terminated at the UPS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627111&prj=626&rqi=O9gBPGjXQYSCjxqGEPMxygeSru
YT1ELEC-18-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627114&prj=626&rqi=xOjI9ij4decVBIbINvrc8vWqgY
YT1ELEC-20-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Grounding busbar is not sufficient for all grounding cable terminations. Please extend the busbar to avoid cable stacking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627110&prj=626&rqi=YZlaOTYVyeo1dYfp7Ak6aZRSAu
YT1ELEC-13-013 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Busduct) Busduct LBSB 3200A 1MSB_F_1 & 1UDP_F_1 clash with sprinkler pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627128&prj=626&rqi=oMKs9uSHL9GBUMBtC5RpsV2vog
GI-028 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_A_2 | LIBATT - UPS Battery |  |  | The existing water leak cable is trapped between the Li-Batt racks. Based on site walk with Aurecon, the cable must be pulled and re-laid to cover the new Li-Batt racks | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627028&prj=626&rqi=FWzqmIxtGAQ3CPEBIqy0bfzjUi
GI-025 | JK01-2 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_5 | ERTH - Earthing |  |  | Lev 2. MV Riser 2. Grounding tray size does not accommodate all the grounding cables in the riser, so the cables pile up and cannot be tied up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627025&prj=626&rqi=LlQVTbgYMTGuEJew14NirRa96b
YT1ELEC-18-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Control cable needs proper dressing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627108&prj=626&rqi=BXp9Mq9X3JKqwPe6SoovW51qgF
YT1ELEC-16-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Grounding busbar is not sufficient for all grounding cable terminations. Please extend the busbar to avoid cable stacking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627104&prj=626&rqi=3YUjgAQvw59JUJERtwvqQ5s8nQ
YT1MECH-14-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1EF_D_53 | EF - Exhaust Fan |  |  | (Issue CxL2A LV Cable) Cable over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626843&prj=626&rqi=tym2pI6yJH5f0XFp98dxMl1xgK
YT1ELEC-117-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Incorrect label outgoing (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626842&prj=626&rqi=vyJMe9K9RzDWJOUHo7VRI4KV98
RT1ELEC-52-005 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | Need to upload calibration certificate for torque wrench | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626858&prj=626&rqi=aB0R0XkstPUKopEITb0IkbAdgF
YT1ELEC-21-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Control cable UPS to LIBATTSYS not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627046&prj=626&rqi=HBlnTORVHF2ucAAD55OxoWwOPF
RT1ELEC-52-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | Minor dents & scratch, need to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626854&prj=626&rqi=aY9OPelck6MRqegfNRXNSsPFjs
YT1ELEC-125-003 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Incorrect cable termination for grounding (refer to attach photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626881&prj=626&rqi=S6DR9Qqvz7rbcKm8pPfjuZvJ7E
YT1ELEC-21-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Please tidy up the control cable conduit installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627043&prj=626&rqi=CZ3IiO2IAME4hqjXLnHO4wbP0U
YT1MECH-106-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | Pipe not connected yet, and also for Cable not yet for Tamper Switch, Solenoid and Flow Switch. Trim set also not done yet. Attach photo once already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626879&prj=626&rqi=Bn59IsVB90jZzaPZtak24TOLMz
YT1ELEC-21-002 | JK01-2 | APAC | Closed | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Please tidy up the DCOS cable installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627045&prj=626&rqi=90yFFHcdjtFmfJ79w8JXBtbdp1
RT1ELEC-56-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | Anchor bolt loose cannot be tightened and not properly for anchor (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626859&prj=626&rqi=DEiJxewiRrlFAQUrUZaVjg79he
RT1ELEC-20-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_A_2 | UPS - Uninterrupted Power Supply |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626853&prj=626&rqi=pGXtr97yfH6mUQFxFaasGquoLq
GT1ELEC-11-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626688&prj=626&rqi=IxjSzGx72i636A34heZ3UMQMSm
YT1MECH-18-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | cable tagging not installed yet for cable communication for outdoor to indoor unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626462&prj=626&rqi=FPXl2r9d8fNQsNPpzZlVIKnvHC
RT1ELEC-21-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Door foam damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626453&prj=626&rqi=oxksSkLEqxdDGSasvnTMj3t1lU
GI-023 | JK01-2 | APAC | Closed | P3 Low CX | ariagandanegara@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | Please rectify and repaint the peeled off pipe coating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626450&prj=626&rqi=hKngQrUJ7CTPZIcSWbrQoVjlxR
RT1ELEC-26-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Missing bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626466&prj=626&rqi=5SIvhEdUfdKfiYiTfKDfmBi5Fg
RT1ELEC-21-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Minimum 3 exposed threads required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626452&prj=626&rqi=PUri6TJUuQc4jwQ1b0Ukn3WGKA
RT1ELEC-22-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Minor scratch & dents, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626458&prj=626&rqi=iZgdi90YUNtozxtMuDaPlWY2y8
RT1ELEC-24-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Door foam damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626461&prj=626&rqi=cXw5kbYxxs6rhDQvmCxuRqWkvV
RT1ELEC-26-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Discrepancy between drawing & actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626463&prj=626&rqi=6mWfPkpBYUEXKCNyckaTYfA1bt
RT1ELEC-22-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Need to torque verification & mark for rear anchor bolt | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626457&prj=626&rqi=9BP70TNvP26lfZRbBqRurxjxYx
RT1ELEC-26-009 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Need torque verification & mark for rear anchor bolt | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626464&prj=626&rqi=w3fwrqOynD8snZbQ4isS3OP1kx
RT1ELEC-26-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Please protect HMI display to prevent from construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626467&prj=626&rqi=iN77E25SvYtX3zQGDxZnSqp63h
RT1ELEC-24-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Please protect HMI display to prevent from construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626460&prj=626&rqi=g0LJTvEbSJAtjYkxZ4dbCUsiTS
RT1ELEC-24-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Minor dents, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626459&prj=626&rqi=Ln5RvQH6eO9rL00Avv5uaOXvy1
RT1ELEC-22-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Discrepancy between drawing & actual position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626455&prj=626&rqi=IhCI7OdPJvmQ4lwLj1cRR59MYb
RT1ELEC-26-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Door foam damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626465&prj=626&rqi=VbWSkbBlp1rUgs9OV0ItgFfTty
RT1ELEC-21-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Minor dents, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626451&prj=626&rqi=LrQ5qrThdJOdWcmIZUGuGzmDrr
YT1MECH-43-002 | JK01-2 | APAC | Closed | P1 High CX | DimasKurniawan@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor | L2B | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | During Tie-in activity for CHW Pipe Cooling Array Level 4th floor, leak was discovered at CHWF mainline pipe. Please provide RCA for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626357&prj=626&rqi=RkaUlYvX9VEPv6ddX5uNVt9gAr
YT1DCOS-14-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Controls | equipment | 1DCOS_1_SCP_04 | DCOS - Control Panels |  |  | (Issue CxL2A LV Cable) Cable over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626248&prj=626&rqi=pNagoj7hygiuiW6gdrLNDImb4U
YT1ELEC-16-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable) Incorrect cable tagging, should be from 1UPS_B_2 to 1LIBATTSYS_B_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626242&prj=626&rqi=ekWCg7gBNPadovi8AW6b5xVZKD
YT1DCOS-12-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Controls | equipment | 1DCOS_1_SCP_02 | DCOS - Control Panels |  |  | (Issue CxL2A LV Cable) Cable over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626246&prj=626&rqi=Rd4cNoWi36zvsWGOisbcWRAXNQ
YT1ELEC-19-005 | JK01-2 | APAC | Closed | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | DCOS cable installation is not neatly arranged. Please tidy up and secure all DCOS cabling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626245&prj=626&rqi=cYSX7DBRdB2xK1MuNH0d7Rm8SS
YT1ELEC-116-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | Incorrect breaker label, please follow new breaker outgoing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626244&prj=626&rqi=yBfTYRtXJNN9fdWQqw72zZ4HZO
YT1DCOS-9-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626241&prj=626&rqi=gQK41ZhR2qpYjquLwzWPQszAGa
YT1ELEC-26-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | (Issue CxL2A LV Cable) Incorrect cable tagging, should be from 1UPS_B_2 to 1LIBATTSYS_B_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626243&prj=626&rqi=G8bN2nI0Z9LN25245s1kWDyqhq
YT1DCOS-15-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Controls | equipment | 1DCOS_1_SCP_07 | DCOS - Control Panels |  |  | (Issue CxL2A LV Cable) Cable over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626249&prj=626&rqi=6mTRnZnq9KLiYnxHvcsgPWRAaV
GT1ELEC-2-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Several point lists included in the approved Point List could not be verified in DCOS during RMU CxL3 P2G testing. LS Electric confirmation and Statement Letter are required. Potential impact to all similar RMU units. Need to update SICD approved and signed by Orise, LS, and GC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625636&prj=626&rqi=7YWeI5kzLdS2DHzq40p0yp5XYY
RT1SEC-15-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Security | equipment | 1CCTV_level_7_DH | CCTV - Closed Circuit Television |  |  | issue CCTV C:07-43 not installed yet because cable tray is not installed yet by GC, the CCTV shall be installed under tray | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625797&prj=626&rqi=IWJhnsGpfE3bo6648sg0ERhXfS
YT1ELEC-17-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Auxiliary and DCOS cables are not properly connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625634&prj=626&rqi=f9ztG5iMd68wvOtxmTyYOOU393
YT1ELEC-117-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Incorrect label outgoing breaker, should be: - Q1-3: to 1EF_B_31/32 - Q1-4: to 1EF_B_21 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625790&prj=626&rqi=O8JWa4jwMkiT0MVyVw8jOED7rg
YT1ELEC-17-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Control cable UPS to LIBATTSYS not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627048&prj=626&rqi=JalVPLXjoJevJHQoOzy5FIsuy3
RT1FD-6-002 | JK01-2 | APAC | Closed | P2 Medium CX | ariagandanegara@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Fire Detection | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | The Pipe is not Installed yet. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625782&prj=626&rqi=V49agzNxzFY9XzvQoYTVtrvqG4
YT1ELEC-17-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | General Contractor | L2B | Torque required | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Bolt torque under 3 threads under the nuts & please perform re-torque verification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625635&prj=626&rqi=hlPE8Ptw8m6vqrCdLTq0IipDeH
RT1FD-6-001 | JK01-2 | APAC | Closed | P2 Medium CX | ariagandanegara@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Fire Detection | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | 1. Solenoid Cable is not Installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625779&prj=626&rqi=AS0MqSSqoyqre3SZdX6QCPYeSl
YT1MECH-35-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Labelling / equipment name tag not yet (Issue from L2A) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625581&prj=626&rqi=GP5ZUUcs3782wjbDM9U0D0dDWa
YT1ELEC-168-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | (Issue CxL2A LV Cable) Ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625306&prj=626&rqi=LTYPwOm1Q6r2DOIauHlPBiQ8pb
YT1ELEC-171-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625305&prj=626&rqi=xTuQ5XlIfK8uQPAXtixCC7odWZ
YT1MECH-72-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_4 | FFU - Air Scrubber |  |  | (Issue CXL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625331&prj=626&rqi=VNDWBjvZbRC1ODN2tc9MMOcseL
YT1ELEC-53-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Cable) Cable insulation damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625317&prj=626&rqi=STQGCpXIz53AtgeuSLSFDVsIf8
YT1MECH-71-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_3 | FFU - Air Scrubber |  |  | (Issue CXL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625330&prj=626&rqi=Y5zQr7lgQleflJwlxe2xxf6SLS
YT1MECH-74-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_1 | FFU - Air Scrubber |  |  | (Issue CXL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625328&prj=626&rqi=I4SWZqW4bAMzy9GfYKjXe3OAN1
YT1MECH-70-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_2 | FFU - Air Scrubber |  |  | (Issue CXL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625329&prj=626&rqi=YojO28MNLqqBCoKJ66fwyuzkjn
YT1MECH-73-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_5 | FFU - Air Scrubber |  |  | (Issue CXL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625332&prj=626&rqi=4mAWmgJGptFPCf6iAT5OneFiV0
YT1ELEC-52-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable) Ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625316&prj=626&rqi=6kxP7FkPULoIZB7Vc1NYgY2YOX
YT1ELEC-52-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable) Remove temporary marker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625315&prj=626&rqi=gY1675jhxyWnnzGUJ4XeC5ua2w
YT1ELEC-168-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625304&prj=626&rqi=MudVW8wJI2VBTO2TJeRe5Rg8w7
YT1ELEC-117-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625203&prj=626&rqi=CF14SjJ2lgAqLicIdmOoBcW8wc
YT1MECH-47-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_D_07 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625226&prj=626&rqi=GNw60GqPRYlmZOoszAefrosBrz
YT1MECH-98-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Bonding jumper on tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625218&prj=626&rqi=tKRnrbNHVMsrOrmuoo6qBY2YIS
YT1ELEC-117-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Ensure the gland is properly covered and sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625204&prj=626&rqi=Ruoax1OSIOwsIx2KsCtlVNjLQ8
YT1MECH-44-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_D_03 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625223&prj=626&rqi=YmaMpIIjUoITdgPXIvOIDbgk8i
YT1MECH-46-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_D_06 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625225&prj=626&rqi=jhA0HZ8XMWaY3JJSk4f3KFA4Cm
YT1MECH-95-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cable tray not finished yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625211&prj=626&rqi=PnUdrukkgpEJRldBuES6pLzEJI
YT1ELEC-119-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1DB_D_CRITICAL to 1CRAH_D_42) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625212&prj=626&rqi=2qQVlArfSxNIyQLR1fLQDmP8vS
YT1MECH-89-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625221&prj=626&rqi=5LKEQmvfxMu81QBesAqL5LCiS1
YT1MECH-43-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625222&prj=626&rqi=nSyqRoKHQAPTSB7onTFHQtdpYa
YT1MECH-6-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | (Issue CxL2A LV Cable 1DB_B_EWALL to LCP_EF_B_21) Cable & conduit needs to install labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625200&prj=626&rqi=GLIto2uT9IzfzZkfWLmxWAPWm1
YT1MECH-36-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625230&prj=626&rqi=lrnv8TdklP70kGfOS1wDspr20F
YT1MECH-42-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625237&prj=626&rqi=GSLb7JMFJBIDeNau9hMCfv5W6j
YT1MECH-48-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_D_09 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625228&prj=626&rqi=tSb5AolmhNSg5E4IMqKOtYlP5U
YT1MECH-96-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cable installation is not neat and several cables are over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625220&prj=626&rqi=cdhy6scp5jXwcj1dAgvX9Q4yO7
YT1MECH-6-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | (Issue CxL2A LV Cable 1DB_B_EWALL to LCP_EF_B_21) Cable over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625199&prj=626&rqi=beRiSLiT4Blz6jqv5BCYFftmr1
YT1MECH-91-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625217&prj=626&rqi=CbRfFbTkcFeuMcSHUYxUTxv4YS
YT1MECH-96-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | (Issue Cxl2A LV Cable) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625210&prj=626&rqi=fe6lybEDLp6ttT9WVzCx2YRUh2
YT1MECH-49-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_D_11 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625229&prj=626&rqi=y6SgZcVnGpNLDiJxtYGfisRQ5x
YT1ELEC-119-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1DB_D_CRITICAL to 1CRAH_D_42) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625213&prj=626&rqi=f7BJt90cPT873MRCHswNMjfTWP
YT1ELEC-16-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_B_1 to 1UPS_B_2) Several cable gland caps are damaged (torn) and not properly covering the gland, please ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625208&prj=626&rqi=Mu64nWHPfZSlOzCo9k6daxLcIx
YT1ELEC-16-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_B_1 to 1UPS_B_2) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625207&prj=626&rqi=dewZwrQsJScSiVCiIS7P9VsSa6
YT1MECH-45-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_D_05 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625224&prj=626&rqi=1XsHiHYmskTMhvkln6hODEuv38
YT1ELEC-117-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1DB_B_EWALL to LCP_EF_B_21) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625202&prj=626&rqi=z9j2ZWcZ6s2cGpyRuPlUxc2IZY
YT1MECH-41-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625235&prj=626&rqi=IaQcgKDn2UwHQkEA791srl39MH
YT1MECH-97-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_62 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cable installation is not neat and several cables are over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625219&prj=626&rqi=RQ9GZOJvs5RVN3y3Np4bqyJTxh
YT1ELEC-125-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625216&prj=626&rqi=FT9kjG3KT4YBid6AmPyNYcdtIF
YT1MECH-40-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_B_06 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625234&prj=626&rqi=MF3h15zYHkJfrEowXJ8LUmgYXS
YT1MECH-39-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625233&prj=626&rqi=M6aBIVA3f2HvPzsPhmj5Lp7Zwa
YT1MECH-38-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_B_03 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625232&prj=626&rqi=xkXctS3upwXNS2BxwN1fEuOvU8
YT1MECH-37-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_B_02 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625231&prj=626&rqi=cxcUwfn9JxyloVezhLRm3qcdYO
YT1MECH-99-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cable installation is not neat and several cables are over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625215&prj=626&rqi=x4wHA3C1R0dxM6W8juH1U6az5X
YT1ELEC-125-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Discrepancy identified between the breaker protection settings applied in the panel and the latest approved Discrimination Study. Short Time Delay (STD) and Ground Fault Protection settings do not match the approved study (Refer to the attached images) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624913&prj=626&rqi=u1tM3bTrOPm1hB3sJ56hAvHNKv
GT1SEC-12-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning | Security | equipment | 1ACS_level_6 | ACU _ Access Control |  |  | Door handle not yet installed (D:06-09 E-wall room & D:06-38 Battery room) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625059&prj=626&rqi=JszLDauZmMX95UMKkXmwZLcGvZ
YT1ELEC-126-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Discrepancy identified between the breaker protection settings applied in the panel and the latest approved Discrimination Study. Short Time Delay (STD) and Ground Fault Protection settings do not match the approved study (Refer to the attached images) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624922&prj=626&rqi=vre6H9OUEabkfwK2nXhNzI96xw
YT1ELEC-6-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | Incorrect vinyl cable color at Panel DB Aux. Vinyl cable color for L1=Black, L2=Brown, L3=Grey, Neutral=Blue, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624878&prj=626&rqi=UOYrI05cQEberE6Yug9Bb0IZrk
YT1ELEC-7-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Incorrect vinyl cable color at Panel DB Aux. Vinyl cable color for L1=Black, L2=Brown, L3=Grey, Neutral=Blue, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624879&prj=626&rqi=vcncgLpK9tLgoV1EgnHxHBR61V
YT1ELEC-8-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Incorrect vinyl cable color at Panel DB Aux. Vinyl cable color for L1=Black, L2=Brown, L3=Grey, Neutral=Blue, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624881&prj=626&rqi=P7SFEEfDJ5T2sr8hCBzLz61EAU
YT1ELEC-170-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | (Issue CxL2A LV Cable 1MDSB_D_2 to 1TOU_D_1) Missing bonding jumper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624873&prj=626&rqi=JgNtwDdgtm94428gtgJHz1iaFc
YT1ELEC-9-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Incorrect vinyl cable color at Panel DB Aux. Vinyl cable color for L1=Black, L2=Brown, L3=Grey, Neutral=Blue, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624876&prj=626&rqi=fgVy46NxJYThMlZRz08y3xpCj3
GT1MECH-80-001 | JK01-2 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_3.01 (Existing) | PAV - Pre-Action Valve |  |  | Seismic Bracing not yet installed and will be planned to install asap by GC. (This issue for all floor) Ensure that when installing those, there will be not affect piping and support pipe. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624812&prj=626&rqi=L6OXeEcTtTvNomltif6LOufYsR
RT1ELEC-155-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | (Issue EWALL Room F) Incorrect cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624888&prj=626&rqi=B7J5jM5Fhd3BHA06KRskeXee63
YT1ELEC-50-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Cable Aux) Cable conduit label not installed. Please provide the label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624862&prj=626&rqi=IPRxF0QN9LN8xGP7eYYI95fHrS
RT1ELEC-155-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | (Issue EWALL Room F) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624887&prj=626&rqi=3OwD44TLtbrPEtDQL82PFC5pvv
YT1ELEC-50-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Cable Aux) Cables are not neatly arranged. Please tidy up and secure all cables properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624861&prj=626&rqi=ht4P8djwCu3TERmVDmkx9ghEnU
RT1ELEC-153-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue EWALL Room C) Cable tag naming does not comply with the project standard. Please correct accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624884&prj=626&rqi=orYB1Fp3ZtbvOMdUew83zmXzr3
RT1ELEC-153-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue EWALL Room C) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624883&prj=626&rqi=I74m88zziPhGlZzfwtqbeSwY5i
RT1ELEC-153-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue EWALL Room C) Cable Tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624886&prj=626&rqi=Kgjlgf4rRS624kcD8WinKxI36Q
YT1MECH-18-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | (Issue CxL2A LV Cable) Missing bonding jumper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624866&prj=626&rqi=B004WsmUiSGPFmuJEMQewUay92
YT1ELEC-52-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Cable Aux) Need to install label at conduit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624860&prj=626&rqi=UryxGLlAJMsOvQTR0Ly1cf3cmL
YT1ELEC-9-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MDSB_D_1 to Panel DB Aux) Incorrect vinyl cable color. Vinyl cable color for L1=Black, L2=Brown, L3=Grey, Neutral=Blue, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624875&prj=626&rqi=H5DLWhje6Obb3CPxVPyoHjltA4
YT1ELEC-52-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Cable Aux) Cables are not neatly arranged. Please tidy up and secure all cables properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624859&prj=626&rqi=mWivCsvZbzv7IVAih1zcyBjQiv
YT1MECH-66-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_3 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_3] tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624509&prj=626&rqi=qgX3bBPvfX94DGQLRJHgAht6I5
YT1MECH-68-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_5 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_5] Tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624513&prj=626&rqi=8Kf3OuIQw0IScpPvUb8A0tuJXZ
YT1MECH-88-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable DB_C_Critical to ISO 1CRAH_C_41) Cable tagging and cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624488&prj=626&rqi=PTlK1nl8sxEsxTmiZOktcwfSML
YT1MECH-66-001 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_3 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_3] Cable over bending, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624508&prj=626&rqi=cuUqMTCfdY9ylcrukEsDRzVMa9
YT1MECH-65-001 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_2 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_2] Cable over bending, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624505&prj=626&rqi=eDUWAeEFWKCVF8tgl4Nd5RqKd8
YT1MECH-19-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | (Issue CxL2A LV Cable 1MDSB_F_1 to DB 1VRFOD_F_61) Bonding jumper not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624708&prj=626&rqi=0cllchX2In2HiCsFZq8KqvYfu4
YT1MECH-30-005 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A Laying cable 1DB_CHWSTR_B_07_CH1 to 1CHWSTR_B_07_CH1) Vinyl cable identification for Phase R and Phase T has been installed incorrectly. Please revise according to the cable tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624558&prj=626&rqi=bqDZFhuxbOeXhTdQZVn6vCpBEQ
YT1ELEC-126-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1MDSB_F_1 to 1DB_F_EWALL) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624703&prj=626&rqi=FfzegOVAy9iPsq7teBq5oculwY
YT1MECH-87-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable ISO 1CRAH_C_22 to 1CRAH_C_22 ) tagging cable phase R not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624495&prj=626&rqi=nMmQIk38OXezw9NnG1vAxBi6uw
YT1MECH-84-001 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable DB_B_Critical to ISO 1CRAH_B_21) Cable scratch until insulation is visible all phase (R,S,T,N,G) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624485&prj=626&rqi=myFiW1UimREmZszMffk5QQSLSc
YT1MECH-87-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable ISO 1CRAH_C_22 to 1CRAH_C_22) Vinyl Cable was installed in reversed, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624494&prj=626&rqi=9jSZ9YkwqEu37FnGjb4bLUB3O7
YT1MECH-31-005 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A Laying cable 1DB_CHWSTR_B_07_CH1 to 1CHWSTR_B_07_CH1) Vinyl need tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624556&prj=626&rqi=wnLcmDgKvxaT45byVBQlYs9PFh
YT1ELEC-166-004 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | [Issue CxL2A 1TOU_B1] Protection neutral not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624500&prj=626&rqi=8kGRvKhmkjhPoWax14AhmhGH4q
YT1MECH-93-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_41 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable ISO to 1CRAH_D_41) Label isolator not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624716&prj=626&rqi=JklevmOvZVgeaxchHhmcIZmPaE
YT1MECH-41-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1CA_B_7] Grounding cable was incorrectly terminated on the panel body, need rectify it according to the attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624514&prj=626&rqi=wm8KBJTByTY8nyzzhVudz3vLUj
YT1ELEC-166-005 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | [Issue CxL2A 1TOU_B1] Vinyl grounding not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624501&prj=626&rqi=RknLOleKfWINfzE4ZBpxCFykWN
YT1MECH-30-004 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A Laying cable 1DB_CHWSTR_D_04_CH1 to 1CHWSTR_D_04_CH1) Vinyl cable need tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624557&prj=626&rqi=3kjr9ufQG5CdvVN7e9Unrh0TfL
YT1ELEC-166-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | [Issue CxL2A 1TOU_B1] Cable tagging blurry need rectify (phase N) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624499&prj=626&rqi=nXnMEoOXHHz5THV8noAdPI4VKf
YT1MECH-92-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_41 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable DB_B_Critical to ISO 1CRAH_B_41) Labelling panel not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624492&prj=626&rqi=EAfYYVF7CoUh8NYbqbavk5AxNf
YT1MECH-91-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable ISO to 1CRAH_F_42) Bonding jumper not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624717&prj=626&rqi=uJOmGvAKivpRbLD1bUx9fQFvm4
YT1MECH-65-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_2 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_2] tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624507&prj=626&rqi=yyq4NQtt4Bb8LoS1InHUpuKHJ0
YT1MECH-86-001 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable ISO 1CRAH_B_22 to 1CRAH_B-22) Cable over bending at phase T, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624489&prj=626&rqi=xEtkPZnfCl8zuWgbmUyf3q4kPD
YT1MECH-64-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_1 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_1] tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624503&prj=626&rqi=zeZiImcNG0zGDjfutCjkNWmpY1
YT1MECH-110-005 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV CABLE ISOLATOR_1CHWSTR_B_07_CHWP_1 to AHF 1CHWSTR_B_07_CHWP_1) Cable end caps rubber need to be properly installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624560&prj=626&rqi=0O5wKnV2N5r75plfE5rjrQkaoY
YT1MECH-67-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_4 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_4] Tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624511&prj=626&rqi=YXUrdczTCflxr8FLx6jSr9vj89
YT1ELEC-122-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable DB_C_Critical to ISO 1CRAH_C_22) Protection Neutral not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624487&prj=626&rqi=igYKobUOJ7u4DuzEOBW2A0BQef
YT1MECH-110-004 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV CABLE ISOLATOR_1CHWSTR_B_07_CHWP_1 to AHF 1CHWSTR_B_07_CHWP_1) Grounding Cable Scratch until copper wire is visible | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624559&prj=626&rqi=Rme5XOx1VmPFg9TJ9FFV600jic
YT1MECH-65-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_2 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_2] Cable lug phase R is broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624506&prj=626&rqi=pUcJyX42nNf7e7cI1AFqFXkyGD
YT1MECH-19-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | (Issue CxL2A LV Cable 1MDSB_F_1 to DB 1VRFOD_F_61) 1. Cable lug not yet installed 2. Cable gland not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624705&prj=626&rqi=B1BPAFRj4NGuSxrznsdKvYnA1x
YT1MECH-64-001 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_1 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_1] Cable over bending, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624502&prj=626&rqi=CqWDY1M1Pd7sy55jhFhyNXrnOb
YT1MECH-31-004 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A Laying cable 1DB_CHWSTR_B_07_CH1 to 1CHWSTR_B_07_CH1) Belleville washer size is larger than the cable lug size. Please replace it with the correct size. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624519&prj=626&rqi=j3g6vgg6U5YnHUTdR7567PWonr
YT1MECH-84-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable DB_B_Critical to ISO 1CRAH_B_21) Need install cover tray and tagging cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624486&prj=626&rqi=7Jk0HehP9AjW3nyqeRj4NDmWAL
YT1MECH-67-001 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_4 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_4] Cable over bending, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624510&prj=626&rqi=VeMtwyEvrRrQLnPw5SiEKH711x
YT1MECH-68-001 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1FFU_B_5 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_5] Cable over bending, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624512&prj=626&rqi=x3crSFGACMvoZ1QjNjp2Iz9TaD
GI-020 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-06-08 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | pressure gauge does not match the unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624424&prj=626&rqi=RU3K8HFjPXLRf62cHT0oxllN8t
GI-019 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-06-08 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | pressure gauge does not match the unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624422&prj=626&rqi=nhhUQmJneYN0qaYixI7fGqtQeu
YT1ELEC-13-011 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Please re-check the contact resistance test results for ACB Q1. Based on the acceptance criteria (deviation shall not exceed 50% of the lowest measured value), the recorded values exceed the allowable deviation limit. Kindly perform retesting if necessary | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624393&prj=626&rqi=W0sjfFsmlRAJQzlLqXumSWKkl1
YT1ELEC-10-009 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Breaker Q1-3 protection settings are not in accordance with the latest approved Discrimination Study. Please update all breaker setting values and re-testing to match the approved protection coordination study and resubmit the report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624388&prj=626&rqi=hXLPFQIJ13zMD4TW8uyGmHNa4T
GT1ELEC-4-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Arc flash label on the RMU is still temporary. Please replace it with the permanent label as per the approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624421&prj=626&rqi=ZXSh3hOD7ju1JuLGVh6Zia0rb9
GT1ELEC-1-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Arc flash label on the RMU is still temporary. Please replace it with the permanent label as per the approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624417&prj=626&rqi=i4Qys612Uwk8OzrIFCPN1G5nxd
YT1ELEC-13-012 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Breaker settings in 1MSB_F_1 do not match the latest approved Discrimination Study. Please update the settings accordingly and perform retesting if required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624395&prj=626&rqi=vPfB6WEZS3SWQY85weq2KvJH9w
GI-021 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-06-08 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | pressure gauge does not match the unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624426&prj=626&rqi=Est9zxUi2TTwE1V4zHE8oqKGHx
YT1ELEC-11-011 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Breaker settings in 1MSB_C_1 do not match the latest approved Discrimination Study. Please update the settings accordingly and perform retesting if required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624409&prj=626&rqi=g7v62F6bbNmOR8C0I8Om9KJtpL
YT1ELEC-12-015 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Breaker settings in 1MSB_D_1 do not match the latest approved Discrimination Study. Please update the settings accordingly and perform retesting if required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624411&prj=626&rqi=RgimnO5hdAQuLAzYIJC4PShXDB
YT1ELEC-116-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable DB_B_Critical to ISO 1CRAH_B_21) tagging cable not yet installed for Q-2, Q-3, Q-4, Q-5 DB side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624444&prj=626&rqi=3qEe0QI9AGsUZwO4deYN1pI3uh
GI-022 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-06-08 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | pressure gauge does not match the unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624427&prj=626&rqi=6BpBFFcYtkl27TnaOxvDbrTz9c
GT1ELEC-2-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Arc flash label on the RMU is still temporary. Please replace it with the permanent label as per the approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624419&prj=626&rqi=d0B4Scyfx1XetPgnD6DOpWFpp8
GT1ELEC-3-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Arc flash label on the RMU is still temporary. Please replace it with the permanent label as per the approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624420&prj=626&rqi=iz7tGP5JOlsSRGsBomP9cEIWuZ
RT1MECH-34-002 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-06-06 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | During the Chiller 4 tie-in activity, water leakage was observed from the Buffer Tank. Later found out that the source of the leakage as a torn flange gasket at the venting connection. The issue was promptly rectified by replacing the damaged gasket. Following the rectification, the tie-in activity resumed and was successfully completed in a safe and controlled manner. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624247&prj=626&rqi=cZOFNkf6j9quE2xyug7d9dg5EB
YT1ELEC-27-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) This is a DC cable. Cable tagging is incorrect; please replace all "L" and "N" identification with "+" and "-" accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624100&prj=626&rqi=VVwTivCJvv1TRS2MyGcEtHTRwA
YT1ELEC-17-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Cable tray cover is not installed. Please complete the installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624086&prj=626&rqi=B5kcy3IxvmU3YDIfrC3puPwja9
YT1ELEC-29-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Apply correct DC cable identification: Red vinyl for DC+ and Black vinyl for DC- | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624095&prj=626&rqi=ZSGoTyUtOSP1WJBTlJ90W3set0
YT1ELEC-29-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624094&prj=626&rqi=FV5Gw725fplAOF0aAdHAhOdPKj
YT1ELEC-29-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) This is a DC cable. Cable tagging is incorrect; please replace all "L" and "N" identification with "+" and "-" accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624091&prj=626&rqi=mBR87diQXaTF24GdLNClgtzhdA
YT1ELEC-19-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) Washer size is larger than the cable lug. Please replace with the correct washer size | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624120&prj=626&rqi=3pyqsLHt3IxDaftzBWdJu1t2X4
YT1ELEC-17-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Apply correct DC cable identification: Red vinyl for DC+ and Black vinyl for DC- | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624085&prj=626&rqi=fjehpooaTthX2zOBSu5KWqzb2c
YT1ELEC-19-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) Flat washer and Belleville washer are missing at cable terminations. Please install as required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624106&prj=626&rqi=vgP7H6wfqqYN3cWUJ0efRwS4cv
YT1ELEC-27-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) Remove all temporary markings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624119&prj=626&rqi=jgvTCsY0HAenkJ2TaSSKzHY7xZ
YT1ELEC-19-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) This is a DC cable. Cable tagging is incorrect; please replace all "L" and "N" identification with "+" and "-" accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624105&prj=626&rqi=olsl38MlqJ5iD6NwbSihDaaGBT
YT1ELEC-17-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) This is a DC cable. Cable tagging is incorrect; please replace all "L" and "N" identification with "+" and "-" accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624082&prj=626&rqi=AZsPBUwS1Zu9FugG6vYvpwhKng
YT1ELEC-17-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624084&prj=626&rqi=JRQIcjcumKzfkumYeVoLTdY0JO
YT1ELEC-17-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Glanding is not fully covering the cable entry. Ensure proper sealing and full coverage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624087&prj=626&rqi=KuBDUjOOj6ZkMHEwOkWqOu5XvD
YT1ELEC-27-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) Apply correct DC cable identification: Red vinyl for DC+ and Black vinyl for DC- | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624102&prj=626&rqi=ToDQpI2Ew58GIJ9ODhMUuTUtl3
YT1ELEC-19-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) Apply correct DC cable identification: Red vinyl for DC+ and Black vinyl for DC- | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624118&prj=626&rqi=Tr0xigovgjCBh3OlQrx2ZaA5wY
YT1MECH-28-006 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Discrepancy noted between the approved MAR and the installed Pressure Gauge (PG). The approved pressure range is specified in kgf/mÂ², while the installed gauge scale is in kPa. Please provide clarification and justification for acceptance. Note: for all Chiller. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623913&prj=626&rqi=whxgdawsD0r0qtrWWpqm0ZVZzQ
YT1MECH-28-005 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | During the Chiller 2 tie-in activity, leakage was observed at a tee reducer connection that had previously been used for temporary flushing. GC shall inspect and properly tighten all tee reducer connections following flushing activities to ensure system integrity and prevent recurrence of similar issues | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623911&prj=626&rqi=VQdS1E1vx3petdZscM59louwU6
RT1ELEC-160-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L6 | DB - Distribution Boards |  |  | Need provide labelling inside panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623918&prj=626&rqi=xtlWt9bXxAh1ciZjjq64SN1An4
YT1MECH-107-012 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_C_2 To ISOLATOR 1CHWSTR_C_02_CHWP_1) Need cleaning inside Iso panel, too many foreign object | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623702&prj=626&rqi=K7HHJzgp6f4WA1BLm3Mst64m4L
YT1MECH-107-008 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_C_2 To ISOLATOR 1CHWSTR_C_02_CHWP_1) Need to install ferrule cable connector for termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623697&prj=626&rqi=iAu6KDBcHUvftOqTnhLC4ZOh4H
YT1MECH-107-011 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_C_2 To ISOLATOR 1CHWSTR_C_02_CHWP_1) Nut broken on the upper neutral side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623701&prj=626&rqi=7qa3nHLTXZ5ysu016cXwsDMuuv
YT1MECH-107-009 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_C_2 To ISOLATOR 1CHWSTR_C_02_CHWP_1) Please ensure that the grounding and neutral termination positions are in accordance with the design, as on the other isolators the grounding termination is installed on the top side while the neutral termination is installed on the bottom side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623698&prj=626&rqi=f33ELJaAu6moryjAzDCfpD28bv
YT1MECH-110-002 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_B_2 To ISOLATOR 1CHWSTR_B_07_CHWP_1) Need to install ferrule cable connector for termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623690&prj=626&rqi=nD5PN4okrVjYLTvGNgfeOZt9vh
YT1MECH-107-010 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_C_2 To ISOLATOR 1CHWSTR_C_02_CHWP_1) vinyl damage, please rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623700&prj=626&rqi=6DWCETogOQHtC1Bcdm8SqQ3OId
YT1MECH-110-003 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_B_2 To ISOLATOR 1CHWSTR_B_07_CHWP_1) Cable scratch until exposing the copper wire | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623695&prj=626&rqi=rsvAj2uXLX5609kBfeY0pETJra
GT1ELEC-1-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | During energization of 1MLTX_B, for power, voltage, and current readings could not be displayed on the RMU panel. Please to investigate and rectify the issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623759&prj=626&rqi=gyhr1OvwTrU0PCves61yRHd6JY
YT1ELEC-11-009 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cable termination not yet completed and cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623587&prj=626&rqi=XKN5U5a1LVzHCDw4xUcAbLckKr
YT1ELEC-12-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623591&prj=626&rqi=d8g7ahkfmeTURRACp5UfgzwVKE
YT1ELEC-12-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cable termination not yet completed and cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623590&prj=626&rqi=xTl0n3YsORnJKQavg0ABONweF1
RT1ELEC-150-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue CxL2A BD R-Block Lv. 5) Incomplete bolts bracket support busduct, please check all bracket support | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623638&prj=626&rqi=gV11qDdkvZ8pdQFoN27ia01mrW
YT1ELEC-12-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cables with insufficient bend radius, cable is over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623588&prj=626&rqi=IqEKuPT8XdW2wQ5Be2GVeZEohm
YT1ELEC-12-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Outgoing nameplate should be to "1CHWSTR_D_04_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623592&prj=626&rqi=kmvaXnWR0o3IGeFRBtH7QMni3M
YT1ELEC-12-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Incorrect cable tagging, should be "High Temp / Over Temp" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623589&prj=626&rqi=umo3IrN6nqgDc9PGJC44Ch4F41
RT1ELEC-150-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue CxL2A BD R-Block Lv. 5) Label not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623639&prj=626&rqi=cs7rKE0C89NO1QWjfd6QOOzB94
YT1ELEC-13-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623585&prj=626&rqi=WI2f7UKKOvI22XjH2ZssqDLa9Y
YT1MECH-108-008 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_F_2 To ISOLATOR 1CHWSTR_F_03_CHWP_1) Nameplate Panel ISO Not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623617&prj=626&rqi=xupSlW5WhSd1ijWnXNf4bAtLnl
YT1ELEC-13-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cables with insufficient bend radius, cable is over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623583&prj=626&rqi=n1EKQHdE3OqmiFthpEAu0xlRBr
YT1MECH-109-005 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_D_2 To ISOLATOR 1CHWSTR_D_04_CHWP_1) Cable insulation is damaged/scratch until exposing the copper conductor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623620&prj=626&rqi=6963pnCyT0C5UD13Pe9H627zNm
RT1ELEC-12-010 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable From 1MSB_B_1 to 1GPC_B) Tagging Cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623606&prj=626&rqi=Ujb2SJrnQ1MC2Nlk8BeE04ECCT
YT1ELEC-10-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cables with insufficient bend radius, cable is over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623594&prj=626&rqi=NW5azKWiJybqbw4fY9CBliZlaS
YT1ELEC-13-009 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cable termination not yet completed and cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623584&prj=626&rqi=kbezbARVeoAocaZ0QmlLAB6ODj
YT1ELEC-10-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Incorrect cable tagging, should be "High Temp / Over Temp" and cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623596&prj=626&rqi=Gj0lolvo9yDQZlSdKjV0QvI6Ox
YT1MECH-109-006 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_D_2 To ISOLATOR 1CHWSTR_D_04_CHWP_1) Need install Ferrules cable connector | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623635&prj=626&rqi=nFpErHHT4cTWyXVI01Y5xv6lSn
YT1ELEC-10-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cable termination not yet completed and cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623595&prj=626&rqi=xmoKfsNPV36rfDAEGTtIkHtpCC
YT1ELEC-11-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623586&prj=626&rqi=MCr46FZopggQ7UprJ7Mg6fLL2w
YT1ELEC-11-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Incorrect cable tagging, should be "High Temp / Over Temp" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623593&prj=626&rqi=cILjI4WLAY3SDVsd7M7d4eElaf
YT1ELEC-5-009 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Busbar inside MLTX incomer cubicle in MSB panel still dirty and dusty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623442&prj=626&rqi=tEWFLvXQ3MRF3ZiWqA1ZFRGIG5
YT1ELEC-18-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_C_1 to 1UPS_C_2) Cable vinyl not yet installed & missing bolt termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623460&prj=626&rqi=h2YdVep8dg0qSkvLQCpea6fJTj
YT1ELEC-18-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_C_1 to 1UPS_C_2) Several cable gland caps area damaged (torn) and not properly covering the gland, please ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623458&prj=626&rqi=DmUDODhw94vZTrb6rKJWdt7jm2
YT1ELEC-119-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1MDSB_D_1 to 1DB_D_CRITICAL) Please ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623456&prj=626&rqi=ch2mmqKx9ENu6Pz3FKLR9RMxcQ
YT1ELEC-120-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1MDSB_D_1 to 1DB_D_EWALL) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623455&prj=626&rqi=G9eIGqwamZL2QZYdIDNEkBVH2X
YT1ELEC-5-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Busbar joint between MLTX busduct and MSB not yet torqued and marked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623440&prj=626&rqi=QktJcAHIWu6bfcVC12yY7uQQ3g
YT1ELEC-120-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1MDSB_D_1 to 1DB_D_EWALL) Several cable gland caps area damaged (torn) and not properly covering the gland, please ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623450&prj=626&rqi=ZCGMXVg8YimXVvmCdT9vH33rXx
YT1ELEC-18-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_C_1 to 1UPS_C_2) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623459&prj=626&rqi=XF26fj2w1GjgLi0SfugVGYNjBx
YT1ELEC-5-010 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Grounding cable from MSB panel to earth bar and from earth bar to SUDB need to be checked to ensure ready for MLTX energization | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623443&prj=626&rqi=kpcJImIuxpvFoAqs0iQYWzghTs
YT1MECH-89-003 | JK01-2 | APAC | Closed | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | DCOS cable has not yet been pulled into the CRAH unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623299&prj=626&rqi=TVMdt65lWyKt1oyG4mkpW2VJQX
RT1SEC-20-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_5_DH | ACU _ Access Control |  |  | reader not yet installed, door 05:16 Note: it's because GC's work (flushing pipe), that make the door cannot close so there will also become GC scope to rectify this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623273&prj=626&rqi=ysYLyU753r8WZE0JEwESCW1bxv
YT1ELEC-11-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to Chiller) Please ensure glanding cap fully properly sealing & cover tray installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623314&prj=626&rqi=NvkLju2bfDVfSMGPApsPshs2Cg
YT1ELEC-12-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to Chiller) Standardize the cable tagging "from 1MSB_D_1 to LBS 1CHWSTR_D_04_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623318&prj=626&rqi=vXFrgBWASk4fu1b0CJgqOFJcL6
YT1ELEC-10-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_B_1 to Chiller) Standardize the cable tagging from "1MSB_B_1 to LBS 1CHWSTR_B_07_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623303&prj=626&rqi=aGe25MYKyaUG7rRdaD2Os5GmBc
YT1MECH-85-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_21 | CRAH - Computer room air handler |  |  | Incomplete insulation and jacketing observed at several points along the CHW piping | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623302&prj=626&rqi=EQgDN9WmPdpV6uXb9VWKYyWF2x
RT1SEC-20-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_5_DH | ACU _ Access Control |  |  | door 05:16 cannot close because of temporary flushing pipe, it causes the reader for this door cannot installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623281&prj=626&rqi=pAzJNc4VTwUEexsRgBfBy48UqO
RT1SEC-20-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_5_DH | ACU _ Access Control |  |  | door 05:10 not yet install at all | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623284&prj=626&rqi=alF5W1sbEcdSfccGyQ0PQQRFU5
RT1FD-32-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Fire Detection | equipment | ASDSP-6.09 | VES - Vesda |  |  | support pipe misalignment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623305&prj=626&rqi=3hvdLlzahtQJGJg8KBH4ScCehe
YT1MECH-31-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A LV Cable 1MSB_B_1 to Chiller) Standardize the cable tagging from "1MSB_B_1 to LBS 1CHWSTR_B_07_CH_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623308&prj=626&rqi=8RHDjBwfqS5hlxYI6bkmiFo324
YT1ELEC-11-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to Chiller) Standardize the cable tagging from "1MSB_C_1 to LBS 1CHWSTR_C_02_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623309&prj=626&rqi=LeONYrcQoqlDCaMiF3cTQ7XdGE
RT1FD-32-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-6.09 | VES - Vesda |  |  | Pipe affected by paint | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623304&prj=626&rqi=58BhwRdcoxgu2YsdueD2gqqZfV
RT1SEC-7-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_2 | ACU _ Access Control |  |  | door 02:19 wall finishing around the pinpad installation require proper finishing, temporary flushing pipe are blocking the door so it cannot close, and also door accessories not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623297&prj=626&rqi=9VvgvhVvGsXKWmghaC56zbDquA
YT1ELEC-11-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Aux power control cable inside MSB panel found over-bent. Please rectify the cable routing/installation Also, GC to clarify the reason why this cable was skipped during CxL2A & CxL2B process | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623300&prj=626&rqi=GGDESCpedyblcrdGHsj6iOmKca
RT1MECH-35-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | manhole and drain pipe not yet insulated and jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623313&prj=626&rqi=8OMu66wAdnY6aea1MNRysWxmoi
RT1MECH-35-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | anchor bolts need re-torque and re-mark (it still moves when perform torque check) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623310&prj=626&rqi=qf5blyMMbKxQDJbGo4TsC3adml
RT1SEC-20-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_5_DH | ACU _ Access Control |  |  | door 05:12, 05:17 handle and accessories not installed yet. door 05:11, 05:13 accessories not yet. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623287&prj=626&rqi=FDUkYA3JcWQkecXROMk0c2oTrX
YT1ELEC-11-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Outgoing nameplate should be "to 1CHWSTR_C_02_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623312&prj=626&rqi=ukjhxY9RWr3dL3id9uAddspCs2
YT1ELEC-10-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_B_1 to Chiller) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623306&prj=626&rqi=vvsLsmgoTrbET5QAxundpUtEug
YT1MECH-88-001 | JK01-2 | APAC | Closed | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | DCOS cable has not yet been pulled into the CRAH unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623298&prj=626&rqi=5EEFUNtpJMxcuO5exMR1EvdHGk
YT1MECH-96-001 | JK01-2 | APAC | Closed | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | DCOS cable has not yet been pulled into the CRAH unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623307&prj=626&rqi=M2AJPS5SHM9xaIfrazADzvTA4h
YT1ELEC-12-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to Chiller) Please remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623319&prj=626&rqi=WkXj33OUpcSvQ5f6zpUGNCqlg6
YT1MECH-32-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to Chiller) Standardize the cable tagging from "1MSB_C_1 to LBS 1CHWSTR_C_02_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623316&prj=626&rqi=l0w48h3A0GoHwB53ENm8LKLaIH
RT1SEC-20-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_5_DH | ACU _ Access Control |  |  | door 05:11 & 05:13 door contact not yet install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623286&prj=626&rqi=WGM0fcNwOtCyiM7xoWorYXpQiC
YT1MECH-30-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to Chiller) Standardize the cable tagging "from 1MSB_D_1 to LBS 1CHWSTR_D_04_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623320&prj=626&rqi=Athz7Nl3I4Zw5DXyfIDWP1dzQL
RT1MECH-35-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Labelling / equipment name tag not yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623315&prj=626&rqi=rD93GGe6ksBAXD0vTaLFHquXY8
RT1FD-32-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-6.09 | VES - Vesda |  |  | please upload Factory Test Data & Material submittal document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623110&prj=626&rqi=cNkC6t5HVdqkIjGT55uYWxazGW
RT1MECH-108-008 | JK01-2 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-05-25 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | LCD display is damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622964&prj=626&rqi=NaANv3IEH8hrqwuo1EnkPwVi37
RT1ELEC-22-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | [issue CxL2A LV Cable 1UPS_B_2 to 1MDSB_B_2] Belleville need to installed in two side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622969&prj=626&rqi=pUdgCqxGrnJPNzAm1gc33RPQa9
YT1ELEC-51-001 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A Laying Cable 1STSSB_D_2 To 1RPP_DR1_02_05] Cable scratch damage until the insulation is visible. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623009&prj=626&rqi=kyNdCJdw6Q0FI11PMag1IaTKtl
RT1ELEC-56-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A Laying Cable 1STSSB_D_1 To 1RPP_DR1_01_05] Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623013&prj=626&rqi=3XHXm509h2kqbnTUjNjzNlIZLZ
RT1ELEC-26-006 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | [Issue CxL2A Laying Cable 1UPS_D_2 to 1MDSB_D_1] Vinyl need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623025&prj=626&rqi=L2JQfDdy7NC2HRxqt8FAPg86gQ
GT1ELEC-2-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | BTU of RMU_D energized from temporary power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623035&prj=626&rqi=Aljvx8I1jVASjuZZWqvmCSlDws
YT1ELEC-51-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A Laying Cable 1STSSB_D_2 To 1RPP_DR1_02_05] Vinyl need to rectify and cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623012&prj=626&rqi=zPKGtGHt2fbzodYf3V39bBasuH
RT1ELEC-26-007 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | [Issue CxL2A Laying Cable 1UPS_D_2 to 1MDSB_D_1] Need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623026&prj=626&rqi=SL1PIsgzAhVMezhNn4jfArZDFM
RT1ELEC-22-004 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | [issue CxL2A LV Cable 1UPS_B_2 to 1MDSB_B_2] 3 Grounding cables are stacked on one busbar. (for All UPS Mech & possible IT) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622971&prj=626&rqi=PF1gUQwaJIeboJYdtY5BnDbIvt
RT1ELEC-56-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A Laying Cable 1STSSB_D_1 To 1RPP_DR1_01_05] Vinyl need to rectify and cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623014&prj=626&rqi=EiLdFkb6hhS8n2RPcT1v2U4fBE
YT1ELEC-4-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | During white glove inspection, equipment body bolts are missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623036&prj=626&rqi=JiFxBEd9JHLpDr4ncR0n7tQp0Y
YT1ELEC-51-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A Laying Cable 1STSSB_D_2 To 1RPP_DR1_02_05] Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623011&prj=626&rqi=bz5AQFZbOa8xHrdSMeZDGjAsHw
YT1ELEC-166-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | [Issue CxL2A LV Cable 1MDSB_B2 to Cooling Array Fan 1TOU_B1] Need to add belleville/spring washer on both side (Phase N,R,T) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622986&prj=626&rqi=wJnL1MTwEgRk9rjHXFhvVt3l4V
RT1ELEC-22-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | [issue CxL2A LV Cable 1UPS_B_2 to 1MDSB_B_2] Need to add cover tray | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622970&prj=626&rqi=bEV5ezqUZV2wq9a3Y9D9wRyify
RT1ELEC-52-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_1 To 1RPP_BRI_01_04] Cable Tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623002&prj=626&rqi=Nc45BjyobOPtRW4C9rpGmSJoSU
RT1ELEC-52-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_1 To 1RPP_BRI_01_01] Dressing cable need to tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623004&prj=626&rqi=iojvkbGIAhRNyIwLjbzFGqngGM
YT1ELEC-166-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | [Issue CxL2A LV Cable 1MDSB_B2 to Cooling Array Fan 1TOU_B1] Need to remove temporary marking cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622984&prj=626&rqi=sWXWakHstyFfY8z0q68iUapRkB
YT1ELEC-3-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | During white glove inspection, equipment body bolts are missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623037&prj=626&rqi=fZoEFa32CO35fnmcKO3YSOsKVX
RT1ELEC-22-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | [issue CxL2A LV Cable 1UPS_B_2 to 1MDSB_B_2] Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622968&prj=626&rqi=b0PELhfyX5xSNDqt1O9h5P2D2p
YT1ELEC-47-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_2 TO 1RPP_BRI_02_01] Need to remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622988&prj=626&rqi=FlRv1Fql2911t6LduhxzcChzv2
YT1ELEC-47-003 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_2 TO 1RPP_BRI_02_04] Grounding Vinyl loose, need to add cable ties | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622992&prj=626&rqi=xzB3Ud1nWNxtH3eJkBxHXjSotS
YT1ELEC-47-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_2 To 1RPP_BRI_02_01] Grounding has not been fitted with a cable lug and has come loose. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622991&prj=626&rqi=70JpT7hVUK7o1EnXHTIPKWzTUN
RT1ELEC-52-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_1 TO 1RPP_BRI_01_01] Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623003&prj=626&rqi=eFng7YEEfTGebqvRMVsY3nfB0b
GT1ELEC-3-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623032&prj=626&rqi=XCeI7To8L4eTW8mLLHFphCKUwG
GT1ELEC-2-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623034&prj=626&rqi=rDqETdcVpZIaZbBHhbJdj0QrB3
RT1ELEC-26-005 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | [Issue CxL2A Laying Cable 1UPS_D_2 to 1MDSB_D_1] Cable tagging is incorrect, need to rectify revise to: from 1UPS_D_2 to 1MDSB_D_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623023&prj=626&rqi=YVYdJ6aJkQL2mVII6sqWr6T8gV
YT1ELEC-18-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1UPS_C_2 to 1LIBATTSYS_C_2) Cable inside UPS has not been provided with cable tagging, cable termination is not properly installed, and cable vinyl is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622908&prj=626&rqi=8Si4QQxtHwc1qcEFZ8pt15ekRl
YT1ELEC-30-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | (Issue CxL2A LV Cable 1UPS_C_2 to 1LIBATTSYS_C_2) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622910&prj=626&rqi=R9Io25KVxEekHLju8tiF8z3wb9
GT1ELEC-1-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622895&prj=626&rqi=4RKWLIxwr19eLM9u1SUCg3GTm0
YT1ELEC-18-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1UPS_C_2 to 1LIBATTSYS_C_2) Incorrect cable tagging, should be "to 1LIBATTSYS_C_2" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622907&prj=626&rqi=FqgSQGqSbUeCuNH8ANct0Kv6YQ
GT1ELEC-4-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622894&prj=626&rqi=KBeXSD1D6eOVjBLrTwv2KHEprm
RT1ELEC-15-023 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Temporary marking need to remove | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622901&prj=626&rqi=JPhZK7hDJ5ew4hPNH0vLPLG9PI
RT1ELEC-15-024 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Need to add additional base frame as per design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622902&prj=626&rqi=M6iSGKHdypeATKgZgTUSGGQ4V0
RT1ELEC-15-020 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Corrosion observed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622898&prj=626&rqi=DNK44a9StwirGYggLPpoiEbzvu
RT1ELEC-15-022 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Equipment tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622900&prj=626&rqi=CjkYlyUhl3yrRMR7flvdx8cvAs
RT1ELEC-15-025 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | All bolts need to torque & marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622903&prj=626&rqi=YzpfgdATEfrMUgahfZ69IxSvZm
RT1ELEC-15-027 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Generator cable not yet torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622906&prj=626&rqi=s9N1GK23MYOVDb05rPlJIdYyg0
YT1ELEC-5-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Incorrect cable tagging external cable to MSB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622792&prj=626&rqi=IOepaANsfE9SwA6clPkdWOQaSj
RT1ELEC-15-026 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Need to install cable tagging & remove temporary marker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622905&prj=626&rqi=GIzHq9tQ1LWq5imyTufg8y0PEa
RT1ELEC-13-026 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Need to rectify the corossion pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622766&prj=626&rqi=MmqDshYZhVs7MpPDYXDFMfFNZP
RT1ELEC-13-025 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | many scratch on body generator, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622765&prj=626&rqi=PeLz3bHL0WiI0VZAKqaKcXSnxn
RT1ELEC-13-027 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Need remove straps and blocks for shipping (Cleaning) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622767&prj=626&rqi=HqOJ8CKdqNKU6oze29AUa3syWp
RT1ELEC-15-021 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Generator dirty & dusty. Need deep cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622899&prj=626&rqi=FrwC4zEdPfC2Spg13aqPmIvKp1
YT1MECH-76-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622445&prj=626&rqi=4UoXWduyppOTr2dYCsrH0wFpJs
YT1MECH-52-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_C_05 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622431&prj=626&rqi=b7SG1URDJiWgWubzR7UlskcUMm
YT1MECH-50-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_C_01 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622426&prj=626&rqi=YplomLBa8qWMwfP79iZdgrFkW4
YT1MECH-51-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CA_C_03 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622430&prj=626&rqi=XvxD2LTNSTpvUVW0KlvrhRfVAT
YT1MECH-54-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_C_07 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622434&prj=626&rqi=ZazaiyWIGTw7idQKhERNH8TLbX
YT1ELEC-4-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | During white glove inspection, flexible busbar was found disconnected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622656&prj=626&rqi=7J288TJUwMuHO1Zqi1cfcNiNC4
YT1ELEC-169-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) Bonding jumper not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622419&prj=626&rqi=tSD6bSQdyDwTXCeXTyAYI8dD2f
YT1MECH-77-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622451&prj=626&rqi=Rlbz54w8sYYXSiPEwmVm53J6ch
YT1MECH-56-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_C_11 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622438&prj=626&rqi=IRSovZrbzjF3t8ONfAxRN1IyL5
RT1ELEC-13-024 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Please add labelling cable to GCP Gen_D | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622597&prj=626&rqi=eGM5Ns4wYPMrGMSDWYS5q3UBoK
YT1ELEC-165-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_2 to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622459&prj=626&rqi=sGrcTOCs6DwSSAmntceohbcmHM
YT1MECH-78-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622448&prj=626&rqi=9orHuSDcmqReFZ4v79Kxh5ULiV
YT1MECH-77-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622446&prj=626&rqi=lUS7yNlPXffHBXYTY1uDPtfutL
YT1ELEC-169-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) incorrect cable tagging feeder name | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622415&prj=626&rqi=jbqmqSfxQ8BQs7XlxJKYm6gdLU
YT1ELEC-4-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | During white glove inspection, control cable was found disconnected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622668&prj=626&rqi=7Is4SpePYsZXG89m8dSFnr32dY
YT1MECH-69-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622442&prj=626&rqi=3pJyU4Ao9Cl3WHJKlDfObQFx03
YT1MECH-76-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622455&prj=626&rqi=c35JE57rfj1xRAfI1d0OYGih4n
YT1ELEC-169-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) Cover trunking not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622417&prj=626&rqi=uZg2z8wTBy7oiig4opLPsJfQsP
YT1ELEC-169-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) Cable tagging not yet installed & please rectify the cable vinyl | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622414&prj=626&rqi=geh30ZAqQ9ycOx1CmdoaLiTkUg
YT1ELEC-169-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622416&prj=626&rqi=6KnXJ0YTEgy4mGaDELJD3xpDKH
YT1MECH-53-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_C_06 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622432&prj=626&rqi=PYyZGLbXwSXaQGZdf7nFk3gZuk
YT1MECH-55-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_C_09 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622437&prj=626&rqi=ZXP6ktm0UEOASDwrheCUTx6DYM
YT1MECH-78-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622450&prj=626&rqi=Iwt0e4rMj77JJ8UvnhcWlvlx9m
YT1ELEC-169-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) Cable tray end sections are open. Please confirm and install end caps where required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622425&prj=626&rqi=cV0IcfM0OhYcXLYZKLyzwu3VSL
YT1MECH-75-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622456&prj=626&rqi=p6Qo2YzHiPN6DR2XvPBhvpSpuK
YT1MECH-75-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622444&prj=626&rqi=1pjwWNUwitnNg3XuoeC42IwrJd
YT1MECH-69-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622457&prj=626&rqi=7WmCkBeCkIv0G5w194w0Hen5Uq
YT1ELEC-4-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622275&prj=626&rqi=qoemQ7xjeplPer3uwCcMq0kO7P
YT1MECH-89-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | Need to add water flow direction labeling on the inner pipe of the CRAH unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622378&prj=626&rqi=nOLDo6BMICn5TS77SpqA8z1LsZ
YT1ELEC-1-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | During site walk for RMU energization readiness, solenoid was found not functioning properly resulting in energization activity unable to proceed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622274&prj=626&rqi=diEmoLbhSXsnZOJJ3BRbIEz6I9
GT1ELEC-1-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | BTU_B Energized using temporary power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622911&prj=626&rqi=6tPRFXmQYSYNItD1jpQDEfFlCc
YT1ELEC-1-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622277&prj=626&rqi=Q6gDsgHkMZ7iQSt0boIOimvlfF
YT1ELEC-4-015 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | During RMU energization readiness inspection, several panel bolts were found loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622362&prj=626&rqi=WbFVp3uvaDlKBakS9wmCKwAEo0
YT1ELEC-1-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | General Contractor | L2B | Missing Components | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Rear panel bolts of the RMU are still missing and not yet installed (around 10-15 pcs) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622361&prj=626&rqi=ySxBPcNR5GR15mFXVOngVEOFnj
YT1ELEC-4-014 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | The panel door lock cannot function properly due to the earthing key not being removable and causing the panel door unable to close normally | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622276&prj=626&rqi=ThcAgHsSC2gYW3V9rMxTvmXvvT
YT1MECH-89-002 | JK01-2 | APAC | Closed | P1 High CX | DimasKurniawan@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | \e observed during Cx activity (CRAH_F_41) that the HMI was damaged due to impact during ongoing construction work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622382&prj=626&rqi=qiiB1gkPipOJJqVrEowm5Svu75
GT1ELEC-3-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | BTU_C energized using temporary power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622159&prj=626&rqi=PqQ3Bwo3tsNfSH71AaBeSMUWzf
RT1ELEC-14-020 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Need to rectify the corrosion pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622255&prj=626&rqi=lJ7Tyqgkx7vIetas0lUSqLAvzl
RT1ELEC-14-026 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Need install jumper grounding tray cable containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622263&prj=626&rqi=gJqbHV3dwlyCdCG4Mt8P3MTh9T
RT1ELEC-14-022 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Need remove straps and blocks for shipping Gen (Cleaning) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622258&prj=626&rqi=I6JrAfYmNReU3CuooId4aSGTBo
RT1ELEC-14-025 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Please install cover tray grounding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622262&prj=626&rqi=tAglJBcOhISb4PBfXI3nW29Jfq
YT1FD-38-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Fire Detection | equipment | ASDSP-7.09 | VES - Vesda |  |  | Please provide more proper labelling name for isolator switch, refer to phase 1 (photo attached) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622267&prj=626&rqi=9nQHtyvT7l7YmwHYHxf7y0XO1k
YT1FD-13-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Fire Detection | equipment | ASDSP-3.10 | VES - Vesda |  |  | need to clean and provide proper cover for equipment to minimize debris, dust and also need to repaint pipe which affected by wall painting | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622268&prj=626&rqi=eiUxPp7YmiQ5ckIdNoVjTeHagC
YT1ELEC-1-002 | JK01-2 | APAC | Closed | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | DCOS conduit pipe damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622156&prj=626&rqi=wvr5CkQVCgtnDN0js1C9cMDL4z
GT1ELEC-4-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | BTU_F energized using temporary power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622158&prj=626&rqi=8rC9SotJt53DeY7ZbwoSEW730O
YT1ELEC-1-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Please update the breaker nameplate numbering to follow the approved nameplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622155&prj=626&rqi=yzJIA6zfhj2wcoOAxEnLjFO4SO
RT1ELEC-14-023 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Please add labelling grounding + tidy up heat shrink | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622259&prj=626&rqi=QTlNyDthk7cmJ7unLwf6TrLjg7
RT1ELEC-14-019 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Equipment damage (body scratch) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622252&prj=626&rqi=LUhlGApWB7FNlE3BCDS0WyElMM
RT1ELEC-14-021 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Please provide shop drawing for inspect dimension panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622257&prj=626&rqi=puXpsJsMaLEpFQgUI3gPJxu7UU
RT1ELEC-14-027 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Need install vinyl properly and cable ties | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622264&prj=626&rqi=ZwOvAuAcRFcLONI1qoADZ63dGA
RT1ELEC-14-024 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Spring mounting need rectify, cannot be tightened to the specified torque | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622260&prj=626&rqi=IsHmfpcI4TuYrmYOTNgUEiQbiv
YT1ELEC-4-009 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Tagging Grounding incorrect, Revise to: 1RMU_F_1 to EB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622100&prj=626&rqi=4msFcO7RBlmzM8T3hxSqMElBdM
YT1ELEC-4-010 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Need install Cover rubber cable gland, because make debris inside panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622101&prj=626&rqi=UIoLDofX2iryvOQmt3mAdgE46Y
YT1ELEC-4-011 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Need replace connection grounding system at 1SUDB Side to 1RMU_F_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622102&prj=626&rqi=jx76UuEhv8SKxiyqcZziAtmRRG
YT1ELEC-2-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Please provide the termination point cover at the RMU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622113&prj=626&rqi=dHIdC64PIVizo3HV2zbDhftUsg
YT1ELEC-3-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Please update the breaker nameplate numbering to follow the approved nameplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622110&prj=626&rqi=2hpQJcb1cQsMODgOhyQmkhxpg6
YT1ELEC-4-008 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Tagging MV Cable incorrect, Revise to: 1SUDB to 1RMU_F_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622099&prj=626&rqi=tT08eNFXblY6oL0MA9yuOMLdzU
YT1DCOS-15-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Controls | equipment | 1DCOS_1_SCP_07 | DCOS - Control Panels |  |  | During the site walk, CTA observed damage to the conduit at the SCP07 panel to sensor, and please add support to the conduit for reinforcement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621956&prj=626&rqi=atu4VMtdZ0MmpStsrNtaMIs4Sl
YT1ELEC-4-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please update the breaker nameplate numbering to follow the approved nameplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621953&prj=626&rqi=Cu3JgxwoWmtIy7S85ELHg5AspG
YT1ELEC-4-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please provide the termination point cover at the RMU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621955&prj=626&rqi=g4sZF4LzfTIxOJVSy4g7P56LNu
RT1ELEC-55-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_2 to 1RPP_CR1_02_03) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621593&prj=626&rqi=ze4FksspHGJQropwRraMCshBLw
YT1FD-11-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-2.09 | VES - Vesda |  |  | Report CxL2A need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621582&prj=626&rqi=TxE8zskNc0Nb1S4p9KAZNavru4
YT1FD-12-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-2.10 | VES - Vesda |  |  | Report CxL2A need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621583&prj=626&rqi=pAXtwuMxtXpyASISvzb1hbQGvQ
YT1FD-10-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-2.08 | VES - Vesda |  |  | upload report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621581&prj=626&rqi=yimmZhEYwJSNHL952UsBD6LsXf
RT1FD-10-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-2.08 | VES - Vesda |  |  | upload RFIT doc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621570&prj=626&rqi=Bewrygft8Jv9oGG6Lb0SxLMu1g
YT1FD-7-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-2.04 | VES - Vesda |  |  | Report CxL2A need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621572&prj=626&rqi=apdsEwpwQEdVEJkZDIQviZI6YV
RT1ELEC-54-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_1 to 1RPP_CR1_01_05) Remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621587&prj=626&rqi=NIqj9BrUYiKYFbNvkmeE03QXtj
RT1ELEC-152-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue Tx Room B) Earth bar label not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621344&prj=626&rqi=FPwD8lUBpp5XoSIdEZbW6TjJUo
RT1ELEC-152-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue Tx Room B) Grounding cable size for the RMU & MLTX is not in accordance with the design. The installed cable is 300 mmÂ², while the approved design requires 240 mmÂ² | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621342&prj=626&rqi=3O1rzy1pNre4S74QH5y3zAyAk7
RT1ELEC-27-001 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Any scratch on body panel 1UPS_F_1, need to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621608&prj=626&rqi=J4mVjo9DIadYnzfGpc6HiJPquY
RT1ELEC-54-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_1 to 1RPP_CR1_01_05) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621585&prj=626&rqi=aF2BBeuofnlvrVNeLSb18nWByW
RT1ELEC-152-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue Tx Room B) Please follow Equinix standard for cable termination, not yet installed flat washer & spring/belleville washer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621343&prj=626&rqi=7EsJMVEIDObj0fKjOvzjnzRb8m
RT1ELEC-27-006 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Equipment is dirty with dust and foreign object, Cleaning (FOD) is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621634&prj=626&rqi=8T5dNaZ7jjgPWIVjjBiB2dTTbU
RT1ELEC-27-005 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Add temporary protection to prevent for construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621633&prj=626&rqi=mpFKze94Sz222p4osrnH5troKG
RT1ELEC-27-004 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Nameplate panel not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621632&prj=626&rqi=DSn4vmuQAklkF32AVhT9HlN7sj
RT1ELEC-27-002 | JK01-2 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Drawing inside panel not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621615&prj=626&rqi=igZ4NCAoj0DtlEwG07akb6lFhG
RT1ELEC-27-003 | JK01-2 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621631&prj=626&rqi=7eLte5YDRa4E9iLJja5jpZjvGT
RT1ELEC-15-019 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual breaker rating: - Breaker Q3: 6A actual 16A - Breaker Q4: 6A actual 16A - Breaker Q5: 6A actual 16A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621339&prj=626&rqi=JLzFEjgmEd6Fr964perPapzE5M
RT1ELEC-152-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue Tx Room B) Please ensure all grounding cable tagging consistent as per standard | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621345&prj=626&rqi=14Yihafh5pgod95aTcbNChA2i6
RT1SEC-21-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_7_DH | ACU _ Access Control |  |  | issue for CSA GC team. a long thread blocking the door so it cannot close properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621044&prj=626&rqi=QElSTu2rwVUBqkph2xCseZeWnR
RT1MECH-2-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | Fusible link cable issue. attach photo once already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621069&prj=626&rqi=5kkyVe8d9r99PoaK5gTjVBAbIT
RT1FD-23-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.01 | VES - Vesda |  |  | Factory Test Data need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621042&prj=626&rqi=UmHNMMZOV11zP6yz78k5LOl1mn
RT1MECH-6-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | issue LCP panel. labelling cable not yet complete | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621048&prj=626&rqi=2WcJ6mPJMgJcPbldYDulr4bUAo
RT1MECH-2-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | need to upload doc: 1. O & M Manuals 2. Shipping & Delivery Receipt (if any) 3. Approved SoO 4. Report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621067&prj=626&rqi=3d0GIOa2S3Jibx8IuywsLPHCfo
RT1FD-14-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-4.01 | VES - Vesda |  |  | need to upload doc: 1. Technical Submittal 2. Factory Test Data 3. RFIT 4. Drawing (already approval) 5. Report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621063&prj=626&rqi=TPm0mtLOtDZS4M2E0Oa9TEueuP
RT1SEC-19-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_4_DH | ACU _ Access Control |  |  | issue for CSA GC team; door accessories have not installed yet, such as door handle, door loop, mortise lock, door closer, and even there is one set of complete doors have not been installed yet (one of door at caging door) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621046&prj=626&rqi=kdOla63s9qG4FNxgCMUs76n19r
RT1MECH-9-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | issue LCP panel. labelling cable not yet complete | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621049&prj=626&rqi=JWm9btMt6OvmrbYHoANN0Ygn4j
RT1FD-16-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-4.03 | VES - Vesda |  |  | need to upload doc: 1. Technical Submittal 2. Factory Test Data 3. RFIT 4. Drawing (already approval) 5. Report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621065&prj=626&rqi=ENg6KSrzehL1Oq8dx0bfF2ZQYH
RT1FD-18-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-4.05 | VES - Vesda |  |  | need to upload doc: 1. Technical Submittal 2. Factory Test Data 3. RFIT 4. Drawing (already approval) 5. Report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621066&prj=626&rqi=QXZ6lGqnPAKy5KwoGIjRKHMMGT
YT1ELEC-2-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable 1RMU_A to 1RMU_D) Need to add cable tagging/label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621090&prj=626&rqi=P0aRfdaoPicudfxGnO4dCfeen3
YT1ELEC-2-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable 1RMU_A to 1RMU_D) Need to add tray/support cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621093&prj=626&rqi=WJlr8mdhra1f9URniwqT6Sokcd
YT1ELEC-2-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable 1RMU_A to 1RMU_D) Cable cleats not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621092&prj=626&rqi=KwnKh4J0zzM5NaqbPf7fqhmXRy
RT1SEC-21-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_7_DH | ACU _ Access Control |  |  | door contact sensor has not been installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621045&prj=626&rqi=zIcUw0ORBFKHSertqqlQH1QXtA
RT1MECH-2-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | Pipe overflow does not install yet. attach photo once already done. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621072&prj=626&rqi=cRPTyru1c6iwQwvO8xj7SWfxO4
RT1SEC-19-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_4_DH | ACU _ Access Control |  |  | door contact sensor has not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621047&prj=626&rqi=mq26EkBSyNsNXuIr5SCVJ4jfTa
RT1MECH-2-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | Pipes need to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621068&prj=626&rqi=7nm1vkfIMdG1zhCVjh1NLS13q7
RT1MECH-2-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | solenoid cable issue. attach photo once already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621074&prj=626&rqi=q11A7J8P5QFshaw8cZMoGhd9Ir
RT1FD-15-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-4.02 | VES - Vesda |  |  | need to upload doc: 1. Technical Submittal 2. Factory Test Data 3. RFIT 4. Drawing (already approval) 5. Report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621064&prj=626&rqi=ZX02sPjGyvgB9AkiOQLYvyDIbG
RT1SEC-21-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Security | equipment | 1ACS_level_7_DH | ACU _ Access Control |  |  | issue for CSA GC team; door accessories have not installed yet, such as door handle, door loop, mortise lock, door closer, and even there is one set of complete doors have not been installed yet (cool spine area) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621043&prj=626&rqi=9bsiOmV720yusyLUPTIt816wGJ
YT1ELEC-12-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Missing bonding jumper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621027&prj=626&rqi=r1aOH0Zb6menEHYVmZwdOAOesn
RT1ELEC-154-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_5 | ERTH - Earthing |  |  | (Issue Tx Room C) Conductor still exposed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621031&prj=626&rqi=G8RLELJbRolRTUy0pd5dlmSyP8
RT1ELEC-13-021 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Please remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621028&prj=626&rqi=lFXvVMOmGMEEjMvhnmu8aFsqtI
RT1ELEC-13-023 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Vinyl cable color for Phase S / L2 should be brown, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621030&prj=626&rqi=OqagVsalWVQsMJMUdvuITmj9ym
YT1ELEC-11-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to 1GEN_C Panel GCP) Cable vinyl is not properly covering the termination area between the cable and cable lug | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621019&prj=626&rqi=Xo3Fj1kfT3P0P5HsQqh6tp9UMj
RT1ELEC-14-018 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to 1GEN_C Panel GCP) Vinyl cable color for Phase S / L2 should be brown, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621021&prj=626&rqi=0vMyYROonAntWmJNlT9y2ZbYcZ
RT1ELEC-154-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_5 | ERTH - Earthing |  |  | (Issue Tx Room D) Please follow Equinix standard for cable termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621033&prj=626&rqi=MZFYjLrpVEAHDnl03SBCR93mKb
YT1ELEC-12-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Vinyl cable color for Phase S / L2 should be brown, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621025&prj=626&rqi=8Q4ZjOJsqhyQqGKp2VTSSZzeg6
RT1ELEC-13-022 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Cable vinyl loose & not properly covering the lug | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621029&prj=626&rqi=2OmiuftKB7StL9P7T5zmtIJDyx
YT1ELEC-11-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to 1GEN_C Panel GCP) Need to add belleville or spring washer on the bolt termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621018&prj=626&rqi=8Ltj7qeRe2rfaSBwIPFaQRwOIE
YT1ELEC-12-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Cable vinyl is not properly covering the termination area between the cable and cable lug | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621023&prj=626&rqi=IfTZM5T2RJJrmi2o6QYST5Dy0E
YT1ELEC-12-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) 1. Cable tagging not yet installed 2. Glanding cap is torn. Ensure the gland is properly covered and sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621026&prj=626&rqi=DYQwfbV9HZVI5T3MiLbi25SlI9
YT1ELEC-11-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to 1GEN_C Panel GCP) 1. Cable tagging not yet installed 2. Glanding cap is torn. Ensure the gland is properly covered and sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621020&prj=626&rqi=Jos0dLtfxcQvNpRDhnB4IeWwAO
YT1ELEC-12-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Need to add flat washer & spring washer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621024&prj=626&rqi=ud1J2DQTW7jpuylZMAPSrFjWSB
RT1ELEC-154-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_5 | ERTH - Earthing |  |  | (Issue Tx Room C) Please follow Equinix standard for cable termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621032&prj=626&rqi=hLbeWKHgRZ4Av09yvyVjzr6umi
YT1ELEC-13-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1MDSB_F_1) Tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620731&prj=626&rqi=3z4GUrgs5J7STTea8XKfqufbVS
YT1FD-34-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Fire Detection | equipment | ASDSP-7.02 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620890&prj=626&rqi=I7S0IKHVBMCXjTRrihvaiznWbM
YT1FD-24-002 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Fire Detection | equipment | ASDSP-5.02 | VES - Vesda |  |  | 1. Isolators switch existing but cabling not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620868&prj=626&rqi=WQqeS8gv10W3JHiUfOb9TB2x9y
YT1FD-28-003 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Fire Detection | equipment | ASDSP-5.07 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620872&prj=626&rqi=dGL0T7TjUnIgQtVxW6MPFl86wL
RT1ELEC-28-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_F_1 to 1UPS_F_2) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620727&prj=626&rqi=lqiRgHz2GqajnTfvC1kz2RwHNJ
YT1FD-33-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Fire Detection | equipment | ASDSP-7.01 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620867&prj=626&rqi=7pibgfagM1p8Xpt2npAB5Qc2KW
YT1FD-26-003 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Fire Detection | equipment | ASDSP-5.04 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620870&prj=626&rqi=uVwKzOs9X6ph3e9Wgs2QD2U45B
RT1ELEC-15-017 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620750&prj=626&rqi=lhJY1D8z6NQZKEKD5Sae7PiIlv
YT1FD-25-003 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.03 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620869&prj=626&rqi=HwYvnfmg7VZ4wvvhfqyNR9oN96
RT1ELEC-15-016 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Need to add flat & spring washer on the bolt termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620749&prj=626&rqi=dKIocUuq4golGyXQYzu6KRXpr1
RT1ELEC-15-018 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Vinyl cable color for Phase S / L2 should be brown, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620751&prj=626&rqi=s696dcub5VxM48whybDoZ0yvmM
YT1ELEC-12-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1MDSB_D_1) Please add grommet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620912&prj=626&rqi=lWKk1lrtlIvjiFcqmIvW3NRGOx
YT1ELEC-12-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1MDSB_D_1) Glanding cap is torn. Ensure the gland is properly covered and sealed & please remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620911&prj=626&rqi=NUJpbZRqxzNEZFKdPuZQdTGDM3
YT1ELEC-13-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Need to add spring washer on the bolt termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620740&prj=626&rqi=1ecL7aKpN84HKhPyRmgn0AGIvt
YT1ELEC-13-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Vinyl cable color for Phase S / L2 should be brown, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620747&prj=626&rqi=90EqvLuxcyQGf25Nd5IBHuSvNy
YT1ELEC-13-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1MDSB_F_1) Conductor still exposed & cable vinyl loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620728&prj=626&rqi=LtPUIzzY3m78C87BclvzLqa3ST
YT1ELEC-13-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620738&prj=626&rqi=5A1KJzY00BxrQzXbfLScyqPTz2
YT1ELEC-13-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Glanding cap is torn and not properly sealing/covering the gland | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620739&prj=626&rqi=Qsr6Ea4LFxilGFcf7p2ULHKHde
YT1ELEC-13-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Cable vinyl broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620737&prj=626&rqi=DUZiCzNxaK2RxDhZBUPmvgF9a0
YT1ELEC-48-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_1 to 1RPP_CR1_01_03) Cable vinyl & cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620917&prj=626&rqi=QhI1eqY1FSGB2Kt80vlJLAZZ3L
YT1ELEC-48-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_1 to 1RPP_CR1_01_03) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620916&prj=626&rqi=1dGNHtPl5EYmmFIzouOoe88YMI
YT1ELEC-48-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_1 to 1RPP_CR1_01_03) Please add grommets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620918&prj=626&rqi=2SGlKKgvO1nss7TKQoq7dFql9m
YT1FD-29-003 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Fire Detection | equipment | ASDSP-5.08 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620874&prj=626&rqi=y0eIcFV7YNjtkBXDmEqkCe75rZ
RT1ELEC-26-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1UPS_D_2 to 1MDSB_D_2) Glanding cap is torn. Ensure the gland is properly covered and sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620907&prj=626&rqi=w7UOa1rPlZuo2tK0dHDUZiJq7x
RT1ELEC-26-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1UPS_D_2 to 1MDSB_D_2) Temporary marker to be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620905&prj=626&rqi=uQ4z7uB5aiNXfnCXmkJ2S3HGfE
YT1FD-27-003 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Fire Detection | equipment | ASDSP-5.05 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620871&prj=626&rqi=k1XMURXjABLsIyPeHfPZpelE3O
RT1ELEC-26-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1UPS_D_2 to 1MDSB_D_2) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620906&prj=626&rqi=Vykrm6SEKvXXW2gTIkNYyfZLLf
RT1ELEC-12-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Dual Battery Charger) Please revise drawing to match with actual condition for panel door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620649&prj=626&rqi=XgQGDku8j3FQSmiA3SXuFCPQcb
RT1FD-39-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-7.10 | VES - Vesda |  |  | Installation and Start-up Manual document need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620656&prj=626&rqi=n0yVSP5FjmtitimLw1LUrNN2UU
YT1ELEC-128-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1WLEAK_L2 | LEAK - Leak Detection |  |  | issue from L2A. permanent labelling equipment issue. attach photo if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620646&prj=626&rqi=e2ZG7R8ttHEe8rPqqOR3rtLPkF
RT1ELEC-12-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing and actual breaker size: - F5: 6A (actual 10A) - F6: 6A (actual 10A) - F7: 6A (actual 16A) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620655&prj=626&rqi=cX0gpuEx2ltNXNtE98hSeA8lSM
YT1ELEC-162-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Fuel Leak_L3 | LEAK - Leak Detection |  |  | issue from L2A. permanent equipment labelling issue. attach photo once it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620650&prj=626&rqi=N24I6WrIl2GeVJIOmWILG7iWor
RT1ELEC-12-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Panel surface need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620651&prj=626&rqi=ND5l4tGnCTJABpsrtL6EiLbaDJ
RT1ELEC-12-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Missing bolt | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620653&prj=626&rqi=3ne26wVfZr0QMvPq35qRgDOa8T
RT1ELEC-12-009 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GCP) Discrepancy between drawing & actual panel length | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620658&prj=626&rqi=0vB7i5KsOGn2snZO6bYv4Y7HfM
YT1ELEC-32-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | External cable to the AC/DC converter has not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620401&prj=626&rqi=xwCKilL2sC3P4LWrvtAithKwRT
YT1ELEC-32-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | MCCB AUX 1 cable has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620398&prj=626&rqi=IBCHnoo08V8SdZHgxBZubrRokP
RT1ELEC-12-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual breaker size: - Q3: drawing 6A (actual 16A) - Q4: drawing 6A (actual 16A) - Q5: drawing 6A (actual 16A) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620509&prj=626&rqi=LMSFvG1LEi7MC6eFzenhiH81ju
RT1FD-13-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Fire Detection | equipment | ASDSP-3.10 | VES - Vesda |  |  | The equipment nameplate labels for ASDSP and PSU are incorrectly swapped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620479&prj=626&rqi=i5rvPw2BxQ7ZDt2Z7KZYxek9nO
RT1ELEC-155-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | (Issue Tx Room Area) Cable termination bolts are not in accordance with Equinix standard. No flat washer at the back side and no Belleville washer before the nut at the front side. If Belleville washer is not available, use spring washer. Please comply with Equinix standard, refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620379&prj=626&rqi=J8dbsBQLI5WEQiIjuoslsmR9RB
RT1ELEC-13-017 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual breaker capacity: - Breaker Q3: 6A actual 16A - Breaker Q4: 6A actual 16A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620381&prj=626&rqi=r4O4y8knrPTIBQwZh4JNEsBUXk
RT1ELEC-13-019 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual position. Refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620384&prj=626&rqi=ejVxFRbDhpGj726hYGyguJilkd
YT1ELEC-31-002 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | DCOS control cabling to panel 1LIBATTSYS_F_1 has not yet installed and terminated at Battery cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620392&prj=626&rqi=VuP5WcKrhxyvIZoLrvaVe0aPWk
RT1ELEC-13-018 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Missing cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620382&prj=626&rqi=GcZOgPu92QM6zRzujMooSDAxr1
YT1ELEC-32-002 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | DCOS control cabling to panel 1LIBATTSYS_F_2 has not yet installed and terminated at Battery cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620399&prj=626&rqi=piNsx7bWhBIsm43hh2MCOGXa53
RT1ELEC-155-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | (Issue Tx Room Area) Missing bonding jumper on cable containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620378&prj=626&rqi=D9Z1Ag1mPm7UWqq6nJ7cSx8IeI
RT1ELEC-149-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1MSB_C_1 to 1UPS_C_1) Busduct support is not aligned / tilted. Please adjust to ensure proper alignment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620380&prj=626&rqi=kuzJU5qvcxuyHSYQBnkCnmAp4J
RT1ELEC-155-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | (Issue Tx Room Area) Please confirm the new grounding cable tagging and ensure all grounding cable tagging is consistent as per standard. Kindly attach the latest grounding cable tagging standard document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620377&prj=626&rqi=iJnMz3MxtQ4iHwPXof8fMBeoxz
YT1ELEC-31-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | UPS temperature sensor has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620394&prj=626&rqi=TwrRJApnzQ6kjqVgl9Q5BlwuDU
YT1ELEC-31-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | DC power supply from external AC/DC converter polarity has not been verified yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620397&prj=626&rqi=ctcz3hzgKGYwcdEbXLQX5IKxs4
YT1ELEC-31-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | External cable to the AC/DC converter has not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620395&prj=626&rqi=Vf9nYi4zGqhGlQuQhTNhHprwOf
YT1ELEC-32-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | DC power supply from external AC/DC converter polarity has not been verified yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620402&prj=626&rqi=QDgihVx3RLLgZI4ctlJT3j14pD
YT1ELEC-31-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Communication cable between Module 2 & Module 3 in panel 1LIBATTSYS_F_1 not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620396&prj=626&rqi=thgjvhxEnmIeApkzk8UljCjaV6
RT1ELEC-12-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620510&prj=626&rqi=ncaEk6gsQHfZ6Tq2x88W29LYZi
RT1ELEC-13-020 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A - 1GEN_D Panel Battery Isolator) Discrepancy between drawing & actual breaker capacity: - Breaker F3: 25A actual 10A - Breaker F4: 25A actual 10A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620385&prj=626&rqi=ynQ5D9pUu3yxGF957PpgkCKHc9
YT1ELEC-32-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | UPS temperature sensor has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620400&prj=626&rqi=CfNKCD9SVsn5rpGrhjN5WeysR2
YT1ELEC-31-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | MCCB AUX 1 cable has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620389&prj=626&rqi=PpUt6blnhBPiv5GP0ypG6WcJDA
RT1ELEC-12-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Isolator) Discrepancy between drawing & actual position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620512&prj=626&rqi=ZUGTdP532IAyoOQLfCBr9Y7oT9
RT1ELEC-54-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-03 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Dents & scratches on panel surface observed, need touchup | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620200&prj=626&rqi=iUqOPJN1m50azJl2d3VcXLzTbn
RT1ELEC-54-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-03 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Discrepancy between drawing & actual position. Refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620204&prj=626&rqi=xA8shRsaVlsTqp2EXlgjIJLCHo
RT1ELEC-54-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-03 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Missing bolt on back side panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620202&prj=626&rqi=YRNdEbBVIV94eNoLmE7BqK9KzR
RT1ELEC-54-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Drawing not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620203&prj=626&rqi=goSK9SpTqDB8A3emPSm0GfcMVm
RT1ELEC-54-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Please ensure all ACB & HMI are properly protected to prevent construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620201&prj=626&rqi=oiCDuhTFw7zPmd0LT5vPYR3hBB
YT1MECH-108-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) need to install vynil cable accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619970&prj=626&rqi=YIYdsqCNSIAVHkpWf9WprWW8al
YT1MECH-108-007 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable AHF to Chiller Pump) provide vynil cable and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619979&prj=626&rqi=CS8QeCmyx3RVIK5n2bZyqsS2pZ
YT1MECH-108-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) provide cable label inside isolator switch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619971&prj=626&rqi=p2EqvDGMKq2ckDvhC2GnzLMapx
YT1MECH-108-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) Ensure that the cable routing is uniform and consistent for all isolator switches, pay attention to cable neatness, disconnect cable which unused and isolated accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619972&prj=626&rqi=j8l6rhhbp9VhrhIe2UdsGaP81s
YT1MECH-109-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable AHF to Chiller Pump) provide vynil cable and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619980&prj=626&rqi=AQYKIVkfkG7qcvFNjiwsrX1UJh
YT1MECH-109-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) need to install vynil cable accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619974&prj=626&rqi=ZksOqm5AAddIQJU4GPBCca71sk
YT1MECH-109-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) provide cable labelling inside iso switch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619975&prj=626&rqi=lQmoNgy7Xb4jyWPxtsleZ5HeJK
YT1MECH-109-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) Ensure that the cable routing is uniform and consistent for all isolator switches, pay attention to cable neatness, disconnect cable which unused and isolated accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619973&prj=626&rqi=JiNdIJtfCIYmktH2sVyp5eJLIT
YT1MECH-107-007 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable AHF to Chiller Pump) provide vynil cable and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619978&prj=626&rqi=Xe11BkjN76GVEGAwg2dIkhamdR
RT1ELEC-158-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L4 | DB - Distribution Boards |  |  | Discrepancy between drawing & actual position for grounding & neutral location inside the panel (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619985&prj=626&rqi=yYvggA83esT0xbG2DPbHX4XrDy
RT1ELEC-158-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L4 | DB - Distribution Boards |  |  | Minor dents need to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619984&prj=626&rqi=pGqj5DMHOc9vnOhmVewBUwfeMz
YT1MECH-110-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable AHF to Chiller Pump) provide vynil cable and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619981&prj=626&rqi=64kzqItNSxzYTfyIPQqhv59Ggn
RT1ELEC-158-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L4 | DB - Distribution Boards |  |  | Please confirm the correct equipment tagging as per design: 1DB_DALI_L4.1 or 1DB_DALI_L4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619982&prj=626&rqi=N2fCM5m9MEdhcjarYTFrpk2XFY
RT1ELEC-158-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L4 | DB - Distribution Boards |  |  | Each component shall have two labels (terminal and component body). Proper component labelling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619983&prj=626&rqi=WTKeqMjAo5Dz8v6jVvDuqt9pTB
YT1MECH-28-004 | JK01-2 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | inside the rusty chiller pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619859&prj=626&rqi=Y9K7XvRC0WvQ7Tdt5GWXBuXDjO
YT1MECH-31-002 | JK01-2 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | inside the rusty chiller pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619855&prj=626&rqi=fuQvf13ty1n6RdfujeOmbSBrRC
YT1MECH-30-001 | JK01-2 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | inside the rusty chiller pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619852&prj=626&rqi=CftWnvKShqInM1AB9mkV0NdrFE
RT1ELEC-122-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | Cable tubing/tagging faded need to replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619812&prj=626&rqi=jTdemPGJAsXmBosOLR2tJVn0Cj
YT1MECH-10-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_C_53 | EF - Exhaust Fan |  |  | YT tagging status changed, some documents missing 1. Cx Report 2. Ducting visual inspection report 3. Grounding test report 4. O&M | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619825&prj=626&rqi=jeb4BZZe75Bpq83rQUm97fB2pD
RT1ELEC-14-017 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Please update drawing to match with actual door component location | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619837&prj=626&rqi=0CInPrfBCbVye1aQWLSDqsajY0
RT1ELEC-14-015 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual position. Refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619834&prj=626&rqi=7gqpLMNF4xCPn60n4MjcrWzwcX
YT1MECH-11-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_C_54 | EF - Exhaust Fan |  |  | YT tagging status changed, some documents missing 1. Cx Report 2. Ducting visual inspection report 3. Grounding test report 4. O&M | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619827&prj=626&rqi=H6965VdKRl3XI5Qxi534Sfciii
YT1MECH-30-002 | JK01-2 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | inside the rusty chiller pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619860&prj=626&rqi=twR42tUt9yRDmlGfWj8uMkSWzn
YT1MECH-13-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | YT tagging status changed, some documents missing 1. Cx Report 2. Ducting visual inspection report 3. Grounding test report 4. O&M | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619826&prj=626&rqi=9r8ZY37P0zUWils2IQa4xhLpIY
YT1MECH-14-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_D_53 | EF - Exhaust Fan |  |  | YT tagging status changed, some documents missing 1. Cx Report 2. Ducting visual inspection report 3. Grounding test report 4. O&M | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619821&prj=626&rqi=W5TiGMkNHGCKKsUPs7PqLhkyD0
RT1ELEC-14-016 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy breaker size rating on Q3, Q4, Q5. In drawing 6A actual 16A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619836&prj=626&rqi=3FOagKgrN0PUpRUXKzmkh0Voyt
RT1ELEC-14-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Isolator) Please provide protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619830&prj=626&rqi=L9y29W8HV4c40KGZfPoq0tk6dh
YT1MECH-29-001 | JK01-2 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | inside the rusty chiller pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619861&prj=626&rqi=yTcbKevIPvoSaHfTFyP48GgEqZ
RT1ELEC-14-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Isolator) Please provide drawing pocket & as built drawing in panel door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619829&prj=626&rqi=XL6fpOBZdcGYoj0UeGbC0cw7Er
YT1MECH-107-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) Ensure that the cable routing is uniform and consistent for all isolator switches, pay attention to cable neatness, disconnect cable which unused and isolated accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619847&prj=626&rqi=EcRRy2Mgpfq0czly18EVjorVff
YT1MECH-107-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) need to install vynil cable accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619841&prj=626&rqi=bNNcUnsIUTz3RXiFM45mJfgMHP
YT1MECH-107-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) need to install labelling inside isolator switch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619845&prj=626&rqi=2tBTD88D9iK5KTs0bOj4asXQUR
YT1ELEC-143-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue from CxL2A BD 1UDP_C_2 to 1STSSB_C_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619542&prj=626&rqi=DiQAZcuBUb79yTHofyy6LE1n3p
YT1ELEC-164-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | (Issue CxL2A LV Cable) Several cable tags are mismatched (should be labeled as CA_B_1 but tagged as CA_B_2). Kindly recheck all and correct accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619666&prj=626&rqi=gNhrbfB83KbZPcTfBMUvVZc89g
YT1ELEC-164-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | (Issue CxL2A LV Cable) Incorrect cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619665&prj=626&rqi=CIXCRW6HZZWrNbe9GTkL2QmBtC
YT1ELEC-164-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | (Issue CxL2A LV Cable) Bolt supports have not been properly tightened & unistrut support is found cut. Please adjust to match other unistrut installations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619667&prj=626&rqi=xIdT4dXXrqk1dYYFBvwLyAxOgx
YT1ELEC-164-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | (Issue CxL2A LV Cable) Several cable gland caps are damaged (torn) and not properly covering the gland. Replace all damaged gland caps and ensure proper installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619671&prj=626&rqi=ZIVeKRtRiBs2FWo6HKDfZ0ogRw
YT1ELEC-164-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | (Issue CxL2A LV Cable) Cable conductor is still exposed. Please ensure proper termination is completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619664&prj=626&rqi=qx4f4wvMQ6UpZOETRnamKig6VB
YT1ELEC-142-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_2 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue CxL2A BD 1UDP_B_2 to 1STSSB_B_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619663&prj=626&rqi=28WR2B9Cju6oYkQml5EweJrmWW
RT1ELEC-157-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L3 | DB - Distribution Boards |  |  | Each component shall have two labels (terminal & component body). Proper labelling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619685&prj=626&rqi=q4nKeP7aTQSKkGSmnh1WQ03tpp
RT1ELEC-157-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L3 | DB - Distribution Boards |  |  | Discrepancy between drawing & actual position. Refer to the attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619682&prj=626&rqi=eKfWISO9Ew3BSkcnBSlzaGkmlm
RT1ELEC-157-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L3 | DB - Distribution Boards |  |  | Please confirm the correct equipment tagging as per design: 1DB_DALI_L3.1 or 1DB_DALI_L3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619686&prj=626&rqi=m57PiqXLSYS0FcHKIWzOxk18LH
YT1MECH-36-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tray covers are not yet installed. Please ensure all covers are properly closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619668&prj=626&rqi=UrA3jcIEQHjiRXdQhznNtAtbzf
YT1ELEC-143-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue CxL2A BD MLTX_D to MSB_D) Sleeve and firestop at wall penetration are not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619558&prj=626&rqi=v8fx4q20xrxkhgx7Loryd0MYtd
YT1ELEC-143-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue CxL2A BD 1UDP_D_2 to 1STSSB_D_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619560&prj=626&rqi=7sFDmfm1IvV1SlzktlhxxvDb0Z
RT1ELEC-122-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Please remove all temporary markings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619672&prj=626&rqi=Dd2hKRafKy6l8I8Y6xaGInD992
YT1MECH-42-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tray end sections are open. Please confirm and install end caps where required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619670&prj=626&rqi=K6qlxhMyRLaYC4oyPsbuHR95LH
RT1ELEC-122-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Several cable gland caps are damaged (torn) and not properly covering the gland. Replace all damaged gland caps and ensure proper installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619673&prj=626&rqi=b5Ugj0kOQGWICKJBz1MojLs5c1
RT1DCOS-15-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_1_SCP_07 | DCOS - Control Panels |  |  | Provide MoS CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619477&prj=626&rqi=DjisuLQEPLHUgPTLiNKTf6Uvlc
YT1MECH-16-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | Provide calibration certificate of test tools been used for CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619462&prj=626&rqi=4xjH5rpzQq86TJl3TI2L44AA4G
YT1MECH-8-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_B_32 | EF - Exhaust Fan |  |  | Provide MoS CxL3 doc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619458&prj=626&rqi=sHe4FbbDe4bZ6Almob577hiEOK
YT1MECH-17-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_F_74 | EF - Exhaust Fan |  |  | Provide calibration certificate of test tool used for CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619465&prj=626&rqi=EdRBaoC0w9SCaDeGRhLDkaM3PP
RT1DCOS-15-001 | JK01-2 | APAC | Closed | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Controls | equipment | 1DCOS_1_SCP_07 | DCOS - Control Panels |  |  | Please add label for incoming power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619475&prj=626&rqi=T4DkWlpkDp8X8ucNAZiwQf1lZL
YT1MECH-7-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_B_31 | EF - Exhaust Fan |  |  | Provide MoS CxL3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619457&prj=626&rqi=S3sLox3skcPRMfsovLr9W5vD54
YT1MECH-8-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_B_32 | EF - Exhaust Fan |  |  | Provide calibration certificate of test tools been used in CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619460&prj=626&rqi=GoZ1OpqUc6t3BtN7vW2dqO9Cwf
YT1MECH-7-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_B_31 | EF - Exhaust Fan |  |  | Upload calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619459&prj=626&rqi=f1XHuQMVJ3EhIpenY6AHHz2Mfl
YT1MECH-17-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_F_74 | EF - Exhaust Fan |  |  | Provide MoS CxL3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619464&prj=626&rqi=8CYLOKJxvesBFtH4IrBNcubyry
YT1ELEC-10-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Input/Output PLC verification test has not yet been conducted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619282&prj=626&rqi=kFYUyYF5wuAy2oO9xZMUPwr79E
RT1ELEC-148-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_2 | BUST - Bus Duct Temperature Monitoring |  |  | [Issue BD 1UPS_B_1 to 1UDP_B_2] Please clarify with engineering, busduct support location different from the drawing. Confirm if this is approved and safe? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619293&prj=626&rqi=QyyFKtsizQMlfCIZF0wutLJg5W
YT1ELEC-10-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | MCCB Q1-4 long time trip test result indicates a failure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619281&prj=626&rqi=SJYH6xeG4CSUukhVUXozq4HaAo
YT1ELEC-10-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Short time protection test for breakers Q1â€“3 was skipped during testing. Kindly perform the required test to verify proper protection functionality | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619280&prj=626&rqi=FLrXJj0tWfvafH0obr0NkepNO2
RT1ELEC-148-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_2 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1UPS_B_1 to 1UDP_B_2) Laser measurement shows about 15 mm elevation difference (not level). Please adjust to make it straight and level. Refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619292&prj=626&rqi=P3hU6ZRINzrsxj9Ssh5GTU1wPE
YT1MECH-111-003 | JK01-2 | APAC | Closed | P2 Medium CX | JulianJensen@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_2.01 (Existing) | PAV - Pre-Action Valve |  |  | Pressure drop during pipe hydrostatic pressure test (STS Room B & C-Wall B). Refer to the attached image. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619170&prj=626&rqi=XHhHnr69TvTrYUVssoXs4QRu8P
GI-018 | JK01-2 | APAC | Open | P3 Low DCOS | dickyhermawan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS | [6 empty] | Configuration "Asset Data" is currently in progress by DCOS program Orise. After finish need to verify with CTA Note: - The Maximo asset data from GC has been completed, and Orise has confirmed that the data is complete, except for the ID numbers, which will be provided by the Ops Equinix team. FG GC issue GI-016 (Closed) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619210&prj=626&rqi=Sv9TrDIdAomKQgwOyWqzHicW3o
YT1MECH-18-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | Provide as built drawing because there was discrepancy between shop drawing and actual layout | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619171&prj=626&rqi=gNUDDynNyNcUAOxAQGF1C55e3l
RT1FD-3-001 | JK01-2 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Fire Detection | equipment | 1FAS_4 | FP - Fire Panel |  |  | Spilled white paint on Fire Alarm and the cable cover pipe. Refer to the attached images. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618994&prj=626&rqi=kbP1ag7GAX6mcGK0lpTKIxQCdS
RT1ELEC-15-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Drawing and actual panel are not the same: location of voltage and ammeter is different. Please update the drawing to match actual condition | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619047&prj=626&rqi=bKU5l2nJpIIoszwlUeIYC9WQmG
RT1ELEC-15-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Drawing not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619023&prj=626&rqi=Ec6hrdZtucZ1mpOSiG72rlpKSu
RT1ELEC-15-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Based on the RFIT inspection results, a discrepancy was identified between the drawing and the actual panel position (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619036&prj=626&rqi=9EO0SgLCNchm0rltdvSs0uV8Hg
RT1ELEC-15-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add clear labels for ammeter and battery to show which one is Battery 1 and Battery 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619050&prj=626&rqi=nb5nkj6jv4LR9eiTnoFaGDongY
RT1ELEC-15-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Cable entry/exit location is not in accordance with the approved drawing. As per drawing, cable routing shall be from the bottom of the panel. However, actual installation is from the top of the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619053&prj=626&rqi=V6welSD8bzdfR5Trxb4nyjd1qn
RT1ELEC-15-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add component RSH1 & RSH2 in the drawing component list | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619051&prj=626&rqi=y8oYKlO48b4r3uiEbDvqSHy1ky
RT1ELEC-15-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add labels above pilot lamps for â€œBattery Charger 1â€ and â€œBattery Charger 2â€ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619049&prj=626&rqi=b7inB6jfzt4NHlehXlbIZQCvPb
RT1ELEC-15-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Incorrect generator rating on the drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619030&prj=626&rqi=NCz5CUCeSJzkXsduGw7K3Ftdm2
RT1ELEC-15-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Missing bolt on the panel body | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619021&prj=626&rqi=ByOp0v5CHo3XoZddNUIQ3K11DW
RT1ELEC-15-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Minor dent found on panel surface, please touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619022&prj=626&rqi=YowvaoxObrrkkEoO7hmyghecbc
RT1ELEC-15-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Discrepancy between drawing and actual breaker capacity: - Breaker F7: 6A (actual 16A) - Breaker F5: 5A (actual 10A) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619033&prj=626&rqi=YHKPEe1LfpdnvwN65GAcJfkVf3
RT1ELEC-15-015 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add temporary protection to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619054&prj=626&rqi=x8nGOETZ463TlBpoiXngzLnzYp
RT1ELEC-15-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A GPC Panel) Please add temporary protection to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619044&prj=626&rqi=BAQKIjUfqxO0gKQTEzlhq2Bzga
RT1ELEC-15-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Rear anchor bolts have not been torque tightened | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619020&prj=626&rqi=n8BLy7OOdcWdZHZfOZhdVIBBxA
RT1ELEC-15-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Incorrect generator rating at panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619019&prj=626&rqi=jlVGJHLJyerncOzSVEvposUM3J
RT1MECH-131-001 | JK01-2 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_2.01 (Existing) | PAV - Pre-Action Valve |  |  | Pipe has white paint residue. Refer to the attached image. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618991&prj=626&rqi=Rm80GRgn4mIkWdTY4t8HNPQvB4
RT1FD-3-002 | JK01-2 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | 1FAS_4 | FP - Fire Panel |  |  | Cable tagging not installed. Refer to the attached image. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618997&prj=626&rqi=tG3zfg9LraNEVxwG4jnEYZHz5o
RT1ELEC-134-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1WLEAK_L2 | LEAK - Leak Detection |  |  | permanent equipment labelling issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618811&prj=626&rqi=r8MdU794dFSCQXUUmDVBBJeJCa
YT1ELEC-30-002 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | DCOS control cabling to panel 1LIBATTSYS_C_2 has not yet been installed and terminated at Battery Cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618845&prj=626&rqi=p6EBkaE6sXTEohuQlgytdoPa1s
YT1ELEC-29-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | MCCB AUX 1 cable has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618834&prj=626&rqi=Kp0p1Xhx5j8Oo9zYZi67k7tJu0
YT1ELEC-29-003 | JK01-2 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | DCOS control cabling to panel 1LIBATTSYS_C_1 has not yet been installed and terminated at Battery Cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618835&prj=626&rqi=ho5DF0NR6GJxwTHvwko9aqOQG3
RT1ELEC-134-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1WLEAK_L2 | LEAK - Leak Detection |  |  | need to upload document shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618810&prj=626&rqi=juVTrRmSaS2XlLP3biBDDbfAbo
YT1ELEC-30-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | MCCB AUX 1 cable has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618843&prj=626&rqi=g3sgd71ehJfMnm4m9kPnUZMNq6
YT1ELEC-30-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | UPS temperature sensor has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618847&prj=626&rqi=DtPQQ38EE3JQc5TfWR7TZT8ocg
YT1ELEC-30-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | External cable to the AC/DC converter has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618848&prj=626&rqi=pJVZEsGQx3gMkaBdmBWoXdOkVV
YT1ELEC-29-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Communication cable between Module 2 and Module 3 in panel 1LIBATTSYS_C_1 has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618839&prj=626&rqi=XRLznyEBpUNoaTT6QrvgbbmEMG
YT1ELEC-29-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | UPS temperature sensor has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618836&prj=626&rqi=wJh9ZqFedPsUG955ZJeaVNIsYx
YT1ELEC-29-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | External cable to the AC/DC converter has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618837&prj=626&rqi=BqktiBLAhTJXRtfwKPTrtkXFBW
YT1ELEC-29-001 | JK01-2 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | There is dust inside the battery rack. Refer to the attached image. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618832&prj=626&rqi=6EwBZNk0lM8pFZfCeBtNSiN6ad
RT1ELEC-168-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Fuel Leak_L3 | LEAK - Leak Detection |  |  | document related need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618812&prj=626&rqi=SxTqaHuh4u5jY42TfNfHvKsRxE
RT1ELEC-168-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1Fuel Leak_L3 | LEAK - Leak Detection |  |  | Permanent equipment nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618813&prj=626&rqi=o5PE47gKl7zij710kpFHfABTSY
YT1FD-24-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.02 | VES - Vesda |  |  | related documents need to upload on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618678&prj=626&rqi=ufmaYbkmqgu9zqRplFZ2c1vtwz
YT1FD-28-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Component/Equipment Failure | Commissioning | Fire Detection | equipment | ASDSP-5.07 | VES - Vesda |  |  | related documents need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618689&prj=626&rqi=eMVDleGH7Xp1kjf14KwglsbsPL
RT1MECH-9-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | provide airflow direction | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618700&prj=626&rqi=1LbaZwKTHh5bZCrtclP1RS8w7a
RT1FD-25-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.03 | VES - Vesda |  |  | report L2A need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618682&prj=626&rqi=1V1SH42vypGRqElHRp2k0gzxg2
RT1MECH-12-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_D_41 | EF - Exhaust Fan |  |  | provide airflow direction | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618705&prj=626&rqi=7otm7hYRcrzPbGqjb7l3hCsMZr
RT1MECH-12-003 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1EF_D_41 | EF - Exhaust Fan |  |  | Exhaust Fan ducting not connected yet to opening and wall penetration not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618704&prj=626&rqi=1oPlq47JThwmo5Q9gczVy8CjVz
RT1MECH-9-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | need to upload related documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618696&prj=626&rqi=Ezn9ZE4XXudnmBqsFAvbeVnIJ9
RT1MECH-12-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1EF_D_41 | EF - Exhaust Fan |  |  | vibration mounting need to adjust because it's not straight | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618702&prj=626&rqi=yv1FVDuydsy2gVTo7iTKVHLNoq
RT1MECH-12-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_D_41 | EF - Exhaust Fan |  |  | need to upload related document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618703&prj=626&rqi=nwxaiH6PNnYVzGrky624S9yKO3
YT1ELEC-4-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Control cable signal testing for alarm and trip contacts cannot be performed. GC to confirm the cable routing and termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618718&prj=626&rqi=YAw1gqGdkilAU5o6IXoKCqkHXo
YT1FD-26-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.04 | VES - Vesda |  |  | related documents need to upload on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618685&prj=626&rqi=xcPmvz35Rh2xrIdLqDcHCXXpi6
RT1MECH-9-002 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | Exhaust Fan ducting not connected yet to the opening wall and Wall Penetration not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618697&prj=626&rqi=7LJBArhyjzJcbEb2PJrDNaQPMx
YT1FD-25-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.03 | VES - Vesda |  |  | issue and document report L2A need to comply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618684&prj=626&rqi=9xJ1e27JY7m2r0Ya8de5OhY3T5
YT1ELEC-2-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Control cable signal testing for alarm and trip contacts cannot be carried out. GC to confirm the cable routing and termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618714&prj=626&rqi=YUEFF6oUCwG1XPJZAFrLHOn1RE
YT1MECH-28-001 | JK01-2 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Chiller side panel is dirty. Refer to the attached image | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618728&prj=626&rqi=rWTfsnAsPKjxRbR4igFiT4m1T2
YT1ELEC-2-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Simulated trip from thermal relay to VCB cannot be performed due to incorrect wiring. GC to rectify the control wiring between MLTX and RMU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618720&prj=626&rqi=iO84OQ2ltU00NR6CXfIA2zzNBd
YT1FD-28-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.07 | VES - Vesda |  |  | L2A issue and report document need to comply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618690&prj=626&rqi=mCYqhsPATg7XHrQlr4cCVCji87
YT1FD-29-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.08 | VES - Vesda |  |  | related documents need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618693&prj=626&rqi=SKKki7WeLAhlm1mu6pkSGDKHqh
YT1ELEC-3-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Control cable signal testing for alarm and trip contacts cannot be performed. GC to confirm the cable routing and termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618717&prj=626&rqi=3myyZjhoWJNpTfBByzZJsK64os
RT1FD-24-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.02 | VES - Vesda |  |  | issue and report document L2A need to comply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618680&prj=626&rqi=RXstvu1fHarGlItUXVSBtLXVuG
YT1FD-25-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.03 | VES - Vesda |  |  | related documents need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618683&prj=626&rqi=ZdlQ2u7J7b1iWNElIb2aeAU44v
YT1FD-27-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.05 | VES - Vesda |  |  | L2A reports and issue need to close and comply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618688&prj=626&rqi=ucARh5ITWBvdfB5ogYWpAsvV0E
YT1MECH-28-003 | JK01-2 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Plastic cover not installed. Refer to the attached image. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618730&prj=626&rqi=9tWsM37eKh9wL6Hm0fHNFm6rTg
YT1FD-26-002 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.04 | VES - Vesda |  |  | issue and L2A report need to close and comply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618686&prj=626&rqi=IV5uecf5Zv01IMszdXHmCUlklB
YT1ELEC-5-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Control cable signal testing for alarm and trip contacts cannot be performed. GC to confirm the cable routing and termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618719&prj=626&rqi=dC7AWDKNYX3eJahss0f5DXXSAW
YT1MECH-28-002 | JK01-2 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Paint is not smooth. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618729&prj=626&rqi=llV3LOUVxjBvnji0PgTtCKqT0f
YT1FD-27-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.05 | VES - Vesda |  |  | document related need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618687&prj=626&rqi=yeMvlS65IVBfwHjNQqjgv6mQev
YT1FD-29-001 | JK01-2 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-5.08 | VES - Vesda |  |  | L2A issue and report document need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618691&prj=626&rqi=SIKD2u0WaBxWnrto0ymCxX0SuT
YT1ELEC-2-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Point to point testing for earth cables cannot be performed as the grounding cables have not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618713&prj=626&rqi=IqII8UER1bYcPqHLshx4fmy9pq
RT1ELEC-1-022 | JK01-2 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (BTU Issue); Missing washers on cover panel. Refer to the attached images. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618709&prj=626&rqi=57ysJpNM5NQKVk5E6Om1teRa6z
RT1ELEC-13-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add clear labels for ammeter and battery to show which one is Battery 1 and Battery 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618659&prj=626&rqi=M10X7UqnoXautwVWsA8kqmxXNZ
RT1ELEC-156-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Please confirm the required torque value for the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618642&prj=626&rqi=D2qcEgnIAelKmYiigRk4gj29gz
RT1ELEC-161-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Please confirm the required torque value for the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618623&prj=626&rqi=0E52IVrJPuRUpYKQ68yuk7JS0c
RT1ELEC-161-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Please upload factory test data document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618618&prj=626&rqi=AfJ2H8PwgDYtrKRUPHdNHLbdqy
RT1ELEC-13-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Missing bolts on the panel body | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618649&prj=626&rqi=8J0hGWI1kmaAp02VE7PPOc9cHr
RT1ELEC-13-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Dirt and dents found on panel surface, please clean and perform touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618648&prj=626&rqi=pbrRGwovhRp72AXSuaPIZ2LXBT
RT1ELEC-13-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Rear anchor bolts have not been torque tightened | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618653&prj=626&rqi=ws6qg5x1R1EwkRFscOTlXWj3az
RT1ELEC-13-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Discrepancy between drawing and actual panel position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618654&prj=626&rqi=MEKdhZBE073fF5ZynxDZAwlmdQ
RT1ELEC-156-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Grounding cable at panel door still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618640&prj=626&rqi=o9VS8hyfzagKmIIXxMq1sUbA65
RT1ELEC-159-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Internal panel bolts are still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618632&prj=626&rqi=q1l5y5sf9y1dTbGKwDmDMZYHSj
RT1ELEC-13-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Drawing and actual panel are not the same: location of voltage and ammeter is different. Please update the drawing to match actual condition | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618657&prj=626&rqi=Ig7ariD1de29VOSmkzuHXZfqyG
RT1ELEC-13-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Length of panel actual 1480mm, please revise drawing panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618655&prj=626&rqi=gkWfkPknggzkvrw4CSOhrFZTSg
RT1ELEC-13-016 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please provide temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618662&prj=626&rqi=TFkuckTfYUjA8giIO2DlWS7wvE
RT1ELEC-13-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Panel requires proper cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618650&prj=626&rqi=yF0WMEQlOK4CKF2nWT3lPV3HpC
RT1ELEC-159-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Please upload factory test data document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618628&prj=626&rqi=ke25AJMAiHgwqaKQnwXooXZyNz
RT1ELEC-159-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Each component shall have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618630&prj=626&rqi=vgU102zPUFxlx6qxgdrlk5MJP9
RT1ELEC-159-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Please confirm the required torque value for the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618633&prj=626&rqi=IvDemrhCya7MtvGUJevSfxn4jB
RT1ELEC-159-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Please provide temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618634&prj=626&rqi=kBYckuWh0Vul9x86w7hHUmjNXW
RT1ELEC-156-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Each component shall have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618638&prj=626&rqi=NtQN1QJ0LUKrEjzRLI2MDmlF02
RT1ELEC-159-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Please confirm the correct equipment tagging as per design: 1DB_DALI_L5.1 or 1DB_DALI_L5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618629&prj=626&rqi=JjHjyXnHJMfbKVAgP2kVV5rvRj
RT1ELEC-156-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Please confirm the correct equipment tagging as per design: 1DB_DALI_L2.1 or 1DB_DALI_L2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618637&prj=626&rqi=qEUEQEcYAshfvntL05dXJM32bb
RT1ELEC-13-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Acrylic panel broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618651&prj=626&rqi=hOwqfXwq2zCEs6fW6Bo3LEE1IG
RT1ELEC-161-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Internal panel bolts are still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618622&prj=626&rqi=aOLKfTUTVguXUsbgqo9uITsCvG
RT1ELEC-13-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Incorrect label of capacity generator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618652&prj=626&rqi=Y0VLPRdUS9c70wxQs3y4WqOnoR
RT1ELEC-13-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Please provide temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618656&prj=626&rqi=FKTpTnHwR2oObtpN69QqQw5QJ3
RT1ELEC-159-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Grounding cable at panel door still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618631&prj=626&rqi=6DHeHGd3PRwgDuZYRb4qmEOYa5
RT1ELEC-13-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add component RSH1 & RSH2 in the drawing component list | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618660&prj=626&rqi=VRSYkM93QXi9iY5twX5MnBR3YW
RT1ELEC-161-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Each component shall have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618620&prj=626&rqi=0TjAlWcKL59NqXK3n53RSw6wgr
RT1ELEC-156-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Please upload factory test data document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618636&prj=626&rqi=yYStm9I8ffgltnKJR57MHgFkgO
RT1ELEC-161-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Panel surface is stained. Please clean the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618624&prj=626&rqi=o9XUbu8vm26olE48GlHUCnLPPq
RT1ELEC-13-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add labels above pilot lamps for â€œBattery Charger 1â€ and â€œBattery Charger 2â€ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618658&prj=626&rqi=ImNj8W1wJBtKQA0EU0gScRMFcv
RT1ELEC-161-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Please provide temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618626&prj=626&rqi=o6vUJpuIdnNnSvWJW5AnFAJbAV
RT1ELEC-161-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | There is a discrepancy between the drawing and the actual installation position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618625&prj=626&rqi=G7fTzsXKNvGiraWvwZ9ndVapim
RT1ELEC-156-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Internal panel bolts are still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618641&prj=626&rqi=eY9V9oc1D1zUpNutqVzxwWDI4o
RT1ELEC-156-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Please provide temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618644&prj=626&rqi=GLkZ2xDvcxmuYqaFjXCYsBL6it
RT1ELEC-13-015 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) GC please clarify why the positions of DB Aux panel and Dual Battery Charger panel are swapped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618661&prj=626&rqi=TwdOcT6mAQvN5IYGzqYYPfCcRJ
RT1ELEC-161-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Please confirm the correct equipment tagging as per design: 1DB_DALI_L7.1 or 1DB_DALI_L7 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618619&prj=626&rqi=orTXMmpCv0ZvEjETTNDL6s9Zws
RT1ELEC-161-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Grounding cable at panel door still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618621&prj=626&rqi=hihm6xkrtqwThnoaft8V1ZQYen
RT1ELEC-156-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Please clarify the panel location for 1DB_DALI_L2 in the drawing. The yellow color means Phase P1, not Phase 2. If it should be Phase 2, please update the drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618643&prj=626&rqi=9kLb768gc8Cm5Hiq4Qa1nAG76S
RT1MECH-5-008 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Discrepancy between shop drawing and actual measurement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618459&prj=626&rqi=UEHxVmb5hFi27kXEPq4M3CXe6j
RT1MECH-4-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Fusible link cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618450&prj=626&rqi=VgeV5YANvW4eaDbfCLfD4rRnSy
RT1MECH-5-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Fusible link cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618457&prj=626&rqi=p2SLjUj6Tavt1ePSBnBGbWskK7
RT1MECH-4-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Need to upload document related to the checklist; SoO, schematic drawing, O&M manuals, etc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618446&prj=626&rqi=Y6texKzdpHpqRIRmsZujyRZgFO
RT1MECH-5-007 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Solenoid cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618458&prj=626&rqi=3d4TQiNAbqL5Vp76FJuIDhBZPM
RT1MECH-5-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Need to upload document related to the checklist; SoO, schematic drawing, O&M manuals, etc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618453&prj=626&rqi=IQI1iYBHUgePseS59IKRCgARai
RT1MECH-4-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Pipe overflow has not connected yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618448&prj=626&rqi=UrHuh2EMglj0pwhbcSZoSlkwBO
RT1MECH-4-008 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Discrepancy between shop drawing and actual measurement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618452&prj=626&rqi=EhCMku69I9pAFUikoduOouRUvB
RT1MECH-4-007 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Solenoid cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618451&prj=626&rqi=AADHjbLNUv6nVIYGXNS8NQRfUI
RT1ELEC-14-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add labels above pilot lamps for â€œBattery Charger 1â€ and â€œBattery Charger 2â€ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618370&prj=626&rqi=iHO36dzpd1mDWNVYRHzdamvcL0
RT1MECH-4-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Equipment permanent label and tagging valve issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618447&prj=626&rqi=pjfHjQSMg6JpANMuHhLsUd3DQs
RT1MECH-5-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Pipework needs to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618456&prj=626&rqi=ULyW4ilJfA6bwDxP9Ox3M3wktT
RT1ELEC-14-011 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) GC please clarify why the positions of DB Aux panel and Dual Battery Charger panel are swapped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618372&prj=626&rqi=QtQdV8w6LUQBfEXx5x988ggKGz
RT1ELEC-14-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Minor dents found, please do touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618373&prj=626&rqi=XMycAP9iqqvpRW8mRRlACKMVd2
GI-017 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [6 empty] | (Issue CxL2A MV Cable RMU C to F) Sleeve and firestop at wall penetrations have not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618460&prj=626&rqi=oc4l0q645Yu1tg2Ij3bSquWWlB
RT1ELEC-14-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add clear labels for ammeter and battery to show which one is Battery 1 and Battery 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618371&prj=626&rqi=jx1mRu05SKRWgA3JRz5V97Vnm6
RT1MECH-4-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Pipework needs to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618449&prj=626&rqi=aXPO1CCKd1c1X4Ft1e2J6BDwus
RT1MECH-5-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Equipment permanent label and tagging valve issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618454&prj=626&rqi=fzNAiZVYaONRKIawB2Oee2ZRs3
RT1MECH-5-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Pipe overflow has not connected yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618455&prj=626&rqi=ziItsNCRfUXBk7hDMKzybZ5mtH
RT1ELEC-14-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Drawing and actual panel are not the same: location of voltage and ammeter is different. Please update the drawing to match actual condition | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618369&prj=626&rqi=gCHeFPTYdYP2FzTwmI38gLIW4V
RT1ELEC-14-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Discrepancy between drawing and actual panel position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618368&prj=626&rqi=LXVNRilDVpssKgVOrCHLuT8uHm
RT1ELEC-59-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Minor dents & scratches require touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618224&prj=626&rqi=0TRTa2wbG2eB3VBSGTjL50HKsD
RT1MECH-35-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | issue from Dirt Separator; paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618318&prj=626&rqi=NMW6ITMp8xOVe8d2u9xr7oC5nH
RT1ELEC-23-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Minor dents require touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618269&prj=626&rqi=IyuBf4QZnVUXZEdiIhnGodRJoZ
RT1ELEC-23-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Deep cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618272&prj=626&rqi=4sLtoJhshOHivlFvIIUc5FExqR
RT1ELEC-148-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_2 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1UDP_B_2 to 1STSSB_B_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618280&prj=626&rqi=rrfHuGwSN3iIsJSCdbC6ii71bx
RT1ELEC-59-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Ensure all ACB & HMI are properly protected from construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618225&prj=626&rqi=MzEdvdxYdnukP0uwD8aFUr7Wd8
YT1ELEC-4-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Component/Equipment Failure | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Testing of the RMU control box panel could not be performed due to a fault in VCB. LS to clarify and take corrective action to resolve this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618363&prj=626&rqi=POlAyTTquZYJPZwTynOHVrBV3h
RT1MECH-3-008 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | Need to upload document related to the checklist; SoO, schematic drawing, O&M manuals, etc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618361&prj=626&rqi=HO96cjVdo3efEZgaxxqDMz28Ls
RT1ELEC-14-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Panel requires proper cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618365&prj=626&rqi=yqG7M5UxS2vgP1Z0yyvNl0PqSJ
RT1MECH-3-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | Pipe overflow has not connected yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618349&prj=626&rqi=GKrevd0dE90XrgZ75jB8WNJjyl
RT1ELEC-59-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Provide temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618226&prj=626&rqi=VCQuc2EIoFcK2m1ihmumqhkspA
RT1MECH-33-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Dirt Air Separator issue; paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618482&prj=626&rqi=ukIyJa0vgTLoz8LOorY9xEu3h2
RT1ELEC-14-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Dirt and dents found on panel surface, please clean and perform touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618364&prj=626&rqi=jJ03jpmbDcFMZmQibV0b3SapT3
RT1MECH-28-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | DB Panel issue; Cable labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618358&prj=626&rqi=2qc27TSc5fVtikoYQvUwrsNFjb
RT1ELEC-23-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Please ensure HMI display is properly protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618270&prj=626&rqi=JD5VaSRwo10mjdZpDLj45JKcZ5
RT1ELEC-59-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Permanent equipment label/tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618222&prj=626&rqi=T6NL4WHVrWWUTUjcSjprTt7Iwj
RT1ELEC-149-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1UDP_C_2 to 1STSSB_C_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618257&prj=626&rqi=EnK4BnfimfdpfDOvhErTtZkxqe
RT1ELEC-14-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Rear anchor bolts have not been torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618367&prj=626&rqi=v1s9z2iIljw48FsXmQTsDiTOci
RT1MECH-32-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Dirt Air Separator issue; paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618483&prj=626&rqi=0tbAu23iNetZugCzzNpeQhm1np
RT1MECH-3-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | Equipment permanent label and tagging valve issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618347&prj=626&rqi=0qftt8NZeHp27eiMzWk3y7LUWZ
RT1MECH-3-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | Fusible link cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618354&prj=626&rqi=Vrs98QoAnkQmkNBdVGn08xEGPV
RT1MECH-3-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | solenoid cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618357&prj=626&rqi=bsLNIj9qAxH29lmHgj9KvdrWdr
RT1MECH-29-008 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | DB Panel issue; Cable labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618359&prj=626&rqi=tKBIwm9Fn9MiFO1B7qVlX2PL0c
RT1ELEC-59-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Deep cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618221&prj=626&rqi=79rdXIT4F2JOw8Xi5I1T0QkJTI
RT1MECH-3-007 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | discrepancy between shop drawing and actual measurement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618360&prj=626&rqi=0CiDoGRKQv8OZESDmMMfGiK26y
RT1ELEC-59-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Please provide correct GA & SLD drawings for 1STSSB_F_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618223&prj=626&rqi=sBZyLBAez6s1T24eUnjKMDNUaa
RT1ELEC-23-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Door foam damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618271&prj=626&rqi=hY4kg3qdVOi9bIFelbxBKzeTq7
RT1MECH-3-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | pipework needs to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618353&prj=626&rqi=2X5c5IUFVl2JjN8QL909RUEjr5
RT1ELEC-23-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Discrepancy between drawing & actual position (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618268&prj=626&rqi=ra6fIhF0lZFUnz9ONWI1FmDCIH
RT1MECH-34-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Dirt Air Separator issue; need to repaint | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618481&prj=626&rqi=nbAZv6m2qUKfeMHu6UBTDHReTT
RT1ELEC-149-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1UDP_D_2 to 1STSSB_D_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618259&prj=626&rqi=e1FJO5usVhOOmscLPXrbgnJKFg
RT1ELEC-14-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Panel is not level based on waterpass checking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618366&prj=626&rqi=quBuls6G0vMB9wqykgOKItcdFu
RT1ELEC-58-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | ACB has scratches | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618207&prj=626&rqi=5mCMMAQuzNnIwrf2OgfXQDzRax
RT1FD-8-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-2.06 | VES - Vesda |  |  | Upload all related documents to this checklist | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618195&prj=626&rqi=U7NvPxXLisfEKMflvBWq3fXyJS
RT1FD-25-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.03 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618187&prj=626&rqi=o0B3zSGV9ZMQjtQu1gkGGbgddI
RT1ELEC-58-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Permanent equipment label/tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618205&prj=626&rqi=FKesawwszN0p5cACPr5V8k0HY2
RT1ELEC-59-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Discrepancy between drawing & actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618213&prj=626&rqi=Yn1Nh2TlABPvnCQovhBQ8d9rZ2
GI-016 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | DCOS graphic configuration for asset data equipment is pending due to missing data from GC and MCE. Please expedite submission of the required Maximo data so the DCOS team can proceed with configuration. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618202&prj=626&rqi=A94SbPTNLTvvJWz7RD9lLeczKI
RT1FD-26-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.04 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618190&prj=626&rqi=SXDlezblBut4pFbYpBhCEctX2E
RT1FD-27-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.05 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618191&prj=626&rqi=MzdOCxGcNMzyaFmE4xGuxZ6U9R
RT1FD-9-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | ASDSP-2.07 | VES - Vesda |  |  | Upload all related document to this checklist | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618198&prj=626&rqi=j1XlHQ4s51vysUXYmjNzwxbLHZ
RT1ELEC-58-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Minor dents & scratches require touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618209&prj=626&rqi=SpRRpcQwRNZlh5J7mkEg8Oc8pl
RT1FD-24-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.02 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618189&prj=626&rqi=dpfkQL3YgYlHd77rrDvvLXM91w
RT1FD-9-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-2.07 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618199&prj=626&rqi=zAK2LybPnJpDehi5HJS8j6zAbV
RT1ELEC-58-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Provide temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618212&prj=626&rqi=Z601OG6mJeHlqG9BfK2VE4k1qh
RT1ELEC-58-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Please provide correct GA & SLD drawings for 1STSSB_F_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618206&prj=626&rqi=K9QRTLo0XXalJ04eh51mNUAmID
RT1ELEC-58-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Please upload calibration certificate of torque wrench | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618204&prj=626&rqi=M6iDPHh48FCZPNLZxnQUwEaDtM
RT1FD-31-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.10 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618193&prj=626&rqi=mQq38PwM172VT7Nr357R1VfYro
RT1ELEC-58-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Deep cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618208&prj=626&rqi=oNM3rLBkgw7kKg6YBa8WtCyijf
RT1FD-8-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-2.06 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618197&prj=626&rqi=2dZ49mjXBCgscHFZatVs4bE1sP
RT1ELEC-58-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Ensure all ACS & HMI are properly protected from construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618211&prj=626&rqi=Wn0HjXXRTeTPHEj2KAPw1hnGRP
RT1FD-28-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.07 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618192&prj=626&rqi=LtZyv3plvs7XezgLGM9IPtOM7z
RT1ELEC-58-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Discrepancy between drawing & actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618210&prj=626&rqi=VfSIe8EmwR821U93aVbhNoMnpe
RT1MECH-96-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_2 | FFU - Air Scrubber |  |  | nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618038&prj=626&rqi=1x0ZjJDFi9A18XMqIqwEhEzKEv
YT1MECH-32-001 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | jacketing not proper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618011&prj=626&rqi=awQAKYMN8tVZ0kBar5NfghlTdl
YT1MECH-82-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_4 | FFU - Air Scrubber |  |  | issue from L2A; nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618045&prj=626&rqi=3H2QroSKGY8VV7nuzvISnMikaH
RT1MECH-98-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_3 | FFU - Air Scrubber |  |  | nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618039&prj=626&rqi=Rm4mF0Ap28GtBdfsgDWuWtUIqb
YT1MECH-81-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_3 | FFU - Air Scrubber |  |  | issue from L2A; nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618044&prj=626&rqi=GX7AmXwBfwppTa4PdTfO33HDCC
YT1MECH-83-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_5 | FFU - Air Scrubber |  |  | issue from L2A; nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618047&prj=626&rqi=aVJkLRKLGd8F2WDEGhJ2AbWDZe
YT1MECH-80-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_2 | FFU - Air Scrubber |  |  | issue from L2A; nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618043&prj=626&rqi=fx675ovEEzFg87MiM1ex0YgAW1
RT1ELEC-149-010 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1MSD_D_1 to 1UPS_D_1) Please clarify with engineering, the drawing shows 5 busduct supports, but only 4 are installed. Confirm if this is approved and safe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617946&prj=626&rqi=EmkExESR7DvBmY8sP5S5vgTroD
RT1MECH-100-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_4 | FFU - Air Scrubber |  |  | nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618040&prj=626&rqi=GBliQp7P9H6mVzdA3iYu2fpjhW
RT1MECH-102-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_F_5 | FFU - Air Scrubber |  |  | nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618042&prj=626&rqi=MH4T1hYTtz3EEwiMIydgXBR052
YT1MECH-69-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | issue from L2A provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617895&prj=626&rqi=jXWDlorAvLJPe96Zlk6bk9i54q
YT1MECH-76-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | issue from L2A; provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617897&prj=626&rqi=2ub1TYclSQSQphBgc8gHYRjzjg
YT1MECH-78-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | issue from L2A; provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617899&prj=626&rqi=AKVs2xk4lrCMC3EEUnor7D7VQS
RT1ELEC-1-017 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Cable installation not yet completed? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617901&prj=626&rqi=Z217XfAUZ65GZWfpmuAaeWoYdX
YT1MECH-77-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | issue from L2A; provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617898&prj=626&rqi=MH20ZrT9fOhHCaOG1wAitl7NFu
YT1MECH-75-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | issue from L2A; provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617896&prj=626&rqi=9pWLLp8trILH72lLRm9FfesnM4
RT1ELEC-124-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617891&prj=626&rqi=VNYOPtrPq9hvC5XCfrmwTfh05i
RT1ELEC-174-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | Discrepancy between drawing and actual installation. In drawing this for 1TOU_C not 1TOU_D. Please clarify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617915&prj=626&rqi=V4DLhjt8E7mw8Nf0KLcjEE5a2E
RT1ELEC-176-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Cable tube marker is faded. Replace or re-label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617912&prj=626&rqi=iZZuqJPHFhsjpsltmccidLB8is
RT1ELEC-176-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617911&prj=626&rqi=Hx7dFu9Mlss9LJ6aRE2cs0tcpW
RT1ELEC-1-016 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Equipment not level/titled, please refer to the attached water pass result photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617900&prj=626&rqi=DHSmGju3L2JTyDcr7eRKg4g0fQ
RT1ELEC-1-019 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Incorrect cable connection between batteries (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617903&prj=626&rqi=KorrA1h6GqZGRCg8T0N4Xin2cu
RT1ELEC-176-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Discrepancy between drawing and actual installation. In drawing this for 1TOU_C not 1TOU_D. Please clarify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617910&prj=626&rqi=z2KBCFBl0DlWbtGae9gFf6b9mz
RT1ELEC-176-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Please provide temporary cover to protect form construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617913&prj=626&rqi=YuoggiQtraTfl33bgF8iCXpPNK
RT1ELEC-174-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617916&prj=626&rqi=eyHdiYCKDvvI24sJltePgmNIRm
RT1ELEC-1-021 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Discrepancy between drawing & actual positioning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617905&prj=626&rqi=40NyH8Oy8QSOCtLoiIlqgaYZ9o
RT1ELEC-174-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | Please provide temporary cover to protect form construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617918&prj=626&rqi=wfZQ0fm0bvvCFC80pghQC9KJzF
RT1ELEC-1-020 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Busbar joint between battery not yet torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617904&prj=626&rqi=LOzEzMRO4UrscbLln6f1a1JnEp
RT1ELEC-124-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Glanding cap damage/broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617890&prj=626&rqi=Jm5F9ef5s6fqqKnp0qaalmb3OU
RT1ELEC-176-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Door gasket panel broken/damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617914&prj=626&rqi=CJYha6tAfcjh7UirDKpr91JuBO
RT1ELEC-123-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Sleeve and firestop at wall opening/penetration not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617888&prj=626&rqi=QS6jUPSbPx2iwZPB0lKBMpyxt1
RT1ELEC-174-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | Cable tube marker is faded. Replace or re-label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617917&prj=626&rqi=eDvQ21CkTsJSh53OAXC32NqSUl
RT1ELEC-123-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Glanding cap at cable gland not properly installed. Reinstall to ensure fully proper sealing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617889&prj=626&rqi=59tPXpsM5TkqS9KyNmkDl4z43V
RT1ELEC-1-018 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Battery stopper not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617902&prj=626&rqi=bXZ6WVmf8SsK8atkO7YES4I1dp
YT1ELEC-4-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Earth cable point-to-point continuity cannot be verified as the earth cable has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617659&prj=626&rqi=3Rob3OiEAzFsOX4KwlO365fNLe
YT1MECH-107-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | some parts of the safety valve are rusty, need to replace/touch up, because some other valve seems ok with no rust at all | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617772&prj=626&rqi=nTxcrx8cLSWS8I3IFp4vK89mjc
YT1MECH-108-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | Grouting base plate support pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617736&prj=626&rqi=ETYtJ8PIxtSgEaIwKdrw065Zod
YT1MECH-107-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | the bolt appears to have less than 3 thread and there is one bolt with no washer on it | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617739&prj=626&rqi=aR5GPffC4Thu7J6xGYPoZz1P3h
YT1ELEC-5-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Earth cable point-to-point continuity cannot be verified as the earth cable has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617660&prj=626&rqi=BzXiYgzpwEBe5crercGWQeg196
YT1MECH-108-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | some parts of the safety valve are rusty, need to replace/touch up, because some other valve seems ok with no rust at all | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617738&prj=626&rqi=JPqd8vPSy6o5I0j20Dqqa81gsA
YT1MECH-107-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | Grouting base plate support pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617740&prj=626&rqi=lP06ND3TpYVkO5bE0ImctuXPtR
YT1ELEC-5-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Improper grounding cable termination at BTU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617661&prj=626&rqi=j8wurZAH0vdAimValHQ9bIVd9q
YT1ELEC-3-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Earth cable point-to-point cannot be verified as the earth cable has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617656&prj=626&rqi=ZaACZSuHHKgfyeEW1XvQYgQvAw
YT1MECH-108-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-08 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | some bolts appear to have less than 3 thread | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617619&prj=626&rqi=Xy8zlIV9f7df2WGTqRNLpttki0
RT1ELEC-132-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617513&prj=626&rqi=Nhs2F8mqCN1SuLPl8huSeQVWaO
RT1ELEC-131-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (should be 1MDSB_F_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617495&prj=626&rqi=OQr93LsKk8H3oCzopvF4DQzllk
RT1ELEC-131-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_F_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617497&prj=626&rqi=d5CsxipQnrHhd2ZpfwNGpwMB78
RT1ELEC-132-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Equipment need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617505&prj=626&rqi=v5HP2qxFHNAZ30JeRGPcavEtj4
RT1MECH-5-001 | JK01-2 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Fuel day tank not install yet sight glass, tagging and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617487&prj=626&rqi=TndVmA1fD15vxdZEyvuwUE2fQx
RT1ELEC-132-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Discrepancy between drawing and actual positioning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617506&prj=626&rqi=e4VbNKjQNEOUZCDeI9SgyDgrih
RT1ELEC-132-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (should be 1MDSB_F_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617504&prj=626&rqi=7JJevs3q6pD04hB7O18SXXA5kF
RT1MECH-4-001 | JK01-2 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Fuel day tank not install sight glass, tagging and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617486&prj=626&rqi=89w1ml6mcSYh1BHlVQnAXZRzz4
RT1ELEC-131-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Discrepancy between drawing and actual positioning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617499&prj=626&rqi=lcLV4Kk8UOW2gDH4Atll6gx6RD
RT1ELEC-131-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Please add protection to prevent from construction damage, dust & debris also please protect HMI display | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617496&prj=626&rqi=KiIURoScvFiWAk4b1Mz55ZkVml
RT1ELEC-132-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_F_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617511&prj=626&rqi=hrskLBWzS3MG8nn4TfT0hrtcOY
RT1MECH-3-001 | JK01-2 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | Fuel day tank not yet install sight glass, tagging and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617485&prj=626&rqi=EPkrTSzkCQchCxXXr39XHNtRIi
RT1ELEC-131-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breaker, similar to breakers Q1-1 to Q1-5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617494&prj=626&rqi=6lwSwNYeH4roOs3WhOo7DKuYFV
RT1ELEC-14-002 | JK01-2 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Panel Isolator, DB Aux any part not tagging, cable not tight and cover acrylic not install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617489&prj=626&rqi=SjUDbbZP41ZX3Pt03QTCmSm7P6
RT1MECH-2-001 | JK01-2 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | Fuel Tank not yet install sight glass, tagging and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617480&prj=626&rqi=XyZgXamxqYMLMQiLG3U1BCpgzP
RT1ELEC-12-001 | JK01-2 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | Panel Isolator, DB Aux any part not tagging, cable not tight and cover acrylic not install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617488&prj=626&rqi=UdbX8fX37Hxr4iwFZT5qId6WhL
RT1MECH-28-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | some parts of the safety valve are rusty, need to replace/touch up, because some other valve seems ok with no rust at all | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617419&prj=626&rqi=4Wcrtyx7GtDwGFU9eMvhPgy1Qd
RT1ELEC-25-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Latest drawings are not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617368&prj=626&rqi=gTqVExvyGjaxfEzZ9sAIyXqiYc
RT1MECH-29-007 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | DB panel: there was some scratch inside, need to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617421&prj=626&rqi=WoqGgKoZcAqS46xEdxIAtoIBNG
RT1FD-38-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-7.09 | VES - Vesda |  |  | provide Cause and Effect Matrix is approved document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617427&prj=626&rqi=SATooqIibTF1x65EQRrHIFdT2m
RT1MECH-29-006 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | DB Panel anchor bolt seems not straight / tilted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617420&prj=626&rqi=rJC21xN4xTnlL6GtRXM3GT95KJ
RT1MECH-28-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | the bolt appears to have less than 3 thread and there is one bolt with no washer on it | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617410&prj=626&rqi=GD9IVGNoyIgNPfUs0UUzh3mrdW
RT1ELEC-25-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Minor dents require touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617370&prj=626&rqi=XVLbt3gAbfUwS4OMujCII6EXEi
RT1MECH-28-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Grouting base plate support | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617418&prj=626&rqi=pJk2iJnDU5Oojfg9yRLLJgsBbN
RT1ELEC-25-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Equipment permanent label/tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617374&prj=626&rqi=2DEvDBSZ7qeKSwZmJFvFuf4i7j
RT1ELEC-25-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Please ensure HMI display is properly protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617371&prj=626&rqi=uzfq9qOwqda03b90aIRGjfQ6hk
RT1ELEC-25-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Deep cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617369&prj=626&rqi=Rpo1JTk5dkPb4N2DzlFrGD8JpE
RT1MECH-74-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617308&prj=626&rqi=ZoYvtBtQF1Fk7S92CXXGgtKSAk
RT1MECH-82-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_5 | FFU - Air Scrubber |  |  | cleaning issue and remove unused material inside equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617331&prj=626&rqi=ajBynBw7hHSZ3R9Ixu53CNhndX
RT1MECH-88-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617313&prj=626&rqi=7rIr03fWreRsQoE2UpJ6GtVpiS
RT1MECH-78-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_3 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617325&prj=626&rqi=Uw4Eb19GNqFtddDzYd5R1u9a3a
RT1MECH-74-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617307&prj=626&rqi=7VqvyQPBKMgwnjMhePsdCMfGSQ
RT1MECH-74-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | provided Approved method statement for L2B static testing upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617306&prj=626&rqi=85jkyRe1jXZKVHJ0TfsG9cFtqJ
RT1MECH-88-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | provide Approved method statement for L2B static testing upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617314&prj=626&rqi=oLlmamu4Fl4et3JBvhf5IzF37W
RT1FD-38-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-7.09 | VES - Vesda |  |  | minor scratch and paint damage at pipe vesda | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617304&prj=626&rqi=D3wPhgvuYtlROkjLHGmX2w1iRb
RT1MECH-88-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | provide permanent equipment label / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617312&prj=626&rqi=dJ2Oon7ep1IGujxzLLVBU1zc20
RT1MECH-29-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | some bolts appear to have less than 3 thread | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617350&prj=626&rqi=Fmq3QcBCYfF5HoCgAy1C7Q2Y8r
RT1MECH-92-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | provide Approved method statement for L2B static testing upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617318&prj=626&rqi=aAIjHXCzTesDyAiFNBBcuUliGX
RT1FD-33-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-7.01 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617305&prj=626&rqi=kWOZzfhcUtyFgQkoUiFsjzwa3W
RT1MECH-90-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | provide Approved method statement for L2B static testing upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617315&prj=626&rqi=3WLIHZpMv5PsL3ksSjsYXkdbZC
RT1MECH-84-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_1 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617333&prj=626&rqi=FvkmJFdNpTZ0Jn8LDImUvZD4zw
RT1MECH-90-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | Cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617316&prj=626&rqi=kXx2fLcviHzSMaxCIzFjHLOjVf
RT1MECH-92-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617320&prj=626&rqi=No7RVEUiXpQLnO3403BbkkclZ1
RT1MECH-86-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | provide permanent equipment label / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617310&prj=626&rqi=310gDbGT8H9Bf5fxlTsvWsLYNp
RT1MECH-86-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | provide Approved method statement for L2B static testing upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617309&prj=626&rqi=AYLXg63Af6oExtJuEYe5jn7j4D
RT1MECH-76-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_2 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617321&prj=626&rqi=TWPn3Sx0TW4WMiMjp4aqQlTEEA
RT1MECH-29-005 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | some parts of the safety valve are rusty, need to replace/touch up, because some other valve seems ok with no rust at all | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617352&prj=626&rqi=D5R5JhkWLglbjTsxoaONYelgU5
RT1MECH-92-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | Provide equipment permanent label / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617319&prj=626&rqi=gbcxjZr2P8iyfXFhkQ0rvKuwai
RT1MECH-80-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1FFU_D_4 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617327&prj=626&rqi=uDvdOpsPHQ7mOnvqY4nSyANnJT
RT1MECH-86-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617311&prj=626&rqi=SV0w8Xbv86OrUnvLJda9G0KCPZ
RT1MECH-29-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Grouting base plate support | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617351&prj=626&rqi=TZqAhr3p2hWFv3KBCqJw6ASIAM
RT1MECH-90-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | Provide permanent equipment label / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617317&prj=626&rqi=KrMLUc2dWNFNoRdyHwu5HVLGYO
YT1MECH-115-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1LCP_FPUMP_B2 | FT - Fuel Tanks |  |  | Invalid Testing Tools due to expired calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617136&prj=626&rqi=XBcrDsgDSWtJZvAg85zrPriRFZ
RT1FD-37-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-7.05 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617150&prj=626&rqi=FwtT0I280AAhGlHWQ4IGCdk5lk
RT1MECH-15-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_F_61 | EF - Exhaust Fan |  |  | marking of support installation has not been applied | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617123&prj=626&rqi=orcFqvuONxCXZJx8bIZremMPv5
RT1FD-30-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.09 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617146&prj=626&rqi=neAO9kRWspXT5mtavzXrku0SXc
RT1ELEC-37-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617129&prj=626&rqi=LNwQHnZ94bK0zx7S3MLj9XOQUr
YT1MECH-114-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Fuel | equipment | 1LCP_FPUMP_A2 | FT - Fuel Tanks |  |  | Invalid Testing Tools due to expired calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617131&prj=626&rqi=hmx6H5hLnr1U744mPiw4oFPz6q
RT1FD-34-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-7.02 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617147&prj=626&rqi=d1k6m7FVMpMSdVLCSL1YETTdjH
RT1FD-29-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-5.08 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617145&prj=626&rqi=aWe5ABo7rjUbn2fJRzPBk69uBu
RT1MECH-15-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_F_61 | EF - Exhaust Fan |  |  | Airflow direction / orientation has not been affixed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617122&prj=626&rqi=kKClOF5FnYcpAuugnmgszcea8B
RT1FD-36-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-7.04 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617149&prj=626&rqi=aU7LP7fXdYf74XcHadMHBj7ZRX
RT1FD-35-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fire Detection | equipment | ASDSP-7.03 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617148&prj=626&rqi=EgldRwUqaG2Uso3RZkcE3lvw4B
RT1ELEC-37-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Please add temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617130&prj=626&rqi=JtRXsmtDHZ5fnQxHzQQF4LDAUq
RT1MECH-15-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_F_61 | EF - Exhaust Fan |  |  | equipment name tag has not been affixed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617120&prj=626&rqi=F9JE7Wf2D5AJxZCK7psi7daqe5
RT1ELEC-38-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | GC to upload following documents: 1. Certificate calibration of torque wrench 2. Approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617021&prj=626&rqi=dGaUafVkStAL89na6JukriXd7K
RT1ELEC-37-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | GC to upload following documents: 1. Certificate calibration of torque wrench 2. Approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617029&prj=626&rqi=LXNFDUx0NPiF10Pn8VOBeIYof5
RT1ELEC-129-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Unused bolt observed at cable gland entry. Remove if not required. Glanding cap also not fully covering | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616955&prj=626&rqi=ldW1nrBsrg3CjJVSXYX94SlHGC
RT1ELEC-38-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | Please upload factory test documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617020&prj=626&rqi=e56DSQTwptCg7X78oBBCrWyUc5
RT1ELEC-37-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Equipment labelling still temporary. Install permanent labels as per approved scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617030&prj=626&rqi=6ZlrO57BZVUyRJT4XOKYD4aJfC
RT1ELEC-39-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617012&prj=626&rqi=nT2qtqQAMMkD473ESYdoNLirmr
RT1ELEC-37-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Anchor bolts too long, torque wrench cannot be applied. Re-torque and re-mark all anchors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617032&prj=626&rqi=ZyQDGVnAvMvL4FNxyqU3cFtTuv
RT1ELEC-38-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | Anchor bolts too long, torque wrench cannot be applied. Re-torque and re-mark all anchors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617024&prj=626&rqi=KG189B26vKDcsZvGLpUKcauhh3
RT1ELEC-129-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable containment penetration not firestopped. Provide firestop | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616956&prj=626&rqi=CFywmzLymE2bZqrhjQlyErWue1
YT1ELEC-3-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2B | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | During function test of CxL2B, the alarm signal stayed ON and could not be reset due to incorrect wiring, the same issue also affected fault and trip signals. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617423&prj=626&rqi=5T4wvmv1IQsMuVV9lL7VitBjO3
RT1ELEC-38-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | Equipment labelling still temporary. Install permanent labels as per approved scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617023&prj=626&rqi=hnVjtVDQb4AggZkyewSETAeCTO
RT1ELEC-39-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | GC to upload following documents: 1. Certificate calibration of torque wrench 2. Approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617017&prj=626&rqi=CPkaE2baN5KmBhd9YvMrS38Lqs
RT1ELEC-39-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Equipment labelling still temporary. Install permanent labels as per approved scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617013&prj=626&rqi=nTeQo9XWpLDqI1Qy2uXURy2WPW
RT1ELEC-39-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Please add temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617018&prj=626&rqi=ZfTuhvrq5vbYzrkZs2wnqYkaKh
RT1ELEC-39-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Please upload Factory Test documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617016&prj=626&rqi=zL3I9jjC6IuL0fihnLlhdY6len
RT1ELEC-39-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Busbar joint marking not consistent. Standardize to red | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617015&prj=626&rqi=AtJY2ovm6HqFcoKn03vzY0Z1St
RT1ELEC-37-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Busbar joint marking not consistent. Standardize to red | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617031&prj=626&rqi=A4FCumxOgM0Qb9YJ4kW47Mz6kq
RT1ELEC-38-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | Busbar joint marking not consistent. Standardize to red | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617025&prj=626&rqi=x6Emrwsli3cGrnD6D3quvtrUza
RT1ELEC-37-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Please upload factory test documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617028&prj=626&rqi=ksWxprJgUN7hNQjnp6YPsi3ueS
RT1ELEC-39-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Anchor bolts too long, torque wrench cannot be applied. Re-torque and re-mark all anchors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617014&prj=626&rqi=HLeXlv8Rcm8Dzx64YjRjCKBFKM
RT1ELEC-55-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Panel tagging not as per design (should be 1STSSB_C_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616828&prj=626&rqi=HrG5bwx6NjOK3r321uWFOXsG8o
RT1ELEC-55-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Control cables appear not connected, please verify and confirm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616830&prj=626&rqi=kTgOvcdxspFfiI0WYIctEwsx3u
RT1ELEC-129-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable tagging not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616954&prj=626&rqi=Fn629tJluvFRBUQCigqTxQws1O
RT1ELEC-55-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Vertiv emblem on panel door is loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616835&prj=626&rqi=X67VSDaSuFIO5nBDSiwXba6rqf
RT1ELEC-130-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable insulation (vinyl) is torn. Please replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616945&prj=626&rqi=GOv6HHatNMAxXdwqGGv3q50scK
RT1ELEC-130-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable containment is not properly aligned/levelled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616944&prj=626&rqi=xr1hpm5lS5q9EDHLJfx9aYE8oA
RT1ELEC-55-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Please provide correct GA & SLD drawings for 1STSSB_C_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616834&prj=626&rqi=bd1pOjt2VWJhCqkTIk7prhrXR4
RT1ELEC-128-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Missing cable tagging for L2, N, and G | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616948&prj=626&rqi=OpfQCGD7iwa5rQ6Im9soHp6JlW
RT1ELEC-55-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Busbar joint bolts not yet torqued and torque-marked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616831&prj=626&rqi=C7WAk2IgUWaVORgWKTByg4zSAL
RT1ELEC-128-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Remove temporary marker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616952&prj=626&rqi=SOSs4KrPH29QGeJVsyoUSdOR2D
RT1ELEC-128-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable arrangement is not neat. Re-arrange properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616950&prj=626&rqi=EKA8ZQBs2Zb6JEgO1o1Ny3yTVX
RT1ELEC-130-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Improper termination, conductor still exposed. Please rectify cable vinyl | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616943&prj=626&rqi=bCZs8bwJ2WBBhs4cfHrNkt4JYq
RT1ELEC-130-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Incorrect cable tagging. Should be: from 1MDSB_C_1 to 1DB_C_DATA HALL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616946&prj=626&rqi=5WwKj9bKVhlJc23HZub8y64v2G
RT1ELEC-128-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable tagging incorrect and no phase identification (L1, L2, L3). Revise to: from 1MDSB_C_1 to 1DB_C_CRITICAL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616951&prj=626&rqi=AQq07ys8bgvI1rDL1Z3DltMOlz
RT1ELEC-128-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Glanding cap at cable gland not properly installed; incomplete coverage observed. Reinstall to ensure proper sealing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616949&prj=626&rqi=09fGuI52S0tOm7zmjVLdhTq3XJ
RT1ELEC-55-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616826&prj=626&rqi=PZ3yQ9EbJGKpudg7DMzenZ72PZ
RT1ELEC-55-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Ensure all ACB & HMI are properly protected from construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616836&prj=626&rqi=eICE3mCDFpl0Y7KtOTjb74Ivou
RT1ELEC-55-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Deep cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616832&prj=626&rqi=YTu8smcM3Q5iAnw1m8IKKhp4i7
RT1ELEC-55-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Minor dents & scratches require touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616829&prj=626&rqi=PoqIsOrENopoGxnQS9pPaoTSbi
RT1ELEC-55-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Provide temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616838&prj=626&rqi=57D9SkJfMlO5lrgR8tkYavOjgb
RT1ELEC-129-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Missing bonding jumper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616953&prj=626&rqi=MNrP04fp89HAXl87rOhuEEMcJD
RT1MECH-115-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | please remove unused material / object, and also need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616791&prj=626&rqi=YAqg4yn5YxXRZByoAVdDicHHJ4
RT1ELEC-35-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Approved layout drawings not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616796&prj=626&rqi=qYvh1Y6igJg1PQS2YDFgnXkey6
RT1MECH-115-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616790&prj=626&rqi=bhGlPod2O98VLigQn77KIWlK4j
RT1ELEC-36-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | General cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616811&prj=626&rqi=6NAyS3oQbPn8L0tmzobcUdoAA7
RT1ELEC-35-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Anchor bolt thread minimum 3 threads exposed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616799&prj=626&rqi=IJkxC4DOym6VQCNazZUUG4ipMS
RT1ELEC-36-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616807&prj=626&rqi=j97ixVN1a0g2AKiMncV0jrrAB5
RT1ELEC-35-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | General cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616803&prj=626&rqi=hTT0mDc8EzIF9EyUt3AEFSb8yY
RT1ELEC-35-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Provide temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616802&prj=626&rqi=ugtAZQ7fyc7YoBVLIHLPukSc6V
RT1ELEC-35-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616801&prj=626&rqi=k5dq5N8cXWsXegSamCj5kgMVia
RT1ELEC-36-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Provide temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616810&prj=626&rqi=OrJV68ghcDiu9m2QVQgHtOSuyp
RT1ELEC-35-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Panel tagging not as per design (should be 1LIBATTSYS_C_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616800&prj=626&rqi=I4RlJbjwxSgtpkSocoV7ABBy1P
RT1MECH-115-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | minor scratch has found | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616788&prj=626&rqi=vrjfubUpGJ7GGPPvKIOWzPdPGA
RT1ELEC-36-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Panel tagging not as per design (should be 1LIBATTSYS_C_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616809&prj=626&rqi=3YRIvcrQKCpozFjY5UNoB45dS4
RT1ELEC-36-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Approved layout drawings not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616805&prj=626&rqi=JT2l7ECPVFy6cbYw6yQhTQhy2B
RT1ELEC-170-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Approved Technical Submittals / Material approval / Specs not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616664&prj=626&rqi=07uBFoYmSmzcQ1Pcm7UYHUpwhk
RT1ELEC-171-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | There is a discrepancy between the drawing and the actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616671&prj=626&rqi=viw5Q4dWUKDgJq6NYVeW6r3l96
RT1ELEC-170-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Cable tube marker is faded. Need replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616666&prj=626&rqi=Kb32L7sxsa3WiUcMHoPVPUF2Hd
RT1ELEC-170-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Please provide temporary cover to protect from construction damage, dust and debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616669&prj=626&rqi=iEyRi0J4bFBEOrDYnUflgU4XZv
RT1ELEC-171-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | Please provide temporary cover to protect from construction damage, dust and debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616673&prj=626&rqi=9rspaxQ0ownDBxokqxDXafd0Te
RT1ELEC-171-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616670&prj=626&rqi=1eZBKO8XbxBbmwWnYAflcfZ891
RT1ELEC-170-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616668&prj=626&rqi=8d6YIrFcK9SQqkp1TRrFTNdfV7
RT1ELEC-170-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | There is a discrepancy between the drawing and the actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616667&prj=626&rqi=hqACM231cHRZsBpfirE6n0Cphz
RT1ELEC-170-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616665&prj=626&rqi=TjPV3w3ztUGM9V5VTj4NMgnesd
RT1ELEC-171-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616672&prj=626&rqi=yfNS3eSfoEvyajpv5voMKc70Rq
RT1ELEC-175-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616523&prj=626&rqi=3x7bIbbldypASN6NhKFZVaVpZe
RT1ELEC-133-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Cable tube marker is faded. Need replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616495&prj=626&rqi=AEaYr6Yen4wpar6jiVpvTKapHH
RT1ELEC-133-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels (feeder) on the acrylic cover above the breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616489&prj=626&rqi=2FGMhsYK774xprtmModukU7keT
RT1ELEC-172-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616480&prj=626&rqi=gTOfrvtDwBJiGzuG4591eTWkA8
RT1ELEC-172-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616481&prj=626&rqi=bZ2B2CuhBOx8h0HLOkGBFEJ1u1
RT1ELEC-172-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Cable tube marker is faded. Please replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616479&prj=626&rqi=SBqn14QVRRXjc7Lr1b6z9spg5l
RT1ELEC-175-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Please upload following documents: 1. Approved technical submittals documents 2. Factory test data documents 3. GA & Schematic drawing 4. RFIT documents 5. MoS CxL2B documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616518&prj=626&rqi=jORiRWCnRpFT4lqmp695ylaeEw
RT1ELEC-175-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Phase separator / barrier is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616520&prj=626&rqi=n5B8h0KbRYrO5D077P304k7f6a
RT1ELEC-175-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | TOU F positioning is not shown in the latest approved layout drawing (only TOU A). Revise drawing and include dimensions (mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616519&prj=626&rqi=z8RakTWqnhT3AO9QtvNdTEecQU
RT1ELEC-175-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616522&prj=626&rqi=FgIKkGMCrgsBXZyxzJlKmnj7MM
RT1ELEC-173-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616475&prj=626&rqi=tN5uoGzqqByzkQ1zl4lLgtCEf3
RT1ELEC-177-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616509&prj=626&rqi=rTymeeoaztZafML711imlPo7GR
RT1ELEC-177-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | TOU F positioning is not shown in the latest approved layout drawing (only TOU A). Revise drawing and include dimensions (mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616508&prj=626&rqi=ITz6RgVuwi3PyVPFDe4uwKX3YQ
RT1ELEC-177-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | Cable vinyl material (neutral) is inconsistent with others. Standardize to match | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616510&prj=626&rqi=AGC8gPWLbjHPQk0WWmfWpakRWF
RT1ELEC-173-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Approved Technical Submittals documents not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616474&prj=626&rqi=9KfCgoWoNNwOvDQU8xnodGPlQI
RT1ELEC-173-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Please provide temporary cover to protect form construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616478&prj=626&rqi=w15wMHZ9bc9mxrAhSfdeBuQM0k
RT1ELEC-173-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Cable termination is not properly done. Copper conductor is exposed. Please rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616476&prj=626&rqi=zHSd0DX3mlpZs1GMJ2W7YajkaP
RT1ELEC-173-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616484&prj=626&rqi=JdqJxVh1VZ8azj0WQfpG5vy4LG
RT1ELEC-128-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (1MDSB_C_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616409&prj=626&rqi=i4yeyPzTvvQ6pxbqbMO6vSiw6t
RT1ELEC-128-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_C_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616411&prj=626&rqi=KWbbc1Xl80fjZoKljfM7TXhu1b
RT1ELEC-128-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Please confirm torque value applied to panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616414&prj=626&rqi=A3mpHDAWqN1Ger6qyz9XmwRNkY
RT1ELEC-128-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | There is a discrepancy between the drawing and the actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616410&prj=626&rqi=AAT1s3lzKCkHaO7CRSJUwNrxcJ
RT1ELEC-128-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Equipment need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616413&prj=626&rqi=H7MhfDUvpJ7qxpTba8PaW2jfyb
RT1ELEC-128-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Please upload correct document for 1DB_C_CRITICAL. This documents for 1DB_D_CRITICAL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616340&prj=626&rqi=KOns8AqlDsjQUDtZLrrr9ECIwF
RT1ELEC-128-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breaker, similar to breakers Q1-1 to Q1-3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616412&prj=626&rqi=UwN0KCyocSpqEmtWWN4qExarmH
RT1ELEC-173-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Paint stains on panel surface. Need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616477&prj=626&rqi=4mWdQoyvj68aRCWqMgvbsjzqCw
YT1ELEC-4-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2B MV Cable RMU_F to MLTX_F) Tan delta values on phase S increase significantly, indicating possible insulation degradation. Please clarify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616528&prj=626&rqi=6uxfLcjfk0IQQBh827nKlBgzG6
RT1ELEC-133-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (1MDSB_F_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616487&prj=626&rqi=hu42OOs3ZXMrt2Zc7HnqzQE88M
RT1ELEC-133-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_F_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616471&prj=626&rqi=95ZIRGadUOOoiIJmvumATsAFgb
RT1ELEC-129-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please remove any temporary marker markings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616404&prj=626&rqi=zNlglhBfAlvYtGQ2hwJSLngGVd
RT1ELEC-133-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616490&prj=626&rqi=qOcCI9F7IcNOjP16LEdJzxWxQG
RT1ELEC-129-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breaker, similar to breakers Q1-1 to Q1-4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616401&prj=626&rqi=ZJwq15qfp2XO2NE8eqmapXZvWi
RT1ELEC-129-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | There is a discrepancy between drawing and actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616406&prj=626&rqi=dJGFGqC8QOa56tmWluWvjnN4kH
RT1ELEC-172-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Missing phase separator / barriers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616482&prj=626&rqi=RFWaKeag300Hi5AxqWaGIRVtaZ
RT1ELEC-129-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616403&prj=626&rqi=mHMRBiH7hK9XaMuUvGkNO0kwuw
RT1ELEC-133-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | There is a discrepancy between the drawing and the actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616486&prj=626&rqi=4R07e18Dy5qvm9IUzeQNG4gq7O
RT1ELEC-133-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Incorrect document uploaded. This for 1DB_D_CRITICAL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616493&prj=626&rqi=R4nIqqngWAnt6QtwgMhQ7djnIA
RT1ELEC-129-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (1MDSB_C_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616399&prj=626&rqi=5gTblbIBggbr2oPhec8JONY4pp
RT1ELEC-129-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_C_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616407&prj=626&rqi=8uIpWA5rE8CyvKA9HMa5aPRRcF
RT1ELEC-177-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616511&prj=626&rqi=aOMxOwo8THRGYYgWWFTJfCR4vJ
RT1ELEC-177-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | Approved Technical Submittals documents not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616507&prj=626&rqi=fhqIE3D16Zsb4kJZkXv6mIPo2R
RT1ELEC-130-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels (feeder) on the acrylic cover above the breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616417&prj=626&rqi=1NxomZAUC1Wpg8SRBItla2EBGn
RT1ELEC-130-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (1MDSB_C_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616422&prj=626&rqi=UZxZgfTlA2q1fXquPU8sqE3iU7
RT1ELEC-130-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | There is a discrepancy between the drawing and the actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616415&prj=626&rqi=YxAg1TYOLWG4iyES4p48w0NZ3l
RT1ELEC-130-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_C_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616424&prj=626&rqi=hxKqUEuAukhtnfgHo1bUFkoYj9
RT1ELEC-129-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please upload correct document for 1DB_C_EWALL. This documents for 1DB_D_CRITICAL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616341&prj=626&rqi=7IsAlDomvbYvqFhfYPhQTsRGKA
RT1ELEC-130-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Please upload correct document for 1DB_C_DATA HALL. This documents for 1DB_D_CRITICAL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616342&prj=626&rqi=JPGjwkPDAYwvyxVUUh7wOAIp9C
RT1ELEC-130-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Please confirm torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616423&prj=626&rqi=wruPEsQa5jJkNLUuOWfvvpzdwa
RT1ELEC-130-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Panel body is dirty. Need to clean | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616419&prj=626&rqi=8ymEy79HwGq8sHVorXHv3cGavU
RT1ELEC-123-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Remove temporary marker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616246&prj=626&rqi=9Sfmc964qOXUzaULSEG6FswSra
RT1ELEC-122-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breakers, similar to breakers Q1-1 to Q1-5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616243&prj=626&rqi=K9t8DNozdQl4zZgHGlqnUdkbKJ
RT1ELEC-124-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | Cable marker is unclear/faded. Please replace with a proper label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616250&prj=626&rqi=B6F4PVO5WvPWGpUCBrrcRGkLtU
RT1ELEC-123-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Please confirm the torque value for the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616245&prj=626&rqi=IiaDA4DoDC5rZQ5TpsDNr5iSJW
RT1ELEC-124-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | Please correct the incoming (source) label in accordance with the approved drawing/design (1MDSB_B_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616249&prj=626&rqi=KX863O0mYxc3Vh5JeEqhKAYigl
RT1ELEC-124-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | Please update the drawing to reflect actual unit positioning based on the RFIT inspection results | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616253&prj=626&rqi=TbJtfS4hfRMFCfvXkEqJMOgxKc
RT1ELEC-123-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Please update the drawing to reflect the actual unit positioning based on the RFIT inspection results. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616248&prj=626&rqi=JA6tbTZQhtf0PczBVsKtDL5iNc
RT1ELEC-124-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breakers, similar to breakers Q1-1 to Q1-5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616252&prj=626&rqi=vVZ68ik6JejKn8lVD9shqfQhrn
RT1ELEC-123-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Please correct the incoming (source) label in accordance with the approved drawing/design (1MDSB_B_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616244&prj=626&rqi=fYNCqDdBlJAprgHNcKHxcP59gd
RT1ELEC-123-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breakers, similar to breakers Q1-1 to Q1-4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616247&prj=626&rqi=xO9rdSXxyH09lVxOWiq7Ekvndj
RT1ELEC-122-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | Please correct the incoming (source) label in accordance with the approved drawing/design (1MDSB_B_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616240&prj=626&rqi=5b7ZcislC1iFQVPWvG9Q0IncgI
RT1ELEC-124-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | Please clean the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616251&prj=626&rqi=P7MPtjYwtdWo7bEVL1R6yiTcll
RT1ELEC-122-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | Please update drawing based on RFIT report for positioning unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616238&prj=626&rqi=nZsRccEIzQ70xMKjOaUfXEZgaQ
RT1SEC-12-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Security | equipment | 1ACS_level_7_General | ACU _ Access Control |  |  | Please upload following documents: 1. Approved technical documents 2. Installation Startup manual documents 3. Inspection checklist 4. Approved shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616228&prj=626&rqi=eUMxnVmJjIUz5AEAvTo5hLjoIg
RT1ELEC-53-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Please ensure all ACBs are properly protected to prevent construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615860&prj=626&rqi=Kkst0c2x7qrzFlL33gpbzKxKJB
RT1ELEC-53-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Torque wrench calibration certificate does not match the tool used during inspection. Please upload the correct and valid calibration certificate for the actual torque wrench used | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615856&prj=626&rqi=odL2hfiIRzYUpCGufnI4r3vcWC
RT1ELEC-53-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Please upload Installation and Start-up Manual is documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615854&prj=626&rqi=M6z15GjKr4CrE0Cw5z5lVkzvdp
YT1ELEC-3-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Please apply cable vinyl for proper insulation and finishing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616234&prj=626&rqi=sEcd1iccXRP1lie5wcV4jzNzIC
RT1ELEC-53-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | MoS CxL2A document is still empty and has not been uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615857&prj=626&rqi=iRMPqWWTCH8OR0wmAX2LH00ZOT
RT1ELEC-53-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Anchor bolts shall have minimum 3 exposed threads | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615861&prj=626&rqi=1rWVTiU0NdHs2vWT8ExxNW6e74
RT1ELEC-53-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Minor dents/stains on panel surface observed, need touchup | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615858&prj=626&rqi=a4OYDufRrS6TZp8pNJNi6tIGWM
RT1SEC-10-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Security | equipment | 1ACS_level_5_General | ACU _ Access Control |  |  | Please upload following documents: 1. Approved technical documents 2. Installation Startup manual documents 3. Inspection checklist 4. Approved shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616224&prj=626&rqi=Q8bFtCqarrdHHXjWmr2iwGleNs
YT1ELEC-3-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Grounding cable is not connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616233&prj=626&rqi=dpOkfieXRIB9vsoqW7rVhOYHFS
YT1ELEC-3-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L2B | Torque required | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Busbar connections between batteries have not been properly torqued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616232&prj=626&rqi=nw4BtygTxdDp6WN2fCnAOSyD3D
RT1ELEC-53-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Please confirm busbar join not yet connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616235&prj=626&rqi=N42Lro6hpYDyJFXCxgBmAXyxVS
RT1SEC-9-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Security | equipment | 1ACS_level_4_General | ACU _ Access Control |  |  | Installation does not comply with approved drawing and is positioned too close to the manual call point (MMR B Level 4) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616223&prj=626&rqi=WfEcl1omLk4d6hh7LBRMZcZ0Cm
RT1ELEC-53-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Factory Test Data document not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615852&prj=626&rqi=8FgqUwBUl4VigpY8zZ3FOuzrpl
RT1SEC-10-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Security | equipment | 1ACS_level_5_General | ACU _ Access Control |  |  | Tx room level 5 is installed with a single reader device instead of a double reader as per approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616227&prj=626&rqi=Qnom7wdYLSrKOEWhGbePQ9n1Nr
RT1ELEC-56-001 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-03-16 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | STTSB rear back frame anchor bolt not installed. Front panel anchor bolt also not complete | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615755&prj=626&rqi=AewHZGKSbe5bVF3niEZq0cFg26
RT1ELEC-2-017 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) The equipment needs FOD | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615750&prj=626&rqi=UPMDYbw15PTOeGOq5Ccb1350Rn
YT1ELEC-4-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Please confirm the BTU incoming breaker rating. As per approved MoS it is 15A, while the actual installed breaker is 20A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616231&prj=626&rqi=Rx74beljKXI0WO4NnsEQ9NmarK
RT1ELEC-26-001 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-03-16 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | UPS Mech D2 rear anchor bolt not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615772&prj=626&rqi=4DZ9df8tTDqTeU47H50OUYwX9D
YT1ELEC-2-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Please confirm the BTU incoming breaker rating. As per approved MoS: 15A, actual installed breaker is 20A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616230&prj=626&rqi=KThwHmU15JXu8l2m9a6Tyzrhif
RT1ELEC-24-001 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-03-16 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | UPS Mech C2 rear anchor bolt not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615771&prj=626&rqi=lEDZNVl0ckhqbpIqAGwTDEuFnm
YT1ELEC-4-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Busbar connection each battery not yet torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615698&prj=626&rqi=vi9bDrbeNeXikEZqta2jR1dCVb
RT1ELEC-2-015 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Grounding cable not yet connected to main earth bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615703&prj=626&rqi=XDic4sRZqBRVOeGQslGMDlZfFD
RT1ELEC-2-016 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Minor dent & scratches observed, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615704&prj=626&rqi=HcHtyCG3W6xRNusfwsMMyjoLSE
YT1ELEC-4-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Grounding cable not yet connected to main earth bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615695&prj=626&rqi=uXyq5QSirJJdUHUAlkROUunsiy
RT1ELEC-11-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | (Issue CxL2A MV Cable) MV cable grounding braid not properly installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615671&prj=626&rqi=JRDbPeGy924bNxuDm9ltJqVTZi
RT1ELEC-4-025 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable) MV cable grounding braid not properly installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615672&prj=626&rqi=SCyDviYYZ6WARb0iumNKEYJZ3d
RT1ELEC-1-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Latest GA & schematic drawings not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615402&prj=626&rqi=N87azgNphinwNW3ySEI6ETyzZw
RT1ELEC-1-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | HV cable design not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615393&prj=626&rqi=JYstkliAvmwigL5oggShFZat0t
RT1ELEC-1-015 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Equipment positioning different from latest approved drawing (please refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615407&prj=626&rqi=yfSo4fBuZGLL6dS1rgF2Phx9ea
RT1ELEC-1-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Dust & debris found inside the equipment need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615398&prj=626&rqi=ppOEAcn5E8ueljoEEDYcJ971OO
RT1ELEC-1-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Multicore cable schedule not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615392&prj=626&rqi=dq9D72bBMwuob3BzzKwmWs77Vt
RT1ELEC-8-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Tap changer opening is not covered. Please provide a proper cover for the opening to prevent dust ingress and accidental contact | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615387&prj=626&rqi=12eqClu6tziuTtYGj7MtNDve91
RT1ELEC-8-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Door scratches, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615385&prj=626&rqi=ADaxZudc1PpuhnBqMmEWveqYBv
RT1ELEC-1-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | L2B Static Testing Method statement not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615395&prj=626&rqi=VjeyyJrBSQFjCuU17afInOUeWF
RT1ELEC-1-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Sticker found damaged and shall be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615405&prj=626&rqi=rlASUYIyfQUYLWEINogsGzVtJL
RT1ELEC-1-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Bolts found rusty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615406&prj=626&rqi=5cLFldKumxdo0fd7UzkNElgqJD
RT1ELEC-8-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Fan cables are not properly dressed. Poor cable arrangement may cause damage or disconnection during maintenance activities. Please tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615386&prj=626&rqi=DJE7ttnion3FKSfVIM9DxmZzZb
RT1ELEC-1-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Some components have only one label on the mounting/body, and terminals are not labeled. Each component should have two labels (on the mounting and on the component body) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615403&prj=626&rqi=CNuEjAuvr0Ja0hC3p0UUDtgKhi
RT1ELEC-8-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Equipment positioning different from latest approved drawing (please refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615388&prj=626&rqi=GLAXYgS2YbEfZcmDs8g8h2m4Ij
RT1ELEC-1-009 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Relay protection unit is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615399&prj=626&rqi=1EJNA3NnK90jgz4FQdBKkEQDvV
RT1ELEC-1-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Switchgear Installation and Operation manual documents not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615390&prj=626&rqi=OwMAFCr3ECTvVxTp6laX2IIp92
RT1ELEC-1-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | MV LV Network Discrimination Study documents not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615391&prj=626&rqi=RBEpk1nNBi7TFPSIcVVS1eX1eM
RT1ELEC-1-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Please upload RFIT report document for positioning unit RMU not MV cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615397&prj=626&rqi=Yes13d72ijvh5asa0rDvo75faP
RT1ELEC-1-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Factory test protocol calibration certificates not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615389&prj=626&rqi=qwwpiwjmS2QPuSgM1Z9vhubRrC
YT1ELEC-2-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Invalid Testing Tools due to expired calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615441&prj=626&rqi=qTJMdRGRJkB5Jdy82B37FVPlTg
YT1ELEC-2-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Some of test not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615439&prj=626&rqi=O6x1ON91sZWSxhCUY6V9XZoij2
YT1ELEC-3-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Some of test not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615442&prj=626&rqi=71MDYuFAljttNNRMXDoEZ0uAns
YT1ELEC-3-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Invalid Testing Tools due to expired calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615443&prj=626&rqi=N312i1WlXUMlKbK2VDO06lJ4cC
RT1ELEC-125-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Please rectify cable tube installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615210&prj=626&rqi=GlK7REDQtyj6gKcYlrVpuq7MAL
RT1ELEC-125-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Factory Test Data/ Factory QA/QC document not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615201&prj=626&rqi=wtWOClI6mvB37VoRoYUXTWnKex
RT1ELEC-126-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615221&prj=626&rqi=RzzGoxWgIP10bDTAPPmHogiRLt
RT1ELEC-31-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Dust & debris found inside the panel, cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615235&prj=626&rqi=XIXjzsl2SVkLMPiEURtdJiOpUF
RT1ELEC-125-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Confirm cable gland hole quantity and size as per approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615208&prj=626&rqi=Lze9yBU36SwaJxWTXefcC9ztDc
RT1ELEC-126-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Please upload material approval/specs documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615215&prj=626&rqi=2c4ZEEWHTMt1tMcYc1fzSHB7O4
RT1ELEC-32-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | Dust & debris found inside the panel, cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615241&prj=626&rqi=tIxWcU2dfv7bfHqrEJqBcd0BlD
RT1ELEC-31-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Equipment positioning not aligned with the latest approved shop drawing (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615232&prj=626&rqi=hr131k8lWpJrzx4yXnEpy8uaYz
RT1ELEC-126-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Factory Test Data/ Factory QA/QC document not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615214&prj=626&rqi=f4ozlrktJmI163xruwEzqAwdD4
RT1ELEC-126-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Neutral termination bolts found loose, please tighten | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615217&prj=626&rqi=9upciD8M8qo1TDOSIS4VUQQorH
RT1ELEC-125-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Acrylic bolt missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615209&prj=626&rqi=GBOkEhat6eCCoFkHjsUiGvPWs7
RT1ELEC-126-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Confirm cable gland hole quantity and size as per approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615218&prj=626&rqi=nFD4FSYIqtmWeXvlrZ7Qf0LMIA
RT1ELEC-125-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Provide protection for power meter | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615212&prj=626&rqi=gEosUdroHtvhncFm4517r7uCwi
RT1ELEC-32-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | Anchor bolts found loose during torque check. Please check all anchor bolts, re-torque, and apply torque marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615240&prj=626&rqi=EWzaaZw4MtnIWu9FtXDWKN1RXa
RT1ELEC-32-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | Installation checklist from Vendor completed (signed off) not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615242&prj=626&rqi=0aItbsngHL4Id7d3bremPMZWZT
RT1ELEC-31-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Unused anchor holes found, please seal/cover all unused holes | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615237&prj=626&rqi=ow7mnarqcPyKl9uGDxib5F88Xt
RT1ELEC-32-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | GC to upload latest approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615238&prj=626&rqi=odk8yBSCZjUbukdjREWDrGOIPo
RT1ELEC-126-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Dust and debris found inside panel, cleaning required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615219&prj=626&rqi=i4jh2Gw7Cweg8kcikWQIMp3osi
RT1ELEC-31-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Anchor bolts still loose during torque check. Please check all anchor bolts, re-torque, and apply torque marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615234&prj=626&rqi=BZt575aZrMskkSHDxu4ayNnc1Y
RT1ELEC-125-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Add temporary cover to prevent construction damage, dust, and debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615211&prj=626&rqi=drJzoFNpY7WG2ZkV5lEPRpPfnI
RT1ELEC-125-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Neutral termination bolts found loose, please tighten | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615207&prj=626&rqi=sesylV8XQeUPwidlwkk3oCvqe1
RT1ELEC-31-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Anchor bolts must have at least 3 threads | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615236&prj=626&rqi=0tUZfv0O7Kko3fH0vah849QVwC
RT1ELEC-126-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Gland plate bolts not properly tightened | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615220&prj=626&rqi=BUIxSb748OvLPUp7LH7GJpoSIC
RT1ELEC-125-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Dust and debris found inside panel, cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615213&prj=626&rqi=fKZFgwaqxcce7g1J92w7VETYaJ
RT1ELEC-31-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | GC to upload latest approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615225&prj=626&rqi=ZbCdO2BzuRtXVRbzzy29sZyRoL
RT1ELEC-125-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Equipment positioning not aligned with the latest approved shop drawing (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615204&prj=626&rqi=e1uWr7nxk1cIV2trMtv8gvWIn4
RT1ELEC-126-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Equipment positioning not aligned with the latest approved shop drawing (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615216&prj=626&rqi=6vG0qcze5UDeeiTelrurZapJBG
RT1ELEC-31-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Equipment labelling/tagging still temporary. Permanent labels/tags shall be installed as per the approved labelling scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615233&prj=626&rqi=u9A2kv78mUcq91YWEfpIknFLWQ
RT1ELEC-32-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | Equipment labelling/tagging still temporary. Permanent labels/tags shall be installed as per the approved labelling scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615239&prj=626&rqi=BN2qFDn42Gfs8OuSQzUognvWRs
GI-010 | JK01-2 | APAC | Closed | P2 Medium DCOS | dickyhermawan@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Issues SFAT DCOS 24 February 2026 â€“ Day 2 as per the Issue List in the Attached Picture for the issues open. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615099&prj=626&rqi=ClELtRYylpDbwDJ71fojp5cjsH
RT1ELEC-14-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A DCOS UTP Cable) - Cable installation on GEN_C still not completed (labelling & terminated) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615058&prj=626&rqi=LOUx3sWPXhV6Bl37StTn4wXY9m
RT1ELEC-148-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_2 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MSB_B to UDP_B_2) Busduct installation is not level. Please refer to the waterpass photo and the elevation measurements differ at each point as shown in the photos | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615094&prj=626&rqi=CMjrSyNRwlLiP4HUFi9kYPlf8I
RT1ELEC-13-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A DCOS UTP Cable) - Cable installation on GEN_D still not completed (labelling & terminated) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615062&prj=626&rqi=4qsziM80pfCYwahanzlsTtjw1m
GI-009 | JK01-2 | APAC | Closed | P2 Medium DCOS | dickyhermawan@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Issues SFAT DCOS 23 February 2026 â€“ Day 1 as per the Issue List in the Attached Picture for the issues open. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615097&prj=626&rqi=AI1oHYrPAqOUcDyhZJ8QvqZ5vY
GI-011 | JK01-2 | APAC | Closed | P2 Medium DCOS | dickyhermawan@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Issues SFAT DCOS 25 February â€“ Day 3 as per the Issue List in the Attached Picture for remaining open issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615100&prj=626&rqi=zh5VSSGU29MKhcaz2nCWaXGRqR
YT1ELEC-5-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Simulated trip from thermal relay to VCB cannot be performed as the control cable installation is not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615435&prj=626&rqi=hUbAYMZbUm7yIwAwnCmoRluIkS
YT1ELEC-5-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Point-to-point verification for control/signal cable cannot be performed as the cable installation is not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615436&prj=626&rqi=Qc9dBHwKDTxPCASYDRux1VGgyd
YT1ELEC-5-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Auxiliary supply not yet connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615437&prj=626&rqi=R32t6d729wKg77FuTaFGDUN3gR
RT1ELEC-9-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Clean construction debris on cable containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614754&prj=626&rqi=jjcTauUKl9bAjmxShJYuIIZKPg
RT1ELEC-4-024 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Discrepancy between drawing and actual equipment position, refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614762&prj=626&rqi=7dsAOh41E6f2JqS3kM6gvu0gSk
RT1ELEC-9-015 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Incomplete firestop at all wall openings/penetrations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614757&prj=626&rqi=seOaxIh7CoW0TaJmXAKDbNggqa
RT1ELEC-10-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Install bonding jumper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614752&prj=626&rqi=OWBXr6dJyliKgN8EngQsMAa78C
RT1ELEC-9-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Temporary labels shall be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614756&prj=626&rqi=qkR34u2v2uhKexYfh4NH42Op1H
RT1ELEC-10-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Standardize all bonding jumper colors to silver | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614750&prj=626&rqi=SkPbC5YUKVkmdeKpXUSj37TDiD
RT1ELEC-4-020 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Busbar connection between batteries not be properly torqued? Please verify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614758&prj=626&rqi=SJpFCQrXyk1WanTQJbSGdRy232
RT1ELEC-4-021 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Cable lug connections may not be properly torqued? Please verify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614759&prj=626&rqi=1pB5FzC2931xDSOrerC37x9Egm
RT1ELEC-4-023 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Cable over-bending observed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614761&prj=626&rqi=FlLJ4thjYbvhRL8M8JGKG9YmvL
RT1ELEC-9-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Remove binding wire from cable containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614755&prj=626&rqi=XpNU181RrzMUfAeQD50jiPzk3V
RT1ELEC-4-022 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Battery stopper still not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614760&prj=626&rqi=Gkn30YhIeuPbAk8QDEBxkz4MQY
RT1ELEC-10-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Incomplete firestopping at all wall openings/penetrations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614751&prj=626&rqi=WxN4HN4CsPlhvRr5lb5WbpMF1M
RT1ELEC-19-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | There is a discrepancy between the panel drawing and the panel label. The drawing indicates â€œ1CHWSTR_F_05_CH_1â€, while the panel label shows â€œ800A TPN ISOLATOR FOR AIR COOLER CHILLER.â€ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614666&prj=626&rqi=8DuuQoApKp9hRCLW3fAnIOkmqI
RT1ELEC-19-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | GC to upload torque wrench calibration certificates for anchor bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614664&prj=626&rqi=N2nwrEa8nt6ovxaHYRyeVLJPyK
RT1ELEC-19-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Minor dents need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614668&prj=626&rqi=FK8zGjZdsdC49al6NRyWWnoWd4
RT1ELEC-19-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Based on the RFIT inspection document, there is a discrepancy between the drawing and the actual equipment positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614665&prj=626&rqi=bV5Rts32yajrpRwl1KBmWwnzTv
RT1MECH-17-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_F_74 | EF - Exhaust Fan |  |  | The equipment name tag shall be fabricated from the same material as the name tag used on the other equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614603&prj=626&rqi=JTAB2Pc9TdfQXDrJ0c5TA1nBP1
RT1ELEC-19-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Please upload on site (Internal) Torque connection sheet documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614662&prj=626&rqi=nsuaJ1VIAHRNixwn9e8NFezp3P
RT1ELEC-10-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | (Issue CxL2A â€“ MV Cable) Grounding braid is not properly installed (joint observed) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614691&prj=626&rqi=ryOrEnNBu8w0fVL1d7EszlDsRX
RT1MECH-16-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | The equipment name tag shall be fabricated from the same material as the name tag used on the other equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614604&prj=626&rqi=avItJclenOd0VpCjebxBTeTJLY
RT1ELEC-19-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Please upload Discrimination/ Co-ordination Study documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614663&prj=626&rqi=4P4Y9L7elo2D6mxlslkQ13yqqc
RT1ELEC-19-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Please ensure the HMI display & all ACBS is properly protected to prevent construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614667&prj=626&rqi=adlTKQhQZ9rxZwL2IZBqDxita5
RT1MECH-18-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | Please provided approved method statement for this equipment and also method statement for pressure testing/ vacuum testing (if applicable) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483524&prj=626&rqi=Rqi7TTCOdti85ScMcjCm6wTQAk
RT1MECH-19-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | Please provide approve shop drawing of the equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483526&prj=626&rqi=ANgP6X7uhvSpDdmOejQ4qtaiEN
RT1MECH-19-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | Please provide approved method statement for this equipment and also method statement for pressure testing/ vacuum testing (if applicable) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483527&prj=626&rqi=lMybl5z6jA9XyZzYPIEZFr0f3i
RT1MECH-19-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | The distance between the equipment and the wall does not comply with the approved shop drawing (120 & 390 in drawing, while actual distance is 305 & 665) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483525&prj=626&rqi=eioTclFKnVs6Ol3idRqCadaRAC
RT1MECH-18-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | Please provide approve shop drawing of the equipment and floor layout also | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483516&prj=626&rqi=608Cx9AVyOJDuRGqRVkKieMidK
RT1MECH-18-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | Visual inspection observes defect minor scratch on VRFOD body and nameplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483521&prj=626&rqi=SxEY5cj46PZgJXoQyHKdaYzFxo
RT1ELEC-9-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Minor dents and scratches were observed on the transformer body and enclosure. Touch-up is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483412&prj=626&rqi=EBneBEtEy3MYNxkyM8vrUjoHzU
RT1ELEC-9-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Please upload Factory Test calibration certificates | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483408&prj=626&rqi=wjsktwD5Yan0lr0fUXp7OpWf5C
RT1ELEC-9-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Temporary labels shall be replaced with permanent labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483416&prj=626&rqi=GDIKMEq1x4z8L7sGbIbv88GBeF
RT1ELEC-9-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Tap changer opening is not covered. Please provide a proper cover for the opening to prevent dust ingress and accidental contact | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483413&prj=626&rqi=FJ6RLENekQjevirq3h8FTwuOyy
RT1ELEC-9-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Please upload cable schedule documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483410&prj=626&rqi=GqdP7uLt48BysEHGujWmGTtZU5
RT1ELEC-9-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Dust and debris found inside the equipment. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483417&prj=626&rqi=qXJANfWV9zMvoisu51yikYJ75s
RT1ELEC-9-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Why is the nameplate tagged as â€œMLTX_Bâ€? Please clarify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483419&prj=626&rqi=WEyQWI78arBNH2fSXTFclL24m0
RT1ELEC-9-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Please upload CxL2B MoS document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483411&prj=626&rqi=zjAdX5K5oWs6nymS2kVwYIss67
RT1MECH-11-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_C_54 | EF - Exhaust Fan |  |  | The equipment nametag shall be made from the same material as the other equipment installed on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221137&prj=626&rqi=P4cKuXuRZAVyrY3OCGSqzmU1go
RT1MECH-13-004 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | The equipment nametag shall be made from the same material as the other equipment installed on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221138&prj=626&rqi=k5XtpBYRfJuItsc0Vw99acSlNA
RT1MECH-14-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_D_53 | EF - Exhaust Fan |  |  | The equipment nametag shall be made from the same material as the other equipment installed on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221139&prj=626&rqi=QHgAPQRyUZmvPiLZfxCFauXVx8
RT1MECH-55-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CA_C_09 | CA - Cool Array |  |  | Dust and debris were observed on the equipment and shall be properly cleaned. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221121&prj=626&rqi=IvaGgc2Dfag7dMWBJJF6nM3GHB
YT1MECH-31-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | During the penetrant test witness conducted on 13 February 2026, approximately 20% of the total number of weld seam were found to be not acceptable. Rectification works were carried out, followed by a re-test; however, the results were still not acceptable. Consequently, another re-test was conducted on 25 February 2026, and the results were found to be acceptable. All test results have also been verified by NDT Level II personnel, pak Wiwid Dwihartanto from KIK. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221132&prj=626&rqi=XyLZPxwREpg8aXWFiMYuAzLezm
RT1MECH-10-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_C_53 | EF - Exhaust Fan |  |  | The equipment nametag shall be made from the same material as the other equipment installed on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221136&prj=626&rqi=1uQoeuBHwseScMgBnWECE0jHjL
RT1MECH-55-001 | JK01-2 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_C_09 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221120&prj=626&rqi=mJprd9kI4xvY7994Eck2fTP3cZ
RT1ELEC-149-009 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MSB_D to UDP_D_2) Busduct above 1UDP_D_2 is not level, adjustment is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212894&prj=626&rqi=hTteHYVVcpxb7tjalNStSWUQ7T
RT1ELEC-150-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload equipment delivery note / material incoming inspection document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212876&prj=626&rqi=rY3ch6CwD14AY4KDqC9VuDVsyt
RT1ELEC-146-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS | Controls | equipment | 1RPP_1_GW_15 | CP - Control Panel |  |  | Cable gland washer is not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199921&prj=626&rqi=G0sc8C1COChyQhG7MT8N8TVg1u
RT1ELEC-150-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload calibration certificate for torque wrench | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212872&prj=626&rqi=uGHHMau74ZjkJ8SrRadYk0jWjs
RT1ELEC-150-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_D to MSB_D) Provide temporary protection to prevent construction damage, dust, and debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212886&prj=626&rqi=RsF7WXDyyXxeqfoGuMP1pKEaws
RT1DCOS-10-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Please install temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212861&prj=626&rqi=z3BVCMToIpnoAcss4VQXSIzAgY
RT1ELEC-147-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_16 | CP - Control Panel |  |  | Some bolts are rusty and need to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199925&prj=626&rqi=VMnT1WrD6goWflZM4XXWaFuGMo
RT1ELEC-147-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS | Controls | equipment | 1RPP_1_GW_16 | CP - Control Panel |  |  | Cable gland washer is not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199924&prj=626&rqi=3RmH3Kj4SPCcUF92uny6rnqicT
RT1DCOS-10-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Anchor bolts have not been torqued and marked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212863&prj=626&rqi=KDJAEaWb2S5c8WjGXHgU17xKFy
RT1DCOS-9-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | Based on panel drawing, power supply is tagged as â€œPS 1,â€ but the actual label inside the panel is â€œPS-A.â€ Please update accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212853&prj=626&rqi=dw05O74KqlGBbsGXDLuVBKCAxl
RT1ELEC-147-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_16 | CP - Control Panel |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199923&prj=626&rqi=H9hSw6LsPQrgIVlptgOB76Vzjc
RT1ELEC-149-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload O&M documents of busduct | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212875&prj=626&rqi=29iqnxlNkTGdHppumfcxnijXG5
RT1ELEC-149-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_D to MSB_D) Elevation discrepancy (refer attached photo): Drawing: 4500mm AFFL, actual: 4444mm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212891&prj=626&rqi=eGwmZBNi3TVdWdDAerLqkM9q8a
RT1ELEC-149-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_D to MSB_D) Sleeve and firestop at wall penetration are not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212892&prj=626&rqi=Cy9mxo2Qf2p4bXmdHv2KV0uLtb
RT1ELEC-149-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload approved latest shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212870&prj=626&rqi=siinZcEV0qt4fNMcrNGhT9TopK
RT1DCOS-10-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212864&prj=626&rqi=7sGaGLdAJo2YtL2RQ91oZ4PYUU
RT1DCOS-10-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Based on the panel drawing, the power supply is tagged as â€œPS 1,â€ but the actual label inside the panel is â€œPS-A.â€ Please update accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212865&prj=626&rqi=TynglNXffhiFs4p00fpbDbH1RO
RT1ELEC-149-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload equipment delivery note / material incoming inspection document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212878&prj=626&rqi=Hqk8ZcN6eUmUTWkCzwNSdKeU6V
RT1DCOS-10-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Please upload MoS CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212860&prj=626&rqi=WAJVt3cQaDJkkHKSsM4VXjUVlG
RT1DCOS-10-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Minor dents on the panel body need to be touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212862&prj=626&rqi=oXGQ47sf53QQE44VOeqyFswsym
RT1ELEC-149-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_D to MSB_D) Unistrut support is misaligned/not straight, rectify accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212893&prj=626&rqi=qrOrU6zWFScDGIJeAvru9HC4ON
RT1ELEC-145-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_14 | CP - Control Panel |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199928&prj=626&rqi=YML9s6tTHI2Mlyk2WtzFzZGyD1
RT1ELEC-149-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_C to MSB_C) Elevation discrepancy (refer attached photo): Drawing: 4200 mm AFFL, actual: 4351 mm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212889&prj=626&rqi=g5swJBunejt8rJWJnst0MZyfoY
RT1ELEC-149-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload torque wrench calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212869&prj=626&rqi=wLnH72LWMK4bTEUk1IJ4c3ahDD
RT1DCOS-9-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | Please upload factory test data documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212857&prj=626&rqi=fO8zPwOtEYy7aKSS4lD5J56sHY
RT1ELEC-150-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload approved latest shop drawings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212873&prj=626&rqi=qHhEl0icvLcvqEkwwXBx6EXLfl
RT1DCOS-9-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | Inside panel is dusty and dirty, cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212855&prj=626&rqi=B9cB9CHWw5tWbEN8XVtFrFBE3H
RT1ELEC-2-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue DCOS Cable UTP) - Please align the conduit to ensure it is straight and properly aligned (location RMU_D Lv5) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212866&prj=626&rqi=r2KpTX4jHz20dULslTFnZkkQzb
RT1DCOS-9-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | Please upload MoS CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212852&prj=626&rqi=zj3ApwifYDgbUvQL1J5SIG9png
RT1DCOS-10-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Please upload factory test data documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212859&prj=626&rqi=d8A0nR37hY0Lcc4QY9mvzz0GsX
RT1ELEC-150-005 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_D to MSB_D) Busduct installation at Tx Room does not comply with the latest approved drawing. Drawing shows straight routing, actual installation differs (refer to attached photo). Please clarify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212885&prj=626&rqi=0IyARSqlS4uNz3u8trTgfmX9Pp
RT1ELEC-144-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_13 | CP - Control Panel |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199926&prj=626&rqi=e3PVNmATQZYoxBAzV67Bo6MtAI
RT1DCOS-9-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212854&prj=626&rqi=Iue5Dp0Vs8gLIPArSgCFS8blAo
RT1ELEC-144-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_13 | CP - Control Panel |  |  | Dust & debris found inside the panel, need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199927&prj=626&rqi=FIZmp6qrYdH5zmrtfVXbjdiIUy
RT1ELEC-150-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload O&M documents of busduct | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212874&prj=626&rqi=O47zYXfgkWkM7pmjTjPMEIGrvO
RT1ELEC-145-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_14 | CP - Control Panel |  |  | Dust & debris found inside the panel, need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199930&prj=626&rqi=0pWmOuyLj9hneUoeF2T5MqHt0f
RT1ELEC-146-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_15 | CP - Control Panel |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199920&prj=626&rqi=RtkyhjMh39r7GgYn0MOqZoC9k9
RT1MECH-16-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | During the inspection of LCP panels F_73 and F_74, the bolts and nuts located at the upper left side of the panel failed the torque test, not even failed, the anchor bolt is keep moving when it get tighten. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199759&prj=626&rqi=YMpLyNGfSNmPm2exVYyxdL2uvg
RT1MECH-16-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | During the inspection of LCP panels F_73 and F_74, there were dirt, dust, and unused materials inside the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199762&prj=626&rqi=Kf3UlweRkXKdAs1cTdi25iAjdK
RT1MECH-7-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_B_31 | EF - Exhaust Fan |  |  | During inpection of LCP Panel B_31 & B_32, loose bolt and disconnected cable lug was found inside the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199809&prj=626&rqi=6Qz5ogw4zyA2Q4taTUL2j2oUVV
RT1MECH-16-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | During the inspection of LCP panels F_73 and F_74, A cable lug was found disconnected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199760&prj=626&rqi=akXXR7osOoM8c9NR6gtH9JVXE0
RT1MECH-13-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | During the inspection of LCP panels D_52 and D_53, there were dirt and dust inside the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199763&prj=626&rqi=RIdi24Ih4zN8qRFBulzJwx53ZH
RT1MECH-13-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | During the inspection of LCP panels D_52 and D_53, the nut at the upper left side of the panel failed the torque test, the nut is keep moving when it get tighten. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199807&prj=626&rqi=SJNcbQYcg4GRNOsr0sIhV4LH4R
RT1MECH-13-003 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | During the inspection of LCP Panel D_52 & D_53, loose bolt was found inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199808&prj=626&rqi=AyQictkGZqnQdGpXfdGBLn5pGW
YT1MECH-57-001 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-22 04:00:00.000 +0400 | General Contractor | L2B | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | During the hydrostatic test of the CHW pipe in the cool spine area at 10-11 Feb 26, a pressure drop of 0.6 bar was observed over a 24-hour period, exceeding the 0.5 bar acceptance criteria. Consequently, a re-hydrotest was conducted on the CHW pipe the next day, and the result for the second test is within the acceptance criteria. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199744&prj=626&rqi=kwEFm9atL00QfZTNU7goBnOSMt
RT1ELEC-3-022 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) Grounding braid has not been connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199695&prj=626&rqi=gYLlNvGy48P6kQl0FjJrQOUqqE
RT1ELEC-4-016 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) Sleeve and firestop at wall penetrations have not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199698&prj=626&rqi=HsVfKzuhu9QGf3HjzodAImb9Gn
RT1ELEC-4-017 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) Bonding jumpers at several cable ladder joints have not been installed. Please re-check all cable ladder joint connections | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199699&prj=626&rqi=yik83qa4Oh3FxZgdrhXEEO08WP
RT1ELEC-3-023 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) Cable skirt installation not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199696&prj=626&rqi=rS78ySlzj6mEHUKcqTo1MUWwbs
RT1MECH-30-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Findings of scratches were observed at several locations on the equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199654&prj=626&rqi=f2Va84fkOLH23juicBsLQZeiHS
RT1ELEC-4-019 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) Cable containment alignment is not straight as per approved drawing (at Level 6) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199701&prj=626&rqi=ilXdKHgfCguUIDcpirwWTuzDXO
RT1ELEC-4-018 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) MV cable grounding braid looks not properly installed, with too many joints observed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199700&prj=626&rqi=lEy0v1b38HcR4wq92Qwiy60mq8
RT1MECH-29-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Findings of damage, scratches, and dents were observed at several locations on the equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199653&prj=626&rqi=D8SsRD8drX9Dac36kpdCFREhuT
RT1MECH-28-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-16 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199250&prj=626&rqi=JDoFboX5PTcvfbhxO1VT28a0iB
RT1ELEC-33-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | GC to upload the latest approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199197&prj=626&rqi=lZE3aUKkTwggDPjmVcQY3uRGzt
RT1ELEC-143-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS | Controls | equipment | 1RPP_1_GW_06 | CP - Control Panel |  |  | All unused holes must be properly covered to keep the enclosure fully closed and protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199210&prj=626&rqi=x0SabET3iwJupTDXBzAIZWGg1s
RT1ELEC-34-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_2 | LIBATT - UPS Battery |  |  | Equipment labelling/tagging is still using temporary. Permanent labels/tags shall be installed in accordance with the approved labeling scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199205&prj=626&rqi=PDA8yemA1E1KmLeY6w635PmqBA
RT1ELEC-33-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | Please upload battery busbar join connection report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199198&prj=626&rqi=Jp0Bz6LEazdfiRwEh9cUVdGKL1
RT1ELEC-142-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_05 | CP - Control Panel |  |  | There is dust and debris inside the panel. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199209&prj=626&rqi=bU5niwsqRlewd8NQtdNobi6z3F
RT1ELEC-33-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | Please upload battery cabinet (inc circuit breaker) Factory Data document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199196&prj=626&rqi=64p9MuIm1ILTbJhRDuZQm8inEt
RT1ELEC-34-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_2 | LIBATT - UPS Battery |  |  | GC to upload the latest approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199203&prj=626&rqi=QRfAEuLxMxib5OwefrM3tnBBYo
RT1ELEC-142-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS | Controls | equipment | 1RPP_1_GW_05 | CP - Control Panel |  |  | All unused holes must be properly covered to keep the enclosure fully closed and protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199207&prj=626&rqi=v8dU9U6CNbppIzLO8n5MylUmUL
RT1ELEC-33-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | Equipment labeling/tagging is still using temporary. Permanent labels/tags shall be installed in accordance with the approved labeling scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199200&prj=626&rqi=LN8XXIsZ6MnFiOF9w9N0hTWv82
RT1ELEC-34-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_2 | LIBATT - UPS Battery |  |  | Please upload battery cabinet (inc circuit breaker) factory data document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199202&prj=626&rqi=ZgSQUfRRYBfkHw2naQTdRFOUev
RT1ELEC-34-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LIBATTSYS_D_2 | LIBATT - UPS Battery |  |  | Please upload battery busbar join connection report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199204&prj=626&rqi=rRxrkilBrNJbrBobZ9tLW7B4G7
RT1ELEC-143-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS | Controls | equipment | 1RPP_1_GW_06 | CP - Control Panel |  |  | There is dust and debris inside the panel. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199211&prj=626&rqi=nJbjjLPGPzBa32YTlQ2etBM5GX
RT1ELEC-4-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Verification of the circuit breaker serial number could not be carried out. The MCE vendor is required to provide clear photographs of the circuit breaker serial number for verification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198912&prj=626&rqi=E7hZ4HBRNBDWcmbFlhxfzATnIT
RT1ELEC-4-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Panel is not level (tilted) refer to the attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198904&prj=626&rqi=kuShNYrKQTErbNhCAf2wbeSC1s
RT1ELEC-57-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Control cables appear not connected, please verify and confirm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198998&prj=626&rqi=6z4sImbieogTczMplHR4qgUomL
RT1ELEC-4-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Drawings are not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198911&prj=626&rqi=pCRpRtg72mS01UkNKk8OF3XnLd
RT1ELEC-4-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please upload HV cable design documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198903&prj=626&rqi=41aGlelVuGsIcF6t6b025oZ0fc
RT1ELEC-4-011 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Anchor bolt torque could not be verified during inspection due to excessive bolt length, torque wrench head could not be applied | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198910&prj=626&rqi=H0j0ROpQqYvTzvghheIzIh9tEQ
RT1ELEC-57-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Dust and dirt observed inside the panel, cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198996&prj=626&rqi=iYikNeSwDINbZEsdjlnFF1wwSv
RT1ELEC-57-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Please upload Installation and Start-up Manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198988&prj=626&rqi=6uppq1rVa5xsjuJGIefmM1l0vz
RT1ELEC-57-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Busbar joint bolts have not been torqued & torque-marked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198997&prj=626&rqi=sydwWUJ3S2i7zScKmrPHQWxRtt
RT1ELEC-4-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please upload cable schedule documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198902&prj=626&rqi=CQZ7nyWzgzAitkbzKBCQOLJPWE
RT1ELEC-4-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Permanent equipment tagging/nameplate not yet install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198913&prj=626&rqi=FuueV9QEu8ZrKs2h7U0l1l1xom
RT1ELEC-57-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Drawing not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198994&prj=626&rqi=a2DwzZlDrZsuk634URxinTYok5
RT1ELEC-4-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Scratches on the door body, touch-up repair is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198908&prj=626&rqi=cNhYBxkFtlBUIqWiVQTmyvlM2d
RT1ELEC-57-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Please upload calibration certificates tools | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198984&prj=626&rqi=XNcS9jq3MLxNA5jaH7C9CB6S7e
RT1ELEC-57-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Minor dents, need touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198990&prj=626&rqi=wqZR73qQ565GlmMnmlyuzEnaVP
RT1ELEC-57-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Need to install temporary cover to protect equipment from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198991&prj=626&rqi=01rJlor9VG3HScvVFJ8dnKRuIK
RT1ELEC-4-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Equipment is dusty and requires cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198906&prj=626&rqi=LFjCCbm3di9qsVH0xhlnmofUfj
RT1ELEC-4-015 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Relay protection unit is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198914&prj=626&rqi=Gu5mt3LXHt10Igy7FCahZC8EEv
RT1ELEC-4-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Gaps observed between cubicles, need to rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198907&prj=626&rqi=4BQk5qMidrKWoIEAQJt1v0jYku
RT1ELEC-57-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Equipment positioning does not comply with the latest approved drawing: - Right side to wall: drawing 1425 mm, actual 1440 mm - Rear side to wall: drawing 483 mm, actual 575 mm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198989&prj=626&rqi=oHejZH5JNBUn93AefaYiTsPFV0
RT1ELEC-4-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Terminal blocks require sticker/labeling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198909&prj=626&rqi=exuoG2VkqDVmrvYyWC7VLAhU78
RT1ELEC-4-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please upload factory test protocol calibration certificates | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198899&prj=626&rqi=8TEK8pXfk1mLxvwxrXmlQuNXkF
RT1ELEC-4-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please upload Installation and Operation manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198900&prj=626&rqi=oCNetc8hEHUBTQSSsOuxt63Sif
RT1ELEC-4-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please upload MV Discrimination Study | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198901&prj=626&rqi=o2Ov0KdaA9dZuVf5QKVZcVA80s
RT1ELEC-10-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Fan cables are not properly dressed. Poor cable arrangement may cause damage or disconnection during maintenance activities. Please tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198889&prj=626&rqi=gj6ho2n3nmzDQ0oDy1hyc7vold
RT1ELEC-10-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Please upload cable schedule & L2B MoS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198894&prj=626&rqi=9jfB8J7g4Vb6oYFj7YcVahn8xp
RT1ELEC-10-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Please upload cable schedule documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198863&prj=626&rqi=loYhxPbmyTQk7INGaiapLPuNE3
RT1ELEC-10-008 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Bolts were found loose during torque check, clarify the required torque value and re-torque with proper torque marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198892&prj=626&rqi=8LFbRaWalmZeYcb8tifYmnO9cR
RT1ELEC-10-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Need to provide "danger" sticker/label on the transformer body | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198866&prj=626&rqi=mhxRKWP7Jdbi0ErP3Q6e8RAzeT
RT1ELEC-10-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Minor dents observed, touch-up repair is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198890&prj=626&rqi=Ls4rgchxpzVascVmn6pxqQQpW6
RT1ELEC-10-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Cleaning is required, excessive dust observed on the transformer, and cable tie and plastic debris found inside the enclosure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198893&prj=626&rqi=CtEx1qvmBWeEHcdoQpa6vjVSQp
RT1ELEC-10-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Control cables appear not connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198891&prj=626&rqi=E93akqtOHv563UZ1Gp5u67WtWn
RT1ELEC-10-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Some components have only one label on the mounting or body, and terminal labels are missing. Each component shall have two labels (on the mounting and on the component body). Terminal labeling is mandatory | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198886&prj=626&rqi=Bq3PC1pEEwhhpcQJU4EH6coF60
RT1MECH-31-002 | JK01-2 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Visual inspection observes defect minor scratch on chiller body and nameplate unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198884&prj=626&rqi=9dNFWlj2CWba8NfyLWsdOfNYxG
RT1ELEC-17-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Provide protection to the ACB to prevent construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198622&prj=626&rqi=vrdiYGMbYoWcxAZFxOMlSrJn4O
RT1ELEC-17-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Temporary labels shall be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198621&prj=626&rqi=Z1LN6znzwg0Gw7ou3VJQsjgd5N
YT1MECH-23-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_42 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198677&prj=626&rqi=sm4wo9MQNpltbib0FlnSGdX5YI
RT1ELEC-17-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Equipment cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198625&prj=626&rqi=qr1h0wkbR5z6WveTCRT0DMRJIs
RT1MECH-52-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_C_05 | CA - Cool Array |  |  | The unit support is misaligned. Rectify the alignment and remove any unused bolts if not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198668&prj=626&rqi=UaHOy68jbkLBmM1i6cO4bcM1cX
RT1ELEC-17-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Please upload on site (Internal) torque connection sheet document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198619&prj=626&rqi=xeruOoshnjVPylOcSVPwp3AEE7
RT1ELEC-17-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Anchor bolts were found loose during testing, re-torque and apply torque marking to all anchor bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198623&prj=626&rqi=HFQVzptk8legK5wLznBheeY8hu
RT1ELEC-17-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Remove marker pen markings on the busbar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198624&prj=626&rqi=lwD45gxnvn8Ty5ajKB0wUmB3QR
YT1MECH-25-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198680&prj=626&rqi=zykqHvSI1i5JYDU5niEnq0hAxP
YT1MECH-24-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_B_41 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198675&prj=626&rqi=In3MIy7vWIQNWuO7Sk3zgy7mTh
RT1MECH-52-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CA_C_05 | CA - Cool Array |  |  | Please upload approved method statement for flushing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198667&prj=626&rqi=EjzY4JVcRe59Z9gtVJ1lkN1UgZ
RT1ELEC-17-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Minor dents on the panel body shall be repaired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198620&prj=626&rqi=ZOYAYqL9A0gbwmFq8frqGz5xCj
YT1MECH-26-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198679&prj=626&rqi=1H3tbTb0OVvEjCDqtBeabtR0Xg
YT1MECH-27-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198678&prj=626&rqi=qU2fKwPvIzLb954auJsFap0ohF
YT1MECH-22-001 | JK01-2 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198674&prj=626&rqi=SkcZh5QdfjbZDtmacZDWJgUm9o
RT1MECH-114-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Internal equipment is dirty with excessive dust, cleaning is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198329&prj=626&rqi=bk7OkUMe7LtzFRyVYCQ3ENK3Lt
RT1MECH-114-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Fan cables shall be properly dressed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198331&prj=626&rqi=zSY7MOcswmYgwN7I5ZrKXB9W0X
RT1MECH-114-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Body-to-baseframe connection bolts are missing and must be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198334&prj=626&rqi=PMsbdPaJLhc0WSVuPuxAR96i9V
RT1MECH-114-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Stains on the equipment body shall be cleaned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198327&prj=626&rqi=oOJv7aLzmEa1qoFw6yW7sarXc7
RT1MECH-114-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Damaged insulation at the chilled water outlet shall be repaired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198335&prj=626&rqi=4H2yPh64ZhipcwIDl2uuXcAMRI
RT1MECH-114-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Left-side access door cannot be fully opened due to obstruction by the STSSB panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198330&prj=626&rqi=fUa4OC16mF7wYGFXwNcKFvORZB
RT1MECH-114-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Air openings are left open. Temporary covers shall be provided to prevent dust and foreign object ingress | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198326&prj=626&rqi=FxgbclnZyKgbwON43ijpnosQG7
RT1ELEC-18-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Equipment is dirty with dust and foreign materials. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198312&prj=626&rqi=V4vVvF0JnLPOuH5dmfhIvhXMEj
RT1MECH-29-001 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198298&prj=626&rqi=qhwdL6ryXZ9hz1TFfbFqSB20jR
RT1MECH-134-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1LCP_FPUMP_A2 | FT - Fuel Tanks |  |  | The device tagging label inside panel is different from the approved drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198293&prj=626&rqi=bvJtPcJSxXDs024oc8EjhdQoxg
RT1ELEC-18-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Phase separator / barrier between phases is missing and must be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198314&prj=626&rqi=smCSRPPkB88JlLdGn2zxHXxU8V
RT1MECH-135-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Fuel | equipment | 1LCP_FPUMP_B2 | FT - Fuel Tanks |  |  | The device tagging label inside panel is different from the approved drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198292&prj=626&rqi=trEQSChxPmUzKqmVH3JBGNeeAN
RT1MECH-32-001 | JK01-2 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-02-03 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Buffer Tank _C Jacket insulation broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198295&prj=626&rqi=I6LzHax7fWYicmQlAmvZmppJjQ
RT1ELEC-18-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Fuse labels shall be replaced with new labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198311&prj=626&rqi=WVC6QagraCKqImaaIDMugJZuRz
RT1MECH-135-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Fuel | equipment | 1LCP_FPUMP_B2 | FT - Fuel Tanks |  |  | LCP_FPUMP_B2 Panel Installation not level | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198291&prj=626&rqi=LiJ6p6jFwAuR5SsADFajysaeAm
RT1MECH-31-001 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198300&prj=626&rqi=DwBstKaultl2A1b4gzK5K5MHEh
RT1ELEC-18-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Marker markings on the busbar shall be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198313&prj=626&rqi=7L8zuH2LlJxyN1dRkPeWatLfqG
RT1MECH-30-001 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198299&prj=626&rqi=cNkbEBEOghTj1POR8pbLXupSPu
RT1ELEC-18-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Temporary labels shall be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198310&prj=626&rqi=CsuuU2WDvEcdoAjmHnOMKX9c5I
RT1MECH-28-001 | JK01-2 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | paint broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198297&prj=626&rqi=jzsPWp6l3ROGhUKwDEoMYz92AH
RT1ELEC-18-002 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Equipment positioning does not comply with the latest approved drawing (photo attached): - Left side to wall: drawing 1598 mm, actual 1629 mm - Rear to wall: drawing 244 mm, actual 235 mm - Front clearance to 1STSSB_D_2: drawing 1478 mm, actual 1580 mm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198309&prj=626&rqi=2MKYTJE2R8LR6WSwPZdsUVmb7o
RT1ELEC-2-013 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | BTU panel HMI display loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198175&prj=626&rqi=ZDyCEAFPxBMb6vByiKfAbfQfcr
RT1ELEC-9-003 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | the door cannot be closed properly. scratches on the door frame | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198162&prj=626&rqi=s9aHoNcox12J4O9EUxaUDwZ6KE
YT1MECH-6-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-02 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | (Issue from CxL2A) - Please provide permanent equipment labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198171&prj=626&rqi=tm6IQ8z7a8LM2d3QHWSu0zC3rQ
RT1ELEC-18-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Please upload calibration certificates for factory test | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198126&prj=626&rqi=vJuLrizY419XM00kLOLK3bKL3S
RT1ELEC-3-021 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Design correction needed | Design | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | BTU battery panel need to add battery stopper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198167&prj=626&rqi=4diptcahULZrTV3EtPkvseKJv0
RT1ELEC-3-018 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | 1BTU_C all battery connection not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198163&prj=626&rqi=n9WCrcpTyYO2b1cLT6U8izPbq8
RT1ELEC-10-001 | JK01-2 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Maintenance doors facing wall, need to relocate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198159&prj=626&rqi=IIBqw7E2LiizngJIIpNWZqnqN2
YT1ELEC-2-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue from CxL2A) - Permanent equipment labels were not installed. Equipment tagging with the correct language and approved colour scheme is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198170&prj=626&rqi=tBkHzi14qKCt2qb5nQ8AEJzp7v
RT1ELEC-3-019 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | BTU_C HMI display loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198164&prj=626&rqi=vYufzuv0SXmKYz6HpwdLvOI81c
RT1ELEC-2-011 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Design correction needed | Design | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | BTU panels are at risk of water splashes from the louvers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198173&prj=626&rqi=bspEHuVyGZXdav2bWOL2qDTCVR
YT1ELEC-3-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue from CxL2A) - Permanent equipment labels/tagging have not been installed (Main Tagging Equipment) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198172&prj=626&rqi=7l6XPibhjX4vu8NWDnQRUA6k4z
RT1ELEC-3-020 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Design correction needed | Design | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | BTU panels are at risk of water splashes from the louvers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198165&prj=626&rqi=jLLtdlI39ENnM3qzNfb7wSaevQ
RT1ELEC-9-001 | JK01-2 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Maintenance doors facing wall, need to relocate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198160&prj=626&rqi=2arAHzIoRgAmiqf20kWk0SJ5io
RT1ELEC-9-002 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Missing door hinge | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198161&prj=626&rqi=8o0hA5aqMyMaH7lU2NQa640nDg
RT1ELEC-2-012 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | BTU battery connection not complete. need add battery stopper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198174&prj=626&rqi=qVe07SMz2D7qpdxp7QgQkMgM8Z
RT1ELEC-11-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Please upload following document: 1. Approved factory test calibration certificates 2. CxL2B Method Statement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198086&prj=626&rqi=dgBnsdDhGNyOU9umvsryb6gtbi
RT1ELEC-11-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Scratches and dents are observed on the equipment. Touch-up work is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198107&prj=626&rqi=uWNEjPXOOy7zreITSDpZmTxlgo
RT1ELEC-11-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Permanent equipment tagging is not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198108&prj=626&rqi=AgnpklIYzQuxWncilAG1BvDRQ7
RT1ELEC-11-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Fan cables are not properly dressed. Poor cable arrangement may cause damage or disconnection during maintenance activities. Please tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198106&prj=626&rqi=ODAWTU6wZGhMKqPkIfsvsZ2cGp
RT1ELEC-11-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Need to be cleaning & touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198103&prj=626&rqi=DtElE3XZdrsTeVz9ZrtZjYesCS
RT1ELEC-11-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Please upload cable schedule documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198111&prj=626&rqi=LsfTxz6vcJwrU8F0VCGQDtQEwL
RT1ELEC-11-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Side access door installation MLTX enclosure (for maintenance access) differs with the approved drawing. GC/MCE shall clarify. Incorrect installation or missing access door will result in no proper maintenance access. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198101&prj=626&rqi=ZPoO8DYvfxg2pKifQCr9egRYVO
RT1ELEC-11-010 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Anchor bolt size does not comply with approved LS specification (required M12, installed M16) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198109&prj=626&rqi=OSXizrxlWd1BkdB7lyRfDvNBr5
GI-008 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | MLTX_F - Incorrect Enclosure Maintenance Door Direction | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198084&prj=626&rqi=OQeaBSan7nINxPahDtTBIfl0u9
RT1ELEC-11-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Vibrations pads has not been torque-tightened and torque marking is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198102&prj=626&rqi=55W45sOMX0aI12LH0dQ9Tensem
RT1ELEC-11-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Need to provide "danger" sticker/label on the transformer body. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198105&prj=626&rqi=SDM8hM0dQICdAlFSU77COTcKgl
RT1ELEC-11-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Some components have only one label on the mounting or body, and terminal labels are missing. Each component shall have two labels (on the mounting and on the component body). Terminal labeling is mandatory | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198104&prj=626&rqi=JmXxea63Tm0uUpxdNDfhe7OKRV
RT1ELEC-3-016 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-28 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Bonding jumper on cable ladder not installed, please re-check all jointing cable ladder | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197869&prj=626&rqi=l7tj0QmiEQb7BUIxvND2kr156e
YT1MECH-111-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_2.01 (Existing) | PAV - Pre-Action Valve |  |  | Seismic bracing not yet installed (drawing not yet approved) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197847&prj=626&rqi=ctvAxmqnAp7Z8CcOkkF0EwTZsO
RT1ELEC-3-017 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-28 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Sleeve and firestop at wall opening/penetration not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197874&prj=626&rqi=s0RJvo4O1Z8e08q4ZLxfJserNi
YT1MECH-111-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_2.01 (Existing) | PAV - Pre-Action Valve |  |  | At cool spine area level 2, sprinkler pipe BOP elevation differs from the latest approved drawing: 5300 mm (drawing) vs 5100 mm (actual) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197848&prj=626&rqi=VIMsjBrf2nJSLSnhEcMgkkf3zG
GI-005 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-01-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | BTU panel position is not the same as in shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197643&prj=626&rqi=O90y8eLiQSghNw9cij15JPvRbY
GI-002 | JK01-2 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-01-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | RMU_F MV2 missing PQM | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197636&prj=626&rqi=9PCHVFd7aDp3f664oa3xVR5j42
GI-004 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-01-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Design correction needed | Design | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | BTU panels are potentially exposed to water splashes from the louvers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197642&prj=626&rqi=nF3iJERP1OucQvX72h9pzEjytT
GI-003 | JK01-2 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-01-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Battery cable termination not proper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197637&prj=626&rqi=8YbaRo2dwxhPikYR6GmVIxgh5s
RT1SEC-4-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Security | equipment | 1CCTV_level_5_General | CCTV - Closed Circuit Television |  |  | Please upload calibration certificates | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197300&prj=626&rqi=MohPPwEAhNjKlCHT0cZYHLzxag
RT1MECH-119-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | Equipment labels/tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197318&prj=626&rqi=GEQrzIKEeVf04LP3ncLFZBuhGt
RT1MECH-118-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Equipment labels/tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197309&prj=626&rqi=ytlXfHUtpM7elR0K92yVug6jYf
RT1MECH-118-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Please cut and tidy up the cable ties | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197310&prj=626&rqi=BotVAmbZ0b2W6u07Cfs56p4AYH
RT1MECH-118-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Please install the proper covers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197307&prj=626&rqi=a0cWtO7d65Ikvmc8nEU87n5lsP
RT1MECH-119-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | Please cut cable ties and tidy up the cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197317&prj=626&rqi=5i6n7NC8S5nXr7kbxVZXEhuhUp
RT1MECH-119-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197314&prj=626&rqi=geB7oa7HDK0VP0lT71lzcOVXBO
RT1SEC-3-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Security | equipment | 1CCTV_level_4_General | CCTV - Closed Circuit Television |  |  | Please upload calibration certificates | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197298&prj=626&rqi=jG5m3VwkjuJ69UeKNibj6zMoU4
RT1MECH-118-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Physical dents identified on the equipment body | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197304&prj=626&rqi=yJ8aGiy8gQuUSpWHyLuiGACxzl
RT1SEC-3-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Security | equipment | 1CCTV_level_4_General | CCTV - Closed Circuit Television |  |  | Why is the uploaded inspection report for CCTV Level 7? This checklist is for Level 4. Please replace it with the correct report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197299&prj=626&rqi=RyXVFTR7CFA2YGFY17iOGfzATZ
RT1MECH-118-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197301&prj=626&rqi=zmobCTDRsqQQPdrcqDkmyfhRBA
RT1MECH-119-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | Equipment is dirty with dust and foreign objects. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197315&prj=626&rqi=CNQjM2mNlz7wuFTW3zu3Ly3NRa
RT1MECH-118-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Equipment is dirty with dust and foreign objects. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197311&prj=626&rqi=pXZa6d9wdKmvI7GwULhhdxjRw4
RT1MECH-106-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Equipment needs a temporary cover to protect it from dust and foreign objects | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197162&prj=626&rqi=Kc9O61p96h0a26L6vcLGic1PGf
RT1MECH-111-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Equipment position does not match the latest approved drawing. Rear: 290mm in drawing (actual 300 mm), side: 190 mm in drawing (actual 100 mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197180&prj=626&rqi=gLJysumakJDj5p8uTsUo61tdha
RT1MECH-106-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | nameplate / equipment tag is not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197157&prj=626&rqi=fZLkqviqAtcGKwm6Y3wllcdmL3
RT1MECH-107-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197165&prj=626&rqi=6hXPYF6aWh00lIc7RgoNAC665f
RT1MECH-111-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Please upload General Arrangement and schematics drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197173&prj=626&rqi=OSV8cpvOLhuTvdKkmWsPQtfvda
RT1MECH-107-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Nameplate / equipment tag is not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197168&prj=626&rqi=HGxaif8MxSuE9Ce4YMsmUHTqyg
RT1MECH-106-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Internal chilled water outlet insulation is damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197159&prj=626&rqi=uNYS2zOOE1wUZHh1FDHlbzNQRE
RT1MECH-106-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197151&prj=626&rqi=xH6AAqWhyMbjkKmNJbptWGDMjH
RT1MECH-107-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Please upload General Arrangement and schematics drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197164&prj=626&rqi=r9tebL4b3FjYLpu4eiZyE91F2f
RT1MECH-107-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Equipment is very dirty with dust and foreign objects. Cleaning (FOD) is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197170&prj=626&rqi=ZcEoHawIu1UdWVP8Z7v4xedJyj
RT1MECH-106-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Please upload General Arrangement and schematics drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197150&prj=626&rqi=LdBeJdWvTrqCBnuTNn9eJSijwO
RT1MECH-111-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Chilled water inlet and outlet pipes are open and need to be covered to prevent foreign objects from entering | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197183&prj=626&rqi=h9rxyrNMWGJxgWWmMiPf8KeSSd
RT1MECH-107-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | FAT report serial number does not match the serial number of the installed unit (FAT Doc: 001156011000007928 / Installed: 001156011000007967) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197166&prj=626&rqi=la4ui7A3UGPdh2P6LXrWAf81Vj
RT1MECH-111-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Control cables are messy and need to be properly arranged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197184&prj=626&rqi=2TbnrbLhY6X3hE8DR8HGUnc4O7
RT1MECH-106-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Control cables are messy and need to be properly arranged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197160&prj=626&rqi=ziPonvJmf0NgfmUBazhQq7jk6S
RT1MECH-107-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Update the layout drawing for 1CRAH_C_22 based on the actual site condition. Ref JK1-2-M130-02-IFC-DWG - MECHANICAL EQUIPMENT PLAN L2 - FITOUT | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197171&prj=626&rqi=0qlFwdCw7xFhvg7PAsPic4Cvip
RT1MECH-106-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | FAT report serial number does not match the serial number of the installed unit (FAT Doc: 001156011000007967 / Installed: 001156011000007928) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197147&prj=626&rqi=eDiKwitO5LpJTTFydUvAf37J1D
RT1MECH-107-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Internal chilled water outlet insulation is damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197169&prj=626&rqi=jJXguUamD7hPZbuXTGQVpTgmIT
RT1MECH-106-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Equipment is very dirty with dust and foreign objects. Cleaning (FOD) is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197155&prj=626&rqi=VLuuBLuL7EThH1W7oi2M5sLHCa
RT1MECH-106-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Chilled water inlet and outlet pipes are open and need to be covered to prevent foreign objects from entering | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197161&prj=626&rqi=wLjVtxGHqwkAODrDE6BgHtRGJV
RT1MECH-111-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197174&prj=626&rqi=lM3O3aBJQtljQQIKPfETay2FA6
RT1MECH-111-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Equipment is very dirty with dust and foreign objects. Cleaning (FOD) is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197181&prj=626&rqi=aqgK2QAoRGC0dfg315qlRsHD4v
RT1MECH-111-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Anchor bolt markings are unclear and require re-marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197182&prj=626&rqi=PUSauB9rkkVP5bBJHtxOdwXvJ7
RT1MECH-111-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Equipment needs a temporary cover to protect it from dust and foreign objects | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197187&prj=626&rqi=w5JkO8WNxRSHfCmEa1Gm6IzMTW
RT1MECH-107-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Cable arrangement is not neat and needs tidying up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197167&prj=626&rqi=VdA7MUehourgy8wrYXd4XZdrML
RT1MECH-111-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Nameplate / equipment tag is not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197186&prj=626&rqi=opm6LF5tYDy13vdy5g1HXr4knE
RT1MECH-110-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Dents / scratches were observed on the equipment body and doors during inspection. Please refer to the attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196965&prj=626&rqi=2a0kI0fwuliIE8byK8il6IL5pz
GI-006 | JK01-2 | APAC | Closed | P2 Medium DCOS | dickyhermawan@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Issues SFAT DCOS 13 Jan 2026 â€“ Day 1 as per the Issue List in the Attached Picture. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197979&prj=626&rqi=3SLeGYq4sCelOWdtcNeBz0L5aA
RT1MECH-110-007 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Equipment positioning does not comply with the latest approved drawing. The required clearance from the wall is 715 mm as per drawing (actual 820 mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196970&prj=626&rqi=2bAMlMIX8WO8iLHYLepgqaeCsl
RT1MECH-110-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Please re-mark all anchor bolts and body-to-baseframe bolts, as the existing markings are not visible or have not been applied | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196968&prj=626&rqi=IZq4LWeGWXHaDpQMYtwJwfcMUi
RT1MECH-110-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Air openings are still open and must be covered with a temporary protective cover to prevent dust and foreign objects from entering the equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196964&prj=626&rqi=ESJZwvU0G3V6aRwCQRKhfDP13o
RT1MECH-110-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Significant dust and debris were found inside the equipment. Please perform FOD cleaning. Refer to the attached photos | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196966&prj=626&rqi=ZBHxqBz9ruh4eOXAPY5Gmli2H1
RT1MECH-110-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196962&prj=626&rqi=WePxeL5ZrsMoXoL8lUJdYnKR8I
RT1MECH-110-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Connection loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197010&prj=626&rqi=TDYrzos31J39ieaWslgXGvEznt
RT1MECH-110-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Disposable filter found damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196971&prj=626&rqi=698uwmOg11wHVTmKxQU0ju3nqA
RT1MECH-110-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Permanent equipment labels / tagging have not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196967&prj=626&rqi=4RMtJsfQ8X3Y3WXiz2XDw1MJv4
RT1ELEC-16-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Please upload document related to inspection/checklist from Vendor completed (signed off) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196742&prj=626&rqi=iEVIISdVegKwY2u5thSXDr8YnT
RT1MECH-6-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | Please upload Approved Engineering Sequences of Operation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196756&prj=626&rqi=FtyTDJjiBrsSSXIGabCvesuM7D
RT1ELEC-16-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Defects, scratches, and dents were found on the panel body and door during visual inspection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196734&prj=626&rqi=Hhpsi49tXHwOmi3dxk0dYKysD6
RT1ELEC-16-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Loose cable found disconnected from the terminal | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196736&prj=626&rqi=SoEZmcKeeQp2hyo9vSEXjcVGVf
RT1ELEC-16-001 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Panel position does not match the latest approved drawing. Rear: 235mm in drawing (actual 250mm, side: 1450 mm in drawing vs (actual 1410 mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196733&prj=626&rqi=Ui9itEQJbrR09ZAvgCYOWOcoox
RT1ELEC-3-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Permanent equipment labels/tagging have not been installed (Main Tagging Equipment) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196726&prj=626&rqi=EXwdUDxBx0DsY8P0ASdLJWNO4A
RT1ELEC-16-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Please upload on-site torque wrench calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196741&prj=626&rqi=voFhS6RDXei9Mg9tiNnAfmt0cX
RT1ELEC-3-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Construction is incomplete. Cable termination has not been done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196727&prj=626&rqi=twousYTMAC9HACfXG0fyeeBoig
RT1ELEC-16-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Cable marker/labels are faded and unreadable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196737&prj=626&rqi=IeyDEtIcAeTyThlFVliKCD6vEr
RT1ELEC-16-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Equipment found dusty and dirty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196739&prj=626&rqi=b6z37nVh9ya3J3kjOC1wcZA3iN
RT1MECH-6-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | Number of spring mountings installed does not match the approved drawing (actual: 2, drawing: 4) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196766&prj=626&rqi=T42FOUREnYRynDLbk2XDGEiwpY
RT1ELEC-3-014 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Please provide a temporary cover to avoid debris or foreign objects entering the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196732&prj=626&rqi=5eTbZX1Y6TawNIfxpFDMLKyPSs
RT1ELEC-16-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Several ACBs are not provided with protection, which may lead to scratches or damage during construction. Please provide proper protection for the ACBs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196738&prj=626&rqi=7zpFrhckQ6KSQzWcK5hVkWJjMm
RT1ELEC-3-013 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Verification of the circuit breaker serial number could not be carried out due to obstruction by MV cables under ongoing construction. The MCE vendor is required to provide clear photographs of the circuit breaker serial number for verification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196731&prj=626&rqi=kth63zU6AeNozrMUCX97h5LYHs
RT1ELEC-16-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Several phase stickers/labels were observed missing or detached. Replacement is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196735&prj=626&rqi=yzCPyqTG5auDVFxxXOSbC473a1
RT1ELEC-3-015 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Cable arrangement in the cable duct is too crowded, so it cannot fit the cables properly. Please tidy up and reorganize the cables | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196754&prj=626&rqi=qrHNLDvioH8XLFg2pzWz7sjPlh
RT1ELEC-3-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Some components have only one label on the mounting/body, and the terminals are not labeled. Each component should have two labels (on the mounting and on the component body). Terminal labels are required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196728&prj=626&rqi=fF4PIT9OgzAOOsjOZkpMcBigPJ
RT1MECH-6-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | Please upload Technical Submittals documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196755&prj=626&rqi=PwMNBhmCFFluK167K2YOFoZOR1
RT1ELEC-16-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Please upload on site (Internal) Torque connection sheet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196740&prj=626&rqi=M0dJh0tXxIBvRpAcda32DQpEqI
RT1ELEC-3-011 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | The earth switch has no status indication. Status indication needs to be provided, and an attention/similar label should be installed above the inspection window | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196729&prj=626&rqi=dpJ7y8wrEFO42VYrJEGZCSEIfw
RT1ELEC-3-012 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Component/Equipment Failure | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Cable insulation is not properly covering | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196730&prj=626&rqi=EVEQPDQ670T4R9EfPnAqLOzZaQ
RT1ELEC-3-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | No drawing pocket and latest approved drawings were not found inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196725&prj=626&rqi=IU8Nr5SGd02InSXbAchkdUVIra
RT1MECH-6-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | Please provide permanent equipment labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196757&prj=626&rqi=znhfxxbP4zj7e6mLJuGHzxsgTf
RT1ELEC-3-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Please upload cable schedule documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196690&prj=626&rqi=ueC59pL87rsJJFoh0kvTsPRra1
RT1ELEC-3-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Door has scratches caused by interference with the panel body | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196695&prj=626&rqi=1NVlGfuUTm5zq0RQ9LL7HGUXhR
RT1ELEC-3-004 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Panel position does not match the latest approved drawing. Rear: 100 mm in drawing (actual 115 mm, side: 100 mm in drawing (actual 210 mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196694&prj=626&rqi=Lm0xRfkZHS7oAQnqx5tIFeSPf3
RT1ELEC-3-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Panel is not properly leveled during installation, panel found not level (tilted) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196692&prj=626&rqi=LZRiH4ru4jUN2swbzoFsJkYP6p
RT1ELEC-3-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Please upload HV cable design documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196691&prj=626&rqi=ZNDh1BUWl3o8xDfliXcZKEFo1M
RT1ELEC-3-006 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Visual inspection found defects, scratches, and dents on the panel body/door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196697&prj=626&rqi=SWit6i4XOHHskkONAaFFo1uv79
RT1MECH-45-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CA_D_05 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196547&prj=626&rqi=2u0LKwL4Yf7MGm55K8rz2Lq4Nu
RT1MECH-47-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CA_D_07 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196549&prj=626&rqi=NlmXNlQQXLj8ksvAXfjWmEvNRN
RT1MECH-43-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Torque verification of the unit anchor bolts at the corner positions could not be carried out due to limited access, as the torque wrench could not be properly applied. Confirmation of anchor bolt torque compliance with the specified criteria is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196539&prj=626&rqi=AdTfYH31kL4Kk1WPfkMi8Vc4rG
RT1MECH-46-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CA_D_06 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196548&prj=626&rqi=AHvfiHc3W4K1FP2cnwKUJdvmio
RT1MECH-48-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CA_D_09 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196550&prj=626&rqi=qemKhQ6I7mjvttRR9FERBD4Ek6
RT1MECH-25-003 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | FCU positioning does not comply with the latest approved drawings. For BOU, the drawing indicates 3500 mm (actual 3450 mm), and the wall-to-unit is specified as 450 mm (actual 550 mm). Alignment with the approved drawings is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196545&prj=626&rqi=KDdtsmWMTSabikuzXFhctahPpT
RT1MECH-49-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CA_D_11 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196551&prj=626&rqi=pwVfv7XRKntNllPcoCUXuCaDUC
RT1MECH-44-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning | Mechanical â€“Air | equipment | 1CA_D_03 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196546&prj=626&rqi=LtClSRuwc6UdNUiteuEblbBaoB
RT1MECH-46-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_06 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196430&prj=626&rqi=RAePtmHOYOKQPxoeUPMqDYOFuu
RT1MECH-45-003 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_05 | CA - Cool Array |  |  | Cable sensors need to FoD, tidy up and suggest adding spiral cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196429&prj=626&rqi=ZjsWkWS3xgS1dHo3ClT6y08r05
RT1MECH-27-003 | JK01-2 | APAC | Closed | P1 High CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | Positioning FCU have discrepancy between drawing and the actual onsite. Please refer to drawing attached, GC need to provide the clarification. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196461&prj=626&rqi=73o7Q1Bm9G2en3oyeHMo2qQKmK
RT1ELEC-2-007 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | The equipment was found in a dirty condition. Please provide temporary cover to protect from debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196472&prj=626&rqi=uiBElYWxMHrEx5Mq084uHy9pLD
RT1ELEC-2-001 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Please attach CxL2B testing methode | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196447&prj=626&rqi=eGsYRD61ecEwKWUItlgfWEldlr
RT1MECH-27-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | Equipment tagging ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196459&prj=626&rqi=WkgThI2fli0J5XczX8x3kqOafj
RT1MECH-45-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_05 | CA - Cool Array |  |  | Equipment tagging ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196428&prj=626&rqi=zuPK647nUxaTBZtRAXdUOqZkc1
RT1MECH-27-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | Missing document upload: - MoS - Material approval - QA QC report factory - Drawing installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196458&prj=626&rqi=MUGyzTJkMpT49GqaPLWegJ9cLZ
RT1MECH-49-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_11 | CA - Cool Array |  |  | Tagging equipment ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196438&prj=626&rqi=Yk63E0tQoe5dPA4p4dNHeh08DU
RT1ELEC-2-010 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Exposed copper conductor observed at control cable termination. Ferrule is missing or incorrectly crimped. Re-termination with correct ferrule required to ensure no bare copper is visible | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196476&prj=626&rqi=9McuSLbcxxp9LVn8BjSuDu2Azm
RT1MECH-44-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_03 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196424&prj=626&rqi=ZZQsYU6GQI4E7pNh92Rk4bEchX
RT1MECH-26-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | Equipment tagging ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196466&prj=626&rqi=8sk3oQAiGokFcvwJ4RQohMBgzh
RT1MECH-44-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_03 | CA - Cool Array |  |  | Equipment tagging ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196425&prj=626&rqi=qJvmHfBvKf6rkAIg5Kfr6vMaTe
RT1ELEC-2-002 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Please upload HV cable design is document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196448&prj=626&rqi=WaCAs0lyaqH8WUcJFkfei3a3Ed
RT1MECH-44-003 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_03 | CA - Cool Array |  |  | Bolt torque under 3 threads under the nuts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196426&prj=626&rqi=9usnDlIuil1ZjItpTgeMSNW9yo
RT1ELEC-2-003 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Gland plates are not installed on the RMU panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196449&prj=626&rqi=WD4ave8kUSE8F75RJLHGz4c3ay
RT1MECH-26-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | Missing document upload: - MoS - Material approval - QA QC report factory - Drawing installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196465&prj=626&rqi=uPYHZh8Bb47Gc63MlKjGNdd1Mk
RT1MECH-25-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | Missing document upload: - MoS - Material approval - QA QC report factory - Drawing installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196469&prj=626&rqi=E3iYbFSreCqCtzFXVr28M7hXEe
RT1MECH-26-003 | JK01-2 | APAC | Closed | P1 High CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | Positioning FCU have discrepancy between drawing and the actual onsite. Please refer to drawing attached, GC need to provide the clarification. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196468&prj=626&rqi=QVbAfnYTa40Aj8iT2ACBssX1Az
RT1MECH-25-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | equipment tagging not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196470&prj=626&rqi=pLD0xw8CpEnFroo4n5EX2JaJpJ
RT1MECH-47-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_07 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196432&prj=626&rqi=e30gReny4MJD41t4L4hYtP3HUr
RT1ELEC-2-008 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Permanent equipment labels were not installed. Equipment tagging with the correct language and approved colour scheme is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196473&prj=626&rqi=AivmTOwhYbaMQf5ZIsS8FLgwpT
RT1MECH-49-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_11 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196437&prj=626&rqi=2IWJOcfgzQJwjHPXdL6qsagyfF
RT1MECH-116-003 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | Internal panel need to FoD and cleaning inside the CRAH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196452&prj=626&rqi=p70izJwQG9M0r53q4GNzw0FMHF
RT1ELEC-2-009 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Verification of the circuit breaker serial number could not be carried out due to obstruction by MV cables under ongoing construction. The MCE vendor is required to provide clear photographs of the circuit breaker serial number for verification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196475&prj=626&rqi=gGeFIBxySWRcG3W3lLnEYTCHsT
RT1ELEC-2-004 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Surface scratches, stains, and paint marks were observed on the panel door and enclosure body. Rectification is required to meet project quality requirements | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196462&prj=626&rqi=iPLZOK4OZAsMqy08uvpVgzspAK
RT1ELEC-2-005 | JK01-2 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Latest GA and schematic drawings were not available within the panel. Drawings to be provided and installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196464&prj=626&rqi=pAt7nfsdPjnanhruA0T1UR650w
RT1MECH-116-002 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | Air opening not sealed yet to prevent debriss | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196451&prj=626&rqi=edMtA4vBC2fDc7lKXKDgqszrzi
RT1ELEC-2-006 | JK01-2 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | The switchgear tool board was not secured to the wall and was found placed on the floor. Proper installation and securing to the wall are required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196467&prj=626&rqi=lLH424QqJyFWpxa6o3OgdGLhhs
RT1MECH-47-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_07 | CA - Cool Array |  |  | Equipment tagging not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196433&prj=626&rqi=wKPXkk5BBOFbBt0mGTml4WcRkZ
RT1MECH-43-004 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Sensor cable needs to tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196423&prj=626&rqi=GEMZCi7MT5y9fyVDGdyK5gA0Jt
RT1MECH-46-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_06 | CA - Cool Array |  |  | Equipment ID tagging not yet installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196431&prj=626&rqi=0qrySplNxdnQscLxy8IIYdr33p
RT1MECH-117-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_62 | CRAH - Computer room air handler |  |  | Air opening not sealed yet onsite to prevent debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196455&prj=626&rqi=uKsrE2lNn0JhMEckyfHK8dCETP
RT1MECH-117-003 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_62 | CRAH - Computer room air handler |  |  | Need to FoD and cleaning inside the CRAH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196457&prj=626&rqi=xKHxpKIJ5CGcKO29FUN9Qq7g5b
RT1MECH-43-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Tagging ID equipment not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196421&prj=626&rqi=P4fGE4yDOrJN9OnL6LRkt8lxLI
RT1MECH-45-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_05 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196427&prj=626&rqi=oaEoPxmjEAEzhGLIznoks6A4T7
RT1MECH-43-003 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | bolt torque under 3 threats behind the nuts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196422&prj=626&rqi=6Wz6R2AsCaqD576Q7uSE2cEmrI
RT1MECH-48-003 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_09 | CA - Cool Array |  |  | Installation for 1CA_D_09 is not level. Please refer photo attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196436&prj=626&rqi=muH8bgN1APwfPgCxLegSg0e9Gr
RT1MECH-48-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_09 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196434&prj=626&rqi=uaWK3XB7V6R6asYgrulz5BUVze
RT1MECH-116-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | Tagging equipment ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196450&prj=626&rqi=B4Hdz7EUg0BAoV9AtbuCAGPOiO
RT1MECH-43-001 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196420&prj=626&rqi=tJ3Gz2dxRD7vpxmQh8IBDTkifU
RT1MECH-48-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_D_09 | CA - Cool Array |  |  | Equipment tagging ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196435&prj=626&rqi=Bt24bOsq4c0tOOGsAaGu0MruOa
RT1MECH-117-002 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CRAH_C_62 | CRAH - Computer room air handler |  |  | Equipment ID tagging not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196456&prj=626&rqi=SHnNstUjlZAbi5bbLiW5pk5a3p
RT1MECH-62-002 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196337&prj=626&rqi=gMA12faD8XyD4eh8mIMmXfV4wB
RT1MECH-57-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196325&prj=626&rqi=TUPQ7MpV4KY4ZIUP9hmSzfyDTW
RT1MECH-63-002 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_11 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196338&prj=626&rqi=0IMexQxvijrghSA1yjn5bqnnpH
RT1MECH-57-002 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196332&prj=626&rqi=4XYqtxSDBhoEDAuX2I5dvxKsFI
RT1MECH-59-002 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196334&prj=626&rqi=0hCBaYe6giAXD6WDF8aC7a4cgA
RT1MECH-62-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196330&prj=626&rqi=vPSRTGTLrNYYfoYRHzFqv3Jat7
RT1MECH-63-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_11 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196331&prj=626&rqi=ghXgKn5MCURzc3dgV1ORUmdO3f
RT1MECH-61-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196329&prj=626&rqi=mnWrzJhvzsIJIMyhYpJT4GHE8m
RT1MECH-60-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196328&prj=626&rqi=daIqfdBosi6SPXlYGixT6EpOlg
RT1MECH-60-002 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196335&prj=626&rqi=o1IV557QvGuSci5OzR0oQU9maJ
RT1MECH-59-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196327&prj=626&rqi=9hmFSBGKzhsAseS6YBMUvEnezz
RT1MECH-61-002 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196336&prj=626&rqi=7uSE4RbPrWBBB2oZMRhTwSnEax
RT1MECH-58-001 | JK01-2 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196326&prj=626&rqi=5mHT4o7wUOBlyixINwNhrd9YDk
RT1MECH-58-002 | JK01-2 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196333&prj=626&rqi=9JFJwRMj1tK6KffXo4aYeRr1vv
RT1MECH-620-001 | KL02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | MCP-1EF-M1-08 | MCP - Mech Control Panel |  |  | MCP-1EF-M1-08 Labeling incorrect | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631732&prj=647&rqi=fAdkEfqkBBceqjXdKTHwh096Lj
RT1MECH-621-001 | KL02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | MCP-1EF-M1-09 | MCP - Mech Control Panel |  |  | MCP-1EF-M1-09 Labeling Incorrect | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631733&prj=647&rqi=epNwtaSQ4STzxEaykAKOK4v8WF
RT1MECH-618-001 | KL02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-07-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_09 | EF - Exhaust Fan |  |  | 1EF_M1_09 The equipment tag does not attach as per approved naming convention | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627972&prj=647&rqi=UfaZAR1MTT2gXlmuNiGa39GVw4
GI-044 | KL02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-07-05 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_M1_08 | EF - Exhaust Fan |  |  | 1EF_M1_08 The equipment tag does not attach as per approved naming convention | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627973&prj=647&rqi=YhTkwgM6SDfHTyZ5hjxHGtIA5s
GI-039 | KL02-1/2 | APAC | Open | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Incomplete Connections | Commissioning | [6 empty] | [FWT] Fuel PLC Bench - Modulating valve trigger failed to close after failed to open trigger | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626839&prj=647&rqi=hpOmWKJ2nZNBfcFBOvAs8L2KSl
GI-038 | KL02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | [6 empty] | [FWT] Fuel PLC bench - No password protection & user selection for setpoint page and ATG setpoint modification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626838&prj=647&rqi=Bvi6mhashh345VpgBIiDhoYz7N
GI-041 | KL02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | [6 empty] | [FWT] Fuel PLC Bench - SOO mention the bulk tank 1 is lead signal is pump 2, lag signal is pump 2 and lead is pump 1; reversely bulk tank 2 is lead signal is pump 1, lag signal is pump 1 and lead is pump 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626841&prj=647&rqi=m67i4Togj63hySm9sQUhfI8OdI
GI-040 | KL02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | [FWT] Fuel PLC Bench - Fuel return valve open status should be to the lower fuel level Fbulk, but the return valve maintains to bulk tank 2; status remain until the following Fbulk detect high high level, following return valve faulty and fire mode; | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626840&prj=647&rqi=eM5GoRWkSjWi4uSAISviuCVdHR
GI-034 | KL02-1/2 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | [6 empty] | [FWT] Fuel PLC bench -1FP_M1_2, 1FP_M1_3, 1FP_HMI_1 and 1FP_HMI_2 tagging is block by the outer door panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626653&prj=647&rqi=4Wx4suNlv9DtL6RKFkLyn58cby
GI-032 | KL02-1/2 | APAC | Open | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation not issued/ Required | Commissioning | [6 empty] | [FWT] Fuel PLC Bench -Terminal block quantity and tagging different with approval construction drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626648&prj=647&rqi=Hs6DtORIxOy1SGNfVhpGmA9EWD
RT1MECH-766-002 | KL02-1/2 | APAC | Open | P2 Medium CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not complete | Commissioning | Fuel | equipment | 1FP_A_LCP_1 | FCP - Fuel Control Panel |  |  | [FWT} Fuel PLC bench -Fiber optic media converter is not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626652&prj=647&rqi=jX3jpDBDZV1CWrmVnEZfaEFhxE
RT1MECH-766-001 | KL02-1/2 | APAC | Open | P2 Medium CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning | Fuel | equipment | 1FP_A_LCP_1 | FCP - Fuel Control Panel |  |  | [FWT] Fuel PLC Bench -Setpoint of the voltage relay as default -Pump overload setting as default | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626654&prj=647&rqi=aEa73kpyNzhqdtcrzeLya7lezR
GI-036 | KL02-1/2 | APAC | Open | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning | [6 empty] | [FWT] Fuel PLC Bench - To standardize the equipment labelling at the HMI page, with approval naming convention | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626655&prj=647&rqi=FFSoBuzcb3s6m3qE9MyhdPlIdt
RT1MECH-772-001 | KL02-1/2 | APAC | Open | P2 Medium CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Incomplete Connections | Commissioning | Fuel | equipment | 1FP_HMI_1 | FCP - Fuel Control Panel |  |  | [FWT] Fuel PLC Bench - HMI setpoint is not sync between HMI 1 and HMI 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626656&prj=647&rqi=FzKGE4GuktTEhCfDfD9ct6kVVf
GI-029 | KL02-1/2 | APAC | Open | P3 Low CX | geoffreytan@commtechasia.com | 2026-05-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | [FWT] 1RPP_XX_01_XX 1. Name label of equipment missing 2. Spare Breaker label missing 3. MCMS Card label, too add identifier labels to the MCMS cards | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623428&prj=647&rqi=lFfsDF9jYifccI2eNXXQghz8wu
GI-028 | KL02-1/2 | APAC | Closed | P2 Medium CX | geoffreytan@commtechasia.com | 2026-05-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1LBSB_1 | LBSB - Loadbank Switchboard |  |  | [FWT] Bolt connections, bolt threads come out less than 3 threads above the nuts. To comply with Equinix Commissioning Playbook 6. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623425&prj=647&rqi=zLVbUCJ95wbyxxMyOns23r0AXy
GI-030 | KL02-1/2 | APAC | Open | P3 Low CX | geoffreytan@commtechasia.com | 2026-05-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | [FWT] 1RPP_XX_01_XX - Update the wiring drawing of the MCMS module, to indicate network cable position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623429&prj=647&rqi=qnpgGxSuw7izHhq6aPzXsLXkG8
GI-008 | KL02-1/2 | APAC | Closed | P3 Low CX | geoffreytan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | (FWT) Chiller tagging nameplate to be installed. Equipment S/N: 50612A68708365 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616929&prj=647&rqi=wqIKXq9uwpVpKh9WrWq8lBtpyb
GI-007 | KL02-1/2 | APAC | Open | P3 Low CX | geoffreytan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | (FWT) To install cover for emergency-stop button at chiller control panel. Equipment S/N: 50612A68708365 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616927&prj=647&rqi=42ezp8qD4UIZYLr0sgP5f7LVZb
GI-010 | KL02-1/2 | APAC | Closed | P3 Low CX | geoffreytan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Cleaning | Commissioning | [6 empty] | (FWT) Surface Rust to be cleaned off Equipment S/N: 50612A68708365 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616931&prj=647&rqi=sHDOjobegEEXEZV4nq2c5Saa8F
GI-011 | KL02-1/2 | APAC | Open | P3 Low CX | geoffreytan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning | [6 empty] | (FWT) VSD Panel incoming breaker setting for LSIG to be provided by JCI. Equipment S/N: 50612A68708365 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616932&prj=647&rqi=3I02lUAMsIavtXKf2HdUJCh1L1
GI-009 | KL02-1/2 | APAC | Open | P3 Low CX | geoffreytan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | (FWT) To install missing labelling for cables within control panel. Equipment S/N: 50612A68708365 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616930&prj=647&rqi=k33M490GLTalwrnbslNpfSTFmp
GI-006 | KL02-1/2 | APAC | Open | P3 Low CX | fazandrayusfiandika@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS | [6 empty] | (FWT) DCOS test was conducted based on the pending signed off SICD by the DCOS SI. Observed changes and additions to DCOS point mapping as follows: - Output Breaker 1 Status (CB3A): Modbus address changed from 607 â†’ 609. - Output Breaker 1 Status (CB3B): Point to be removed. - Equipment Over Temperature Warning: To be added (address range 686â€“702). - SCR 1 Shorted: To be added (address range 839â€“847). - SCR 2 Shorted: To be added (address range 873â€“881). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197981&prj=647&rqi=7DgQNfWupkZ2HLYbHmpJ1Vqfwj
YT1MECH-6-001 | LD06 | N-EMEA | Ready for Verification | P3 Low CX | andrew.sharp@implexcritical.com | 2026-08-06 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | TCS/SFN - 01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | Confirm TSC/SFN pipework has been flushed in accordance with the Equinix TCS/SFN Cleaning and Flushing Requirements and all documentation including test equipment calibration certificates are uploaded, reviewed and CxA approved on the Equinix document platform | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632577&prj=675&rqi=scB5BDWZBPlyU3mY0cWHPor8KF
GT1MECH-11-001 | LD06 | N-EMEA | Open | P3 Low CX | andrew.sharp@implexcritical.com | 2026-08-06 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | TCS/SFN - 01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | Confirm (if applicable) any EoR/EQX approved as-built drawings have been uploaded to Equinix document control platform. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632614&prj=675&rqi=YhTgFAkEJmDz4YCXxA5p8cXvpx
RT1MECH-6-002 | LD06 | N-EMEA | Closed | P3 Low CX | andrew.sharp@implexcritical.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | TCS/SFN - 01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | It is recommended that protective caps/covers are fitted to the stems of the PICVs to protect against any potential damage. This comment is applicable to all the TCS/SFN PICVs and the Primary CHW PICVs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628520&prj=675&rqi=WLTd3naSapZ7tbyt3QOwfNW0X1
RT1MECH-6-001 | LD06 | N-EMEA | Closed | P3 Low CX | andrew.sharp@implexcritical.com | 2026-06-18 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | TCS/SFN - 01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | Confirm the EoR/EQX approved DCOS points list has been uploaded to Equinix document control platform. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626206&prj=675&rqi=nGyKVn34Gs78W8HExZmDE3XX6y
GI-017 | LD07.2-P1 | N-EMEA | Closed | P1 High CX | eosman@global-cxm.com | 2026-04-29 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | [6 empty] | UPS-13 Module 4 keeps dropping load during 4 hour heat run. Testing cancelled. Schneider and Socomec investigating | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620004&prj=617&rqi=i14lKYO8s26cpfuuvlhLYzBrns
GI-015 | LD07.2-P1 | N-EMEA | Closed | P3 Low CX | eosman@global-cxm.com | 2026-04-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning | [6 empty] | LV-13 Micrologic Damaged to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618350&prj=617&rqi=yBXybOO3SF1bSnzAznJemXE2ek
GI-014 | LD07.2-P1 | N-EMEA | Closed | P3 Low CX | eosman@global-cxm.com | 2026-03-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning | [6 empty] | PPR's for LD7.2 P2 - Armstrong FAT not including DCOS works carried out due to limitations of equipment being available. To be captured as on site witnessing when available | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616257&prj=617&rqi=KPMqGt9OSfYK19SrTub6KJdGFh
GI-012 | LD07.2-P1 | N-EMEA | Closed | P2 Medium CX | eosman@global-cxm.com | 2026-02-19 04:00:00.000 +0400 | Equinix Commissioning Manager |  | Component/Equipment Failure | Commissioning | [6 empty] | PT100 Sensor on TX-16-D Failed, 6x Replacements have been ordered, Request to replace all PT100 as a preventative measure from Equinix | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199662&prj=617&rqi=aTaVIirCrILPApDwAa8m2vIxLu
RT1ELEC-1-001 | LD07.2-P2 | N-EMEA | Open | P3 Low CX | eosman@global-cxm.com | 2026-08-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Incomplete Connections | Commissioning | Electrical â€“ MV | equipment | GEN-8-01 | GENM - Generator |  |  | LV/ELC Cable entrance box has been left detached and inside the unit to allow steel works to be erected with out hindrance (LOR) to fix in place when they complete their steel gantries. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633013&prj=687&rqi=zntIgBnLoLh1YMOlGYK5PcIZiq
GI-004 | LD07.2-P2 | N-EMEA | Closed | P3 Low CX | jhancill@global-cxm.com | 2026-07-28 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning | [6 empty] | All chillers waiting on shrouding to be installed in front of L1-L3 cables inside panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631146&prj=687&rqi=coYEfD8QmgtuOT1b4OePND92el
GI-003 | LD07.2-P2 | N-EMEA | Open | P3 Low CX | jhancill@global-cxm.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning |  | equipment type |  |  |  |  | All new AACC's missing asset ID's | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624337&prj=687&rqi=3vAPVwjrA8vdDsDSWhqHCUukOO
GI-002 | LD07.2-P2 | N-EMEA | Closed | P3 Low CX | eosman@global-cxm.com | 2026-05-28 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning | [6 empty] | PPR's for LD7.2 P2 - Armstrong FAT not including DCOS works carried out due to limitations of equipment being available. To be captured as on site witnessing when available | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623352&prj=687&rqi=j63LQDJ1n2rPoy6dnMLeJfKS8r
GI-149 | LD09-P2 | N-EMEA | Closed | P2 Medium DCOS | Alen.Francis@eu.equinix.com | 2026-01-29 04:00:00.000 +0400 | Facility Manager |  | DCOS Comms Issue/ Fault | Commissioning | [6 empty] | GDC Requires the folowing Items to be clear of Alarms so they are Resilient. These Items are customer impacting. LD9.PG2_CRAC_12A_01 LD9.PG2_CRAC_12A_02 LD9.PG2_CRAC_12B_01 LD9.PG2_CRAC_12B_02 LD9.PG2_CRAC_12C_01 LD9.PG2_CRAC_12C_02 LD9.PG2_CRAC_12D_01 LD9.PG2_CRAC_12D_02 LD9.PG2_CS_2_3 LD9.PG2_CTA_2_3 LD9.PG2_CTB_2_3 LD9.PG2_UPA_12M | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197891&prj=308&rqi=HEsXwWXejsy1a3BAcB2huHbntm
GI-148 | LD09-P2 | N-EMEA | Closed | P3 Low DCOS | Alen.Francis@eu.equinix.com | 2026-01-29 04:00:00.000 +0400 | Facility Manager |  | DCOS General Issue | DCOS | [6 empty] | GDC Item outstanding in DCIM LD9.PG2.RMU_M_RMU_L2_BSM: measure_active_power SUDB-2 Utility Incomer Power factor GSB3 Gen Incomer Frequency GSB4 Gen Incomer Frequency GSB5 Gen Incomer Active Power GSB5 Gen Incomer Frequency GSB6 Gen Incomer Frequency Issue: These Points cannot be proven at the moment as there is no load on the MV equipment. Can this be proven once load is availble | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197885&prj=308&rqi=SPhCsANNKGHka323cd6davuuDF
YT1ELEC-677-001 | LD14-1 | N-EMEA | Open | P3 Low CX | jknight@global-cxm.com | 2026-09-01 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1HEAT_R1_411 | AH - Air Heater |  |  | Earth on heater frame comes off TX earth bar. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636284&prj=646&rqi=KxM1GZQReJa3KsMIoU0VRtHuvS
GI-069 | LD14-1 | N-EMEA | Closed | P2 Medium CX | jknight@global-cxm.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1EB_PUR1_1 | ERTH - Earthing |  |  | Single link earth bar fitted. Earth bar does not match drawing or spec and main earths are doubled up on one stud. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635550&prj=646&rqi=XAUgijkTN40sEQfFKuEpiIT16T
GI-068 | LD14-1 | N-EMEA | Open | P3 Low CX | jknight@global-cxm.com | 2026-08-19 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1EBPPR-M1_8 | ERTH - Earthing |  |  | Two studs on the earth bar have snapped off inside the nut. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634375&prj=646&rqi=D3fDK87hYt55OUwkUgdXaNqlPZ
RT1FD-104-001 | LD14-1 | N-EMEA | Open | P3 Low CX | abadat@global-cxm.com | 2026-08-06 04:00:00.000 +0400 | VER - Vertiv | L2A | Labelling | Commissioning | Fire Detection | equipment | LD14_FAP_06_01 | FP - Fire Panel |  |  | No identifying label attached. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632710&prj=646&rqi=5lmNmnIBDLvo2y8np7L896UIWe
RT1FD-104-002 | LD14-1 | N-EMEA | Open | P3 Low CX | abadat@global-cxm.com | 2026-08-06 04:00:00.000 +0400 | VER - Vertiv | L2A | Installation not correct | Commissioning | Fire Detection | equipment | LD14_FAP_06_01 | FP - Fire Panel |  |  | The FAP door cannot be opened and closed properly. The interfaces below are installed too close to the FAP. There should be a spacer in between the interfaces and the FAP in order to allow the door to open/close as intended. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632711&prj=646&rqi=i2w61dbhQoKjJWJvuqaVlq0S4g
YT1ELEC-718-001 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-07-16 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1EBLV_M1 | ERTH - Earthing |  |  | Cable References to be Confirmed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629822&prj=646&rqi=8QMjvfwnSVXnADyuwqof6lBYYf
GI-053 | LD14-1 | N-EMEA | Open | P3 Low CX | jknight@global-cxm.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | Electrical â€“ MV | equipment | 1MVTB_R1_HMI | HMI - HMI Panel |  |  | Cable ID missing from earth. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628602&prj=646&rqi=w18uniYLdJXJWbypHD7QobT1ks
RT1ELEC-729-001 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-07-02 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1EBPPR-M1_6 | ERTH - Earthing |  |  | asset ID not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627710&prj=646&rqi=H6nbxtNtxAC5i6lBJ6VucCy0Cx
RT1ELEC-730-001 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-07-02 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1EBPPR-M1_7 | ERTH - Earthing |  |  | asset ID not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627715&prj=646&rqi=fPQIPOSCzmsGt8etAQ5NAKZxv8
RT1ELEC-731-001 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-07-02 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1EBPPR-M1_8 | ERTH - Earthing |  |  | asset ID not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627716&prj=646&rqi=uTP1ZfRWsc15ROCjhTvqEWDENv
RT1ELEC-682-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-07-01 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1HEAT_R1_411 | AH - Air Heater |  |  | Permanent labels not attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627575&prj=646&rqi=dzMrRGZsOBweMPADB84lV9Z8nw
GI-040 | LD14-1 | N-EMEA | Closed | P2 Medium CX | ganderson@global-cxm.com | 2026-06-17 04:00:00.000 +0400 | General Contractor |  | Installation Damage | Commissioning | [6 empty] | Critical MeWall - UPS Switch Room M1 - water ingress took place in switch room M1 due to the removal of the Roxtec blocks. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625666&prj=646&rqi=JlllZklp5bE6kIlIhYDMg1JwJT
RT1MECH-687-001 | LD14-1 | N-EMEA | Open | P3 Low CX | gharbottle@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1WT_M1R1_FLT_03 | WT - Water treatment |  |  | Missing permanent asset label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624835&prj=646&rqi=tUufoH8cs6WrBPojLiJv1RuB3e
RT1MECH-688-001 | LD14-1 | N-EMEA | Open | P3 Low CX | gharbottle@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1WT_M1R1_FLT_04 | WT - Water treatment |  |  | Missing permanent asset label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624836&prj=646&rqi=a3wIZMOI83Phw84ffYGK8P9YDc
GI-032 | LD14-1 | N-EMEA | Open | P3 Low CX | jknight@global-cxm.com | 2026-05-14 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MEB_A | ERTH - Earthing |  |  | Asset labels missing for earth bar. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621958&prj=646&rqi=4bqxYO5Mt34tDsfkIiRhe932j5
RT1MECH-586-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-05-04 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_312 | DXID - FCU/DX Indoor Unit |  | FXHQ100AVEB8 | No asset identification label present on installed FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620375&prj=646&rqi=XsyIRA7abKfr5HrZtvyvkO0hq8
RT1MECH-593-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-05-04 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_410 | DXID - FCU/DX Indoor Unit |  | FXHQ100AVEB8 | No asset identification label present on installed FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620374&prj=646&rqi=5g5PXKRaU4pLEsDxVSrOThmORr
RT1ELEC-79-001 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-04-30 04:00:00.000 +0400 | SCH - Schneider Electric | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1MVTB_C_HMI | HMI - HMI Panel |  |  | HMI selector key set (supplied as a pair) includes one bent key. The second key remains in good condition | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620096&prj=646&rqi=alUmiEJp7gtfuPFy6xtbRUQZ0v
RT1ELEC-75-001 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-04-30 04:00:00.000 +0400 | SCH - Schneider Electric | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1MVTB_R1_HMI | HMI - HMI Panel |  |  | Damaged keys for the HMI selector | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620112&prj=646&rqi=Kt4eemOITtr69LoZBSss8wT004
RT1ELEC-75-002 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-04-30 04:00:00.000 +0400 | SCH - Schneider Electric | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1MVTB_R1_HMI | HMI - HMI Panel |  |  | Two identification labels missing within HMI panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620113&prj=646&rqi=WME4Uttsbwk2ZK7P82YomXGlJw
RT1ELEC-76-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-30 04:00:00.000 +0400 | SCH - Schneider Electric | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1MVTB_M1_HMI | HMI - HMI Panel |  |  | Key snapped within generator selector switch barrel on HMI | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620114&prj=646&rqi=8KIBoEs8qkzYX2AD9LfZ7vkO4J
RT1MECH-307-002 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_410 | DXID - FCU/DX Indoor Unit |  | FXHQ100AVEB8 | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618073&prj=646&rqi=XAWcJzV74xxMWmfQdMujLwyEhx
RT1MECH-307-001 | LD14-1 | N-EMEA | Closed | P2 Medium CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Installation Damage | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_410 | DXID - FCU/DX Indoor Unit |  | FXHQ100AVEB8 | During RT inspection, FCU casing damage was noted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618070&prj=646&rqi=1zuWRTChEzkm13HIiybIuszeWO
RT1MECH-663-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_206 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618037&prj=646&rqi=xJ1jSrrzfvrnPKVAId7Sy3zno8
RT1MECH-673-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_A_412 | DXID - FCU/DX Indoor Unit |  |  | Install correct asset ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617976&prj=646&rqi=pvOsnJxsp5VVYOunUaK702Wl7b
RT1MECH-672-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_411 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617970&prj=646&rqi=17rTq14bseQvaHj35kOJJN45it
RT1MECH-660-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_A_211 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618050&prj=646&rqi=XehpXYSuIRHIBfn0W5UXcKAAm1
RT1MECH-662-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_A_205 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618036&prj=646&rqi=bexdWxeH4Lh6SrRM0b6gUc8EC5
RT1MECH-661-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_212 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618051&prj=646&rqi=sh2TnZS8MU3MV43wOTOJ1l0eti
RT1MECH-655-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_M1_111 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618054&prj=646&rqi=u8mU6QNgKCxpJRWLwvyfCCECJ2
RT1MECH-649-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_M1R1_010 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617568&prj=646&rqi=2FYXv3tN8p5eMB9MALiyHq8Kyp
RT1MECH-650-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_M1_011 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617565&prj=646&rqi=CZ7WYECXzxWBUo86oyGJAZmhHU
RT1MECH-656-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_112 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617563&prj=646&rqi=Q0hsE9F79ZlLqSdJRq86qoN3eX
RT1MECH-654-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_M1R1_110 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617567&prj=646&rqi=JAGmHrBPhGEguLcFdOBpvHfHHG
RT1MECH-664-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-07 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_A_310 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617493&prj=646&rqi=S6yEBHbQF5WGQ3OHBqOrrOjS7E
RT1MECH-665-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-07 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_311 | DXID - FCU/DX Indoor Unit |  |  | No asset Id on fcu | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617509&prj=646&rqi=gETxuXvL7O5PLTqh1qZBEinm6h
RT1MECH-651-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-27 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_012 | DXID - FCU/DX Indoor Unit |  |  | FCU installed without permanent equipment/asset identification label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616711&prj=646&rqi=tajgT2HRH5GdCJw4m0kIcAvWro
RT1MECH-658-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-27 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_114 | DXID - FCU/DX Indoor Unit |  |  | FCU installed without permanent equipment/asset identification label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616708&prj=646&rqi=ClJ3kqpnMmH4xx9GclNCOzsfUU
RT1MECH-653-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-27 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_014 | DXID - FCU/DX Indoor Unit |  |  | FCU installed without permanent equipment/asset identification label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616710&prj=646&rqi=1GTyCnbGexybd5IOQFVEb2W8Ip
RT1MECH-670-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_305 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615942&prj=646&rqi=tuNCOu2oBNKZRzgCI2TQNRYg24
RT1MECH-671-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_C_306 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615948&prj=646&rqi=1497RgP4HqM92SvLKesRRWaUEp
RT1MECH-667-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_R1_302 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615952&prj=646&rqi=PpaSHnSPgrKBEdMNaVhvcvaVdC
RT1MECH-668-001 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_M1R1_303 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615949&prj=646&rqi=Ud7zAv6RupuwfqvjkBSreg5Csz
RT1MECH-669-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_A_304 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615947&prj=646&rqi=0bAahXwDDPZAWwLTcjqL0nAdZL
RT1MECH-674-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-16 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_R1_401 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615800&prj=646&rqi=wF0xSTYIVZD0AqrhtExLD6xk3P
RT1MECH-675-001 | LD14-1 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-03-16 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_B_402 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615810&prj=646&rqi=jZ2SDHNfA4BHBOhySD8Zga2Zfi
RT1MECH-676-001 | LD14-1 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-16 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1FCU_H_403 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615816&prj=646&rqi=FclG3m5nRvCaGRJQ7gkrGP43LQ
GI-027 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General FWT/FAT Issue | Level 1 FWT | [6 empty] | BAC Cooling Tower - during the FAT inspection it was found that there is sharp edging on the stainless steel profile strips on the external corners of the unit that require dressing or chamfering. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198780&prj=646&rqi=bksvb2UuO6gZDTV0D1YHEJfMdZ
GI-031 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General FWT/FAT Issue | Level 1 FWT | [6 empty] | BAC Cooling Tower - During the visual inspection of the unit at the FAT it was noted that there is a slight weep between two mating surfaces of the basin module and the lower chamber wall. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198796&prj=646&rqi=A7eoeVi2xMMWeIAeD2MexUTBQr
GI-030 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General FWT/FAT Issue | Level 1 FWT | [6 empty] | BAC Cooling Tower - It was noted during the FAT that there was slight misalignment of the plates used for locking/securing of the access doors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198795&prj=646&rqi=yKbVTwZfpL9BQnmpXMDFWPHRUG
GI-029 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General FWT/FAT Issue | Level 1 FWT | [6 empty] | BAC Cooling Tower - during the FAT it was noted that the internal wire mesh to support the internal insulation of the upper chamber is not fitted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198784&prj=646&rqi=XJYBVRulsxyviyC9yrJc5m712O
GI-026 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General FWT/FAT Issue | Level 1 FWT | [6 empty] | During the BAC FAT for the cooling tower it was noted that earthing points/lugs were not fitted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198768&prj=646&rqi=lIPGKZqIQkRU2SaAC6SzBaAyQr
GI-019 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-02 04:00:00.000 +0400 | REH - Rehlko Gens |  | Missing Components | Commissioning | [6 empty] | Generators - Selective Catalytic Reducers: The SCR units were delivered to site without protective covers fitted to the exhaust outlet flanges. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198198&prj=646&rqi=Z4UEvzt8dbXYNi2d7BtCOgRDAM
GI-018 | LD14-1 | N-EMEA | Closed | P2 Medium CX | ganderson@global-cxm.com | 2026-01-26 04:00:00.000 +0400 | VER - Vertiv Electrical |  | General FWT/FAT Issue | Level 1 FWT | [6 empty] | Critical MeWall E-house - Transformer has been supplied without anti-vibration pads. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197574&prj=646&rqi=D56lc0Ts4S58rv7oWnHnvrl4Xi
GI-017 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-01-22 04:00:00.000 +0400 | SCH - Schneider Electric |  | General FWT/FAT Issue | Level 1 FWT | [6 empty] | SUDB E-house B - protective conduit to be fitted to DX unit external condensers' piping/cabling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197514&prj=646&rqi=DjS7SUd9AAjrK041FIBKKxt4Ok
GI-016 | LD14-1 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-01-22 04:00:00.000 +0400 | SCH - Schneider Electric |  | General FWT/FAT Issue | Level 1 FWT | [6 empty] | SUDB E-house A - protective conduit to be fitted to DX unit external condensers' piping/cabling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197513&prj=646&rqi=RWiIDk2IOSzQwEXYOUQ0jMneDl
RT1MECH-321-001 | LD14.2 | N-EMEA | Closed | P3 Low CX | gharbottle@global-cxm.com | 2026-06-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_M2_17 | VRF - Variable Refrigerant Flow System |  |  | Missing permanent asset label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625068&prj=686&rqi=t3xKQRxwtoj30gc9hzi5smHoz3
RT1MECH-319-001 | LD14.2 | N-EMEA | Closed | P3 Low CX | gharbottle@global-cxm.com | 2026-06-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_R1_15 | VRF - Variable Refrigerant Flow System |  |  | Missing permanent asst label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625064&prj=686&rqi=rY4cx39Fp8N8a5QHURjsxTuADG
RT1MECH-320-001 | LD14.2 | N-EMEA | Closed | P3 Low CX | gharbottle@global-cxm.com | 2026-06-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1VRFOD_M1_16 | VRF - Variable Refrigerant Flow System |  |  | Missing permanent asset label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625066&prj=686&rqi=M65VF0iqsesAFNsMYTtXix65Lx
GI-053 | LS02-1 | S-EMEA | Closed | P3 Low DCOS | Alen.Francis@eu.equinix.com | 2026-01-29 04:00:00.000 +0400 | Equinix Ops |  | Design correction needed | Design | [6 empty] | GDC Requires the following to be actioned. Due to Low Load in the building and multiple assets in a alarm local Ops needed to open up alarm bands to stop the large amount of alarms coming through to the EOC Please when load is availble can they be put back to the commissioned settings as per smartsheet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197892&prj=455&rqi=fE15mCDYJyNDv5RhJH2vxhfOWA
YT1ELEC-191-002 | LS02-2 | S-EMEA | Open | P3 Low CX | radek.kmak.ext@bureauveritas.com | 2026-09-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1SUDB_01 Feeder Q2 (Feeder to RMU_E) | SUDB - Secondary Utility Distribution Board |  |  | Poor containment installation, bent containment, missing and damaged covers. Missing firestopping | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638070&prj=674&rqi=Gm8fOXTW6HAaGl1x6eXZazFfu3
YT1ELEC-191-001 | LS02-2 | S-EMEA | Open | P3 Low CX | radek.kmak.ext@bureauveritas.com | 2026-09-14 04:00:00.000 +0400 | SCH - Schneider Electric | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1SUDB_01 Feeder Q2 (Feeder to RMU_E) | SUDB - Secondary Utility Distribution Board |  |  | Verify permanent equipment labels affixed, contract specific label colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637946&prj=674&rqi=lGGJMqTw4Qehf9r6aho8YnmGlR
GT1ELEC-123-002 | LS02-2 | S-EMEA | Open | P3 Low CX | radek.kmak.ext@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning | Electrical â€“ MV | equipment | 1SUDB_02 Feeder Q4 (Bypass from SUDB_01) | SUDB - Secondary Utility Distribution Board |  |  | Confirm Live test results (SAT) uploaded to Asite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636720&prj=674&rqi=qzrB9s643sWgirdF7USxxKmkqx
GI-010 | LS02-2 | S-EMEA | Closed | P2 Medium CX | gabriel.matiasarnal@bureauveritas.com | 2026-08-05 04:00:00.000 +0400 | General Contractor |  | General Design Issue | Design |  | equipment type |  |  |  |  | As per Site Specification for Earthing, LS021-QUA-XX-XX-RP-E-ERTH-8001-Earthing. "Separate protective earth networks shall be provided for low voltage and medium voltage of metallic enclosures of electrical panels and equipment" and "Protective grounding system, consisting of the grounding lines and the corresponding grounding electrodes that directly connect to ground the conductive parts of the installation elements not normally subjected to electrical voltage, but which could be put under voltage by faults or accidental contacts, in order to protect people against contacts with dangerous voltages." Under that definition the Container Housing the Generator should have a grounding connected to the BTP Gen and the cable schedule doesnt reflect this. Please confirm if Generator Container needs a Grounding Bound | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632247&prj=674&rqi=ETLImofjm15mmIXCgXhdcfzqUe
GI-011 | LS02-2 | S-EMEA | Closed | P2 Medium CX | gabriel.matiasarnal@bureauveritas.com | 2026-08-05 04:00:00.000 +0400 | General Contractor |  | General Design Issue | Design | [6 empty] | As per Site Specification for Earthing, LS021-QUA-XX-XX-RP-E-ERTH-8001-Earthing. "Separate protective earth networks shall be provided for low voltage and medium voltage of metallic enclosures of electrical panels and equipment" and "Protective grounding system, consisting of the grounding lines and the corresponding grounding electrodes that directly connect to ground the conductive parts of the installation elements not normally subjected to electrical voltage, but which could be put under voltage by faults or accidental contacts, in order to protect people against contacts with dangerous voltages." Under that definition the Metal Frame holding the chiller should have a grounding connected to the BTP Roof 2 and the cable schedule doesnt reflect this. Please confirm if Chiller Metal Frame needs a Grounding Bound | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632270&prj=674&rqi=9vyA2L79CymJCjRp57UqTpYKpZ
GI-008 | LS02-2 | S-EMEA | Closed | P2 Medium CX | lars.dietrich@bureauveritas.com | 2026-07-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Position of Fuel-Kill-Valve. The blow fuse is located in the Air-Intake right next to the FDAY of the Generator Container. See drawings attached. In event of fire, which occurs usually at the Motor these fuses will not trigger as permanently cooled by the Inlet Air. Please review design and explain how the system should operate in event of fire. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630861&prj=674&rqi=VMytuuVqx1BpLYrrRGuKiwB8Kq
GI-009 | LS02-2 | S-EMEA | Closed | P2 Medium CX | lars.dietrich@bureauveritas.com | 2026-07-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | No Drip-Trays under ACC on the Roof. there are no drip trays installed underneath ACC`s. Trane uses POE oil in DX cycle and Glycol N in FC cycle. Both are prohibited to enter rainwater drains or sewer. Please provide the plan to prevent the Glycol and POE oil to enter rainwater drain in event of leak. Even oil separator in rainwater drain ,might still allow the POE to enter and pollute nearby river as POE is made of Acid and Alcohol. Getting in touch with water, it splits up in itÂ´s origin substances and might not be captured by oil separator. Please explain how to prevent substances used in ACC to enter rainwater drainage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630867&prj=674&rqi=CMfHqIXUaJbcVnKA5eaD8kjYCX
GI-007 | LS02-2 | S-EMEA | Open | P3 Low CX | gabriel.matiasarnal@bureauveritas.com | 2026-07-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation not issued/ Required | Commissioning | [6 empty] | LVSB C1/D1/E1 Aux Switchboard generator Technical submitall and drawings not matching installation Your installation and O&M manual (LS021-STE-GT-B1-OM-E-GENL-7063-Switchboard Panel â€“ SWAUX01 O&M Manual-AB01-Phase 2) has only one socket X1.1 However on TN and Drawings on doc holder it has two more sockets, please remove it from TN and reupload new version on ASITE, place correct drawings on panels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630555&prj=674&rqi=rP7uvOpI29ZbyLh83uT4bxXtWN
GI-006 | LS02-2 | S-EMEA | Closed | P2 Medium CX | gabriel.matiasarnal@bureauveritas.com | 2026-07-17 04:00:00.000 +0400 | SOC - Socomec |  | Missing Components | Commissioning | [6 empty] | Internal Busbar connection missing a washer Confirm if bolt and nut wont be affected by vibration when loaded without a washer installed or if STS busbars need extra washers to be installed (Torque mark on the other side, missing the double torque mark but a different issue was created for it) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629881&prj=674&rqi=n9fDFIAFdPpz1k5tJ95G4OpCvD
GI-005 | LS02-2 | S-EMEA | Closed | P2 Medium CX | gabriel.matiasarnal@bureauveritas.com | 2026-07-17 04:00:00.000 +0400 | SOC - Socomec |  | Torque required | Commissioning | [6 empty] | On STS Q30 Connection without washer and less than one thread out If its a design constraint because of space please confirm that installation is ok | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629880&prj=674&rqi=GLJDZmVM4eMhbu2i2BUR97D2JX
GI-004 | LS02-2 | S-EMEA | Closed | P3 Low CX | gabriel.matiasarnal@bureauveritas.com | 2026-07-16 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | [6 empty] | Following RPPs missing permanent labels and arc flash label: 1RPP_CR_1_6 1RPP_CR_2_3 1RPP_CR_2_6 1RPP_DR_1_1 1RPP_DR_1_2 1RPP_DR_1_4 1RPP_DR_1_5 1RPP_DR_1_8 1RPP_DR_2_1 1RPP_DR_2_2 1RPP_DR_2_4 1RPP_DR_2_5 1RPP_DR_2_8 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629609&prj=674&rqi=1082vasf4dXBYwEiDaWxWTcoRj
GI-002 | LS02-2 | S-EMEA | Open | P3 Low CX | gabriel.matiasarnal@bureauveritas.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | Generators missing docs on holder | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628546&prj=674&rqi=AtM5sDnnGNGHPL8Wt6znSbBXF9
RT1ELEC-176-002 | LS02-2 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LVSB_C_2 | LVSB - Low Voltage Switchboard |  |  | loose earthing cable termination Carry out full visual inspection of panel and confirm no defects, scratches, dents, abnormalities | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627322&prj=674&rqi=fDmNpfJ5dphl4EvVreW0OmpqKi
RT1ELEC-142-002 | LS02-2 | S-EMEA | Open | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-25 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1SUDB_02 Feeder Q4 (Bypass from SUDB_01) | SUDB - Secondary Utility Distribution Board |  |  | Multiple dents and scratches Confirm SUDB delivery visual Inspection/checklist is complete with defects noted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626907&prj=674&rqi=UovJ700p3TVvuebraVAp7DVd3n
GT1ELEC-123-001 | LS02-2 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-25 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ MV | equipment | 1SUDB_02 Feeder Q4 (Bypass from SUDB_01) | SUDB - Secondary Utility Distribution Board |  |  | Live circuits not having right colour. grey instead of white. Please check upstream to downstream. Refer to attached screen shots. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626880&prj=674&rqi=0AgNK6LFNC9Qv4pBfCR5SP4y8Q
RT1ELEC-142-003 | LS02-2 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-25 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Torque required | Commissioning | Electrical â€“ MV | equipment | 1SUDB_02 Feeder Q4 (Bypass from SUDB_01) | SUDB - Secondary Utility Distribution Board |  |  | qa4 earth termination missing torque marks. Broken torque marked. Tightness of bolted electrical connections by calibrated torque-wrench method in accordance with manufacturerâ€™s published data. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626908&prj=674&rqi=usLfvQnlPPF40dvA2H5VPTV0Bm
RT1ELEC-142-001 | LS02-2 | S-EMEA | Closed | P2 Medium CX | ismail.kose@bureauveritas.com | 2026-06-25 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1SUDB_02 Feeder Q4 (Bypass from SUDB_01) | SUDB - Secondary Utility Distribution Board |  |  | SUDB_02/Q2: Visual copper spots at ct control cable. BX13 - 9 Earth cable csh200 -S2pe Carry out full visual inspection of switchboard and confirm no defects, scratches, dents, abnormalities | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626906&prj=674&rqi=T211mLLKUm3TCrhheNXslnO5Jl
RT1ELEC-178-002 | LS02-2 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1LVSB_C_4 | LVSB - Low Voltage Switchboard |  |  | Verify Installation of equipment is complete in final location and as per Manufacturers Spec. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624971&prj=674&rqi=Dea3T8bEfRlbcfrewSYMkzFtGp
RT1ELEC-178-003 | LS02-2 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1LVSB_C_4 | LVSB - Low Voltage Switchboard |  |  | main power supply should be torque marked after being torqued with a certified torque wrench. source: Verify Internal bolted electrical connections tightened by calibrated torque-wrench method in accordance with manufacturerâ€™s published data. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624972&prj=674&rqi=B15RGq3dzSMrY4kRdkQRCuor9G
RT1ELEC-186-002 | LS02-2 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1LVSB_R_11 | LVSB - Low Voltage Switchboard |  |  | door hinges support/locking mechanism broken Carry out full visual inspection of panel and confirm no defects, scratches, dents, abnormalities | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624973&prj=674&rqi=RKGtMJq9k8HYEXOkoEHBkkM2S6
GI-001 | LS02-2 | S-EMEA | Closed | P2 Medium CX | serdar.tuccaroglu@bureauveritas.com | 2026-05-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation not issued/ Required | Commissioning | [6 empty] | 75 L2A checklists have been scheduled to be completed by 22/05/2026 while only 41 are signed off, 24 are awaiting documentation and 5 are in progress: Actual vs Planned L2A Commissioning Ratio is 55%. GC Project Cx schedule is not accurate and not aligned with the FG timeline monitor. GC 2WLA is not accurate and not aligned with the FG timeline monitor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622956&prj=674&rqi=L38TJmm1dgbkBy8Ak5sJz1UJRe
RT1ELEC-179-001 | LS02-2 | S-EMEA | Closed | P3 Low CX | andrew.mercer@bureauveritas.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LVSB_C_5 | LVSB - Low Voltage Switchboard |  |  | Technical submittal is provided only in Portuguese. As per Playbook 6.1 Section 1.2.1.1., all commissioning documentation through Cx levels 0 to 6 is mandatory to be written in English, local language can supplement the English language documents based on region specific requirements. Where a discrepancy between English and local language arises in a document, the English language form takes precedence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622467&prj=674&rqi=mMUvWgvnJ1hedvz93enJw8D1Ir
RT1ELEC-176-001 | LS02-2 | S-EMEA | Closed | P3 Low CX | andrew.mercer@bureauveritas.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LVSB_C_2 | LVSB - Low Voltage Switchboard |  |  | Technical submittal is provided only in Portuguese. As per Playbook 6.1 Section 1.2.1.1., all commissioning documentation through Cx levels 0 to 6 is mandatory to be written in English, local language can supplement the English language documents based on region specific requirements. Where a discrepancy between English and local language arises in a document, the English language form takes precedence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622418&prj=674&rqi=HJx0nYkSmBME7lluVTwWNVDdA4
RT1ELEC-186-001 | LS02-2 | S-EMEA | Closed | P3 Low CX | andrew.mercer@bureauveritas.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LVSB_R_11 | LVSB - Low Voltage Switchboard |  |  | Technical submittal is provided only in Portuguese. As per Playbook 6.1 Section 1.2.1.1., all commissioning documentation through Cx levels 0 to 6 is mandatory to be written in English, local language can supplement the English language documents based on region specific requirements. Where a discrepancy between English and local language arises in a document, the English language form takes precedence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622474&prj=674&rqi=wKUtz4a8P1oxo0a0khG432yswE
RT1ELEC-178-001 | LS02-2 | S-EMEA | Closed | P3 Low CX | andrew.mercer@bureauveritas.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LVSB_C_4 | LVSB - Low Voltage Switchboard |  |  | Technical submittal is provided only in Portuguese. As per Playbook 6.1 Section 1.2.1.1., all commissioning documentation through Cx levels 0 to 6 is mandatory to be written in English, local language can supplement the English language documents based on region specific requirements. Where a discrepancy between English and local language arises in a document, the English language form takes precedence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622475&prj=674&rqi=fwYn2LEsZdKNsukM0oSKqmE7iJ
RT1ELEC-177-001 | LS02-2 | S-EMEA | Closed | P3 Low CX | andrew.mercer@bureauveritas.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1LVSB_C_3 | LVSB - Low Voltage Switchboard |  |  | Technical submittal is provided only in Portuguese. As per Playbook 6.1 Section 1.2.1.1., all commissioning documentation through Cx levels 0 to 6 is mandatory to be written in English, local language can supplement the English language documents based on region specific requirements. Where a discrepancy between English and local language arises in a document, the English language form takes precedence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622462&prj=674&rqi=9LE1BMYJ4M9u2VtYJFAQs28aIe
GI-002 | MA05-P1 | N-EMEA | Open | P2 Medium CX | nrae@global-cxm.com | 2026-09-16 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning | [6 empty] | Large nick/slice noticed on HV cable on 1-MLTX-G. Cable ID tag 1-CBL-ML-TX-G 3X1C 120mm2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638444&prj=645&rqi=n8MUE67SlDsIo9fCIrTN6Qzk2U
RT1MECH-57-003 | MA05-P1 | N-EMEA | Closed | P3 Low CX | nrae@global-cxm.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1-CH-E-1 | ACC - Chiller â€“ Air Cooled |  |  | Permanent equipment labels to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624453&prj=645&rqi=x80cXbPU5SCG4hWiwXiRCYrWHw
RT1MECH-57-002 | MA05-P1 | N-EMEA | Closed | P3 Low CX | nrae@global-cxm.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1-CH-E-1 | ACC - Chiller â€“ Air Cooled |  |  | Verify Anti-Vibration mounts are correctly fitted and adjusted Anti vibe mounts still to be installed in 4 locations. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624441&prj=645&rqi=JbH43rdlmmqZGjfzXZPpP8Gply
RT1MECH-57-001 | MA05-P1 | N-EMEA | Closed | P3 Low CX | nrae@global-cxm.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1-CH-E-1 | ACC - Chiller â€“ Air Cooled |  |  | Carry out visual inspection of Equipment and confirm no defects, scratches, dents and any other damage. Bent fins on the chiller coil, minor damage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624406&prj=645&rqi=GY9cwgIpqlauDTGUrhmkeN5f3v
RT1MECH-58-001 | MA05-P1 | N-EMEA | Closed | P3 Low CX | nrae@global-cxm.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1-CH-G-1 | ACC - Chiller â€“ Air Cooled |  |  | Anti vibe mounts are not installed correctly. Vendor has supplied the wrong anti vibe mounts. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624467&prj=645&rqi=CjawB8TZoNNJVt92LXnnGBhbLY
WREPORT-23-001 | MA05-P1 | N-EMEA | Closed | P2 Medium CX | tkhan@global-cxm.com | 2026-04-15 04:00:00.000 +0400 | Equinix Ops | DELIVERABLES | Design correction needed | Design | Multi-Discipline | system | Weekly Report |  |  |  | Approval time for new CR to change the timer values of MSB-T11 and Chiller's restart time was around 5 weeks | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619503&prj=645&rqi=WP3VGjYhj5drbdhO6BUYoR494A | https://equinix.facilitygrid.co.uk/x/project/645/system/13103
RT1ELEC-36-001 | MA05-P1 | N-EMEA | Closed | P3 Low CX | asaville@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1-MSB-E | MSB - Main Input Switchboard |  |  | Permanent labelling to be installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615820&prj=645&rqi=y4clHG2eIRjOMERFjslpesftq0
GI-2677 | MB03-1 | APAC | Closed | P3 Low CX | KunalKavathankar@commtechasia.com | 2026-02-06 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Alarm maintenance mode and alarm shelve duration not demonstrated Asset tab datasheet and weblink was not demonstrated Applicable for all assets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198685&prj=227&rqi=DbJkbU56YhPDiogyruUb9lDJ3a
GI-2676 | MB03-1 | APAC | Closed | P3 Low CX | sganeshmahadik@ap.equinix.com | 2026-02-02 04:00:00.000 +0400 | Facility Manager |  | DCIM Maximo Issue | DCIM | [6 empty] | Maximos not available to integrate with DCIM, BCM and Battery Monitoring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198095&prj=227&rqi=XiUGEH4qGhejzRkPYEhBUeQWsO
GT1MECH-175-003 | MD05-1 | S-EMEA | Open | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-08-05 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | An alarm has been triggered on fire pump No. 2 due to a low engine coolant temperature. The pumpâ€™s temperature sensor is not measuring correctly and will need to be replaced. This does not affect the pumpâ€™s functionality. Once the issue has been resolved, the supervisory alarm associated with that pump should be activated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632284&prj=396&rqi=i1gzvOMT9LBVkF0BpQoRd1dw7q
GI-102 | MD05-1 | S-EMEA | Closed | P2 Medium CX | arkaitz.santos@eu.equinix.com | 2026-08-04 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning | [6 empty] | Vesda fault alarm active sine August 1st. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632134&prj=396&rqi=c2Nricr2OZU832axsNGzqsBFsj
DCOSL5-1-002 | MD05-1 | S-EMEA | Closed | P2 Medium DCOS | arkaitz.santos@eu.equinix.com | 2026-07-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Template Issue | DCOS | Controls | system | DCOS |  |  |  | Need to clean the around 50 assets with warnings at DCOS IDE. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629124&prj=396&rqi=0TOnEfTDsi06MsDr3lsmB9GdMy | https://equinix.facilitygrid.co.uk/x/project/396/system/14475
DCOSL5-1-003 | MD05-1 | S-EMEA | Closed | P3 Low CX | arkaitz.santos@eu.equinix.com | 2026-07-14 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Controls | system | DCOS |  |  |  | PV_1 and PV_2 communication lost every few minutes and during night time. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629180&prj=396&rqi=zpvgnzTRb6IvBReNtIxcvoR633 | https://equinix.facilitygrid.co.uk/x/project/396/system/14475
DCOSL5-1-001 | MD05-1 | S-EMEA | Closed | P2 Medium DCOS | arkaitz.santos@eu.equinix.com | 2026-07-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | Clear the around 13000 alarms generated each day at DCOS Aveva system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628600&prj=396&rqi=Vgu1Rd2U1cCdut3cX1rz39r8j1 | https://equinix.facilitygrid.co.uk/x/project/396/system/14475
GI-100 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-07-08 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Rotor lock alarms are being generated intermittently on low load running 2 happened over the weekend of 03/07-05/07 on WCC A & B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628296&prj=396&rqi=XG4aVEdHnYNJJ8QdkBDdWD8emc
GI-096 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | WCC A & R are failing to restart automatically during transfer to gens in IST | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627300&prj=396&rqi=wbgx4iONKJYNY6Nw2AomRhTsn6
GI-095 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-06-26 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | During IST during Test 3 hall SLAs we're breached for 10 minutes due to slow restart of WCCs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627075&prj=396&rqi=PBvX11NWbw0MECvZigZHlvru20
GT1MECH-310-001 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-06-26 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Fuel | equipment | 1FPCP_B_01 | FPCP (Fuel Pump Control Panel) |  |  | During the IST tests conducted today, it was verified that the fuel system loses redundancy in pump system B during transitions from facility to the generator set. An alarm appears on the Fuel Distribution Loop 2 controller for B, and the pumps B go into alarm. System in A is available and working. The system must be reset from the control panel at fuel pump B. The fuel system has operated correctly during all tests, but redundancy for system B is lost until it is manually reset from the INPRO PLC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627148&prj=396&rqi=aGrDQlVAPcqgPZV2okE1cNk3EJ
GI-094 | MD05-1 | S-EMEA | Closed | P3 Low DCOS | liam.piervulivo@hdrinc.com | 2026-06-24 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Configuration | DCOS |  | equipment type |  |  |  |  | WCC compressor suction/ discharge pressures do not make sense Revise MODBUS addresses with vendor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626686&prj=396&rqi=CQXaEmGOkO2XjwKLXZE4pvI5zI
GI-092 | MD05-1 | S-EMEA | Closed | Outstanding Paperwork/Documentation | liam.piervulivo@hdrinc.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS General Issue | DCOS | [6 empty] | SOO testing docs outstadning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626673&prj=396&rqi=yXX4byO7cwDdEOCQlROqBJCLCF
SOR-17-001 | MD05-1 | S-EMEA | Closed | P3 Low CX | jason.beachill@hdrinc.com | 2026-06-15 04:00:00.000 +0400 | DCOS - Equinix |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Equipo Ref DCOS Ref Facility Grid Bomba 1Âº DAC 1CHWSTR_X_X_CWP_1 1CHWSTR_X_CWP_02 Bomba 1Âº Condensor 1CHWSTR_X_X_CWP_2 1CHWSTR_X_CWP_01 Bomba 2Âº Instalacion 1CHWSTR_X_X_CHWP_1 1CHWSTR_X_CWP_03 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625290&prj=396&rqi=p5HcntWJ8mEQIlq0DzxW2VMYdJ
GI-090 | MD05-1 | S-EMEA | Closed | P3 Low CX | liam.piervulivo@hdrinc.com | 2026-06-15 04:00:00.000 +0400 | Equinix Commissioning Manager |  | Installation Not Correct | Commissioning | [6 empty] | WCC B & R loading to be repeated with glycol in primary circuit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625278&prj=396&rqi=GHxHM5fLEzWvrklHfnAV2kKKSh
FPT-410-001 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | HVAC | system | CHW System |  |  |  | CWST A TT-13 is reading a degree higher than logical, this temp did not drop to TT-08 value when buffer tank is in recharge mode Instrument calibration needs to be checked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625299&prj=396&rqi=crHJFVPDXLuZKIdc68uPYGvWgl | https://equinix.facilitygrid.co.uk/x/project/396/system/13433
GI-089 | MD05-1 | S-EMEA | Closed | P2 Medium DCOS | liam.piervulivo@hdrinc.com | 2026-06-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Loss of DAC run status lost when outlet temps increased past 38 deg C Run status lost due to deviation from SP, as raising SP to 25 deg C resulted in return of run status | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624787&prj=396&rqi=z21JGqxgqfrBGmaWCWMx5IhiVd
FPT-397-001 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-06-09 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Correct | Commissioning | Fuel | equipment | 1FPCP_A_01 | FPCP (Fuel Pump Control Panel) |  |  | During the fire valve simulation in GEN R , it was found that the lever could not be lowered fully as it interfered with a manual valve, and the system was unable to shut off the fuel supply. The pipework must be modified to prevent any contact. This applies to generators A, B and R. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624483&prj=396&rqi=uDASbC8SR2mxVeOpA945Qh1syI
GI-086 | MD05-1 | S-EMEA | Closed | Outstanding Paperwork/Documentation | liam.piervulivo@hdrinc.com | 2026-06-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Design Correction Needed | Design | [6 empty] | SOO not inline with onsite programming as changes have been made SOO needs top be uploaded and approved | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624382&prj=396&rqi=XDkhaojAtlTIS6aWZv2sw8iMkC
GI-087 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-06-09 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning | [6 empty] | DAC supply temps are very oscillatory when SP is above OAT, particularly when difference is more than 10 deg C | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624384&prj=396&rqi=u8NCVCL0fB1mM6jJKNnOkkuuu3
GI-085 | MD05-1 | S-EMEA | Open | P3 Low CX | liam.piervulivo@hdrinc.com | 2026-06-09 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | DAC sending fault signals for less than a second when on and running, this are not considered real failures | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624381&prj=396&rqi=3aGutjBdctIYZvsupiqqDACeXS
GT1MECH-309-001 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Fuel | equipment | 1FPCP_A_01 | FPCP (Fuel Pump Control Panel) |  |  | The differential pressure switch on the fuel filter is not working properly. Inpro will supply a replacement, and its correct operation must be checked. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623633&prj=396&rqi=Myl9h6yfaPO80vgjn2WwZwvPwD
GT1MECH-309-002 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | Fuel | equipment | 1FPCP_A_01 | FPCP (Fuel Pump Control Panel) |  |  | Minor changes have been made to the wiring in the two PLC panels in both Room A and Room B. The diagrams must be updated, and the new cables installed in both the panels and the diagrams must be identified. Furthermore, it must be checked that there are no discrepancies between the panels and the diagrams. Check relay K17 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623637&prj=396&rqi=2lmcWgyjbOngviocJBGzXmGSVr
GI-080 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-05-07 04:00:00.000 +0400 | VER - Vertiv Electrical |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Cool array HOTSPOT functionality not working in DH 1.3 or DH 1.4, to be checked prior to L4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620663&prj=396&rqi=eLNnhfRwUJtcyfSa7cC4FwpCV3
GI-077 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-05-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | Confirmation on what signal type & range is required for PICV valves feedback (V or mA, 0-10V, 2-10V, 4-20mA, 0-20mA) In PPR 1,2 & 3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620511&prj=396&rqi=RfxrS9DfvSDMBGqlUzfMYKpDZJ
GI-079 | MD05-1 | S-EMEA | Closed | P1 High CX | liam.piervulivo@hdrinc.com | 2026-05-06 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | design flow rates are not being achieved on condenser or primary circuits, affecting WCC, DAC and heat exchanger performance Potentially linked to foaming or gas entrained witnessed in water samples | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620515&prj=396&rqi=I8TupozrlJzyYaAt2tSOd27Q0B
GI-078 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-05-06 04:00:00.000 +0400 | ARM -Armstrong |  | General Design issue | Design |  | equipment type |  |  |  |  | Flow switches to be set up with pump min speed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620513&prj=396&rqi=tEFbuG8FxpqKM5ypithc9pN5GQ
GI-064 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-04-27 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Temperature control of condenser water inlet is not fine enough and causing issues with WCChttps://equinix.facilitygrid.co.uk/inquire/?action=eiss&trf=1&PID=619505&prj=396# | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619505&prj=396&rqi=dukSagdMOipIrE0MibgswJ3D9T
GI-063 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-04-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Primary/ condenser loop flowrates cannot be consistently read and appear lowerthan design when read at orifice plate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619504&prj=396&rqi=5YlLGtsWXhftixdQO6mfvljaA8
GT1MECH-175-001 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-04-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | During the internal test of the the pumps verifying the curve and consumption was noted that the jockey pump starts at 8 bar and stops at 8,5 bar with a delay more or less of 2 seconds. As a result of the delay, the pressure in the pipe rises to 13 bar. Please verify the way to improve the settings in order to avoid high pressure in the piping system during the jockey functionality. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617008&prj=396&rqi=aUFg3CixMzuh0hDfEbiYmUiAUY
GT1MECH-175-002 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-04-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | The water liquid cooling system for the fire pumps discharges directly onto the exterior of the building, creating small pools of water. We request that the discharge point be situated near a drainage point. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617019&prj=396&rqi=TLrYqGwSAYfxGzUHw2Xi37dL52
GI-061 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-03-18 04:00:00.000 +0400 | ARM -Armstrong |  | Design Correction Needed | Design |  | equipment type |  |  |  |  | DPT 01&02 range is too high and causing issues with measurement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615971&prj=396&rqi=3M2j5lGL7ZpCzE5rk4hnseoa72
GI-060 | MD05-1 | S-EMEA | Closed | P3 Low CX | luis.newman@hdrinc.com | 2026-03-09 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning | [6 empty] | Blanking panels in Ewall B are not properly fixed down and with a small amount of airflow from the CRAHs the panel is being pushed back and swaying back and forward | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615115&prj=396&rqi=7IXSv1NU0kfh9nscbUFNTVcJ9X
GI-057 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-03-04 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Ready to run signal logic sent to DCOS logic needs to be changed so that chiller is always either in fault or ready to run. One is the inverse of the other | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614681&prj=396&rqi=yTQxv1EvTLfgeS4itgkF5aq3zY
GI-059 | MD05-1 | S-EMEA | Closed | P2 Medium DCOS | liam.piervulivo@hdrinc.com | 2026-03-04 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Design Correction Needed | Design |  | equipment type |  |  |  |  | Ready to run point not used in sequencer logic as per CHW SOO sFAT | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614683&prj=396&rqi=HPqxXP7F3855rzUpYdV6DE6djk
GI-058 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-03-04 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Condenser flow status point monitored by DCOS is looking at a lack of alarm for condenser flow, this is generating a flow status when everything is off (chillers & pumps) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614682&prj=396&rqi=6S7DNZs81h3eD2Xhm8M7EVB758
YT1MECH-327-001 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-02-19 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning | Fuel | equipment | 1FPCP_A_01 | FPCP (Fuel Pump Control Panel) |  |  | Inside the pump rooms, the cable containment system needs to be repaired. The DP copper piping also needs to be repaired, and outside, the valves and pipes need to be painted and checked. At a minimum, the valves, flanges and pipes need to be repainted, cleaned and oxidation to be repaired. To be fixed the cable installed in the bulk tanks (improve the fixation, cables with the correct radios, and to be cleaned). This applies to FPCP_A01, FPCP_B01, and Fuel Pumps in A and B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199527&prj=396&rqi=HPovl5Qpwg7nH5lil2H2mWcS82
YT1MECH-189-004 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-02-18 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | In one of the pump fuel tanks It is observed a leak in the tank. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199458&prj=396&rqi=qFNdAGOGtHef61W9NXAvJGI2Xl
GI-054 | MD05-1 | S-EMEA | Closed | P2 Medium CX | luis.newman@hdrinc.com | 2026-02-11 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning | [6 empty] | Water detected in Ewall B, in front of MDSB_B1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199028&prj=396&rqi=qJAsxfnBTYGsd8qGyOqLC9bWeX
GI-053 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-02-09 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | PPR/ PCR control valves are not actuating correctly as per DCOS signal. Suspect loose 4-20mA connection instead actuator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198789&prj=396&rqi=Ev4A5NVRACJKNncBmZrvlQXvKH
GI-051 | MD05-1 | S-EMEA | Closed | P3 Low CX | liam.piervulivo@hdrinc.com | 2026-02-09 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning |  | equipment type |  |  |  |  | Lagging and cladding to be replaced where it's been removed to install DAC temp sesnors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198787&prj=396&rqi=VtUE10403iKMycZuqMosRiX6r9
YT1MECH-189-003 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-01-30 04:00:00.000 +0400 | General Contractor - Commissioning |  | Incomplete Connections | Commissioning | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | To be verified the leaks in the refrigerant pipe of the pumps | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198005&prj=396&rqi=fm1gQef43F3IlXmIM5Jo81oXLJ
GI-050 | MD05-1 | S-EMEA | Closed | P2 Medium DCOS | liam.piervulivo@hdrinc.com | 2026-01-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Installation Not Complete | DCOS |  | equipment type |  |  |  |  | Hard wired cable to control DAC SP not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198017&prj=396&rqi=ZwqDKpmADek7BCL8xxerpNkvyj
YT1MECH-189-002 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-01-29 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | To be include a water protection in the ventilation pipe out of the fire pump room | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197861&prj=396&rqi=QxaIoazAqzN24gCiJs2qTJHnE5
YT1MECH-189-001 | MD05-1 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-01-28 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | To be repaired the protection element from the pump 1SP_B_01. Also pending to be connected the bonding-earthing cables in 2 pipes | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197782&prj=396&rqi=tCkf4qeWUFph4ekFqlfMdgbqfc
GI-049 | MD05-1 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-01-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Indoor Fan Coil units in battery rooms and NER rooms are not working in heating mode This is causing these rooms to be outside the acceptable temperature range | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196963&prj=396&rqi=Mv7UbgHAkCtx4zsfCxuI2gqX2Q
GI-275 | MI01-3 | AMER | Closed | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-07-15 04:00:00.000 +0400 | General Contractor |  | Documentation Not issued/ Required | Commissioning | [6 empty] | Panel Drawings missing in BCM enclosure - west COLO | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629431&prj=500&rqi=u70vwqi0eMP13nrY7ADJ1azvMl
GI-274 | MI01-3 | AMER | Open | P2 Medium DCOS | sdetardo@equinix.com | 2026-07-15 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | please see Sensor 1 for CRAH 5_25 is in alarm at 81.4 degrees. This sensor does not appear in the floor layout of the colo. Please review all CRAH sensors on the graphics and that alarming is feeding through | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629426&prj=500&rqi=WPOVBoFdsurxUU1k0qdasX9ILq
GI-132 | MI01-EOL | AMER | Open | P3 Low CX | sdetardo@equinix.com | 2026-08-26 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [6 empty] | Installation incomplete - hose for Fire System Nitrogen device - see photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635390&prj=611&rqi=1d6EPzxSYARDKxGZF9CsAreVnO
GI-131 | MI01-EOL | AMER | Open | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-08-24 04:00:00.000 +0400 | Controls Contractor |  | Documentation not issued/Required | Commissioning | [6 empty] | Equinix TES/Controls has not received the IP Address or Password list for the delivered equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634931&prj=611&rqi=RsVhVO96LzpNMo3MGeslSoLZqW
GI-130 | MI01-EOL | AMER | Open | P2 Medium CX | sdetardo@equinix.com | 2026-08-20 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design | [6 empty] | Generator breakers do not have kirk keys. In the event voltage is present from the mobile temp gen - it is possible to backfeed the fixed generator. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634383&prj=611&rqi=1xSJNUCM7IVEpdf03IxqFNEKoO
GI-129 | MI01-EOL | AMER | Open | P2 Medium CX | sdetardo@equinix.com | 2026-08-18 04:00:00.000 +0400 | Design Professional |  | Installation not complete | Commissioning | [6 empty] | Mobile Generator / Rollup Tap Box remote start is inoperable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634134&prj=611&rqi=07VoT5Cb7o3j4UzztOyQYZjsXO
GI-127 | MI01-EOL | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-07-17 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | update graphics to show new sources of chillers and pumps | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629890&prj=611&rqi=0s4kNXLJg179q8EtZDFUid6KK9
GI-122 | MI01-EOL | AMER | Closed | P1 High CX | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Commissioning Issue | Commissioning | [6 empty] | Free hanging wires with ends using tape inside the MSB K | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629792&prj=611&rqi=IA3v1ahASp4euTC8G5aSmKwxvs
GI-123 | MI01-EOL | AMER | Open | P2 Medium CX | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Commissioning Issue | Commissioning | [6 empty] | loose cabling, open raceway, and ethernets using couplers - not home runs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629794&prj=611&rqi=DPpH6tPocMnOff0ZrM89s9jEp7
GI-120 | MI01-EOL | AMER | Closed | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | TGW and associated ethernet inside day tank controller not labeled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629790&prj=611&rqi=CVKKbN1O6O05nNvuNbVEqGJ75d
GI-119 | MI01-EOL | AMER | Closed | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Ethernet to both MSB K + MSB L PLC's not labeled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629789&prj=611&rqi=ukyBhmpgCI1br5tdor0pHd60xW
GI-118 | MI01-EOL | AMER | Closed | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | PLC inside daytank controller not labelled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629788&prj=611&rqi=arJTBvVzaRvmd4RFSWitMdMnJ2
GI-121 | MI01-EOL | AMER | Closed | P2 Medium CX | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Inside K Block HMI - ethernet cable too long, not labeled, and pulling weight on the Power Connection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629791&prj=611&rqi=T3KhJPhKC3KTWwuFEq5w8oqn5r
GI-124 | MI01-EOL | AMER | Closed | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | fuel controller - uplink is labelled with the name of the panel, not the upstream switch + port. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629795&prj=611&rqi=76nGWw6fTyl2k7JJd0o2Kc4xbn
GI-117 | MI01-EOL | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-07-14 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | When navigating - Floor Layout - > Electrical Room -> 2nd Floor -> West Electrical Room There are items in data loss, and a large daytank in the wrong place. See attached screenshot | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629233&prj=611&rqi=7xyerN7zeVsxzmOUpKrRh4PLfT
GI-116 | MI01-EOL | AMER | Closed | P3 Low CX | lily.perrette@veolia.com | 2026-07-09 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | MV-3 relay getting com alarm, and PHS can't bing it, PHS has been able to bing it but stop communicating , can see PQM, | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628598&prj=611&rqi=k8ewFvqYTSxkLaJGESp4M5j1eD
GI-114 | MI01-EOL | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-07-08 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Duplicate entries for MSB PQMs exist in SmartView. Please review all SmartView assets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628441&prj=611&rqi=Dxfm6DuepTAKnI87ThGwexYyoe
GI-113 | MI01-EOL | AMER | Closed | P1 High CX | sdetardo@equinix.com | 2026-07-08 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | [6 empty] | MSB Main Switchgear compartment has high noise and is vibrating the enclosure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628439&prj=611&rqi=AxPJaFeqsayzcum9ehFwCHbm7m
GI-115 | MI01-EOL | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-07-08 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [6 empty] | Maintenance mode is not syncing between Aveva assets and SmartView assets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628442&prj=611&rqi=CYuTLTvBLqeX7NmVKjXllQUPEl
GI-111 | MI01-EOL | AMER | Open | P2 Medium CX | sdetardo@equinix.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment failure | Commissioning | [6 empty] | All battery strings have certain batteries in WARNING and 1 now Critical. K1: 2 Warning K2: 1 Critical ; 6 Warning L1: 11 Warning L2: 6 Warning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627592&prj=611&rqi=7BxGFcpcEux1mbsmYJJVgZ9OeW
GI-112 | MI01-EOL | AMER | Closed | P1 High CX | sdetardo@equinix.com | 2026-07-01 04:00:00.000 +0400 | VER - Vertiv |  | Commissioning Issue | Commissioning | [6 empty] | On K2 UPS HMI - The IOB Breaker is labeled MIB. All other UPS's are correct | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627594&prj=611&rqi=TBOeriRa1vnN6K6R4Jf7juvb1b
GI-106 | MI01-EOL | AMER | Closed | P2 Medium CX | sdetardo@equinix.com | 2026-06-18 04:00:00.000 +0400 | Controls Contractor |  | Labelling | Commissioning | [6 empty] | CAT6's are not labeled inside Control Panel CP-2W-01, in addition PLC does not have an IP address or identifying NAME | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625896&prj=611&rqi=6WEseqfU3RNS1nPE8J93SWC6lJ
GI-108 | MI01-EOL | AMER | Closed | P2 Medium CX | sdetardo@equinix.com | 2026-06-18 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | [6 empty] | Permanent Labels on breakers on SCC-R are missing for feeds down to 2nd floor UDP R's | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625904&prj=611&rqi=pPrBolInL72e0Zg433tDDydzgs
GI-107 | MI01-EOL | AMER | Closed | P2 Medium CX | sdetardo@equinix.com | 2026-06-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [6 empty] | WING Wireless extender is not permanently installed in any type of enclosure. Device is exposed to high heat and conditions of engine room. Wires are hanging . Unit appears to be still in "testing phase" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625897&prj=611&rqi=PrLd5qnjutGWd9SxbRHLsrfJij
GI-105 | MI01-EOL | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-06-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [6 empty] | Controls cabinet "CP-2W-01" is missing schematics inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625895&prj=611&rqi=LW5o4M1Ljzs0WsciIGobrT6TjH
GI-109 | MI01-EOL | AMER | Closed | P1 High CX | sdetardo@equinix.com | 2026-06-18 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | UPS Faceplate has Battery Remaining Time in "Seconds" -- value given "22" - is actually minutes - see screenshot | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625911&prj=611&rqi=xvCDzafj0Od7FMVBYhUdygVduk
GI-103 | MI01-EOL | AMER | Closed | P1 High CX | sdetardo@equinix.com | 2026-06-17 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment failure | Commissioning | [6 empty] | 3 of 4 crahs in the electrical room did not restart after a utility hit. The units were stuck in "Remote OFF" Power cycle of the 480v switch reset the hmi and the units restarted. It was addl discovered that the internal UPS is not holding on these 2 units as the controls should have stayed on when the 480v was killed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625738&prj=611&rqi=uCKb7IQEJdob7dTbwMf8liA1zj
GI-104 | MI01-EOL | AMER | Closed | P2 Medium CX | sdetardo@equinix.com | 2026-06-17 04:00:00.000 +0400 | Electrical Contractor |  | Component/Equipment failure | Commissioning | [6 empty] | Perimeter Receptacles along the exterior colo wall (ex outside colo 255) have no power (northwest side) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625763&prj=611&rqi=6nbgMJyrEqqtQ3PesJl77Br2d0
GI-101 | MI01-EOL | AMER | Closed | P3 Low CX | dustin.haugh@veolia.com | 2026-06-12 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning | [6 empty] | Generator D glycol leak from union pictured | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625096&prj=611&rqi=ECkcoJOxAfKuHFyOmS8qTrc1RG
GI-099 | MI01-EOL | AMER | Closed | P1 High DCOS | sdetardo@equinix.com | 2026-06-11 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [6 empty] | PUE calc and popup do not take into account new blocks K + L | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625041&prj=611&rqi=1sQ12mGLp5U1FUN3ZZAADXdQUL
GI-097 | MI01-EOL | AMER | Closed | P3 Low CX | klemmens@equinix.com | 2026-06-10 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | BTUs connects to the network directly and then bringing in the point for general alarm via OPC. BUT screen disables when that is implemented. Please have this issue fixed with SE. We need to see the display. Assigned to Veolia for redirection of issue by DM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624789&prj=611&rqi=TjdWSf3HNteQlaHh9FoyOjeVjw
GI-096 | MI01-EOL | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-06-09 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | We are missing a Power Overview screen that covers the K + L electrical equipment -SD 6/11 - reviewed screen - MSB-K and STS KR2 are listed twice, please review | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624582&prj=611&rqi=3p4ZNKTKsELXrwqVfiEW2InN9h
GI-095 | MI01-EOL | AMER | Closed | P3 Low DCOS | sdetardo@equinix.com | 2026-06-08 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | On floor layout view for 2nd floor SE - the cage on/off button does not turn off cage backgrounds from background. Addl - cage layout has heavier line width and does not match other floor quadrants | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624342&prj=611&rqi=wTq9GXCNYBqkLzNSnSlyKMgXDQ
GI-087 | MI01-EOL | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-06-05 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not complete | Commissioning | [6 empty] | Provide buckets for all chain valves in the generator and electrical rooms where needed. see attached photos and reference photo of bucket. Also relocate valve tags to the bottom of the chains for visibility. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624148&prj=611&rqi=V5JLzlhYpsxHeMGNfjZlB58veZ
GI-086 | MI01-EOL | AMER | Closed | P3 Low DCOS | samet.ozdemir@veolia.com | 2026-06-05 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment failure | Commissioning | [6 empty] | Leak detection was added in the generator room but cannot be tested due to single use ropes being installed. PHS to provide new rope since current one was wetted or supply new reusable rope if avalible. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624145&prj=611&rqi=AFhQpXgFm8AxM35ouZaVXXNVfg
GI-091 | MI01-EOL | AMER | Closed | P2 Medium DCOS | samet.ozdemir@veolia.com | 2026-06-05 04:00:00.000 +0400 | Owner's Representative |  | Design correction needed | Design | [6 empty] | Installed ASCO solenoid valves on the fuel oil day tanks are not in compliance with the Equinix EBCS-1 standard in that the valve does not have limit switches or aux contacts providing positional feedback. The solenoid valves are also fail close valves because they need 24V to open. Conversations were held with Equinix project team on potentially replacing these valves. Equinix to provide direction. See attached photos for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624177&prj=611&rqi=4S4W4ChfAGO844Z3WhTl0xRwS2
GI-084 | MI01-EOL | AMER | Closed | P3 Low DCOS | samet.ozdemir@veolia.com | 2026-06-05 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Ensure equipment on the electrical floor layout matches the same locations as the drawings. See attached snippet for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624140&prj=611&rqi=BgaoxGehsBbq6omY0TlUaaqN1h
GI-083 | MI01-EOL | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-04 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | [6 empty] | 2UDP L1: orange wire labeled Phase A&B not landed on breaker PDU 21-25 /2E10. Unsure of leadâ€™s purpose, but it is dead ended inside the cabinet.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624134&prj=611&rqi=PwcaB4TksO22CUtwAmkNZ5JM0y
GI-063 | MI01-EOL | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-03 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | UDP-All equipment panel grounds not installed in various cabinets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623798&prj=611&rqi=EToUYbHmU06W03aWPupC4ezKkv
GI-061 | MI01-EOL | AMER | Closed | P3 Low DCOS | samet.ozdemir@veolia.com | 2026-06-03 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Objects on the BMS floor layout need to match the equipment location in the field. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623788&prj=611&rqi=5wcroW18UfcBlieFT9SOdM7eUh
GI-062 | MI01-EOL | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-03 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation Damage | Commissioning | [6 empty] | UDP-L-2 doors are misaligned preventing closure. Some doors are bent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623791&prj=611&rqi=jNmFKPC2OVAlX7sWWeqRrL1Zqy
GI-049 | MI01-EOL | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Incorrect Settings | Commissioning |  | equipment type |  |  |  |  | (Vertiv CRAHs) L4 CHWV fails closed instead of failing last/open. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623337&prj=611&rqi=WOJDF7EGyA1VEsmGrUh2c4Ir6F
GI-052 | MI01-EOL | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-05-28 04:00:00.000 +0400 | CMM - Cummins |  | Component/Equipment failure | Commissioning |  | equipment type |  |  |  |  | (All Glycol Pumps) L4 Pump overloads consistently trip when set to 11A. After review of pump amps rating, overloads have been set to 16A. To be retested and verified | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623401&prj=611&rqi=pOsXkIDrNNje5ymRYncrfVcqoQ
GT1ELEC-2-001 | MI01-EOL | AMER | Closed | P3 Low CX | darren.thurber@veolia.com | 2026-05-27 04:00:00.000 +0400 | SCH - Schneider MV | L3 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 2BTU-1 | BTU - Battery Tripping unit |  | SCH - Schneider | BTU - Verify metering is accurate. Provide points list for metering and alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623228&prj=611&rqi=uH1DYKEpv8XCQZpTC5WnOYgIdF
GI-039 | MI01-EOL | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-05-15 04:00:00.000 +0400 | CMM - Cummins |  | Design not as specified | Design |  | equipment type |  |  |  |  | (BOTH Gen Glycol Pump Skids) L4 When pump skid is called on, the selector will randomize between pump 1 and 2 to equalize lifetime wear. If a running pump fails, the other pump will be called on as a backup. Per Equinix design, this behavior needs to be modified such that pump 1 is the default, and only if it fails will pump 2 turn on. Cummins was directed from pump skid vendor to modify the wiring to the pump selector to conform to Equinix's SOO. The new wiring will default to pump 1, but will not call another pump on when pump 1 fails. Original wiring was left as is, Cummins is awaiting further direction from the vendor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621996&prj=611&rqi=0SNpWNeSG0in1Li8kAjvUP02Rp
GI-041 | MI01-EOL | AMER | Closed | P1 High DCOS | alec.dughi@veolia.com | 2026-05-15 04:00:00.000 +0400 | General Contractor |  | Component/Equipment failure | Commissioning |  | equipment type |  |  |  |  | (BOTH Gen Day Tanks) L4 Float level sensors give slightly inconsistent values between each other and between different trials. When float sensor is physically moved to top/bottom extremes of travel, signal received varies, and is not exactly 4-20mA (more like ~5 - 18mA) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622001&prj=611&rqi=5pZr0tJR1ci1famZ2gnYoolerN
GI-038 | MI01-EOL | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-05-14 04:00:00.000 +0400 | General Contractor |  | Component/Equipment failure | Commissioning |  | equipment type |  |  |  |  | (Gen fuel pump system) L4 Fuel is back-siphoning from each day tank to belly tank on the first floor. The fuel is suspected to be leaking through the solenoid valves FCV-01 and FCV-02, through lag pump piping and pressure relief valve, back into the belly tank. The pressure relief valves at the pumps were tightened from 0psi to ~80psi. This slowed down the siphoning issue but it still persists. Next step is to add check valves to the supply lines to prevent this backflow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621914&prj=611&rqi=NLA3wiMrqrsrsVU4PKew1FbQgD
GI-037 | MI01-EOL | AMER | Closed | P3 Low DCOS | samet.ozdemir@veolia.com | 2026-05-11 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | The command / status of the day tank solenoid valves in the Aveva graphic did not match the faceplate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621127&prj=611&rqi=y8UniqaJ93cXEoPJkusSJKpYEw
GI-036 | MI01-EOL | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-05-08 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [6 empty] | B phase power feeder serving the day tank PLC was found to be loose. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621017&prj=611&rqi=tBpjXyyqci1hTPFM6rkw0hOiJU
GI-034 | MI01-EOL | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | Provide permanent labels for all energized mechanical equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621015&prj=611&rqi=RaD07Vhir8F7o8HNII23hAA8uf
GI-029 | MI01-EOL | AMER | Closed | P2 Medium CX | samet.ozdemir@veolia.com | 2026-05-06 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [6 empty] | 2nd floor day tank fuel oil pumps were found to be spinning the wrong way. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620565&prj=611&rqi=FdRQrEPcNhVjwAG0imdmyGfspV
GI-031 | MI01-EOL | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-05-06 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | When the fuel oil pumps were in operation the pump CTs indicated the pump was not running. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620570&prj=611&rqi=lSdB90RdxCGVueqrUVfpPHYHey
GI-030 | MI01-EOL | AMER | Closed | P3 Low DCOS | alec.dughi@veolia.com | 2026-05-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | (DAY TANKS) L4 Day tank names are switched in BMS. "02240T00_2FDAYK_RAS_LT" should read "02240T00_2FDAYL_RAS_LT" and vice versa. No asset to link to, leaving as a general DCOS issue #fuel pump system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620566&prj=611&rqi=qwUQrAsKLsc2peAbzEuSsL7Al2
GI-028 | MI01-EOL | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-04-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | Battery cabinet L-1 is missing jumper between battery cells.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620089&prj=611&rqi=SNV9cTWwkLjTbcAROMNZf1b2mk
GI-027 | MI01-EOL | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-04-23 04:00:00.000 +0400 | VER - Vertiv |  | Installation Damage | Commissioning | [6 empty] | UPS K1 broken connector.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619219&prj=611&rqi=Ijc8N1lg3baPdtxcsAjKksUwse
GI-025 | MI01-EOL | AMER | Closed | P1 High CX | chase.negich@veolia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment failure | Commissioning | [6 empty] | Kirk key R32 broken off in RMU K.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618855&prj=611&rqi=FeUlFZr9CRvS0hhbAfIjj459aq
GI-022 | MI01-EOL | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-09 04:00:00.000 +0400 | Mechanical Contractor |  | Documentation not issued/Required | Commissioning | [6 empty] | Provide pressure test results for chilled water piping | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617665&prj=611&rqi=2cQgZ9VOZPiuJulEStRLKhjTzi
GI-023 | MI01-EOL | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-09 04:00:00.000 +0400 | Mechanical Contractor |  | Documentation not issued/Required | Commissioning | [6 empty] | Provide pressure test results for generator coolant piping (glycol loop) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617675&prj=611&rqi=Vsy2Pid8KYdHGSOHs90aXfmG5B
GI-019 | MI01-EOL | AMER | Closed | P3 Low CX | francis.callan@veolia.com | 2026-03-25 04:00:00.000 +0400 | Mechanical Contractor |  | Installation Damage | Commissioning | [6 empty] | Duct work inside battery room K has been damaged such that it causes safety concerns with the support able to fall. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616449&prj=611&rqi=8udglxf53DB7GDxD8SgvjE0ZAM
GI-010 | MI01-EOL | AMER | Closed | P2 Medium CX | klemmens@equinix.com | 2026-02-26 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Missing Components | Commissioning | [6 empty] | CW181 should come with 40-50ft Leak detection rope per the standard MCE. Please confirm this will be delivered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352242&prj=611&rqi=hwK4PugFuOe26tk9zw4X0NR4Ng
GI-004 | MI01-EOL | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-02-18 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation Damage | Commissioning | [6 empty] | Mismatched hardware on Schneider 400A breakers There are 3 different bolts that were used across these breakers stamped O1RL, SKS, and UH. All these bolts have different lengths. This might be causing some of the issues with stripping the threads. The common hardware configurations I noted are as follows: O1RL bolts are the most common and have 2 square washers and a Belleville washer. SKS bolts are longer and have 2 square washers, a Belleville washer, and a lock washer. UH bolts only have 1 square washer and a Belleville washer The Schneider documentation I found calls out M10 x 25 bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199485&prj=611&rqi=4PXCX0csilovLNhBRBRcRJ4h0A
GI-001 | MI01-EOL | AMER | Closed | P1 High CX | lily.perrette@veolia.com | 2026-01-26 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Component/Equipment failure | Commissioning | [6 empty] | MSB Sections not lining up - Electrician have run into issues with bus work with connecting sections, bus work is not lining up. We verified the sections are lined up in order and with correct MSB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197597&prj=611&rqi=AXlmyn36ArPsJIWwYqQ4ZxtavZ
GI-006 | ML05-P1 | S-EMEA | Closed | P3 Low CX | stefb@straightlineconsulting.co.uk | 2026-05-08 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1-UDP-C-1 | UDP - UPS Output Switchboard |  |  | ELECTRICAL LV; Whilst investigating an excessive issue on the MLTX in this power string for an unrelated Issue, it was observed that excessive heat was detected on the Load Bank ACB Cubicle of the UDP. Whilst, at time of writing, this Asset is L4 Blue Tag Signed-Off, it may need to be taken back to a previous status, and defective parts replaced/ retested. The excessive heat has led to distortion of the internal PVC arc-flash separation. Clamps of the fixed part of the ACB appear to be not all identical and, during the load tests undertaken after reclosing the ACB and external panels, temperatures exceeding 80Â° were detected on breaker metallic parts. Also refer to attached EoR email. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620964&prj=619&rqi=awwJH8lGtdYGDxf2gdMOt0lxYC
GI-005 | ML05-P1 | S-EMEA | Closed | P1 High CX | stefb@straightlineconsulting.co.uk | 2026-05-07 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1-MSB-C-1 | MSB - Main Input Switchboard |  |  | ELECTRICAL; LV. This Issue was originally raised against the Tx, but further tests on 07/05/26 have revealed that the E & I LV Busbar from the TX to the MSB is causing the problem. Refer to attached documents. The buzzing noise is being caused by the installation, clamping and torquing of the busbar connections onto the Tx secondary side. Previously raised Issue wording; Following completion of the TX L4 Blue Tag, and during 4 hour load burns on the final MV Cables 1-CBL-MV-014 and 015 (test dates 27/04/26 & 28/04/26:, the Tx started to make a noticeable buzzing sound once under circa 80% load; 2.0 MW. Casing inspections and thermal scans have revealed no issues, but the noise continues, for most of the time, when the Tx is under load. Thermal scans revealed low temperatures of 30-45 Degrees Centigrade; temperatures of no concern. SGB have requested that acoustic scans be conducted. 08/05/2026; RESPONSE ADDED; This Issue cannot be Closed as, following tests on 07/05/2026, a new Issue can be raised for E & I Vertiv responsibility, with further detail added. 29/06/2026; RESPONSE ADDED; Testing carried out and witnessed on 26/06/2026 confirmed that origin of issue was discovered and rectified, observed for 2 hour load test at 2MW - no buzzing sound observed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620940&prj=619&rqi=sPNjUHvxFIHof60xYidOEXc2bl
BT1ELEC-5-001 | ML05-P1 | S-EMEA | Closed | P2 Medium CX | garyf@straightlineconsulting.co.uk | 2026-04-16 04:00:00.000 +0400 | General Contractor - Commissioning | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1-UDP-C-2 | UDP - UPS Output Switchboard |  |  | Electrical Communication failure with CB C1 feed from 1-MSB-C-1, this is a loss of communication that has happened post-L3 DCOS screenshots and appears to be a failure of the IFE module or the communication module itself. Closed 06-05-2026 With attached Screenshots 23-1 & 23-2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618522&prj=619&rqi=94Uj8J88CioZzqqXwZUaC9Ob8i
BT1ELEC-5-002 | ML05-P1 | S-EMEA | Closed | P3 Low CX | garyf@straightlineconsulting.co.uk | 2026-03-25 04:00:00.000 +0400 | General Contractor - Commissioning | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1-UDP-C-2 | UDP - UPS Output Switchboard |  |  | ELECTRICAL 26/03/2026 Whilst completing DCOS screenshots for 1-UPS-C-2 Blue Tag, it was noted that the following CB's are not reporting correct data from the trip unit â€¢ 1-UDP-C-2 - LOADBANK CB (see attached image) â€¢ 1-UDP-C-2 SUPPLY FROM 1-UPS-C-2 CB (see attached image) 27/03/2026 On review of SE DCOS response to this issue, it has been reassigned to E+I for corrective works. 30/06/2026 Schneider / E+I engineer attended site to make correction to power sign wave direction settings using EcoStructure software on 1-UDP-C-2 - LOADBANK CB - works complete on this breaker, report and screenshots attached in responses. Breaker 1-UDP-C-2 SUPPLY FROM 1-UPS-C-2 CB - issue still not resolved, breaker not communicating with software. E+I to issue report and recommendations (replace breaker / replace module) 07/07/2026 issue with breaker 1-UDP-C-2 SUPPLY FROM 1-UPS-C-2 CB has been identified by Vertiv. Replacement Micrologic module recommended and scheduled for installation with verification of correct data being reported. Clear close-out scope of works identified and arranged. Issue priority to be down graded to P3 Low, issue will be closed following the remedial works and associated CX report. 17/07/2026 Schneider / E+I engineer attended site to replace breaker micrologic module (NSX630N 5.3E Micrologic) and confirm connectivity to communications, make correction to power sign wave direction settings using EcoStructure software on 1-UDP-C-2 - SUPPLY FROM 1-UPS-C-2 CB - works complete on this breaker, report and screenshots attached in responses / documents. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616499&prj=619&rqi=4rJKIKU0Rre9Nr11iPLtEzVlnl
BT1ELEC-1-001 | ML05-P1 | S-EMEA | Closed | P1 High CX | garyf@straightlineconsulting.co.uk | 2026-03-18 04:00:00.000 +0400 | General Contractor - Commissioning | L4 | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1-UPS-C-1 | UPS - Uninterrupted Power Supply |  |  | Electrical Date: 19/03/2026 Whilst completing the blue tag testing of 1-MSB-C-1, test 2 of the E+I test script requires a mains failure from RMU-C. 1-MSB-C-1 PLC then completes a transfer from Utilities supply to Generator supply (test completed at 2MW via building Load Bank). Once supplied by 1-GEN-C-1, the UPS exhibited voltage fluctuations (see attached images), which caused the rectifier to shut down and the UPS to reject the load. This test was repeated at a reduced load, and the same occurrence was observed; see the attached images of the Voltage relay in MSB-C-1, indicating both over- and under-voltage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616019&prj=619&rqi=DohDUChiWS6TTuUUlmITNeWW8l
GI-004 | ML05-P1 | S-EMEA | Closed | P3 Low CX | stefb@straightlineconsulting.co.uk | 2026-02-05 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1-RMU-C | RMU - Ring Main Unit |  |  | ELECTRICAL; When replacing the Microswitch components in Loop 2 cubicle, a small fixing screw was not fitted as it was not to hand. Refer to attached, marked photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198683&prj=619&rqi=FOnEthZpg3z3BItGeAbgZE1aWR
GI-002 | ML05-P1 | S-EMEA | Closed | P1 High CX | stefb@straightlineconsulting.co.uk | 2026-01-19 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | Electrical â€“ MV | equipment | 1-RMU-C | RMU - Ring Main Unit |  |  | ELECTRICAL; On Tx Feeder Cubicle 3, the mechanical mechanism which operates the microswitch broke during operation, and requires urgent replacement. At present, with the circuit breaker Closed, the microswitch is sending an Open signal. With this being a major safety Issue, the RMU has been shut down and isolated. Temporary remedial works are to remove the corresponding component from Cubicle 2 and fit into Cubicle 3, whilst awaiting new replacement parts. This is to be undertaken ASAP. The defective component is to be removed and sent to SE MV R&D Department for urgent analysis and RCA. 10/02/2026; Updated RCA now attached, so this issue can now be Closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197149&prj=619&rqi=fxgt90zmonjRW90Gka7CGfB7b8
YT1MECH-27-001 | ML05-P1 | S-EMEA | Closed | P3 Low CX | stefb@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1-CRAH-C-18 | CRAH - Computer Room Air Handler (CHW) |  |  | Mechanical; During the 5 bar pressure test on 13/01/2026, a very slight weep was discovered on one of the welded joints. Note that this pipework was installed some years ago in Phase 1. 15/01/2026; Pressure test re-conducted, witnessed and passed. Issue Closed. Refer to Observation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196854&prj=619&rqi=lfyAlemws6EtUfOD1v3mg02108
GI-001 | ML05-P1 | S-EMEA | Closed | P3 Low CX | garyf@straightlineconsulting.co.uk | 2026-01-08 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1-UPS-C-1 | UPS - Uninterrupted Power Supply |  |  | There are a number of paint work defects identified on 1-UPS-C-1, see attached images as examples that were identified 16/101/2025 The paint work defects will be addressed by VERTIV once the L4 Blue Tag commissioning has been completed and this issue will be closed. 26/01/2026; Repairs inspected and Accepted; Issue Closed. Very Well Done. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196631&prj=619&rqi=vesZ3OlrELhshnNxFDEWKGZPo1
YT1ELEC-32-002 | ML05-P1 | S-EMEA | Closed | P2 Medium CX | stefb@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1-MSB-C-1 | MSB - Main Input Switchboard |  |  | ELECTRICAL; There is an earth connection that has not been terminated underneath the MLTX, which is connected to the MSB earth bar. Vertiv/ E & I to address and Close ASAP. This Issue was originally raised against the MLTX L2B Yellow Tag (issue #11), but as Issues cannot be transferred to other Asset's once raised, we could only Close it, and create this new Issue on the MSB, 12-01-2026 UPDATE; Earth cable removed, so Issue can now be Closed. Refer to photos attached to Response. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196559&prj=619&rqi=01D5glLu2VMUUNP2wxQRBtNM3X
WGR-1-003 | ML05-P1 | S-EMEA | Closed | P3 Low CX | garyf@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | DELIVERABLES | Commissioning Issue | Commissioning | Multi-Discipline | equipment | Room 114 - UPS Room | Room Readiness |  |  | Fire stopping of 1 No. Earth cable leaving the UPS switch room (underneath raised access flooring to the right of the earth bar) is to be completed. 12/02/2026; Accepted and Closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196552&prj=619&rqi=5I0ykACAkY5atKt0zgRWidMdt3
WGR-1-001 | ML05-P1 | S-EMEA | Closed | P2 Medium CX | garyf@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | DELIVERABLES | Commissioning Issue | Commissioning | Multi-Discipline | equipment | Room 114 - UPS Room | Room Readiness |  |  | Fire stopping of 1 No. Earth Cable leaving the UPS switch room to go to the Battery Room. 12/02/2026; Accepted and Closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196490&prj=619&rqi=juqim9B5LYx1jF2MiCZSVIB71S
WGR-1-002 | ML05-P1 | S-EMEA | Closed | P3 Low CX | garyf@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | DELIVERABLES | Commissioning Issue | Commissioning | Multi-Discipline | equipment | Room 114 - UPS Room | Room Readiness |  |  | ELECTRICAL; MV & LV Schematics have not been positioned within the switchroom | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196493&prj=619&rqi=YllaQIL65BARiAksHsrl1ziYcc
DCIML4-2-001 | MT01-3 | AMER | Closed | P3 Low CX | Jonathan.Calotes@jll.com | 2026-08-31 04:00:00.000 +0400 | DCOS - Equinix | L4 | Commissioning Issue | Commissioning | Integrated Automation | system | DCIM |  |  |  | EQX working on Modbus license for MT1-03 for JLL access | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636135&prj=622&rqi=tyhoiZ2jKbckvuzMjNE1gzzpCq | https://equinix.facilitygrid.co.uk/x/project/622/system/12546
GI-003 | MT01-3 | AMER | Closed | P3 Low CX | piotr.sosniak@jll.com | 2026-08-24 04:00:00.000 +0400 | Mechanical Contractor |  | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | system | Chilled Water |  |  |  | Provide TAB Plan for chilled water and air systems. Include Flow meter calibration, pump curves, DP initial settings, DP final settings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634932&prj=622&rqi=kRSdSdAgms2gSdwjWr5Jfcdovu | https://equinix.facilitygrid.co.uk/x/project/622/system/14872
GI-002 | MT01-3 | AMER | Closed | P2 Medium CX | Nathan.fu@jll.com | 2026-07-15 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not complete | Commissioning | [6 empty] | The chilled water pump vibration was still observed during the test on July 15, 2026, even with the new VFD settings implemented. The field testing team believes the vibration appears to be from the fluid flow in and out of the pump rather than from the pump motor. The Smardt team has reported this issue to Armstrong and Kolostat, and both parties will follow up and investigate accordingly. Updated to July 17, 2026 (JLL): Armstrong technician is suspecting an issue with the coupling between the motor and pump shafts. He's requesting replacements and should be back on site to install them., Smardt will work with Armstrong next week to plan this. Smardt is hoping to get them to address this issue first thing when the site is operational again in a couple of weeks. From their experience with Armstrong, replacing the coupling is fairly quick | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629423&prj=622&rqi=ngxDemoibo5JJA2keF2Ehx5LN0
GI-001 | MT01-3 | AMER | Closed | Outstanding Paperwork/Documentation | amirreza.barekatain@jll.com | 2026-06-29 04:00:00.000 +0400 | Electrical Contractor |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | - Missing certificate of calibration of phase rotation >> OK | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627289&prj=622&rqi=D1U6pyUkjZcILlEcjQIS1cMmrH
DCIML2B-1-001 | MT01-3 | AMER | Closed | P3 Low CX | roozer.samuvel@jll.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2B | DCOS Design Issue | DCOS | Integrated Automation | system | DCIM |  |  |  | During the SFAT brief, it was identified that the alarm banner around the chiller graphics is missing from the BMS manager interface. This may be due to the site operating on older Aveva standards that do not include this alarm banner functionality as part of the standard configuration. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626571&prj=622&rqi=makt3TVLMW5YziS90hj9bXfT5b | https://equinix.facilitygrid.co.uk/x/project/622/system/12546
RT1ELEC-44-002 | MT01-3 | AMER | Closed | P3 Low CX | amirreza.barekatain@jll.com | 2026-02-08 04:00:00.000 +0400 | Engineer | L2A | Design correction needed | Design |  | equipment type |  |  |  |  | missing some cable specifications on cable schedule E720. BA1-C56 -- E602.6; PDUA1-1-1 BA1-C57 -- E602.6; PDUA1-1-1 BA1-C68 -- E602.6; PDUA1-1-3 BA1-C84 -- E602.6; PDUA1-2-1 BA1-C89 -- E602.6; PDUA1-2-2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198758&prj=622&rqi=zNTieaYKUCTxzPBl4EgY5EJf6V
GI-075 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller â€“ cable management under chiller and to compressors needs tidying up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637090&prj=643&rqi=l85zGF7VlTtqKXlwuUozr4tNn3
GI-086 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ PPU dimensions must be laserâ€‘verified and Hamzah must supply evidence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637102&prj=643&rqi=dinrH50UcNdtJPb6OAN6zZwzn2
GI-107 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Pipework to be capped prior to shipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637128&prj=643&rqi=13uCsY7PKtVAg0V1z6aDVi2tqI
GI-110 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Cleaning | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 : Chiller and all container requires a final clean prior to shipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637133&prj=643&rqi=NdVviXLGE8PxdCSZF3RSkg8nGj
GI-108 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Condensate pipework to be completed prior to shipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637129&prj=643&rqi=Y59y4oUqI06n7AMpIscb0WBgNh
GI-109 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 :Chiller - pipe insulation to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637130&prj=643&rqi=SRCJ8ZJ710DdU6L3eH5VMnzABo
GI-076 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller â€“ cable stuffing glands not tight (under chiller and compressors) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637091&prj=643&rqi=CEwxktlX6TNBWYqmGy6ZvvW2Li
GI-094 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Torque required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Torque reports and any calibration certificates for all flanges, bellows, etc., must be supplied. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637113&prj=643&rqi=b6hDglNzTOjNyci4IkMp9N8Xne
GI-099 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation Damage | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Plinth painting is damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637120&prj=643&rqi=wbhyrv5HgzmUYckX7cskoErnQq
GI-100 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ A drip tray must be installed below the portable valve and above the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637121&prj=643&rqi=UiObJ1ELPXpq7LCgqsYeKyPrWB
GI-101 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Valves after the sockets must be installed for each 3/3 flow meter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637122&prj=643&rqi=Opy01Q7cijL10QAsbWFOHo7mX9
GI-106 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Insulation to be installed on incoming portable water connection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637127&prj=643&rqi=v2uD4xjcABMmrhiYfuYpxDZief
GI-074 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller â€“ temperature sensors have been packed with silicone | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637089&prj=643&rqi=rd9v0AoBK3OcamLNPvyYyjtNmP
GI-084 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Tags missing for instrumentation (please reference latest approved P&ID) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637100&prj=643&rqi=i5G32JZsz1DFEXQmiKspk8RcMY
GI-095 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Labelling | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Both HVAC fans must be labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637114&prj=643&rqi=EkKH8riZl0bKv27f2iuVaIEJkt
GI-102 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ The pneumatic test report must be accompanied by a markedâ€‘up schematic clearly indicating the tested sections. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637123&prj=643&rqi=h2zyLdyU0MNQl1pjZZzgoCOJao
GI-103 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Support clamps for the two vertical copper discharge lines from the safety valves are required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637124&prj=643&rqi=0AO0zrXR1sOVVx6BPRVVm4HdJl
GI-073 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ No way to secondary injection settings on breakers on both switchboards and chiller (this can be verified at L2B onsite) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637085&prj=643&rqi=oLHnfV22he96xp5SEbV8C0Yvx3
GI-083 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Tags missing for equipment (please reference latest approved P&ID) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637099&prj=643&rqi=FqQp61MXFuKa7guKHJFELfs2TJ
GI-072 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller â€“ cannot verify fuses F3, F4â€¯&â€¯F6, F7â€¯&â€¯F1 as no sizes on schematic | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637084&prj=643&rqi=Yy4i0gTXr3FfYM0xmQW3ErBRuc
GI-098 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ The floor is not painted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637119&prj=643&rqi=qsjW0dbvClmaaiwevD8BQkMGap
GI-104 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ The chillerâ€™s cable runs are leaning against copper pipe; ensure these are correctly secured and not touching any pipework. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637125&prj=643&rqi=K8Ufp3fcT8JMSghZxmv99cWrvj
GI-082 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Tags missing for valves | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637098&prj=643&rqi=LFaLtXt39TriQi5H1bhbQWtAkm
GI-081 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ PCRSBâ€‘Fâ€‘1 aux and section D3 missing on schematic | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637097&prj=643&rqi=BnLOPHp2uWb2o5Ko6VWgou4ic0
GI-091 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ All NDT and test reports for the chillerâ€™s refrigerant system must be sent by Aermec. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637109&prj=643&rqi=ZjuEEMdXFXfsCbtzhDYIRxLiH0
GI-090 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation Damage | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Both vessel lagging must be repaired. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637108&prj=643&rqi=mD4jfTVzPeiLKTzf9rUHR6F0Bb
GI-080 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ PCRSBâ€‘Fâ€‘1 primary injection results missing for chiller supply breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637096&prj=643&rqi=3zkgspRstZZfVJz1RTGoIU4tGJ
GI-079 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ All fuses in chiller and electrical panels to have a small key installed on the inside door explaining their size and purpose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637095&prj=643&rqi=nOpgrgYgcywITdoMmyZHvos4Tw
GI-092 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller lifting eyes must be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637110&prj=643&rqi=UuTM1ctQ2S6WQNEUVyeOTyjzsA
GI-096 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Confirmation regarding the proper operation of the check valve is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637115&prj=643&rqi=HAGpdPOq6jAk7RMLPqYJLQp9zK
GI-078 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Modbus module on all VFD to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637094&prj=643&rqi=YeFelw9Vh7d1XGnu9xUitXjsvq
GI-077 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Schematics to be installed on wall (P&ID, both switchboards) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637092&prj=643&rqi=HKTFMFKIdHeiWAjv7nRfcYGhUE
GI-112 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Labelling | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Tags and labels missing for pipework (flow direction) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637135&prj=643&rqi=FjFn2Xz54g4xeQmG0TAMkayDoF
GI-111 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Labelling | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 Tags and labels missing for pipework (glycol) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637134&prj=643&rqi=EqvihsnPMNQvn5NBU9ruhhA5DU
GI-097 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Leak detection was not installed at the time of FWT. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637117&prj=643&rqi=3LqidayhUhVXDiR6rVCRxoRxMv
GI-089 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Nozzleâ€¯3 andâ€¯4 flanges show 750â€¯mm but actual measurement is 761â€¯mm; Armstrongâ€™s asâ€‘built documentation must be sent to Mercury Design. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637107&prj=643&rqi=gwSCYT8wOh2XYfnj66vwphoIRo
GI-087 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Nozzleâ€¯4 external flanges are 30â€¯mm higher than the 3090 actual dimensions; Armstrongâ€™s asâ€‘built drawing must be sent to the MER team. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637103&prj=643&rqi=rbRZhaydPOX5lSGTnANvTrIfRU
GI-088 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Nozzleâ€¯1 andâ€¯2 flanges show 500â€¯mm but actual measurement is 550â€¯mm; Armstrongâ€™s asâ€‘built documentation must be sent to Mercury Design. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637104&prj=643&rqi=V12h51dLoXudX6i2sZ9LNzbjzJ
GI-085 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ The approved size of the external Uniâ€‘Strut supporting the AC unit is longer than the specified dimensions; an asâ€‘built diagram must be sent to Mercury Design to verify there are no clashes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637101&prj=643&rqi=VO7rSd2nSLFbP4zNZIHZdbAnqA
GI-105 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Verification throughout FWT P&ID was an old revision â€“ please reâ€‘upload the latest revision for review | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637126&prj=643&rqi=aI88QOzWmSwD3beqfJzET2iCov
GI-093 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Technical data sheet for bellows must be sent and reviewed against installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637111&prj=643&rqi=NAv0wbtfDTnx7Ny7FVHTAsS9Mu
GI-066 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | AER - Aermec |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ UPCRSBâ€‘Fâ€‘10 metal tieâ€‘wraps inside panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637077&prj=643&rqi=cSgWKRrC3IGO5VK8GTU9SdOsv4
GI-071 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ External louvre not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637082&prj=643&rqi=Y0HxT89ADFL0nBpUwMEEj9rajR
GI-070 | MU04-3 | N-EMEA | Open | P1 High CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller â€“ incoming cable not connected to earth | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637081&prj=643&rqi=mtkVkiP2zaQYC06AKRHwXL6h6n
GI-069 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ 1DCOSâ€‘RIOâ€‘05 no torque markings on the frame bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637080&prj=643&rqi=yWhqtS2YwhJMVxypP80PGds7tz
GI-068 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ No entry for DCOS cable in UPCRSBâ€‘Fâ€‘10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637079&prj=643&rqi=gt9OvEgbVFGDvhfRdW2r6yf2bh
GI-067 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ No Roxtec transit frame installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637078&prj=643&rqi=gsRPuNkUBHJP8261DJdSJIrqum
GI-057 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Pump isolators â€“ missing internal shrouds to ensure IP2X protection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637062&prj=643&rqi=Co9S14o3aukdW07cCynafenxOs
GI-058 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Pump isolators â€“ 400â€¯V labels to be changed to 415â€¯V | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637067&prj=643&rqi=nD2qtLyVYQwNfpn0H0Iw7yEDXr
GI-059 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Grommet trip protection missing from tray work | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637068&prj=643&rqi=7XKpuglRc67wIhFR8wvFNLqjAV
GI-060 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Cable bone tags missing from 1PCRSB_F_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637069&prj=643&rqi=R9181u3R8CRLhM2DaFyKVDCDWm
GI-063 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Earth straps to be installed on all flanges | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637072&prj=643&rqi=TLWGC8W9ZJo2bv6cX7OlJmzCns
GI-061 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ 1PCRSB_F_1 400â€¯V labels to be changed to 415â€¯V | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637070&prj=643&rqi=gT7ZCEfV79jmVVT1HVBdTtZsyZ
GI-062 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Earth bar to be colourâ€‘coded Green and Yellow | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637071&prj=643&rqi=ST1WSjCqDSagsrwqhW7Kb0Uhka
GI-065 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Paint damage on heatâ€‘exchanger frame | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637076&prj=643&rqi=sI7Yvd9n7iz1ioD62VT5QVrnZH
GI-064 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Gland plates to be earthed on pump isolators | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637075&prj=643&rqi=QWw1gKl0gZftdQHVmcet84tR94
GI-056 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller has a number of small water valves with no end plugs. Please install to prevent any accidental leak in future | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636893&prj=643&rqi=FMBFf9JaYwQBommHbF4L9PEBIx
GI-054 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Buffer vessel and other piece of equipment requires to be bolted down. Confirmation will be required that equipment located within bonded area had correct procedure applied ensuring water bund was not compromised. Expansion tank - Not fixed to floor Buffer vessel - Not fixed to floor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636890&prj=643&rqi=2rpIY1Pdl02wqm54nXzgt4kNHx
GI-051 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation Damage | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller insulation was damaged in small amount of areas. Can you please rectify? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636882&prj=643&rqi=Yw8WKV2S3JfYAcb7QRdPdz0sFk
GI-050 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Dosing pots have pipework installed at high level, running above electrical equipment. Can you please review this and provide solution to protect any electrical equipment from potential exposure of liquid from these pipes? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636881&prj=643&rqi=XWCehk5lUUpdDupygbJb6bOTxC
GI-049 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ There is bund installed within area protecting electrical equipment from any liquid exposure during leak incident. Bund area also prevents any leak from plantroom. Please confirm how this is tested or ensured that bund area will hold water following floor being drilled to mount plantroom equipment and all welding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636878&prj=643&rqi=e3sGKgug9dRtjGRVu2fbsHa9mv
GI-048 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Dosing pots are missing end caps/plugs at the bottom valve used to discharge liquid from pot itself | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636876&prj=643&rqi=M9c2R88WiYRz6njSmsQIHwtBLF
GI-047 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ There was a slight misalignment of bellows, manufacturerâ€™s confirmation to prove install is sound | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636873&prj=643&rqi=GjpRspgn8lufzNyZUYwrvckmGb
GI-046 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ There is a requirement in script to prove that when multiple and identical assets are being used, it is important to prove that these are not from the same manufacturing batch. Please provide evidence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636871&prj=643&rqi=kkLH78yiJHjJDmwItZaTErg0Tk
GI-045 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Flow meters have not arrived and it is the clientâ€™s concern that these will cause issue at flushing stage, for example, rather than installed before sending it to the project. Flow meter pockets are left at 90Â° horizontal for these to be installed. Please check with manufacturer if this is acceptable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636869&prj=643&rqi=8PPGagJ1fN1oXkWQy1DSo0mPfA
GI-044 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Labelling | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ General: Equipment labels are to be installed, while matching PIDs: Missing Trafolyte labels of Pumps Missiing traffolyte labels for VFD Missing labels on Pump Isolator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636868&prj=643&rqi=tsUkayW6EQhrn02pcacmVuAgvK
GI-043 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Tags and labels missing for pipework (water) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636865&prj=643&rqi=OPopEsmApgaCfnKtXHaH9t94zj
GI-042 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“Covers to be fitted on studded rod hangers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636864&prj=643&rqi=Ltq4wbwpaYqfTxQjPJ5hrB5KSa
GI-055 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ There are HEX bolts yet to be protected by foam | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636892&prj=643&rqi=I4jKMEoYjYf6V0tFOb54H2cJZp
GI-053 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ There are still some opening to be cut into the structure/wall of plantroom. Please complete and provide evidence of works and include QA cleanliness checks following completion | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636889&prj=643&rqi=pC7xJr30aSMGP3lXOUUBwo8ddR
GI-052 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Condenser side of chiller has no bellows fitted at point of connection with pipework. Confirmation is required that this is correct | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636883&prj=643&rqi=dOUXtn2k11KfzncD3fgiejHdCg
GI-032 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Minor installation works are ongoing, and some of the kit is yet to be bolted down; ensure the bund area remains waterproof | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636819&prj=643&rqi=1cdhqKPVD5K876KAZIBw3im3ZN
GI-040 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Incomplete Connections | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Water discharge pipes from Pressure relief valves are to be mounted securely | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636832&prj=643&rqi=UUy0wGepmPwFCt0TEZCOCUF5OS
GI-039 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | General Design Issue | Design | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ MU043â€‘RHKâ€‘XXâ€‘XXâ€‘SPâ€‘Mâ€‘XXXXâ€‘7110 â€“ CHW Buffer tank specify that buffer tank shall have inspection hatch. Buffer tank within PPCR has no inspection hatch. Can you please clarify if this was agreed? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636831&prj=643&rqi=xL5ucIYSMx2REQ2JFekxr1Q3Xd
GI-041 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Update PID with correct model number of HEX | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636836&prj=643&rqi=THbFQounMPzUGY7RSt1pjZ7CAx
GI-036 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Cleaning | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ General Cleaning shall be carried out following completion of all installation. Swarf, debris, dust shall be removed from plantrooms, any panels and equipment prior shipment. This is particularly important prior to any energisation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636827&prj=643&rqi=6WC1RDpHwM4XMe2fqvIF6z10Tw
GI-038 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Points list to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636830&prj=643&rqi=vSX8IxK9UKczrj4UGLSRJmetMb
GI-031 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPCR FAT module 6 : The Unistrat channels have sharp edges that lack protective covering. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636809&prj=643&rqi=FAXn2cUhdnSTc0kfHTwTgT5UfY
GI-037 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Number of test packs were provide, and some were yet to be provided. Test Packs are to be compiled and complete where required. Calibration certs to be included | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636829&prj=643&rqi=mTY3WlW3w5iN6FZKHfPefQkOww
GI-033 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Please review isolator switch panels. When isolator is used to deâ€‘energize equipment, opening the panel door poses a risk as incoming power is still live, while there is no physical restriction to touch live terminals/cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636820&prj=643&rqi=n2aYs2mLi7FL1AmTdPXY0sAtjK
GI-034 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ MU043â€‘RHKâ€‘XXâ€‘XXâ€‘SPâ€‘Mâ€‘XXXXâ€‘7002 â€“ Pipework insulation states in pointâ€¯5 of additional comments that: All internal pipework that is indicated as â€œnot insulatedâ€ shall still be insulated inside the building after penetrating the outer wall over a length of minimumâ€¯2â€¯m to avoid cold bridges and condensation. Currently there is no insulation applied and it was understood that no insulation will be installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636825&prj=643&rqi=9AMciAxpHbcY2RWd4AJ1zyr6ND
GI-035 | MU04-3 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Ensure any missing panel dimension drawings, wiring diagrams are provided within panels or attached to equipment before leaving factory. Ensure all panels have a documentation holder aa well. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636826&prj=643&rqi=EYMxbYiW3KXEI2AqnlPcam1N3t
GI-012 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR -FWT : Pump glands are loose and incoming cables lack proper labeling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635541&prj=643&rqi=apa6tJwP5E16xDHTe2WpCXN4MR
GI-011 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR- FWT : Chiller panel cables need to be fixed and labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635538&prj=643&rqi=8BhmBqQc6RHNobIdNZdZDbSPvB
GI-029 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT: DCOS cables require termination into WCC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635576&prj=643&rqi=yNLChxlinB49NHJF4gdh3Ld8ao
GI-021 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT: Trip hazards are not marked throughout the pump room, creating a risk of falls. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635558&prj=643&rqi=5n1yw57rv5dZNs6OgsTY4r1VPg
GI-022 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT : The required external opening was not constructed within the room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635559&prj=643&rqi=s1uoo57tmkYG7ZWLeTn8oGYQj8
GI-020 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT: The WCC PRV pipework contains an unfilled hole. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635557&prj=643&rqi=rtDB2WwNXWuMRcfPG8SqFTV1X6
GI-019 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT : The DX unit installation is incomplete because the cable tray requires a notch cut out and the pipework lacks sufficient lagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635556&prj=643&rqi=8HY9SLTrxu2L9H5fkIDOgX3EFb
GI-018 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Cleaning | Commissioning | [6 empty] | PPR-FWT : The waterâ€‘cooled chiller is extremely dirty. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635554&prj=643&rqi=709kMtYzfdbVdFiMtLjriLBmHR
GI-023 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPE-FWT : The condensate pipe lacks sufficient structural support, risking sagging or misalignment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635560&prj=643&rqi=fn7mHfjCEC0YY9frOZlkCQUorj
GI-024 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPR-FWT : No documentation has been provided for the refrigerant circuit, including pressureâ€‘test, evacuation, and charge records. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635563&prj=643&rqi=1wTzDN0gfE9NTnugM49Hz1xnRe
GI-017 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPR-FWT : The exhaust fan has not been installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635553&prj=643&rqi=cf8wdOj97f4VRe7KTh55BsBPuI
GI-013 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR- FWT : Sheet metal on base not secure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635548&prj=643&rqi=XxZ9tDMXQaVctcKmDh1TrbRPaJ
GI-025 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [6 empty] | PPR-FWT: The pump room lacks a declaration of conformity plate, and no conformity paperwork has been provided for any assets within the area. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635565&prj=643&rqi=dzYoZZqhkUf3lD7YE1LIN2xcaO
GI-016 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT : The WCC lifting anchors are no longer required and must be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635552&prj=643&rqi=dDvb9yRbpEOMLkEdskgpZhCWVO
GI-002 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | The PPR system has no earth bonding on the main structure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635290&prj=643&rqi=rJiFqNNWwOrQSNRH3JgsmC1EiY
GI-026 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPR-FWT : Secondary pump isolator - very poor install cable needs re-terminated, no torque marks, no door earthing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635573&prj=643&rqi=WUgAIKIEo98tREnow45Dnfr826
GI-028 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT : Mains cable on VFDs not secure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635575&prj=643&rqi=ElMwqOauwYikOw2KihYP7BsqJO
GI-005 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Torque required | Commissioning | [6 empty] | PPR-FWT : The DCOS panel lacks torqueâ€‘marking on its earth connection, making it difficult to verify that the earth bond is tightened to the required specification. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635327&prj=643&rqi=XxUzhZql9gR8GvDSgOE66UYdDc
GI-006 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Cleaning | Commissioning | [6 empty] | PPR-FWT : All assets are very untidy and require a deep clean, including the panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635328&prj=643&rqi=OQWT4mRfTWJJswKLMcvk5SyXyI
GI-007 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | PPR-FWT : The primary pump isolator is poorly installed: the cables are incorrectly terminated, lacks torque marks, and the door is not earthed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635330&prj=643&rqi=rxtjr6jKbScpJqgZV2z0ayMGrl
GI-030 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT: Cable terminated incorrectly, no torque marks, no bonding on frames. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635577&prj=643&rqi=GreqBZdfXlMEwO1KhQgdjcT5LZ
GI-010 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Incomplete Connections | Commissioning | [6 empty] | PPR- FWT : The distribution panelâ€™s stuffing gland opening is left unsealed, exposing the interior to potential contaminants. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635347&prj=643&rqi=7SuoaTqcaBFz8v6lhjmJ4j8rTh
GI-015 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT : The chiller cables are not properly terminated, leaving an open connection point. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635551&prj=643&rqi=U2qSHGXz5ze4BEk9b6JJTTW1Yx
GI-014 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT :The expansion vessel is not secured to the system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635549&prj=643&rqi=Mtl8AGgUISxA5jSV8ig4rOeePS
GI-008 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [6 empty] | PPR-FWT : Valves lack clutch clips, preventing proper mechanical engagement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635336&prj=643&rqi=2uOB40XYu2WHUMXZG4yWzqeUZN
GI-009 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Labelling | Commissioning | [6 empty] | PPR-FWT : The system lacks traffic labels and flowâ€‘direction markings, making it impossible to identify correct flow paths or routing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635340&prj=643&rqi=l44Xi5m7I7nS1715Z0wlMApQHF
GI-027 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [6 empty] | PPR-FWT : Compressor glands loose on WCC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635574&prj=643&rqi=fkSEzZ2PcAwDA6DoFi5UKNISYO
GI-004 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | DCOS General Issue | DCOS | [6 empty] | The PPR systemâ€™s DCOS panel has inadequate trunking and cable management, leading to cluttered, hardâ€‘toâ€‘inspect cabling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635326&prj=643&rqi=jBU6FGXrqBwZYInE99KjGkvpAn
GI-003 | MU04-3 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [6 empty] | During the FWT of the PPR systemâ€™s, it was observed that the DCOS panel is fitted with a UK socket, which fails to meet EU electrical standards. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635293&prj=643&rqi=1fJ8gzQi8nLpAzrzFmSuQeUnAT
GI-001 | MU04-3 | N-EMEA | Ready for Verification | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-04-28 04:00:00.000 +0400 | AER - Aermec |  | Design not as specified | Design | [6 empty] | Dry Air Coolers and Waterâ€‘Cooled Chillers have been selected by the vendor for seaâ€‘level operation. MU4.3â€™s site elevation is over 500â€¯m, and the vendor expects at least a 3â€¯% performance degradation per DAC due to the reduced ambient air density. DACs will also be used to cool the condensers of WCCs, but the impact of the higher site elevation on WCCsâ€™ cooling capacities is currently unknown. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619831&prj=643&rqi=GrecXjBrSdhfkBAwHxHXPos9rt
GI-455 | NY03-2 | AMER | Ready for Verification | P3 Low CX | Christopher.Federico@veolia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor - BMS |  | Component/Equipment Failure | Commissioning |  | system | CHW System |  |  |  | CHWSTR-ALL: Recharge valve "failed to start" nuisance alarm occurred when thermal storage remained in recharge mode but valve commend was zero because actual was close enough to setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635767&prj=560&rqi=31ocSeieldAUCWKil6Jvk3oIuU | https://equinix.facilitygrid.co.uk/x/project/560/system/11494
GI-451 | NY03-2 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | State_text to be added to missing int points by SI. file already provided also in another INC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634504&prj=560&rqi=IW9SntLwCjpDC8ziiua7CPworx
GI-445 | NY03-2 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Tags not performed once. To be corrected by SI | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634372&prj=560&rqi=cmPgk5rl3udZdsGixD5hWpx5Gd
GI-447 | NY03-2 | AMER | Closed | P3 Low DCOS | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | Negative and/or Non-standard values found in few points. SI to Check and correct the values. Sample images attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634391&prj=560&rqi=vyLghSc3NsjKMdLvxdihoLTu5H
GI-453 | NY03-2 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | UOM to be added by SI. Image attached. To be updated for all the similar asset type points | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634511&prj=560&rqi=EhJdPIHJg6jBrjkmQaKwV08tRT
GI-449 | NY03-2 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Design Issue | DCOS | [6 empty] | Wrong Naming Format of the asset. 022203T00_1GEN_G_DATA. Attribute should not be in Asset name. Numbers overlapping the box in graphics. Screenshot attached. Wrong Maximo Asset Number assigned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634436&prj=560&rqi=PfPfJUtQyUfzcBhFZv39nJm7kl
GI-452 | NY03-2 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Design Issue | DCOS | [6 empty] | Alarm Configuration to be updated by SI in graphics for all CRAHs. Screenshot attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634505&prj=560&rqi=1ORVDB8ooCoieixnOp1E2M67RJ
GI-450 | NY03-2 | AMER | Closed | P3 Low DCOS | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | Non-standard Display Point name needs to be renamed by SI. Iâ€™ve attached screenshots with comments for non-standard points from one asset of each asset type. Please use the Standard Points List to rename all applicable assets accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634487&prj=560&rqi=8mTqHGEnfmLbayTiXTJZyvO8tv
GI-444 | NY03-2 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | Maximo Asset Number updated under Maximo Asset ID for below assets. Maximo Asset ID should be kept blank in DCOS. NY3.011050T00_1CRAH_H_07 NY3.011050T00_1CRAH_H_09 NY3.011050T00_1CRAH_H_10 NY3.022060T00_1CRAH_G_19 NY3.022060T00_1CRAH_G_20 NY3.022060T00_1CRAH_G_21 NY3.022060T00_1CRAH_G_23 NY3.022060T00_1CRAH_G_24 NY3.022060T00_1CRAH_H_13 NY3.022060T00_1CRAH_H_15 NY3.022060T00_1CRAH_H_16 NY3.022060T00_1CRAH_H_18 NY3.01040000_1PDU_E_01_01 NY3.01040000_1PDU_E_01_02 NY3.01040000_1PDU_E_01_03 NY3.01040000_1PDU_E_01_04 NY3.01040000_1PDU_E_02_01 NY3.01040000_1PDU_E_02_02 NY3.01040000_1PDU_E_02_03 NY3.01040000_1PDU_E_02_04 Check thr files for more issues associated, wrong assigment, shifted ones, etc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634367&prj=560&rqi=WcHzPXEJvWTMB0vBGG5xYS56Xl
GI-448 | NY03-2 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Template Issue | DCOS | [6 empty] | Assets missing in DCIM. Please use the correct template and add into DCIM. Screenshot attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634396&prj=560&rqi=n8CBOJmUliZx0CVGvgLIdacSrw
GI-446 | NY03-2 | AMER | Closed | P3 Low DCOS | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Design Issue | DCOS | [6 empty] | Misspellings of Display Name to be changed by SI. All Heat Trace, Transformer and PID. Sample Image attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634374&prj=560&rqi=54qhZh3GdMb3UqgRFpsIuR1BOJ
GI-441 | NY03-2 | AMER | Ready for Verification | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-08-14 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | Topserver errors and warning clean up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633737&prj=560&rqi=tBoXeYAlwW9W4hmGETZGGnU9ZO
GI-443 | NY03-2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-08-14 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Design Issue | DCOS | [6 empty] | MSB alarms incorrect naming and attributes. - the name can not include the "alarms" word -the asset type is switchboard, not generic template -the attrs are not the required ones | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633739&prj=560&rqi=1WipzDNWjOwYbOGxmdm1ZyDkeB
GI-442 | NY03-2 | AMER | Open | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-08-14 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | Aalogmonitor errors and warning clean up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633738&prj=560&rqi=mZVVHztetnXNvHED3GDg7J2Mr6
GI-437 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - On the LBSB Single Lines - Change all the UDP X to UDPR X for the boxes shown on the R spine (between "Block R1" and "LBSB") | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630003&prj=560&rqi=uAJ4jIiETWpFGI3yJYkvM2dQAX
GI-434 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - PUE kW/RT - The calculation is incorrectly using input kW divided by runtime hours should be kW/Ton. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630000&prj=560&rqi=QFQ6nHrxgpb95CDz6pBf6zLX1L
GI-428 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - Generator - When generator is running, the "Summary" reads "Stopped, Auto, Alarm". Not sure why it would show "Stopped". | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629994&prj=560&rqi=4aPAEPHWHIHbN598KZ5DRqKYUR
GI-425 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - Generator Faceplate - The acknowledge buttons disappeared from the Faceplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629991&prj=560&rqi=FNOn1WW11kroiaJBpyAWwWYZoz
GI-431 | NY03-2 | AMER | Closed | P3 Low DCOS | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - UPS - "Bypass Not Available" and "Inverter/Bypass Out of Sync" and "Warning" intermittently come in on transfers to/from generator. Discuss with Equinix a time delay to override nuisance alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629997&prj=560&rqi=We2rFYx3Tf3VGrLmN2Nqm5RsVs
GI-439 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - Chiller - The timer for the recharge valve to open stopped at 234 seconds on the graphics though it appeared to run in the background and valve opened after the approximate 300 seconds. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630005&prj=560&rqi=QG4UjHzeMVrLJqtqjI2UJ8KA0T
GI-430 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - UPS - "Bypass Not Available" is only coming in on UPS-F1/G1 and not on UPS-F2/G2. Need to confirm if this is an equipment or BMS issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629996&prj=560&rqi=aQUHb8kzowAWmpFv83Unoj48O5
GI-436 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - On the UDP Block Single Lines - Show the feeds from the primary UDP to the tethered UDP with a hyperlink to the appropriate UDP page) (ie. UDP-F1 needs to show a new feed to UDP-J1-1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630002&prj=560&rqi=eAtGRFcltOYaObPDctXOyEPIdU
GI-427 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - Generator - "Fuel Hours" show alarm and 0 when generator is running. Should show an actual value with no alarm. Also discuss with Equinix if there are ok with showing "0" when generator is not running. May rather show as "unknown" or blank. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629993&prj=560&rqi=9Ms5YJ9RphFK2xGzuPgjDcB2Xe
GI-424 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - Certain alarms (ie. generator & UPS) are not coming into the alarm banner. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629990&prj=560&rqi=RY1PR3LXbBmhcpbmolYX5jWKaS
GI-426 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - Generator - Confirm the difference in the alarm registers for "Battery Charger AC Fail Alarm" and "Battery Charger Fault". As far as I can tell, we only have one alarm wired from the battery charger, so I am not sure what the second alarm would be. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629992&prj=560&rqi=8mfVjQO2X31qNNXMnigpRBIz5o
GI-435 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - PUE kW/RT Total - The calculation is incorrectly adding the kW/RT of each Chiller. Should do a total kW/total Ton calculation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630001&prj=560&rqi=Q1yF40xYVBXI5MRJcYy1BIrfoW
GI-433 | NY03-2 | AMER | Closed | P3 Low DCOS | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - MSB - "TVSS Alarm" comes in on transfers to/from generator due to power loss on TVSS. Discuss with Equinix a time delay to override nuisance alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629999&prj=560&rqi=cBdHC2HPKjoWzHQ9XDQgDo42Pg
GI-440 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - RMU - The BARD unit template shows two units with a lead/lag setup but the actual controller only has one of two units connected. Recommend discussing with Equinix to update template to show just a single unit with no lead/lag. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630006&prj=560&rqi=MAbjy2yQV1TilEeAaEaaezRbr8
GI-432 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - UPS - PHS indicated that battery runtime provides an out of range value when UPS is not on battery so they mask the value as zero. Discuss with Equinix if there are ok with showing "0" when UPS is not on battery. May rather show as "unknown" or blank. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629998&prj=560&rqi=3gnMSQHMODGBdsdGFx8HouuhvZ
GI-429 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS - UPS - "Bypass Not Available" is showing as a Priority 4. I was under the impression that Priority 4 is only for Communications alarm. Confirm with Equinix. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629995&prj=560&rqi=79F9NPsrUDPM47LV4tLi6702us
GI-423 | NY03-2 | AMER | Closed | P1 High CX | steve.mulakkal@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning | [6 empty] | During Electrical Pre-IST, the UDPR-G1 Main breaker was opened to simulate an 180 degree Out of phase transfer on the G1 STSs. However, when the UDPR-G1 main breaker was opened the following occured. - STS-G1-1, G1-2, and G1-3 transferred from S2 to S1 (Expected Response) - STS-J1-2-1 and J1-2-2 transferred from S2 to S1 (Expected Response) - STS-E1-1, E1-2, E1-3, E1-4 serving customer load transferred from S1 to S2 (Unexpected Response). - UPS -E1 registered a "INV Volt Abnormal-TR" alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629239&prj=560&rqi=G2JcanaaH51eDRCmA5SYIpXUtJ
GI-422 | NY03-2 | AMER | Closed | P3 Low DCOS | jreitz@equinix.com | 2026-07-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCIM Platform issue | DCIM | [6 empty] | Yesterday we looked into and opened a ticket for Topserver at the NY3 site to address an issue with Quick Client. We did some initial investigation to better understand the problem and quickly realized that Quick Client is not connecting to Topserver. We captured a few relevant screenshots of the error, along with UAExpert successfully establishing a connection. The ticket opened with Software Toolbox (CASE Number #46222848275) describes the issue and includes the screenshots. It took a bit of time to gather the required information and work through their bot. It referenced a couple of knowledge base articles which were helpful but did not address this issue, and then connected us with John, a Technical Application Consultant. John walked us through a few additional steps to gather more information, including screenshots of configuration settings and, this morning, a basic set of logs. As he explained, Quick Client connects to Topserver using OPC-DA, while UAExpert uses OPC-UA, which explains the difference in results between the two tools. His next step in troubleshooting is to investigate a potential COM/DCOM permissions issue, despite everything running under the local system account. OPC-DA is enabled, and the configuration appears to be correct. Weâ€™ve submitted the log files and asked what indicators might point to the failure, as well as where we can find resources to review the logs on my own. We will keep you updated as we learn more. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627718&prj=560&rqi=tbjoXv4SiEmpNUNCLKYJ86AwZW
GI-419 | NY03-2 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor |  | General Design issue | Design |  | equipment type |  |  |  |  | Generator Fuel Supplier pipe pressure - RFI#30 - pressure issue with the generator fuel supply line inside the generator enclosures specifically between the check valve and the high level solenoid valve. When the solenoid is engaged due to a tank high level alarm (set to 90% of usable fuel) the heat of the solenoid transfers to this section of pipe and builds pressure. Under this condition this section of pipe in generator C experienced a leak when the pipe pressure surpassed the pressure gauge rating. The tank high level alarms do not automatically clear when the conditions are met (ie the tank fuel level drops below the high level) and will require an operator to manually clear at the fuel supplier panel HMI. At this point and to alleviate the current issue, if a generator fuel tank enters high level alarm the operators can transfer fuel into a lower level tank to exit the high condition and clear the alarm at the fuel panel; however this would require constant monitoring of the fuel system if fuel levels are maintained close to 90%. Outside air conditions and generator runs will also affect the tank fuel temperature and may cause fuel levels to increase or decrease. In the case mentioned above for generator C, the high level alarm and solenoid were active for long enough to build temperature/pressure in this line and break the pressure gauge. One potential solution would be installation of a pressure relief line from the fuel supply line to the fuel polishing return line, as this is open to the tank; similar pressure relief lines have been installed on the NY5 generator fuel supplier/polisher lines. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626566&prj=560&rqi=6oymlT8OdoNplbmHgaAHN45vKG
GI-414 | NY03-2 | AMER | Closed | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - DCOS Quality | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626398&prj=560&rqi=arm0vB7cKOBj2ELfwVPBjVH8cV | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-413 | NY03-2 | AMER | Ready for Verification | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - DCOS Config | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626397&prj=560&rqi=UyjI9WCXTpB7KJRJ64Ddh2ELgx | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-417 | NY03-2 | AMER | Ready for Verification | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - DCIM Quality | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626401&prj=560&rqi=krDjZ7BmvFwf7sAFjY44YP4BAa | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-416 | NY03-2 | AMER | Ready for Verification | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - DCIM Config | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626400&prj=560&rqi=5kQcyVsr02Tgdp2O0tf8pXwNTn | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-415 | NY03-2 | AMER | Ready for Verification | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - DCOS Accuracy | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626399&prj=560&rqi=x7xHSoOegQryIevMdG9FIsp9D5 | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-418 | NY03-2 | AMER | Ready for Verification | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - Asset Mapping | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626402&prj=560&rqi=Km6arIvGp4Q3HyfX2P9ug9g6q5 | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-411 | NY03-2 | AMER | Closed | P3 Low CX | kyle.vogt@veolia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Transformer 1 Over Temperature and Transformer 2 Over Temperature Alarms are present locally but are not present on BMS for F and G PDUs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625142&prj=560&rqi=Am6c2WW1oln2kGWlFBZeBt9MMx
GI-410 | NY03-2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | All Electrical Skid CRAH's: The Electrical Skid Graphic at Skid F and Skid G always displays all CRAH's to have an M, indicating manual mode, whether or not the CRAH is actually in Manual Mode or not. The M on the graphic should appear only when the CRAHs are in Manual Mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624950&prj=560&rqi=aCwBRENE5MnaAQMYUpOqLUOF6l
GI-409 | NY03-2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Installation Not Complete | DCOS | [6 empty] | DCOS-DCIM Validation NOT COMPLETED Check the attached files for reference, but the Validator tool is the real source of truth: https://onboarding.dcim.corp.equinix.com/ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624915&prj=560&rqi=fatCciy9H9Om27bONIfvBAGMJt
GI-408 | NY03-2 | AMER | Closed | P2 Medium DCOS | manuel.gomez@eu.equinix.com | 2026-06-09 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS General Issue | DCOS | [6 empty] | DCOS - DCIM Onboarding validation is not completed. Attached are the reports for evidence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624482&prj=560&rqi=bCtlcEA2t1OyyXIsDPck9JES1K
GI-406 | NY03-2 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-06-04 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Component/Equipment Failure | Commissioning | [6 empty] | PDU H1-2-1 Breaker 2 - Breaker is incorrectly displaying a voltage of 375V when all other breakers are reading 405V. Hanley to investigate and rectify the issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623988&prj=560&rqi=NKEG9LyezuC9mFkj6iDFVih0ng
GI-404 | NY03-2 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - BMS |  | Component/Equipment Failure | Commissioning | [6 empty] | PDU-H1-2-2 - Initially this PDU was not communicating to the BMS. Upon troubleshooting, PHS discovered a bad ethernet cable between the PDU and the IBX network switch. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623986&prj=560&rqi=RcUT1nrlVlFsQePWbpUXP3bNg0
GI-405 | NY03-2 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-06-04 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Component/Equipment Failure | Commissioning | [6 empty] | PDU H1-2-1 Breaker 1 - Breaker is not communicating to the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623987&prj=560&rqi=EpyJoddG1yPWfjOzKsGasp1ltA
GI-403 | NY03-2 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - Electrical |  | Incomplete Connections | Commissioning |  | equipment type |  |  |  |  | PDU-H1-2-1 Breaker #6: While load banking the PDU, the A-phase pigtail connected to the load bank on CB6 reached 350 degrees F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623734&prj=560&rqi=LSzJaiRNk2kShsP7BDNOLzJvTz
GI-402 | NY03-2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-01 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | DCOS - DCIM Validation not completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623552&prj=560&rqi=Sp7T6k2HuupT7SmZIcoifMFdUZ
GI-399 | NY03-2 | AMER | Closed | P3 Low CX | steve.mulakkal@veolia.com | 2026-05-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Component/Equipment Failure | Commissioning | [6 empty] | UDP-G2 (Spare Breaker): Lockout tab is stuck and can not be pulled out to LOTO breaker. Issue was originally discovered on STS-G2-2 breaker. and lockout out tab was replaced with part from spare breaker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623225&prj=560&rqi=ZDaQBZI6BJEDMsNZmqQ98jKM1h
GI-393 | NY03-2 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS | Controls | system | DCOS |  |  |  | CWWT-A-01-CP-1 / Makeup Water Overview - Not communicating to BMS; MCE to check | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622681&prj=560&rqi=9eT5FKGPUhQ3tByk7N32SSY4GS | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-396 | NY03-2 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | MSB-"X" Alarms Symbol / Block E Graphic / Block C and D overviews include a "MSB-X Alarms" symbol and corresponding faceplate, but this is not included on Block E at this time. Does this need to be included on the Block E overview page? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622684&prj=560&rqi=7fDed82kvX2Q9B3YHdB8gKz2YP | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-392 | NY03-2 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCIM |  |  |  | De-icing Manager - Fan Direction control timer analog input boxes - can not be edited from the faceplate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622680&prj=560&rqi=YUayW0lKJCzuZZgOStbiuOfQ3x | https://equinix.facilitygrid.co.uk/x/project/560/system/11779
GI-394 | NY03-2 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-05-21 04:00:00.000 +0400 | Design Professional |  | DCOS Design Issue | DCOS | Controls | system | DCOS |  |  |  | MUW-PMP-1 & 2 / Makeup Water Overview - Flow switch proves flow without the pump operating, head pressure from storage tanks is high enough to make up Cooling towers without starting pump - Pump in alarm on BMS currently sending "fail to stop" even though pump is not running. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622682&prj=560&rqi=lA3Ch70p2pCcDz69ehcuaowI9j | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-391 | NY03-2 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | Data Hall First Floor Area B East Graphic - Graphic needs to be updated by removing the half hot aisle closest to CRAH-F-1. See attached screenshots based on latest design documents. This may cause confusion since there is no CRAH hot aisle temperature sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622519&prj=560&rqi=NcWJw8FxS9OVXI6QCScqx2CGoO
GI-388 | NY03-2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-05-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Incomplete Connections | Commissioning |  | equipment type |  |  |  |  | WSHP F1, F2, G1, G2: Tripping the smoke detector does shut down the unit. MPS needs to update their wiring, so that a trip of the smoke detector is latching and remains in alarm until it is reset. Using the test button, the unit alarms until you remove your finger from the test button, and the alarm instantly clears. Similar issue we had with WSHP's E1 and E2 in the past. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622496&prj=560&rqi=Ui3vLQm6ZYVLSXD0HyKzISBpFm
GI-383 | NY03-2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-05-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | Electrical Skid CRAH's: Cannot place units into manual mode from BMS. Changing the unit int manual mode from the HMI also does not correctly update to "Manual Mode ON" on the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621226&prj=560&rqi=88wHC30U09exELbNaeFL6LWICi
GI-384 | NY03-2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-05-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | Electrical Skid CRAH's: Supply air Hi and Supply air Lo setpoints are unable to write to on the BMS and do not display the correct values on the BMS. Correction: We are now able to write the BMS, however the unit itself does not take the setpoint value. There is no correlation between BMS setpoint input and actual unit HMI setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621227&prj=560&rqi=1IZnY5MGwuhOlKia9RMjUAn4I5
GI-382 | NY03-2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-05-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | Electrical Skid Delta CRAH's: Cannot write a supply temperature setpoint to each E-CRAH. The BMS also does not display the correct Supply Temperature setpoint value. Correction: We are now able to write the BMS, however the unit itself does not take the setpoint value. There is no correlation between BMS setpoint input and actual unit HMI setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621225&prj=560&rqi=VHCpdQbxIYXIOkAMGHIXRH6chU
GI-377 | NY03-2 | AMER | Closed | P3 Low CX | kyle.vogt@veolia.com | 2026-05-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Not Complete | Commissioning |  | equipment type |  |  |  |  | 1PDU_J1_2_1: ground cable lug damaged and disconnected from ground | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620823&prj=560&rqi=DpjBdBFaoC76st8ROR4154TLJR
GI-370 | NY03-2 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | Data Hall CRAH's: Total CFM value is reading ~4500 CFM when all fans are powered off. When failing one fan, the current total CFM value would remain. In most cases, it appears that the HMI is presenting the average CFM output of each running fan and multiplying it by 4, even if only 2 fans are running. However, when failing all the fans from the breaker on a running unit, the total CFM indicator still reads 4500 CFM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620310&prj=560&rqi=EFLx3vSdVlVY8W0itY8lJofWKF
GI-369 | NY03-2 | AMER | Open | P3 Low CX | Christopher.Federico@veolia.com | 2026-05-01 04:00:00.000 +0400 | Equinix Project Manager |  | Installation Damage | Commissioning | [6 empty] | STS-JX-X: STS damaged during transport. Makes opening and closing unit very difficult. Delta to provide a quote for repair. (unit designation TBD) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620118&prj=560&rqi=AHK2hAANywjoevY3BITqcru52T
GI-367 | NY03-2 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor - Mechanical |  | General Design issue | Design |  | equipment type |  |  |  |  | Fuel Supplier/ Fuel Polisher - Upon MSB transfer to generator or Utility power, the respective pnuemercator is power cycled and sends alarms to the fuel supplier - critical low, low, full, high, and critical high alarms. These alarms are nuisance and require operator manual reset at the fuel panel. ISP has added a 30 second time delay to avoid these nuisance alarms on power transfers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619770&prj=560&rqi=UVrmJUK2s2IC7m53gODQUJIJuo
GI-365 | NY03-2 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-04-24 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [6 empty] | Phase 2 - BMS "Electrical One Line overview" page need to be updated for Blocks E, F, G, H to properly display the UPS to IOB breaker line animation. See attached images for discrepancies to match Blocks R1, A, B, C and D. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619348&prj=560&rqi=JMu24U96tVn2g9ymLjeZz58zft
GI-395 | NY03-2 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-03-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | Controls | system | DCOS |  |  |  | PDU-C-1-1 / Electrical One-Lines / Faceplate and graphic are different between phase 1 and phase 2 equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622683&prj=560&rqi=2Jz2k91449jkx0e2QC4aFz4wml | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-340 | NY03-2 | AMER | Closed | P2 Medium CX | steve.mulakkal@veolia.com | 2026-03-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | Phase 2B - All PDUs - Lexan covers for PDU bus protection is missing on majority of Phase 2B PDUs. Hanley to provide and install all missing Lexcan covers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615868&prj=560&rqi=uKHt4aHl6ariY1iNIyOWgwkzkJ
GI-335 | NY03-2 | AMER | Closed | P2 Medium CX | nicholas.leber@veolia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Phase-2A - Chiller Manager - After completion of IST, the "number of chillers required" analog input box would not accept a changed value from OM11 BMS screen. The signal would send from OM11 and start the next in line chiller skid, however the chiller would shortly stage down as the manual input did not hold; rather it reverted back to the original value. Through troubleshooting, determined that OI01 and OM01 were overwriting this point. This issue was previously resolved prior to IST during the points mapping transfer effort reverification. This issue is now resolved, PHS removed the input from OI01 to OI11, such that the manual input to this "number of chillers required" is resolved again. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615344&prj=560&rqi=lNkctPnhEn3gWVgS5drl9M0c0u
GI-333 | NY03-2 | AMER | Closed | P2 Medium CX | Christopher.Federico@veolia.com | 2026-03-05 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Phase-2B - PDU-J1-1-1: Breaker 01A, B-Phase on the breaker is testing 1200+ micro ohms while A and C phases are testing at <350 m ohms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614840&prj=560&rqi=xjz5LpC76Xg4npMbFxDxUMzP6z
GI-397 | NY03-2 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-03-04 04:00:00.000 +0400 | General Contractor |  | DCOS Comms Issue/Fault | DCOS | Controls | system | DCOS |  |  |  | 00027T00_City Water_PMP - Aveva Floor Layout - Popup Faceplate - Failure to communicate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622688&prj=560&rqi=u7j6xJRE4snKLnhYBVjidUR7Ox | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-329 | NY03-2 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-02-13 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | MAU-B2 - Unit was still addressed by both the new and old OI Aveva systems causing conflicting control signals - which may have resulted in the damper actuators dysfunctionality and condensate build up in the unit. This was previously caught on MAU-A1 - mode control was not constantly fluctuating. This issue should now be closed, as PHS confirmed the old OI is no longer writing to MAU-B2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199219&prj=560&rqi=veaDrP4KeRsHBcX7tgwFjXgh6D
GI-324 | NY03-2 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-01-28 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | PHASE-2A - Generators C & D - Fuel system page displays a leak alarm for both of these generator tanks, although there are no alarms at either generators or Pneumercators. Need to confirm if correct modbus point is used for this alarm and/or if point needs to be inverted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197784&prj=560&rqi=Zby8oUdalwv5GHRsUy7Y1GHtrM
GI-279 | NY05-P2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-17 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | DCOS-DCIM Validation did not pass. Attached the doc as evidence and linked it below to the online tool. https://onboarding.dcim.corp.equinix.com/dataflow | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625659&prj=527&rqi=iA6MmrGDdXIyt60pHsugKHnYn3
GI-269 | NY05-P2 | AMER | Closed | P3 Low DCOS | jreitz@equinix.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | Shows an alarm on sensor 2 when the value is within the acceptable range. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624326&prj=527&rqi=nXBJUbyPyaZIADLFltaqeh5y6X | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-260 | NY05-P2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | Controls | system | DCOS |  |  |  | Graphics not aligned as per stds. Numbers over lines. check screenshoot | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623740&prj=527&rqi=MhnEfyEMWBlzZWHP9hE8HLfd6j | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-264 | NY05-P2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Design Issue | DCOS | Controls | system | DCOS |  |  |  | These two alarms from the GENs must be suppressed if the GEN is not running : Frequency not within limits Voltage not within limits | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623750&prj=527&rqi=vcwNs5ZJ3zJtQQ5f8mjA1q0dn6 | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-263 | NY05-P2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | Controls | system | DCOS |  |  |  | Links from different objects are not going to the proper page, eg Gens | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623749&prj=527&rqi=cl46PYiqkb4CCml7UL38udlm4E | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-262 | NY05-P2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | We can not export the logs for topserver neither the project as the system have a poor performance and its crashing due to the huge amount of errors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623748&prj=527&rqi=H3nFP3fM8BQFG4gET5IhQEngP8 | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-261 | NY05-P2 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Installation Not Complete | DCOS | Controls | system | DCOS |  |  |  | Missing PUE link on the home page, and the script is not using the latest standard either. Assign to PHS team, they are not currently on the list to assign | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623747&prj=527&rqi=CLXVSaV10XG6XL0b6RYHTX1eOA | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-278 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-05-26 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | Generetor Breaker Open and MSB switch not in AUTO are both stuck in initializing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624335&prj=527&rqi=o08SZ2svzPX4AAloCsBNwwGRku | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-277 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | When trying to control the electric room RTUs if you click on the unit it opens a faceplate with no actual controls other than to put the alarms in maintenance mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624334&prj=527&rqi=Scn63Aorl0YxRZw753Ly8UJvgt | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-276 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-05-08 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | TL:DR The system does not react to massive water use in an effective way. Recently on hot low humidity days we have been having a major issue with draw down on the MUW tanks. The system is not balancing correctly. City water pressure is varying wildly. The system needs to maintain a bare minimum psi of 22+ in order to replenish the tanks and lift to the roof. However maintaining that pressure requires significant valve manipulation. On 5/6 we burned through ~60k gal of water in the tanks before 11am. LC_PRIMUW_03 and LC_PRIMUW2_03 were open to >65% but the recirc valve PC_PRIMUW_04 was also open about 30% and the city supply valves were open to LC_MUWT1_03 ~13% and LC_MUWT2_03 ~30%. PSI was very lowon the city side of MUWT1_03 <20, but pretty high on MUWT2_03 >35. Tank levels were down to <163K per tank and dropping quickly. The Stilling basins had also dropped to below 12" By closing the recirc PC_PRIMUW_04, opening city feed MUWT2_03 to 100%, and setting city feed MUWT1_03 to 18% we were able to drive all PSI to >20 and start to reverse the draining of the tanks. My ask here is why the system was not modualting the valves to slow or reverse the tank loss? If those tanks had continued to drop at that rate and the conditions existed for more than a day we would have been in serious risk of running out of water. Is there any logic in the system to look at the tank depletion rate and open the city valves as far as they can be while still maintaining lift pressure? Once T2 was open to 100% and started reversing the water loss we opended the bypass valve which in turn slowed and then stopped water loss in T1 even though we could only open MUWT1_03 to ~18%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624333&prj=527&rqi=MJzAlRTUmHf1gxlhrbnznSjqPl | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-275 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-05-07 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | the history service is not running on OM11 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624332&prj=527&rqi=H7XPZ40jWmjAYm4uYI8fhfNEWg
GI-258 | NY05-P2 | AMER | Closed | P2 Medium CX | moutaz.abdelhamid@veolia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | BATT-E2 | UPS Battery |  |  | The end-of-life (EOL) was 21+ minutes, exceeding the expected 19 minutes. However, battery 13 of string 6 dropped 1V between minute 19 and minute 21. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618765&prj=527&rqi=QTzfwCtWnqJbxR5qucTguPR5Gb
GI-274 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-19 04:00:00.000 +0400 | Equinix Commissioning Manager |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | If you move the mouse off of a face plate, while attempting to change the value in any numerical text box contained therein, it will result in the disappearance of the "AnalogUserInputAnimation". The value can still be edited but only by using the keyboard while avoiding moving the mouse. The issue also occurs when attempting to edit values in boxes on the main BMS screen, such as in the Liquid Cooling Skids page, but it seems to be more forgiving. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624331&prj=527&rqi=Prk0PPVXcWgJag0RKlklm08Mna | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-273 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-18 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | If one tries to change the command of LC_MUWT1/T2_03 in manual, the window where you can adjust the value disappears as you scroll over it | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624330&prj=527&rqi=R9SM7Sx6XmfSy9hobABjuD4aYA | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-272 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-17 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | Loss of comms on both STSs. The Loss is constant on 3 intermittent on 4. The screens on both STSs are functioning properly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624329&prj=527&rqi=8fEqclMqbqAJhSXGlEQl9sdn3r | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-271 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | Meter disable checkboxes are backwards | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624328&prj=527&rqi=6BGA1enmZmKitDdJReyJwEnKux | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-270 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | MSB header doesnt show what the values listed represent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624327&prj=527&rqi=W2gQMgsb8CPuaJ9kaDkqsbmIVi | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-268 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | Shows a chem treatment alarm with no other information what does this reference? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624325&prj=527&rqi=X7DVgmoOttqlwZn6CnhzF74PZF | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-266 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | Setpoint of 190,000gal with a deviation of 10gal for hi and lo alarm. Deviation should be a percentage not a unit measure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624323&prj=527&rqi=EXP2xRJEZBgLl2mCL8fWcbeE08
GI-267 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | Setpoint of 190,000gal with a deviation of 10gal for hi and lo alarm. Deviation should be a percentage not a unit measure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624324&prj=527&rqi=s1tAPMoxpNmaojsKKbrm3ImZqh
GI-265 | NY05-P2 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-15 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | system | DCOS |  |  |  | Cooling Tower Stilling Chamber Level Setpoint is not adjustable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624322&prj=527&rqi=xDhtfinqaKIB1mka7tpbo0XDlc | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
FPT-45-002 | NY05-P2 | AMER | Closed | P2 Medium CX | moutaz.abdelhamid@veolia.com | 2026-04-14 04:00:00.000 +0400 | Owner | L4 | DCOS Comms Issue/Fault | DCOS | Electrical â€“ LV | system | H Block |  |  |  | UHD-H1 & UHD-H2 - MIB and MBB breakers are not reading voltage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618157&prj=527&rqi=nuIDLdgQ6DyX9viggRMnEVcVQq | https://equinix.facilitygrid.co.uk/x/project/527/system/14170
FPT-45-001 | NY05-P2 | AMER | Closed | P1 High CX | moutaz.abdelhamid@veolia.com | 2026-04-14 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | UPS H Mech does not appear to have an MBB mapped or available. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618154&prj=527&rqi=zvtpVi2P8nLvt0czB21AcVSHQe
GI-254 | NY05-P2 | AMER | Closed | P1 High CX | moutaz.abdelhamid@veolia.com | 2026-04-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | UPS-E system design has been revised from six (6) VRLA battery cabinets to five (5). Confirm whether the existing single set of 4/0 cablesâ€”originally sized for six cabinetsâ€”remains adequate for the system with five cabinets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617227&prj=527&rqi=QjJ0lgJdyFe47oKEliXjXlWzrc
GI-252 | NY05-P2 | AMER | Closed | P2 Medium CX | moutaz.abdelhamid@veolia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | Electrical â€“ LV | system | E Block |  |  |  | Arc Flash stickers currently installed are temporary. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616718&prj=527&rqi=dmwZWv96YDUa2Q5UBcJ1PapwBu | https://equinix.facilitygrid.co.uk/x/project/527/system/11048
GI-240 | NY05-P2 | AMER | Closed | P1 High CX | moutaz.abdelhamid@veolia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | MSB and UHD MTZ Schneider breakers all lost BMS communication. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616431&prj=527&rqi=L7lEPaDfoqilWRr5h9woghNdyl
GI-246 | NY05-P2 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | Electrical â€“ LV | equipment | BATT-E2 | UPS Battery |  |  | Missing Labels for all strings on battery cabinet E2 Battery E2-1 Battery E2-2 Battery E2-3 Battery E2-4 Battery E2-5 Battery E2-6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616442&prj=527&rqi=pO4wwSroDlDcH0p0bToaRk9XAn
GI-250 | NY05-P2 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | Electrical â€“ LV | equipment | BATT-MECH2 | UPS Battery |  |  | Missing Labels for all strings on battery cabinet Mech UPS2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616446&prj=527&rqi=wf2Cfx0VvRwazCecR6ey2PhgBq
GI-245 | NY05-P2 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | Electrical â€“ LV | equipment | BATT-E1 | UPS Battery |  |  | Missing Labels for all strings on battery cabinet E1 Battery E1-1 Battery E1-2 Battery E1-3 Battery E1-4 Battery E1-5 Battery E1-6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616441&prj=527&rqi=wCNWKvymAAYhIlKzIjsaukFFjP
GI-247 | NY05-P2 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | Electrical â€“ LV | equipment | BATT-H1 | UPS Battery |  |  | Missing Labels for all strings on battery cabinet H1 Battery H1-1 Battery H1-2 Battery H1-3 Battery H1-4 Battery H1-5 Battery H1-6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616443&prj=527&rqi=0QiPPI97DyMQwFuAt2XlIp7I7d
GI-249 | NY05-P2 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | Electrical â€“ LV | equipment | BATT-MECH1 | UPS Battery |  |  | Missing Labels for all strings on battery cabinet Mech UPS1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616445&prj=527&rqi=R9V0papM2p4CGm1y48iaBKaicj
GI-248 | NY05-P2 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | Electrical â€“ LV | equipment | BATT-H2 | UPS Battery |  |  | Missing Labels for all strings on battery cabinet H2 Battery H2-1 Battery H2-2 Battery H2-3 Battery H2-4 Battery H2-5 Battery H2-6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616444&prj=527&rqi=XqptjrNL3xKQ7IZtzpyYjWfqGb
GI-239 | NY05-P2 | AMER | Closed | P1 High CX | moutaz.abdelhamid@veolia.com | 2026-03-24 04:00:00.000 +0400 | Mechanical Contractor |  | Design Correction Needed | Design |  | equipment type |  |  |  |  | The Generator tanks were not manufactured with an internal drop-down line for the polisher return. A possible option of rerouting the 2â€ line into the 4â€ opening then extending into tank. Foley to review and confirm. See attached markup showing current site install and possible alternative. Also attached are the submittals from P1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616323&prj=527&rqi=l8mNSwdrOO8j2fFsJq4bxHzmuf
GI-236 | NY05-P2 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-16 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | The approved ECMP 4.0 controller is currently installed; however, its firmware version differs from the version specified in the approved Modbus point list. I am reaching out to Angel Gray to confirm the latest controller-approved firmware version. The current installation runs FW 4.13, which Foley believes is the most recent version available. I will let you know as soon as I hear back from Angel. All the points from the attached approved list proved functional except for LowCoolantLevelAlarm. The register used was 400354.6 instead of 400351.7. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615734&prj=527&rqi=h2kpYUHPqGStBOQeeXfniCTAWX
GI-238 | NY05-P2 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Generator fuel oil back pressure relief pipe is high off the ground causing a trip hazard. Similar pipe on other Gens are are labelled and painted bright color to prevent tripping. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615739&prj=527&rqi=MUB4d6D4U1lBWeuijCtpSXZbD2
GI-237 | NY05-P2 | AMER | Closed | P1 High CX | moutaz.abdelhamid@veolia.com | 2026-03-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | The fuel water separator system has an NTP thread nipple connection instead of a STOR thread, which is causing the leak. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615738&prj=527&rqi=HCW0JWvZI9pPQRWry3EbH53Ij4
GI-233 | NY05-P2 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Provide labelling to all ports for Generators E&H. See attached Image of generator E as example. Labelling format to match exisiting generators. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615731&prj=527&rqi=Xk275IUb9TEQUK0BVLkJlL9n5C
GI-232 | NY05-P2 | AMER | Closed | P2 Medium CX | moutaz.abdelhamid@veolia.com | 2026-03-12 04:00:00.000 +0400 | Engineer |  | Documentation Not issued/ Required | Commissioning |  | equipment type |  |  |  |  | UHD E1/E2 MTZ breakers maintaince mode settings not specified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615478&prj=527&rqi=VyFo9fV9tSroEbwTffIGzseC0z
GI-227 | NY05-P2 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-09 04:00:00.000 +0400 | Engineer |  | Documentation Not issued/ Required | Commissioning | Electrical â€“ LV | system | E Block |  |  |  | E-509 review comments - Arup to incorporate comments (Attached) as part of NY5-P2 As-built record drawings for both Capacity and Liquid cooling E509E and E509H drawings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615135&prj=527&rqi=yYnVOny01VuRSulC4FdYCURd36 | https://equinix.facilitygrid.co.uk/x/project/527/system/11048
GI-226 | NY05-P2 | AMER | Closed | Outstanding Paperwork/Documentation | moutaz.abdelhamid@veolia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Documentation Not issued/ Required | Commissioning | [6 empty] | GC to provide required documentation for project closeout, this includes Torque sheets, balancing reports, Meggering reports...etc. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615134&prj=527&rqi=DIwiWRJCMokgDQL1j7tlXLvsNg
GI-224 | NY05-P2 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | The MSB-E and MSB-H key interlock SOO placards are inconsistent with the placards provided by Eaton. Veolia identified this discrepancy during the NY5-P3 scope review; however, AMG will need to reprint and replace the placards on the previously installed MSB-E and MSB-H units to ensure consistency. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614810&prj=527&rqi=hszUqRqyAvwKGYkA0cldLr2mow
GI-225 | NY05-P2 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | The UHD-E1 and UHD-E2 key interlock SOO placards are has incorrect statment to return loadbank K21 key to SCC, which is incorrect and required to be updated as called out in Veolia submittal review comments for NY5-P3. AMG will need to reprint and replace the placards on the previously installed UHD-E1 and UHD-E2 units to ensure consistency. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614812&prj=527&rqi=pglI089VgtT9yitFDLJnQMLLvl
GI-009 | NY10-EW | AMER | Closed | P3 Low CX | jimmy.mendoza-farfan@veolia.com | 2026-07-06 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not complete | Commissioning | [6 empty] | P-trap is not installed on the condensate drain line as per contract drawing M501 detail 4. TYP for both units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628100&prj=696&rqi=f4BGiIimdRQjE39cJy0ROD7ta1
GI-008 | NY10-EW | AMER | Closed | P2 Medium DCOS | jimmy.mendoza-farfan@veolia.com | 2026-07-06 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not complete | Commissioning | [6 empty] | RTU power exhaust power and control wiring has not been pulled/terminated inside of the unit. Power exhaust was shipped loose and field installed. TYP for both RTUs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628099&prj=696&rqi=FUfbP4vfSbm4NKLsY2N7oVNTVd
GI-010 | NY10-EW | AMER | Open | P3 Low CX | jimmy.mendoza-farfan@veolia.com | 2026-07-06 04:00:00.000 +0400 | Mechanical Contractor |  | Installation Damage | Commissioning | [6 empty] | Upper top left lip of cabinet is bent. Door can be opened somewhat easily, but closing the door is difficult. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628101&prj=696&rqi=MyRJnEwwtVHXBW7tXGLUS1Sgce
GI-003 | NY10-EW | AMER | Open | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | PNL_H8A panel schedule shows a 15A breaker for heater box but submittal shows 20A. DLB confimed that the most current submittal is 15A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624561&prj=696&rqi=QstuexN2iWYWucHWSz5nRAZKkC
GI-001 | NY10-EW | AMER | Open | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | system | Electrical - LV |  |  |  | Temporary Arc flash stickers are currently installed on site equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624346&prj=696&rqi=Bb8s6N9VYT4Pgo8R8fzNV4rdEf | https://equinix.facilitygrid.co.uk/x/project/696/system/14658
GI-002 | NY10-EW | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-06-08 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | [6 empty] | Breaker feeding PNL_H8A within the exisiting HMD-8 panel require a permenant Phenolic label. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624350&prj=696&rqi=POMv199C74OVFA7ck56Ot8TMCx
GI-200 | NY11-5 | AMER | Closed | P3 Low CX | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | Electrical Contractor |  | DCOS General Issue | DCOS | [6 empty] | Thermal Monitoring - Need to confirm procedure and test thermal monitoring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623656&prj=552&rqi=LKd9uQedGx1IkQc2xPcFPsrQUf
GI-199 | NY11-5 | AMER | Closed | P3 Low CX | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Configuration | DCOS | [6 empty] | Chillers - Need to setup time sync server capabilities. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623655&prj=552&rqi=9oRPmJ2KDePxXnlaHdhPAAyp0p
GI-202 | NY11-5 | AMER | Closed | P3 Low DCOS | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | Installation Not Complete | Commissioning | [6 empty] | RPP BCM's - Some of the NY11-5 RPP's were being moved by Site Ops. Need to be informed when construction is complete. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623658&prj=552&rqi=Vff6MhssUHxGSkuxAFezSb5woT
GI-201 | NY11-5 | AMER | Closed | P3 Low DCOS | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | Configuration | DCOS | [6 empty] | Need to complete BMS Aveva License Transfer - Rovisys is in talks with Equinix controls to complete. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623657&prj=552&rqi=Wnh85DkqNSbDpaZajYKVzIc44l
GI-196 | NY11-5 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-03-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | BMS Single Line - Need to verify the single line graphic is correct after the tethers have been removed/Changed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614925&prj=552&rqi=4FacT96JqjIcwj7j2le2JpUzbU
GI-195 | NY11-5 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-03-04 04:00:00.000 +0400 | Design Professional |  | Design Correction Needed | Design | [6 empty] | CHWP-ALL - The breaker tripped when the VFD was used in Bypass. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614746&prj=552&rqi=9GmWyTJ3m6Ijc2y7tUGKpR4qkn
GI-185 | NY11-5 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-02-07 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | MSB-B SPD Alarm: The unit appears to not to be in alarm. But the alarm is active, and the unit is working correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198735&prj=552&rqi=CGBSb7c4M8cJcQ12wtkGSnqgZZ
GI-184 | NY11-5 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-02-07 04:00:00.000 +0400 | Controls Contractor |  | DCOS Template Issue | DCOS | [6 empty] | ALL UPSs for NY11-4 and NY11-5: Need to have the Alarm limti set to the correct values on KW, KVA and output current. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198734&prj=552&rqi=7bpMUpHyjrmrYn78uEo7PTMn9L
GT1ELEC-42-001 | NY11-P1 | AMER | Open | P3 Low CX | edward.woodruff@veolia.com | 2026-09-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: The generator breaker doesn't change state on the trip unit display and the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638599&prj=660&rqi=ZJvQOwnYFtsplLHuaTVlKsF4XI
GI-048 | NY11-P1 | AMER | Open | P2 Medium CX | dustin.haugh@veolia.com | 2026-09-15 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | Low voltage control wires ran with 480v loads. Blue wires in attached pictures should enter cabinet in provided low voltage knockout at top of control cabinet.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638160&prj=660&rqi=gmxJKQOUbnWFrny0rsyXzdnotz
GI-050 | NY11-P1 | AMER | Work Completed | P3 Low CX | dustin.haugh@veolia.com | 2026-09-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | Cubical 07A door need adjustment for opening and shutting. The top 5 hinges on cubical 8 collide with the door preventing normal operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638190&prj=660&rqi=3gfjwzVSvLOHvGyhdIUiN2I75E
GI-049 | NY11-P1 | AMER | Open | P2 Medium CX | dustin.haugh@veolia.com | 2026-09-15 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MDSB_C_1 | MDSB - Mechanical Distribution Switchboard |  |  | Control wires enter and run with 480v load wires. Wires need routed in factory looms to prevent EMF issues. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638189&prj=660&rqi=7byJdYdRo5vWTR3zscW7HjpMib
GI-046 | NY11-P1 | AMER | Closed | P2 Medium CX | Christopher.Federico@veolia.com | 2026-09-10 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MDSB_C_1 | MDSB - Mechanical Distribution Switchboard |  |  | MDSB-C-1: Top breaker has incorrect lug size. correct lugs need to be ordered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637609&prj=660&rqi=Y1YJzWAayRY7f2YROzzczAN4m5
GI-045 | NY11-P1 | AMER | Open | P3 Low CX | Christopher.Federico@veolia.com | 2026-09-09 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1PNL_C_H1_2 | DB - Distribution Boards |  |  | PNL-C-H1-2: Two set screws on line side of breaker are stripped. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637528&prj=660&rqi=GZCYffalGe4kv86Db5jhHuXYDo
YT1ELEC-45-005 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-09-01 04:00:00.000 +0400 |  | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: The Mimic lines on the swbd are incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636375&prj=660&rqi=mAcaX7FGNad1to4NosAeabY9of
YT1ELEC-50-004 | NY11-P1 | AMER | Open | P3 Low CX | edward.woodruff@veolia.com | 2026-09-01 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | UMDSB-C: Breaker Q3 (MBB) only has one Aux NO/NC contact. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636371&prj=660&rqi=50NDUZIoC1xqB5KJk2tJtwksja
GI-044 | NY11-P1 | AMER | Closed | P3 Low CX | jimmy.mendoza-farfan@veolia.com | 2026-08-28 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | CHW recharge line for ACC7 has the wrong Series 70 Bray valve model installed. Note the different part number for the Series 70 Brays. The DA Bray model is only supports ON/OFF control. The G0 Bray model has modulating control. ACC7 has a DA Bray valve installed on the recharge line that needs to be swapped out with the extra G0 Bray valve installed on the ACC8 discharge line. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635986&prj=660&rqi=9qv3wmmElQWVQBXSAtg2fYoik8
GI-043 | NY11-P1 | AMER | Closed | P2 Medium CX | jimmy.mendoza-farfan@veolia.com | 2026-08-28 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Check valves need to be rotated in the correct orientation. Currently the check valve is oriented to prevent backflow into the return line. Check valve should be installed to prevent backflow into the chilled water supply line. Typ for both chiller skid piping. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635983&prj=660&rqi=KTwlZTjgtsgfME0uyFXQydJeTZ
RT1ELEC-57-002 | NY11-P1 | AMER | Open | P3 Low CX | dustin.haugh@veolia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L2A | General Design Issue | Design | Controls | equipment | REMOTE HMI | HMI - HMI Panel |  |  | No drip pan below AC condensate drain connection. Drip pan above AC unit not tied into the drain.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635631&prj=660&rqi=AAlTx5H277Vxt48HQ1TUIidisx
GI-042 | NY11-P1 | AMER | Closed | P2 Medium CX | dustin.haugh@veolia.com | 2026-08-24 04:00:00.000 +0400 | TRN - Trane |  | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Control wiring to chiller sensor damaged. Right cabinet on back of chiller, top middle area. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635063&prj=660&rqi=J78EbKJyOVmNQ752zKOJ6RbP7d
YT1ELEC-45-004 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: All CT polarity's appear to be reversed on all PQMs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630734&prj=660&rqi=xmM5WhHz0hzEmQIcNuy2jErZ7R
YT1ELEC-50-003 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | UMDSB-C3: The polarity appears to be reversed on the PQM CTs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630733&prj=660&rqi=vPgOB2bNSrttqEpuJwOZNXHCrc
GI-039 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-23 04:00:00.000 +0400 | VER - Vertiv |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | IT AND MECHANICAL UPS Batteries: the cabinets are missing the barrier and spacing required by fm global for lithium batteries and cabinets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630725&prj=660&rqi=ukytGVPxEajxFrmgcUMpkdURxY
YT1ELEC-45-003 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | 1MSB-C: The high contact resistance found on Camlock section 8 and 9 from LBB (both) to the Phase A camlock. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629837&prj=660&rqi=75p9PiNJyz67EbOEbGAMUid0iI
YT1ELEC-50-002 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-14 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | 1UMDSB-C: Breaker Q7 has failed NETA testing due to contact resistance. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629169&prj=660&rqi=hXuvJhbrBVo9L5ps6jWsqEOYHS
YT1ELEC-50-001 | NY11-P1 | AMER | Closed | P2 Medium CX | edward.woodruff@veolia.com | 2026-07-14 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | 1UMDSB-C: Breaker Q1 has failed NETA testing due to contact resistance. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629168&prj=660&rqi=iwnYKx10N9ZbYn2CU4jBARYSXK
GI-037 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-13 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MDSB_C_1 | MDSB - Mechanical Distribution Switchboard |  |  | MDSB-C: The as built breakers sizes don't match the submittel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629035&prj=660&rqi=ibxDBEC3QPgHIMhVQ8rCPh0Sxh
GI-038 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-13 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | 1UMDSB-C: The as built breakers sizes do not match the submittel sizes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629036&prj=660&rqi=nHJSZ1Q7oszdpFVl9GWSxXtRNj
GI-029 | NY11-P1 | AMER | Open | P3 Low CX | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | CMM - Cummins |  | Design correction needed | Design | [6 empty] | GEN-C - As observed on other jobs, the battery charger failure is now an alarm that appears instantaneously on a power failure and creates a nuisance alarm. In the past, we believe we had a 30 second time delay to override momentary power blips to the battery charger before an alarm was initiated at the generator. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623651&prj=660&rqi=qdVXHsgtUXuywpR60mxf1Yue9J
GI-028 | NY11-P1 | AMER | Closed | P3 Low CX | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | HAP - Hitachi Energy |  | Documentation not issued/ Required | Commissioning | [6 empty] | MLTX-C - The submittal did not include the proper primary side cabinet and associated accessories. Components were installed in field. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623649&prj=660&rqi=8ZcI3SfgkX8CYuBKA4HX1S40kQ
YT1ELEC-45-002 | NY11-P1 | AMER | Closed | P3 Low CX | ralph.ciardulli@veolia.com | 2026-05-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C - Section 4 Load Bank Breaker - Factory connections for vertical bus were disconnected for the installation of a bus duct flange. While reinstalling the Phase B left side (when viewed from front) vertical bus into the insulator, the bolt was torqued to 51 ft-lbs and clicked well before the connection was fully torqued down. The washer the spacer was still spinning. The volt was backed out and the same issue repeated. Upon further investigation, it appears that the insulator is spinning as the bolt in the back does not move. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623234&prj=660&rqi=INCEkVaUrly0yLsaSEBLh6s934
YT1ELEC-45-001 | NY11-P1 | AMER | Ready for Verification | P3 Low CX | edward.woodruff@veolia.com | 2026-05-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB B: IOB1 K7 key assembly is not in the breaker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622527&prj=660&rqi=jXR2Phsmyv0zKinJcaCTaFFNkS
GI-026 | NY11-P1 | AMER | Closed | P3 Low CX | jimmy.mendoza-farfan@veolia.com | 2026-05-14 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | Bottom section of SWGR needs to be fixed. Refer to photo attached. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621916&prj=660&rqi=AfFuDDaSYApcQeaZUjRrpI6FeZ
RT1ELEC-57-001 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-05-08 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning | Controls | equipment | REMOTE HMI | HMI - HMI Panel |  |  | MSB-C HMI: Above KS1 the placard should read " Auto Auto/Man Man". all on the same plane. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621005&prj=660&rqi=9U2dNL5k8vpaCDZY35wo1m1vmd
GI-023 | NY11-P1 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1-ACC-C-8 | ACC - Chiller - Air Cooled |  |  | Control wiring located on the left side of the control panel enclosure needs to have wires reorganized. Typical for both chillers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618178&prj=660&rqi=4w9JvDM1LQrEBHyh4Z7IBQbE2q
GI-017 | NY11-P1 | AMER | Ready for Verification | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Missing Components | Commissioning | [6 empty] | Fan guard is missing inside the 480V cabinet. Typ for both chillers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618149&prj=660&rqi=FjfewwXpXf88016kyk6hIv2YAE
GI-018 | NY11-P1 | AMER | Open | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [6 empty] | Provide protective enclosure for transformers inside the 480V cabinet similar to the lugs. Typical for both chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618150&prj=660&rqi=JvB6Ljh9d3FJBVJelKjIG5JMay
GI-022 | NY11-P1 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1-ACC-C-8 | ACC - Chiller - Air Cooled |  |  | Several control wires failed wire tug test | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618177&prj=660&rqi=e5tQ4ttYAJo9Q2aUZHkd2Ro4j5
GI-015 | NY11-P1 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Several control wires failed a tug test. See photos for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618147&prj=660&rqi=8vRMD6n29NVinO4tTUQXsEevmI
GI-020 | NY11-P1 | AMER | Closed | P2 Medium CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Missing Components | Commissioning | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Onicon provided with the chiller skid does not match the approved submittal. Flow meter provided is FT-3000 series (FT-3206). Model number on the approved submittal notes FT-3400. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618171&prj=660&rqi=V2V8napvc5nlAfPVk3OLzVEX07
GI-021 | NY11-P1 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Missing Components | Commissioning | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Provide additional neoprene pads (4 total, 2 per chiller) for chillers. See photos for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618172&prj=660&rqi=ZKFsfTKFrlqzJlEa5ii3PmJl4T
GI-016 | NY11-P1 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Installation not complete | Commissioning | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Ground wiring is not terminated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618148&prj=660&rqi=WuZjll0qrBttgNQvWFMQXh8CEC
GI-019 | NY11-P1 | AMER | Ready for Verification | P2 Medium CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Missing Components | Commissioning | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Chiller came equipped with 2 position bray valve for freeze protection. Per equinix EBCS-3 control valve should be fully modulating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618169&prj=660&rqi=pUdi79zEXDk7jZkV12gVMoso1l
GI-009 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-03-09 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: the Cam loc section of the MSB-B Kirk key does not match existing K2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615142&prj=660&rqi=pjw1IxRiMvDiOkmc0Owq6Vdm4h
GI-008 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-03-09 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: the LBB K2 Kirk key does not match existing K2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615125&prj=660&rqi=SpBdoHuYkYB6nGYubhl9bQy0YC
GI-007 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-03-06 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C- the main CTs are not ridgedly supported on the main bus | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614899&prj=660&rqi=aRbehol4mjso0OUzK6YfSC5Anc
RT1ELEC-46-002 | NY11-P1 | AMER | Closed | P2 Medium CX | Christopher.Federico@veolia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | UDP-C1: Needs phase transition piece to properly terminate busway into the gear. Different phasing between manufacturers was not taken into account. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483376&prj=660&rqi=zam0Jer9JR2256XEyMnTKsrJ9g
RT1ELEC-46-001 | NY11-P1 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-02-25 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: MSB skirt pieces were damaged and dented during shipping. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221109&prj=660&rqi=dy14TIVpmLC3Rw124eY5Bj2XB8
GI-002 | NY11-P1 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C HMI: Labels on HMI are all blank. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199688&prj=660&rqi=Rq4DKyW3QsGBi61kU1TZmXQ7xy
GI-006 | NY11-P1 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: Circuit breaker slots for UPS LBBs in sections 08B and 09B currently have a metal plate over the cutout intended for the breaker when instead it should have a bubble-type enclosure installed on the front in order to lock up the breaker when in use. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199692&prj=660&rqi=e7sAlGazDcUP20lS0bTFqBWxol
GI-003 | NY11-P1 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C HMI: Unnecessary K5 switch is installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199689&prj=660&rqi=wNVonMoBY7oAQSXsxDeHKoTobp
GI-001 | NY11-P1 | AMER | Closed | P2 Medium CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C HMI: Key switches do not release in all positions like they should. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199687&prj=660&rqi=2A8WYq9Z0oKRzDDeKTbMTpCuEy
GI-005 | NY11-P1 | AMER | Closed | P2 Medium CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design correction needed | Design | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: Design of the glastic barrier behind the section 03A incoming cable entry prevents clean installation of the 13th cable that will be landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199691&prj=660&rqi=3EAUr3jiDOOizWZPZKNxpKJp0Y
GI-004 | NY11-P1 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: All voltage indicator lights on the board are white instead of amber. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199690&prj=660&rqi=jvfYhOcRPHn6THhR1vaqoobG9D
GI-052 | OS03-4 | APAC | Closed | P3 Low CX | milanshrestha@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT Electrical During the "System Star-up and Check" on Bus Duct Temperature Sensor, temperature was displayed as "zero" on the GX20(BMS) for BD29 to BD32 (highlighted in red color in figure) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352253&prj=519&rqi=YFZDnyD3aOURO9z8ByVsQ6IaYk
GI-050 | OS03-4 | APAC | Closed | P3 Low CX | milanshrestha@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | FAT Mechanical OS3-P1 CRAH/AHU Regarding the performance test, the actual average value is 173.4kW. Please explain why it is 173.4kW. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352251&prj=519&rqi=aHkyOTfg1LCJHJ7aY9aIeie3ku
GI-051 | OS03-4 | APAC | Closed | P3 Low CX | milanshrestha@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT Bus Duct Test Script (Page 14) Kinden said that the Bus Duct Temperature sensor path was changed (indicated by arrow and cross mark below). Please make the correction when submitting the Test Result. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352252&prj=519&rqi=dHI63OTWLXz9vjZNeyifWQCpSp
GI-049 | OS03-4 | APAC | Closed | P2 Medium CX | milanshrestha@commtechasia.com | 2026-01-27 04:00:00.000 +0400 | Commissioning Authority |  | General Contractor [GC] | Commissioning | [6 empty] | SAT OS3-P1 Primary UPS no. 5 (12F) : Mitsubishi Electrical - UPS - 2400kVA - 24-7MP4093 EF - Cx4 During the UPS functional performance test (load test), a fan temperature abnormality alarm occurred. This issue caused the UPS thermal load test to be terminated. Cause: The required blanking panel (divider plate) was not installed between the UPS module panel and the bypass panel. This blanking panel prevents the inflow of hot air from the module panel to the bypass panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197649&prj=519&rqi=mKqadTjZYdIo0EpRKzOxtP0VxY
GI-082 | OS05x-1 | APAC | Ready for Verification | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-11-05 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | HLT : - Mechanical - (PAC) [Daikin - PAC - FVYCP560MA - Cx4] [HLT Issue No.1]_Mechanical_(DH 3-1-2) During the 100% load test, the RA of PAC No. 40 in UPS Room 3-1-2 recorded a temperature of 30.1Â°C. The temporary data logger also recorded a temperature of 32.3Â°C. At that time, four PAC units were in operation, and the SA setpoint was 23Â°C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622086&prj=521&rqi=Ti3KhXumuhp03FVUkuVmdVzInx
GI-131 | OS05x-1 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-09-07 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | SAT: - Electrical - (Diesel Engine Generator) [CAT / BEMAC - Diesel Engine Generator / DEG Panels - 4875kVA - C175 - 20 - Cx4] On the third day of the UPS No. 9 test, when the power supply switched from the mains to the generator, alarms were triggered on the Fuel Tank No. 1, No. 2 and No. 4 transfer pumps. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637041&prj=521&rqi=ZSh8dpulubmFixGLds1Y3s5K83
GI-132 | OS05x-1 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | SAT : - Electrical - (UPS) [Mitsubishi - UPS - MELUPS 9800G - Cx4] During the 3rd day of the UPS No. 9 test, an overload test was conducted while the UPS was supplied by the generator. The test scenario required the UPS load to be increased to 110%. If the load remained at 110% for 10 minutes, the UPS was expected to transfer from inverter supply to internal bypass. The UPS successfully transferred to internal bypass as expected, and the operation was completed without any issues. However, when the load was subsequently reduced from 110% back to 100%, the UPS was expected to automatically transfer from internal bypass back to inverter supply. This transfer did not occur as expected, and the UPS remained on internal bypass. After the synchronization switch was turned off and the test was done, the UPS successfully transferred from internal bypass back to inverter supply without any issues. However, a failure alarm was triggered on the UPS during the transfer. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637042&prj=521&rqi=roZz8MmUck1sjh05GldP4rckhu
GI-122 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Electrical IST Day 2 Issue No.28] Building Elec IST Preparation: Before the start of the Building Elec IST Day 2, offline alarms were triggered in 2-3-DP-12-U4-2-1 and 1-3-DP-12-U5-2-1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630069&prj=521&rqi=gYYBSg0RN7SyBz8DqcjZQfyn33
GI-126 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Electrical IST Day 2 Preparation Issue No. 32] Regarding the BMS display for the fuel system, â€œLocalâ€ is shown in green and â€œRemoteâ€ in red, but it should be the other way around. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630214&prj=521&rqi=qTOxCbGqkeoqlkoFIuuuI1QSdi
GI-124 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Electrical IST Day 2 Issue No. 30] Building Elec IST Day2 Test No.8 After power was restored to Test-8 on Day 2 of the Building Elec IST, a minor fault for DEG No. 5 was reported on BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630071&prj=521&rqi=mxuP0AgTFG1wGPAcdY5BBpAdbx
GI-125 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | IST : - Electrical - (Diesel Engine Generator) [CAT / BEMAC - Diesel Engine Generator / DEG Panels - 4875kVA - C175 - 20 - Cx5] [Building Electrical IST Day 2 Issue No.31] Building Elec IST Day2 Test No.9 During the building power outage for Test-9 and the subsequent generator startup, major, middle and minor alarms were triggered on Generator No. 5, causing the equipment to shut down. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630072&prj=521&rqi=tE882xbf7YPFeVHBtlggiOb2T9
GI-127 | OS05x-1 | APAC | Open | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Electrical IST Preparation Issue No.33] Not completed the mapping of additional points and the point-to-point check for the BMS display related to generator fuel systems. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630274&prj=521&rqi=s633nFAKQiMTFcXnMF2n8sTCSZ
GI-123 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Electrical IST Day 2 Issue No.29] Building Elec IST Preparation: Since the power factor display on the BMS shows -100%, correct it to 100%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630070&prj=521&rqi=YaAu3HaW2McnFyqKN9jPz8ZWFc
GI-119 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-07-16 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | IST : - Mechanical - (PAC) [Daikin - PAC - FVYCP560MA - Cx5] [Building Mechanical IST Issue No.25 Day 2] High Temperature Alarm for UPS Room 3-2-1: High temperature alarm for UPS Room 3-2-1 was observed during the PLC failure tests. Upon inspection of the temporary data loggers: the max temperature around the modules was observed to be 34 and battery at 23.7â„ƒ (approx 12:30) Temporary data logger Max readings at approx. 16:45: - Module area: Max 36.9Â°C - Battery area: 25.9Â°C | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630066&prj=521&rqi=XT830yQtSkwfivThWqK3uS6aW6
GI-121 | OS05x-1 | APAC | Open | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-16 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Mechanical IST Day 2 Issue No.27] Update the Sequence of Operation (SoO) for the heat source area to the latest version and send it to the relevant parties. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630068&prj=521&rqi=qR6DFsdFvwqkK5Ttum3vJHC56I
GI-120 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-16 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Mechanical IST Day 2 Issue No.26] L2 No. 2 Riser Return Flow Rate Discrepancy: - BMS Display: Constant 4,436 L/min - BMS Trend Data: Fluctuating between 4,435 - 4,456 L/min - On-Site Meter: 0 L/min - Onsite current output measured at control panel: 0 mA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630067&prj=521&rqi=xjLnv2BVHSk8ZC7K9VwKMCntAu
GI-118 | OS05x-1 | APAC | Ready for Verification | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-07-16 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | IST : - Mechanical - (PAC) [Daikin - PAC - FVYCP560MA - Cx5] [Building Mechanical IST Issue No.24 Day 2] High Return Air Temperature alarm generated by the PAC unit that was in standby in UPS Room 3-2-1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630063&prj=521&rqi=WKnzOVGB3k5vBsCVgWlG3LfS39
GI-116 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Mechanical IST Preparation Day 1 Issue No. 22] IT Server Breaker Monitoring Clarification Required -> Clarification is required on why some breakers supplying power to IT servers are not monitored. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630061&prj=521&rqi=dOr89os2tjZwevvd2x0hQGHLlX
GI-114 | OS05x-1 | APAC | Open | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Mechanical IST Preparation Day 1] Supply Air Temperature Fluctuation During DH Load-Up -> During DH load-up, supply air high-temperature alarms were observed on the BMS for the Cool Array Units. Trend review indicated that the supply air temperature on the smaller coils (Top Left and Top Right) was fluctuating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630059&prj=521&rqi=kjYMiZFLto2ZAIrVx895QLdUmM
GI-117 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Mechanical IST Issue No.23 Day 1] During the A-to-B changeover, high-temperature alarms were observed on Risers 1 and 3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630062&prj=521&rqi=VdhM1rPW6ZGqohl17KGO42J3Be
GI-115 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | [Building Mechanical IST Preparation Issue No.21 Day 1] DH Load Adjusted to 2,400 kW Condition -> At the beginning of IST Day 1, the DH load was below 2,400 kW. After consultation with the vendors, the DH load was adjusted to approximately 2,404 kW for both data halls. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630060&prj=521&rqi=tGn40Y6hvf7vUQ5tDKPJWwXWI7
GI-113 | OS05x-1 | APAC | Ready for Verification | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | Mechanical IST Issue No.19 <Cool Array> DH 3-2-1 During the lunch break on the second day of IST, a communication error occurred in the BMS measurement display for 2-3-CRAH-12-2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628796&prj=521&rqi=KqxN3jxJOYl9K5sgyvlnOSLTsF
GI-112 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | Mechanical IST Issue No.18 <Chillers> DH 3-2-1 4-3-CH-12-8 & 4-3-CH-12-9, all compressors stooped due to low flow during test 12 [Simulate the failure of one Cool Array at a time in the Data Hall (fan stopped), record the temperature rise to above 35Â°C, and then restore the temperature to the SLA tolerance as soon as temperature rise to above 35Â°C] | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628795&prj=521&rqi=rlo3cdBrXwrMhwbrY3RQCN40H1
GI-111 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | Mechanical IST Issue No.17 <PAC> DH 3-2-1 Mechanical UPS PAC (2-3-FCU-12-PAC29) exhibited abnormal noise during the pre-IST inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628794&prj=521&rqi=GrRQzguNpVuAruDHUywH6abM9O
GI-110 | OS05x-1 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | IST : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx5] MECH IST Issue No.16 <Chiller> During the monthly inspection on 5 July, discolouration of the thermal labels was discovered on OS5x, PHF floor, units 4-3-MDSB-12-P402 and 4-3-MDSB-12-P411. (Discolouration at a maximum temperature of 80Â°C) It was also found that the circuit breakers for compressors on Chillers No. 2 and No. 11 had tripped due to overcurrent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628793&prj=521&rqi=F03vxdc2Kw3iZkDQxhB4tBAcGT
GI-109 | OS05x-1 | APAC | Ready for Verification | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-07-02 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <Chiller No. 5 & 10> DH 3-2-1 During the 100% load test of Chiller No. 10, Chiller No. 5, which was under exclusion, unexpectedly went offline and then automatically returned to an online status shortly afterward. A major alarm was generated on the BMS when the chiller went offline. Once communication was restored and the chiller returned online, the major alarm was automatically cleared from the BMS. The event was transient, and no further abnormalities were observed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628792&prj=521&rqi=P50HBdUukfjGJNbIAd45DLwFkp
GI-108 | OS05x-1 | APAC | Ready for Verification | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT: - Mechanical - (Cool Array) [Vertiv - Cool Array Unit - TW240 (5 coil) - Cx4] SAT L4 <FPT Issue No.22> Cool Array 3-2-1 During the ATS switching test (A â†’ B), all CRAHs went offline and then recovered. However, 2-3-CRAH-12-3, 2-3-CRAH-12-8, and 2-3-CRAH-12-9 tripped again (offline) before returning to normal operation. During the return switching (B â†’ A), 2-3-CRAH-12-1 went offline before restoring, while all other CRAHs transferred back to source A without interruption. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627200&prj=521&rqi=2J8hkfRSd7HMOs2pePqKvqnord
GI-103 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | IST : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx5] (DH - 3 - 2 - 2 Mech IST No.11, Day-2) During the Chiller Failure and Restoration Test, the chiller was restored successfully at the site and resumed normal operation locally. However, the chiller remained in an offline status on the BMS and did not return to its normal operating condition within the BMS interface. To restore proper communication and status indication on the BMS, Main breaker (é›»æºå…¥åˆ‡ã‚Š) was performed. Following the action, the chiller status was correctly reflected on the BMS, and normal operation was confirmed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626671&prj=521&rqi=5SATfww4zW91fKsa1Y3D3Wf2Eb
GI-102 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | IST : - Electrical - (STS) [Kokubu Electric - STS - 0304301 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0304401 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0304501 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0304601 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0304701 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0304801 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0303701 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0303801 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0303901 - 1150 kVA- Cx5] Mechanical IST Issue No.10, DH 3-2-2. During the site inspection, a high temperature(data logger) of approximately 32Â°C was observed in the STS room under 100% load conditions. A similar temperature trend was also confirmed in the BMS data for the HLT on 17 June. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626660&prj=521&rqi=9Clio01G4sacb6VPQ3z30UWRbR
GI-107 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design | [6 empty] | HLT/IST : - Mechanical - (Hot Aisle Capping) [Shinryo - HAC - N/A - - Cx4/Cx5] Lessons Learned (DH3-1-1) The SLA temperature exceeded 27Â°C during 100% HLT load. It is believed that a problem with the temporary HAC structure caused a short circuit of cold air, resulting in a rise in the cold aisle temperature. Since the upper limit specified in MSFT's SLA requirements is 35Â°C, the test continued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627199&prj=521&rqi=FDh6h7jzVXwIJENY2GqPOrq0Ps
GI-106 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | Commissioning Authority |  | General Contractor [GC] | Commissioning | [6 empty] | IST : - Mechanical - (Sensor) [N/A - Sensor - N/A - Cx5] (DH 3-1-1, DH3-1-2) Lessons Learned Since the cold aisle sensor is installed on the ceiling, move it to the correct position below the ceiling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627198&prj=521&rqi=jx28T23QhxAdDDur3DaLxfcfOf
GI-101 | OS05x-1 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | HLT: - Mechanical - (Cool Array) [Vertiv - Cool Array Unit - TW240 (5 coil) - Cx4] HLT Issue No.9 HLT DH 3-2-2 During the step load test, Supply High Temperature Alarm was triggered on the BMS for several CRAY units at 25% and 50% load. Upon investigation, was observed in the SA temperature for several CRAY units at DH3-2-2. For the 5-coil CRAY units, two different coil sizes exist, and the hunting was observed only in the smaller coils. The SA temperature for the larger coils was stable. The hunting was observed only at low load conditions (up to 50%). The SA temperature became stable from 75% load onwards. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626659&prj=521&rqi=WfCuSSjaJco6YIZMWTus99QbMg
GI-098 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Electrical - (UPS) [Mitsubishi - UPS - MELUPS 9800G - Cx4] SAT L4 [FPT Issue No.19] UPS No.4 DH -3-2-2 During the UPS-4 L4 line changeover test, a discrepancy was identified between the electrical current and power readings indicated by the UPS-4 metering system and the corresponding values supplied from the extra-high-voltage (EHV) source. The difference in measured values has been recorded and will be investigated further. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626651&prj=521&rqi=VFvMVZMHMXfb4ud5W35Op3kFd7
GI-097 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT: - Mechanical - (N2 gas sensor) [Nohmi Bosai - N2 Gas Sensor - 4083 (LGF, DH 3-LG-2) - Cx4] [Nohmi Bosai - N2 Gas Sensor - 4205 (LGF, DH 3-1-2) - Cx4] SAT L4 <FPT Issue No.18> DH 3-2-2 (2F) An alarm was generated on the BMS screen from the Nâ‚‚ Gas Detection Sensor 5093 associated with DH3-2-2. Upon investigation, it was confirmed that the alarm was caused by a faulty detector as there were not any reason for the sensor to activate. The defective sensor was subsequently replaced, restoring normal operation. The faulty sensor has been sent to the manufacturerâ€™s factory for detailed failure analysis. The investigation is expected to take approximately one month, after which the root cause of the failure will be reported. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624066&prj=521&rqi=rXS1S391X3iu41crNTGPZnLDHP
GI-096 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | SAT: - Mechanical - (Cool Array) [Vertiv - Cool Array Unit - TW240 (5 coil) - Cx4] SAT L4 <FPT Issue No.17> Cool Array 3-2-2_ The wall-mounted temperature sensor in DH3-2-2 indicated a temperature exceeding 35Â°C, reaching approximately 36.4Â°C, which is significantly higher than the expected operating range. Upon investigation, it was suspected that the cool air discharged from the Cool Array was unable to effectively reach the area where the wall-mounted sensor is installed. This condition is believed to have been caused by the replacement of the fan cover in accordance with Microsoft's specifications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624063&prj=521&rqi=goVJGnsJp7iildcrFvKVQt7IPr
GI-093 | OS05x-1 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | IST: - Electrical - (Diesel Engine Generator) [CAT / BEMAC - Diesel Engine Generator / DEG Panels - 4875kVA / C175 - 20 - Cx5] <Mech & Elec IST Issue No.8> BMS (3-1-1) A â€œMajor Control Power Failureâ€ alarm was observed in the BMS during a power outage (generator power supply). This alarm was triggered by a momentary loss of power to the fuel pump panel during the outage. A UPS for the fuel pump panel is scheduled for installation in August to prevent recurrence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624055&prj=521&rqi=xIH1NwOEbz6pqbmd4BirTiy7Sl
GI-089 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-15 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | SAT : - Mechanical - (PAC) [Daikin - PAC - FVYCP560MA - Cx4] SAT L4 <FPT Issue No.11> DH - 3-1-1 (DH3-1-1) During testing of Cool Array and STS L4, the temperature in UPS Room 3-1-1 rose under 100% load. The wall-mounted sensor recorded 38.6Â°C, and the PAC intake near the UPS module rack recorded 44.4Â°C. This is believed to be caused by exhaust from the UPS module blowing toward the PAC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624048&prj=521&rqi=WwfZ6UPAERDka3Ea32sI3RVq1c
GI-087 | OS05x-1 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | IST: - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx5] <Mech & Elec IST No.6> (Mech and Elec IST for DH 3-1-2) There are chillers on both the OS4x side and the OS2x side. When two units were operating on one side and a unit on the other side started up, chilled water (return) did not flow, causing the return temperature on the other side to rise. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622092&prj=521&rqi=fy5srMeuXq1H1KewmbBwTzJ5mD
GI-086 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | IST : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx5] <Mechanical and Electrical IST Issue No.5> (DH 3-1-2) It has been determined that the method for obtaining chiller status and the chiller skip logic do not comply with Equinix standards. ãƒ»Chiller status must be obtained via a hardwired connection from the chiller controller. ã€€Current situation: Chiller status is not obtained directly from the BMS; instead, a judgement is made based on the pump status. ãƒ»The chiller must be switched to the standby unit if it fails to meet both of the following conditions for a period of 5 minutes: >>Flow rate at the chiller flow meter is at or above the minimum required flow rate >>Chiller outlet temperature is 21.5Â°C (specification +1.5Â°C) or below | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622091&prj=521&rqi=cY5i36RGyjzK4PkV0NyCC39Kuc
GI-084 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | <HLT/IST No.3>_JCI_(DH 3-1-2) On the BMS screen while the generator is supplying power, the power transmission line remains green, should be red. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622089&prj=521&rqi=XkyiOxwKEZUulbKmNL0gVN5n18
GI-085 | OS05x-1 | APAC | Ready for Verification | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | IST : - Mechanical - (PAC) [Daikin - PAC - FVYCP560MA - Cx5] <IST No.4>_Nikken_Shinryo_(DH 3-1-2) While the system was under 100% load, a high-temperature alarm (60Â°C) was triggered in the UPS DH 3-1-2 bus duct. It was believed that the cause was a rise in temperature in the UPS room. At that time, the temperature on the front of the UPS module panel was recorded at 32.7Â°C. 4 PACs were operating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622090&prj=521&rqi=UAzaj8iajwgS9prddcDl1nqAVB
GI-088 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | IST: - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx5] <Mechanical and Electrical IST issue No.7> (DH 3-1-2) If a power outage occurs while the chiller is operating in tank charging mode, there is a risk that high-temperature chilled water will continue to be supplied to the Cool Array until the chiller restarts, in order to maintain tank charging mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622093&prj=521&rqi=wVLtMcBFft4N4V1EeanR2ElbJQ
GI-105 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Commissioning Authority |  | General Contractor [GC] | Commissioning | [6 empty] | (DH 3-1-1, DH3-1-2) Lessons Learned Incorrect Data Logger Installation Location/ ãƒ‡ãƒ¼ã‚¿ãƒ­ã‚¬ãƒ¼ã®è¨­ç½®å€‹æ‰€é–“é•ã„ The temperature data loggers supposed to be installed at the same location as SLA sensors are not equidistant. E.g. below pic, gap between two adjacent data logger locations is significantly different. Is this as per the Exhibit C section I shared before, or as per the OS4x SLA sensor locations. Please confirm that the data loggers are in same position as the SLA sensors. Pressure sensor locations are also different from aisle to aisle. Please confirm those as well. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627197&prj=521&rqi=YICKLULhoNhz6cQSb8UMGtef0R
GI-104 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Commissioning Authority |  | General Contractor [GC] | Commissioning | [6 empty] | (DH 3-1-1, DH3-1-2) Lessons Learned Issues regarding the installation of Temporary HAC / ä»®è¨­ã‚­ãƒ£ãƒƒãƒ”ãƒ³ã‚°ã®æ§‹ç¯‰é–“é•ã„ â€¢ The HACs are opened from front and back of the aisles, causing a short circuit between cold and hot aisles. This is different from what a DH with permanent HAC would look like and seems to be giving higher temperature reading. â€¢ It seems that to avoid reading too high temperature at the coil, they have put vinyl sheet blocking the airflow. This is basically manipulating the results and needs to be fixed. â€¢ The HAC installation quality is not very good and it seems to be coming off from many locations. Is it purposefully opened? If not, please ask GC for a proper installation. â€¢ The HAC start (in the CRAY side of DH) seems to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627196&prj=521&rqi=HXIcaMC5GK6pgXpt2j49VEM1B5
GI-083 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-11 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | HLT : - Mechanical - (Cool Array) [Vertiv - Cool Array Unit - TW240 (3 coil) - Cx4] <HLT No.2>_Nikken_Shinryo_DKSH_(DH 3-1-2) The Î”T setting for the Cool Array was changed from 12Â°C to 11Â°C, resulting in an increase in the design airflow rate for the Cool Array (66774CMH/unit >> 72000CMH/unit). During the L4 HLT, a temporary capping was installed and an airflow measurement was conducted at 100% load; the results showed that the airflow was insufficient relative to the total design airflow rate following the design change. At that time, the maximum fan speed for the Cool Array was set to 70%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622088&prj=521&rqi=uTq5UJ42bwVmFBIJu0rFobbAXW
GI-081 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.10> (Chiller) DH - 3 - 1 - 2 During Adjustment of flow rate fluctuation during chiller stage-up/down, minor alarm on Chiller No.6, compressor No. 2 was generated. Upon confirmation it was identified as Rotor Starting Torque Fault. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621055&prj=521&rqi=s8l4P5qvwUPaDRxSdZIP75nBJL
GI-079 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.8> [ Chiller] DH - 3 - 1 - 2 During Chiller failure test, 3 phase overcurrent alarm (Chiller No.9 Compressor No. 1) was generated when Chiller No. 9 started. Subsequent investigations revealed that approximately 200 seconds after the chiller started up (with a 120-second stage delay), the condenser fan speed dropped to 0%, causing the compressorâ€™s power consumption to rise and triggering a â€œ3-Phase Overcurrentâ€ alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620894&prj=521&rqi=dF9xpdhotuCpORT0wGB65cAgp0
GI-136 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.5> (Mechanical) Chiller DH 3-1-2 During Chiller failure test, 3 phase overcurrent alarm (Chiller No. 1Compressor No.1, 2 and 4) was generated when Chiller No. 1 started. Subsequent investigations revealed that approximately 200 seconds after the chiller started up (with a 120-second stage delay), the condenser fan speed dropped to 0%, causing the compressorâ€™s power consumption to rise and triggering a â€œ3-Phase Overcurrentâ€ alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620845&prj=521&rqi=oh6x5A6IUIrpXx0gNePszWOcit
GI-077 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.6> (Mechanical) Chiller 3-1-2 Before Chiller No. 6 failure test, all compressors stopped due to low flow protection. It was continued the test after the alarm was reset, but the issue was not observed again. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620847&prj=521&rqi=FdaAVV16HUfgSFwBp4NAB56AhR
GI-078 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.7> (Chiller) (DH - 3 - 1 - 2) When the connector between the chiller controller for the Chiller No. 6 and the UPS battery was disconnected, no major fault alarm was triggered. After that, only the pump continued to operate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620893&prj=521&rqi=XXz77JtUgT1HRfxGmxUU1hJiqZ
GI-080 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.9> [Chiller] (DH - 3 - 1 - 2) During Chiller failure test, a major alarm was generated on Chiller No.10, which was in operation.(temperature sensor fault) After resetting the alarm once, normal operations resumed. NTTF is currently investigating the cause. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620895&prj=521&rqi=qVm3vlimJsWtEUmkTDh3n8OKDl
GI-073 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-04-24 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.2> [Mechanical] <Chiller No.7> (3-1-2) During the pre-startup check for L4, a communication error was detected in condenser fan 10B (#20) of Chiller No. 7. This communication error did not occur during the L3 test. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619436&prj=521&rqi=Rrvif98HKNnGzpaUKkAOjJ9cx5
GI-074 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.3> (Mechanical - L4) (3-1-2) Chiller No.8, System - 1 Chiller No.9, System - 2 Chiller No.12, System - 1 During the pre-startup check for L4, the refrigerant liquid level sensor reading was showing 0% on the chiller screen. This communication error did not occur during the L3 test. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619437&prj=521&rqi=FeKlYFenJSKM0mrrpbMRd8FH2x
GI-072 | OS05x-1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  | equipment type |  |  |  |  | SAT : - Mechanical - (PAC) [Daikin - PAC Unit - FVYCP560MA - Cx4] During the L4 test of cool array , UPS Room 3-1-2 recorded a peak temperature of approximately 46.4Â°C at 100% load. It was confirmed that exhaust from the UPS module was blowing directly onto the temperature sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618787&prj=521&rqi=3HsX7VGj2SKwcTiJDyBOPu10GF
GI-070 | OS05x-1 | APAC | Closed | P3 Low CX | takahirowatanabe@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | A scratch was found on the condenser of Chiller No. 4-3-CH-12-13. Please carry out the necessary corrective action. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618234&prj=521&rqi=pfTyQ7REdHXr3p92Iku1OaICp0
GI-071 | OS05x-1 | APAC | Closed | P2 Medium CX | takahirowatanabe@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx3] Discoloration of servo labels inside the power distribution panel. ãƒ»The report revealed that the servo labels inside the panel had discolored (It is believed this occurred during the commissioning and adjustment phase) ãƒ»During the commissioning and adjustment phase of this project, when the CRAH was operated at 100% capacity, an incident occurred where the fans stopped (breaker tripped) for units equipped with AHF (LG, 1st floor). ãƒ»From April 8 to 10, we performed AHF readjustments on the 22 CRAH units in the north and south sections of the first floor. ã€€For the CRAH units in the south section of the first floor, we operated the CRAH at 100% capacity overnight with the AHF turned on, ã€€and upon measuring the temperature, confirmed it was approximately 45Â°C. (We will continue to perform these adjustment tasks.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618236&prj=521&rqi=EA9jLHJ9nYahupfV49NLku08Bw
GI-068 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT <General> There were electrical equipment that are not included in the Tag tracker which was previously confirmed by Vendor. Such as Panel (LG-3-MDSB-12-PCP-1, LG-3-MDSB-12-PCP-2). We advice to Kinden again to verify the Tag Tracker if any equipment are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197430&prj=521&rqi=BmXXGwl0b5vxtoXRiReAnRnD0t
GI-066 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT <Generator> The generator panel Tag seal has not been signed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197428&prj=521&rqi=DR0aKl3wk8O54UhxhnOdiyQk30
GI-065 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT <DEG Indoor Panel> The actual nameplate of the DEG (indoor) panels were different from the entries in the Tag Tracker, as confirmed by Kinden. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197427&prj=521&rqi=mzwqQOlAQeZSmC6EDQ1n4LyBLV
GI-069 | OS05x-1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT <General> There are lot of equipment which are not yet finished (example : cable installation) but the vender declared L2A completed on the Tag Tracker. (UPS, STS, etc) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197433&prj=521&rqi=6wf3waqF0qmvriF9GLAoIl3sVx
GI-059 | OS4x-F1 | APAC | Closed | P3 Low CX | takahirowatanabe@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | Fire IST DH 2-2-2 During N2 exhaust fan (4-2-EF-12-N2-4) startup, local operation of MD1-N2-4 was confirmed, but display operation on the BMS could not be verified. Subsequently, it was confirmed that the point for the subject MD was not being acquired by the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483407&prj=512&rqi=ZXgTVOP7Iv1hTa4Rk97IboOlTR
GI-052 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 5.) <IST> <DH 2-2-1> <Mechanical> 2026/02/05_ In IST Test-14 (Chiller Failure), the chiller was simulated to fail by disconnecting the connector between the chiller controller and the UPS battery. The chiller was restored according to the procedure written in the script, but the unit on-site and display on the BMS did not return to normal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199318&prj=512&rqi=jAwyipmyKueIIAjXSyFp8EW1D2
GI-039 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 3.) <HLT><DH2-2-1><Mechanical> 2026/02/03_ During the HLT and IST, the following unexpected alarms were raised: Although a manual reset temporarily restored the system, the same fault occured multiple times. DH2-2-1 HLT (Issue no. 39) During HLT Test 5 (100% step load test), a minor alarm (Motor Single Phase Overcurrent) was generated on Chiller No. 8. COMP3. DH2-2-2 HLT (Issue no. 44) 13:29 CH5 COMP4 Motor Single Phase Overcurrent Fault [During Test 5 (100% Load) ] 15:37 CH5 COMP4 Motor Single Phase Overcurrent Fault [During Test 5 (100% Load) ] DH2-2-1 IST (Issue no. 51) During test 12 minor alaram (Motor Single Phase Overcurrent Faul.) on chillor No. 7 COMP2 was generated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199302&prj=512&rqi=5EGTkD6TtCrhoRmt51EFygZIqx
GI-037 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 1.) <HLT> <DH 2-2-1> <BMS> 2026/02/03_ The hot aisle containment was not drawn correctly in the BMS, so this needs to be corrected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199300&prj=512&rqi=PySSJJzyLn72evJmUNvR3KUB8F
GI-047 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 11.) <HLT> <DH 2-2-2> <General> 2026/02/10_ There is hole found in the SLA sensor bracket. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199311&prj=512&rqi=0cnLaOlJMfUl6jXG8bLTetlpQT
GI-046 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 10.) <HLT> <DH 2-2-2> <Mechanical> During the HLT and IST, the following unexpected alarms were raised: DH2-2-2 HLT 13:49 CH6 COMP4 Bearing Fault [During Test 5 (100% Load) ] 17:28 CH6 COMP4 Bearing Fault [During Test 6B (Cool array power supply switching test) ] DH2-2-1 IST CH6 COMP4 Bearing Fault [During Test 13 (Cool Array communication failure ) ] | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199310&prj=512&rqi=W2A2RGd12ZcB1rha61TSijdo2a
GI-057 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 10.) <IST> <DH 2-2-2> <Electrical> 2026/02/13_ During IST Test-15 (utility power failure/ restore), An insulation caution alarm was triggered at 2-SS2-TRB1. Since the affected system is an air conditioning outdoor unit, the test continued while investigating the cause. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199324&prj=512&rqi=rCKebDrm36ricZOoEWHpa2JGUC
GI-055 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 8.) <IST> < DH 2-2-2> <Mechanical> 2026/02/12_ In Test-9 (Cool Array Coil Failure), after disconnecting Valve-5 of 2-2-CRAH-12-19, Valve-3 became offline. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199322&prj=512&rqi=hdGPBB0ZAr6dJEjjqdRo7So0ir
GI-048 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 1.) <IST> <DH 2-2-1> <Electrical> 2026/02/05_ During the simulation of failure of three modules on UPS No. 1, the specification states that the system should transfer to internal bypass after one minute. However, during the actual test, the power transferred to bypass immediately. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199312&prj=512&rqi=Pq1IuhGZSa9kD2QENmtRNoKy59
GI-053 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 6.) <IST> <DH 2-2-1> <Electrical> 2026/02/05_ In IST Test-18 (STS MCDT automatic switching), the control panel of the simulated load banks was connected under a DP panel that did not have a switching function, so if the target breaker on the UPS output panel was opened, the load banks would lose power and the device could have failed. Therefore, the UPS output breakers other than the one on the load banks control panel were opened and the test continued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199319&prj=512&rqi=BQTijtVwHhxbwg8uM6IvH9Ibj0
GI-041 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 5.) <HLT> <DH 2-2-1> <Mechanical> 2026/02/03_ During the HLT test, MSFT pointed out that the CRAY ATS enable/disable and selected priority might be required to be displayed on the BMS screen. The same are not displayed in T1. MSFT will confirm internally and revert back on this requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199305&prj=512&rqi=qZ13MRWOzrIRhdLlgifzowjZTS
GI-049 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 2.) <IST> <DH 2-2-1> <Mechanical> 2026/02/04_ IST Test 9 â€“ Simulated Failure and Recovery of One Representative Cool Array Unit (Coil Failure to N) (Confirmation of Operation without Redundancy): After the communication cables for the CRAY fan and valve were disconnected, the cables were reconnected as part of a recovery operation, but the BMS and the site did not return to normal operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199315&prj=512&rqi=tHFh56Y32z0uOp3qh6bjxFQuVq
GI-038 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 2.) <HLT><DH 2-2-1> <MECHANICAL> 2026/02/03_ During HLT Test-4 (75% Load), an unexpected alarm was triggered due to a condenser fan communication error while chiller unit 10 was operating, and a minor alarm was reported by the central monitoring system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199301&prj=512&rqi=LGFhoQ01RBAef6ZCT75OhHOc44
GI-045 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 9.) <HLT> <DH 2-2-2> <Mechanical> 2026/02/10_ DH2-2-2 HLT During the HLT, the following unexpected alarms were raised: 13:21 CH6 COMP1 Rotor Starting Torque Fault [During Test 5 (100% Load) ] 13:49 CH6 COMP1 Rotor Starting Torque Fault [During Test 5 (100% Load) ] Although a manual reset temporarily restored the system, the same fault occured twice in the same compressor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199309&prj=512&rqi=qbVWLD2hFdubeOnDsEaAjKWVMa
GI-054 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 7.) <IST> <DH> <Fire> 2026/02/05_ As there were no changes to the automatic fire alarm system or gas fire extinguishing system in this project, the test script agreed upon in advance did not include a Fire IST. On the day of the IST, MSFT requested that the test be carried out, and it was adjusted the schedule. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199320&prj=512&rqi=vJSpNg6XyzHR9XIG40Nnpv6tcd
GI-040 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 4.) <HLT> <DH2-2-1> <Mechanical> 2026/02/03_ HLT Test 6B â€“ Cool Array Power Supply Switching Test (Common UPS to AC UPS): In the test script, the ATS switching time to be changed from 25 minutes to 5 minutes in order to shorten the test time, but the CRAH-1 ATS switched after 25 minutes instead of 5 minutes | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199303&prj=512&rqi=RLENVE7sRtdx2Q0S274prLX4FA
GI-050 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 3.) <IST> <DH 2-2-1> <Mechanical> 2026/02/05_ During test No.13 in chiller No. 6, bearing fault alarm was generated. ã€Motor Single Phase Overcurrent Faultã€‘ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199316&prj=512&rqi=cMTrU4h6RjMONS93ymlGd2wIML
GI-044 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 8.) <HLT> <DH 2-2-2> <Mechanical> 2026/02/10_ 13:29 CH5 COMP4 Motor Single Phase Overcurrent Fault [During Test 5 (100% Load) ] 15:37 CH5 COMP4 Motor Single Phase Overcurrent Fault [During Test 5 (100% Load) ] | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199308&prj=512&rqi=Lvh1mUrYB7oWLfgC6or0CUIUFz
GI-056 | OS4x-F1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning | [6 empty] | IST : - Electrical - (Diesel Engine Generator) [CAT / BEMAC - Diesel Engine Generator / DEG Panels - 4875kVA / C175 - 20 - Cx5] 9.) <IST> <DH 2-2-2> <Electrical> 2026/02/13_ During Test-15 (A, B-line utility power failure), an alarm was triggered on the BMS after starting Generator No. 7. Power supply were performed without issue. ãƒ»Auxiliary equipment failure batch alarm ãƒ»Charger 2 failure alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199323&prj=512&rqi=MBs9u27NEeSFwKUbd7piDYWBVL
GI-058 | OS4x-F1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | General Contractor [GC] | Commissioning |  | equipment type |  |  |  |  | IST : - Electrical - (STS) [Kokubu Electric - STS - 0300101 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300201 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300301 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300401 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300501 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300601 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300701 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300801 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300901 - 1150 kVA- Cx5] 11.) <IST> <DH 2-2-2> <BMS> 2026/02/13_ During Test-19 (STS MCDT Switching), The signal wire used to transmit status information to the BMS was found to be disconnected. As a result, the â€œPower ONâ€ indication was not displayed in the operational section of the STS status screen on the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199325&prj=512&rqi=OxpgW8GCNVCGutYd4seWMq2jAl
GI-051 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 4.) <IST> <DH 2-2-1> <Mechanical> 20206/02/05_ During test 12 minor alarm (Heat source unit alarm.) on chiller no. 7 was generated. ã€Motor Single Phase Overcurrent Faultã€‘ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199317&prj=512&rqi=SOLz9zaRtY8n38ja7OW5Z8xbTg
GI-042 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 6.) <HLT> <DH 2-2-1> <Ductwork> 2026/02/03_ After HLT Test-5 (100% load) test, the wall-mounted temperature sensor in UPS room 2-2-1 recorded 29Â°C. Check the design temperature and the recommended environment for the UPS unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199306&prj=512&rqi=bbwgSpkhhzUwVvVszhbAb5VCs2
GI-043 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | 7.) <HLT> <DH 2-2-2> <Mechanical> During the HLT, the following unexpected alarms were raised: DH2-2-2 HLT 12:50 CH5 COMP4 Inverter Temperature Fault [During Test 5 (100% Load) ] 16:44 CH5 COMP4 Inverter Temperature Fault [During Test 5 (100% Load) ] 17:27 CH5 COMP4 Inverter Temperature Fault [During Test 6B (Cool array power supply switching test) ] Although a manual reset temporarily restored the system, the same fault occured three times in the same compressor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199307&prj=512&rqi=KN6qGhu0nGEbK1PjIwO1q13yoc
GI-035 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-26 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | <SAT Mechanical> Water Leakage Sensor, OS4x-F1(T2) The water leak detector sensor in the PAC location was found with a loose cable. Verify that all sensor cables are properly secured before conducting the IST. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197564&prj=512&rqi=K7hDyFHAIHVnyhpZ1KtYbMWhZo
GI-036 | OS4x-F1 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-26 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | <SAT Mechanical> Cool Array, OS4x-F1(T2) The vendor is required to provide the technical specifications for the Cool Array temperature sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197565&prj=512&rqi=bkFBMxJqQ54TM0igEsmHXv3AGo
GI-034 | OS4x-F1 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-01-26 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  | equipment type |  |  |  |  | SAT : - Electrical - (UPS) [Mitsubishi - UPS - MELUPS 9800G - Cx4] <SAT, Electrical> DP Panel, OS4x-F1(T2) During the load test of the DP panel, the UPS triggered an overload alarm and switched to bypass operation. Since the test was conducted at 96% load (2300 kW), investigate the cause of the overload alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197562&prj=512&rqi=Kf7vwGrDrTJFq8VOAzGF4Mb9H2
DCIML3-1-002 | PA10-P1 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS Template Issue | DCOS | Integrated Automation | system | DCIM |  |  |  | UPS Resiliency Calculation must be update to integrate UPSs of Block A Generator Resiliency Calculation must be update to integrate Gen Block A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614833&prj=613&rqi=G3VoaMS0uSWEgbXzjrk56nVL0x | https://equinix.facilitygrid.co.uk/x/project/613/system/12280
DCIML3-1-001 | PA10-P1 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS Template Issue | DCOS | Integrated Automation | system | DCIM |  |  |  | List of assets cannot be upsert on DCIM, sync issue 1_GEN_A 1_GEN_A_DT 1_CWST_01_FCV03 1_MVTB_A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614807&prj=613&rqi=3VeoUXoAnUqeEsxqUYrtACM8iE | https://equinix.facilitygrid.co.uk/x/project/613/system/12280
BT1DCOS-1-001 | PA10-P1 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCIM Cooling Zone Issue | DCIM | Integrated Automation | system | DCIM |  |  |  | Location Vector missing for Mech assets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614797&prj=613&rqi=n9uKh3v2uH6PUUCpj8w0FTBzXp | https://equinix.facilitygrid.co.uk/x/project/613/system/12280
DCIML2B-1-001 | PA10-P1 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS | L2B | DCIM Maximo Issue | DCIM | Integrated Automation | system | DCIM |  |  |  | Maximo ID asset missing for all PA10.P1 assets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614798&prj=613&rqi=Pu2o6pQDXs4O7UPLf2blq4MaCL | https://equinix.facilitygrid.co.uk/x/project/613/system/12280
DCIML4-2-001 | PA10-P1 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCIM Cooling Zone Issue | DCIM | Integrated Automation | system | DCIM |  |  |  | Zone informations (Location Vector) missing for all assets concerned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614809&prj=613&rqi=FJHhpRl8eUtEEr4vOWuwr08smS | https://equinix.facilitygrid.co.uk/x/project/613/system/12280
GI-010 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-02-26 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1-CRAH-M1-043 | CRAH - Computer Room Air Handler (CHW) |  |  | During L4 redundancy testing of the CRAH, The Kopex condensate drain pipe of the CRAH became loose as fans were rotating and became lodged. This caused an audible noise and CRAH was disabled to investigate and test was paused. After investigation was carried out by VERTIV representative, it was agreed the CRAH was not visually damaged and to continue the redundancy test to completion. Replacement of damaged pipe plus any further inspection may be required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352274&prj=613&rqi=GITRHIRXx28mPFBDKss1T4hnBE
GI-009 | PA10-P1 | N-EMEA | Closed | P2 Medium CX | paulm@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | Direct Expansion â€“ DX | equipment | 1-FCU-R1-01 | DXID - FCU/DX Indoor Unit |  |  | Asset name is incorrect. DCOS naming indicates 1-FCU-R1-30 Clarification is urgently required as RT, YT, Test reports and Facility Grid will require amending to the correct asset name. Formal proof of correct name required to close issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198245&prj=613&rqi=SjoymGxQLj2EVQINY9gEL52FqY
SOR-10-001 | PA10-P1 | N-EMEA | Closed | P2 Medium CX | andrewa@straightlineconsulting.co.uk | 2026-01-30 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Racking out system of the G2 Breaker is faulty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198014&prj=613&rqi=8azH69175uLCUmK1pTZYkaE76K
GT1ELEC-2-001 | PA10-P1 | N-EMEA | Closed | P2 Medium DCOS | mirceag@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS Graphics Issue | DCOS | Electrical â€“ MV | equipment | 1-MVTB-A | MVTB - Medium Voltage Transfer Board |  |  | 1-MVTB-A Point to graphic issue As shown in the attached screenshots, the status displayed does not match the graphical status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197719&prj=613&rqi=ganrVIU3PXA6DdXjFI0XiD6M6h
SOR-6-002 | PA10-P1 | N-EMEA | Closed | P3 Low CX | mirceag@straightlineconsulting.co.uk | 2026-01-23 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | Electrical â€“ LV | equipment | 1-GEN-A | GENL - Generator (LV) |  |  | 1-GEN-A FUEL SYSTEM CONTROL PANEL CPA10c During the visit of the CPA10c control panel i found the new cables installed are not labelled and some existing cables but not connected to any terminal .(currently loose) , they should be at minimum isolated and terminated into WAGO | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197505&prj=613&rqi=Yk20E4lRh9s5ddBFovnUXTXui2
YT1ELEC-2-001 | PA10-P1 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-01-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Electrical â€“ MV | equipment | 1-MVTB-A | MVTB - Medium Voltage Transfer Board |  |  | Arc Flash Labels are not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197506&prj=613&rqi=stwaUiCrEmIJsq8MVYVKMyXrAQ
YT1ELEC-53-001 | PA10-P1 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-01-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1-MLTX-A | MLTX - Transformer (MV-LV) |  |  | Arc Flash Labels are not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197504&prj=613&rqi=8tXmhrmbyQQbUYQtIRlHofwlhU
RT1ELEC-22-002 | PA10-P1 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | CMM - Cummins | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1-DP-A-3 | DB - Distribution Boards |  |  | The label for Q7/10A the labels shows Q7/2A . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196767&prj=613&rqi=WnS8eH42x3UVlDJK3MutYoZtde
RT1ELEC-22-001 | PA10-P1 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | CMM - Cummins | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1-DP-A-3 | DB - Distribution Boards |  |  | Permanent equipment labels affixed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196763&prj=613&rqi=Vz0lfOaZrFdFUEpeZufOskICu4
YT1MECH-26-001 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Documentation not issued/ Required | Commissioning | Direct Expansion â€“ DX | equipment | 1-FCU-R1-01 | DXID - FCU/DX Indoor Unit |  |  | Missing Installation and Start-up Manual for DX | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196708&prj=613&rqi=Eiu4Ug641newIwmy9xU4Lh05Ik
YT1MECH-27-003 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Installation not complete | Commissioning | Direct Expansion â€“ DX | equipment | 1-CU-R1-30 | CU - Condensing unit |  |  | Drainage Lines are not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196710&prj=613&rqi=lXj4jlQn4ZHUFXairseHo7T5Wt
YT1MECH-27-004 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Documentation not issued/ Required | Commissioning | Direct Expansion â€“ DX | equipment | 1-CU-R1-30 | CU - Condensing unit |  |  | Vendor L3 Start Up Method Statement not available on Project Portal | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196711&prj=613&rqi=L30emvvmsmoEIi1Zc06jpDrHif
GI-008 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-08 04:00:00.000 +0400 | Electrical Engineer |  | Documentation not issued/ Required | Commissioning | [6 empty] | DX Sequence of operation - PA101-BYE-ZZ-ZZ-TS-M-ZZZZ-0053 Below EQX comments to be updated to SOO and new revision uploaded to ASITE. Part 6 - How are PPR/PCR room low temperatures managed? Part 7.1 - Temperature setpoint adjustment is via DCOS only. How are wall mounted thermostat adjustments restricted to users? Part 7.1 - Battery room conditions are quoted as 22*C +/- 2*C which implies heating-not described here. Clarify including how units are configured to ensure they do not fight each other Part 7.2 - What are major / minor faults? Part 8.1 - Temperature setpoint noted as 22*C-does not cover PCR/PPR rooms Part 8.1 - Does not detail how thermostat is locked against future user adjustment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196595&prj=613&rqi=PkpIOsIgPMrpFZ4Ev7StIwG9Xg
YT1MECH-31-001 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Commissioning Issue | Commissioning | Mechanical â€“ Water | equipment | 1-CWST-01-CWP-M1-03 | CWP - Condenser Water Pump |  |  | Correct source / destination cable required to indicate where equipment fed from. Issue applies to 6no. pumps in PPR room. Photo required of all labels to close issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196503&prj=613&rqi=J7ROwi9DRdZJQKg86q32YUBpAn
YT1MECH-29-001 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Direct Expansion â€“ DX | equipment | 1-CU-M1-30 | CU - Condensing unit |  |  | No drainage lines are installed on unit for condensation. Unit installed inside electrical room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196382&prj=613&rqi=diSISuzNnefmEwFxv52xP8nVMy
YT1MECH-27-002 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning | Direct Expansion â€“ DX | equipment | 1-CU-R1-30 | CU - Condensing unit |  |  | No drainage Lines are installed on unit for condensation. Unit installed inside electrical room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196383&prj=613&rqi=n4ZfZ85b6uyKNtIjpxS8rp8AZ3
YT1MECH-29-002 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning | Direct Expansion â€“ DX | equipment | 1-CU-M1-30 | CU - Condensing unit |  |  | Power Source / Destination cable label missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196384&prj=613&rqi=6ofy92r74ORKx7IJ5hp3ipeISP
GT1MECH-51-002 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-05 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Commissioning Issue | Commissioning | Mechanical â€“Air | equipment | 1-CRAH-M1-043 | CRAH - Computer Room Air Handler (CHW) |  |  | When CHW inlet supply is isolated, high supply temperature alarm is raised at the DCOS but CRAH HMI shows no indication | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196347&prj=613&rqi=e4wQEOUsHWMtkNqR8ROxOvpHDx
GT1MECH-51-001 | PA10-P1 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-05 04:00:00.000 +0400 | Electrical Engineer | L3 | DCOS General Issue | DCOS | Mechanical â€“Air | equipment | 1-CRAH-M1-043 | CRAH - Computer Room Air Handler (CHW) |  |  | When simulating return air temperature / humidity sensor fail, the alarm appears on the CRAH HMI as normal. There is no indication on DCOS of sensor failure or appears in issue log. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196340&prj=613&rqi=XdM9id3meNZc7W5OFbRbIf3CKE
GI-012 | PA10-P2 | N-EMEA | Closed | P2 Medium DCOS | andrewa@straightlineconsulting.co.uk | 2026-07-23 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning | [6 empty] | Temperarture sensor not installed on a section of the Redundant Busbar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630651&prj=661&rqi=1AoE0I66fKrp6uvwDN2avuQsRS
GI-011 | PA10-P2 | N-EMEA | Closed | P3 Low CX | magatte.sene@eu.equinix.com | 2026-07-16 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | [6 empty] | The Transformer door cannot be opened from the inside. it's imperative to resolve the issue to ensure the safety of personnel working inside the transformer enclosure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629805&prj=661&rqi=cf3jGT5w76e5suV1EEFZcxBsDA
GI-008 | PA10-P2 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-06-29 04:00:00.000 +0400 | Electrical Engineer |  | General Design Issue | Design | [6 empty] | Concern has been raised regarding gaps in the false floor around some equipment in UPS. This may affect room cooling when carrying out redundancy testing of the CRAHS during full load testing of electrical equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627321&prj=661&rqi=Ckx9smNEf7K0kgorwSHvQI77Mm
GI-005 | PA10-P2 | N-EMEA | Closed | P1 High DCOS | andrewa@straightlineconsulting.co.uk | 2026-05-06 04:00:00.000 +0400 | General Contractor - Electrical |  | DCOS Comms Issue/ Fault | DCOS | [6 empty] | IP Address and VLAN not configured like describe on the SE document DCOS IP Address Schedule. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620645&prj=661&rqi=KX7G63Q7ysWda9z7hJluiKmg3O
YT1FD-4-001 | PA10-P2 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Documentation not issued/ Required | Commissioning | Fire Detection | equipment | 1-MSD-21 | MSFD - Motorised Smoke Fire Damper |  | VU12 | Static Cable Tests and Inspection Reports (power) documentation not available | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619093&prj=661&rqi=dWodRtYFkqppZshHj1ZqtsIhyk
YT1FD-4-002 | PA10-P2 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Fire Detection | equipment | 1-MSD-21 | MSFD - Motorised Smoke Fire Damper |  | VU12 | Cable labels not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619094&prj=661&rqi=VEUb3f9c0XhlZTZjCoWtjgT0HR
GI-003 | PA10-P2 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-04-22 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | There is an HMI operational issue on SUDB-2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619211&prj=661&rqi=TSy92JQ72zOaInoav3CsR0LgM0
GI-004 | PA10-P2 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-04-22 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | MV Scada issues on SUDB-2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619212&prj=661&rqi=Ux8RLxV09ntMjmKzunBC9VEMvA
GI-002 | PA10-P2 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-04-16 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | There is a issue with the Power factor on the MVTB-E. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618490&prj=661&rqi=W8nZB7dstW3KxdKF8aGVBYn90p
YT1FS-9-001 | PA10-P2 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Fire Suppression | equipment | 1-MFD-155 | FD - Fire Damper |  | CR60-1S VIM | Both cable labels not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617669&prj=661&rqi=uqFe1GkOl6K1jGpFfqhGpVyzLk
YT1FS-4-001 | PA10-P2 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Fire Suppression | equipment | 1-MFD-152 | FD - Fire Damper |  | CR60-1S VIM | Both cable labels missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617653&prj=661&rqi=rNkTJ4VP1U4R9SYGovujSIW3RZ
YT1FS-6-001 | PA10-P2 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Fire Suppression | equipment | 1-MFD-39 | FD - Fire Damper |  | CR60-1S VIM | Both cable labels not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617668&prj=661&rqi=9KE7HW06e8jjPStHrxhZEx8BDZ
YT1FS-3-001 | PA10-P2 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning | Fire Suppression | equipment | 1-MFD-151 | FD - Fire Damper |  | CR60-1S VIM | Both cable labels not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617667&prj=661&rqi=27sScvWVmbcw9IcuVZxS2ucngK
YT1ELEC-74-001 | PA10-P2 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-03-24 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Documentation not issued/ Required | Commissioning | HVAC | equipment | 1-HT-M2-01-1 | TRACE - Trace Heating |  | Eltrace | L3 Green Tag Cx method statement not available on Asite. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616345&prj=661&rqi=AJ0WR3xGU5L0mpIavJGGx8R9dt
RT1ELEC-80-001 | PA10-P2 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-02-26 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1-UMDSB-M1-2-11 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | Permanent equipment labels affixed and are as per approved colour scheme. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483354&prj=661&rqi=6w0v9VVKmKVU59tNlCDfmL5cJi
GI-664 | PA12x-1 | N-EMEA | Open | P3 Low DCOS | aarond@straightlineconsulting.co.uk | 2026-09-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Schneider is required to revise the schematics to show the Max Cool activation contact as Normally Open (NO), as specified in the approved SOO. The current schematics incorrectly show the contact as Normally Closed (NC). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637586&prj=263&rqi=zQcemILwRNhbFnbwv46TqLgfBi
GI-661 | PA12x-1 | N-EMEA | Closed | P3 Low DCOS | aarond@straightlineconsulting.co.uk | 2026-09-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS | [6 empty] | MOT - MECHANICAL - CRAYS The Enable Setpoint Shift function changes the supply temperature setpoint from 25Â°C to 24Â°C when the coil supply temperature remains 5Â°C above setpoint and the valve position is greater than 80% for more than 60 seconds. The setpoint shift is visible on the Vertiv controller but is not displayed on DCOS. DCOS/Vertiv to investigate and confirm that the active shifted setpoint is correctly communicated and displayed on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637433&prj=263&rqi=01FyKJKBEsIj4fWH5kwSvfseZP
GI-662 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-09-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Mechanical - Max cool system - in event of loss of power to Max cool panel both supplies, SOO Max cool indicates it max cool should be operated but wiring of the panel & schematics do not. schneider to confirm to if max cool should operate under full power loss | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637431&prj=263&rqi=FiBQ2Jb2U6hY5H4keCC4SbPCmX
GI-656 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-09-03 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Mechanical - Max cool sensors / DCOS gateway sensors - multiple TT sensors are mixed up & wrongly labelled between Max cool system & DCOS GW TT Sensors, All Data halls to be checked 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636671&prj=263&rqi=6v8Iz5UCNOV8h1PwpXw8S9M3AP
GI-655 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | MOT â€“ CRAYs DH03 Prior to testing the fanwalls, it was observed that multiple sensors were not reporting to DCOS. This issue was first noted following completion of the permanent fanwall shielding rectification, which replaced the temporary fix. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636536&prj=263&rqi=J0ptaFpIukSxLWRjwLL1KvaV5s
GI-622 | PA12x-1 | N-EMEA | Open | P3 Low CX | gabrielsokolowsky@sygna-emea.com | 2026-08-21 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Commissioning Issue | Commissioning | [6 empty] | 1MSB_R1-Q28 : The micrologic menu cannot be accessed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634590&prj=263&rqi=SUnQMfZLbjEDG80tiDzrqSw3Vn
GI-623 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gabrielsokolowsky@sygna-emea.com | 2026-08-21 04:00:00.000 +0400 | General Contractor |  | Cleaning | Commissioning | [6 empty] | Pigeon nest on busbar, phase 1, third floor, above emergency stairs door, MeWall M3 corridor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634595&prj=263&rqi=mGVTIvtlXkyTwVp6GqqAVhV8Lv
GI-620 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | jayb@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning | [6 empty] | IST2 - GEN C showing comm alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634230&prj=263&rqi=j6bbGkox8UKwcAB8RwRbGTTiX1
IST-23-004 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | General Contractor - Commissioning | L5 | General Design issue | Design |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | IST 2 - Fire alarm - Thermal detectors in all Gen rooms to be replaced by Smoke detector. during IST 2x thermal detectors activated due to heat from Gen B+C. All thermal detectors are currently isolated via Graphic operating PC for SSI system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634213&prj=263&rqi=GJT4KakU1ipYUNnV4chrNEVA6C
IST-31-001 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | jayb@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | General Contractor - Commissioning | L5 | Installation Not Correct | Commissioning |  | equipment | IST Phase 1.2/1.3 - Test 7.0 Failure of Mechanical Block M2 and IT Block B | integrated systems testing halls 3,4,5 and 6 |  |  | IST 2 - MLTX B core temps showing high core temp on L3 when all other MLTX show higher core temp on L2, suspected incorrect sensor termination in MARS panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634221&prj=263&rqi=MJ0OOfY6vwBYtNxP0KEIYpy5vD
GI-619 | PA12x-1 | N-EMEA | Open | P3 Low DCOS | jayb@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | REH - Rehlko Gens |  | Component/Equipment Failure | Commissioning | [6 empty] | IST 2 - GEN SCR F,B,M1 and M3 - Power line/ gen graphics showing live on DCOS intermittently even though gens not running. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634229&prj=263&rqi=jimDZeWMnuOBpKhAZILf2uaGlt
GI-621 | PA12x-1 | N-EMEA | Open | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | General Contractor - Electrical |  | DCOS Comms Issue/Fault | DCOS |  | equipment | IST Phase 1.2/1.3 - Test 3.0 Dead Bus Test on String F | integrated systems testing halls 3,4,5 and 6 |  |  | IST 2 - Mechanical - The leak detection alarm for Cable_3_02 was triggered during the test and appeared in the alarm log; however, it was not displayed on the graphics. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634232&prj=263&rqi=n7JnOtW1VBIeE9FZtSaO7TgmEl
IST-23-003 | PA12x-1 | N-EMEA | Open | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | REH - Rehlko Gens | L5 | Installation Not Correct | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | IST 2 - Generator - Fire curtains on ground floor rooms B+C failed to close correctly. during IST activation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634211&prj=263&rqi=mcp7OJXZQhcC2E7OIObrbCPVm2
IST-24-014 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-08-17 04:00:00.000 +0400 | General Contractor - Commissioning | L5 | Documentation Not issued/ Required | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Block R2. All testing documentation to be submitted for Vesda and Smoke Detection ZDA213 ZDA205 ZDA207 ZDA212 ZDA090 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633938&prj=263&rqi=aBLIsOvyyvw31nDOnCrWPnEbaV
GI-618 | PA12x-1 | N-EMEA | Open | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-17 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning |  | equipment type |  |  |  |  | Fire Alarm - SSI Graphic PC not yet tested for Phase 1 system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633936&prj=263&rqi=5UNzTHIxJTzdiItDiko0twTli1
GI-613 | PA12x-1 | N-EMEA | Closed | P3 Low DCOS | joshw@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [6 empty] | Mechanical - HLT 2 - Ras_04 devation alarms - 6,7 13,15,16,17 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633774&prj=263&rqi=7XcSF3V0hY3VoUMJ2RlEjQFCKL
GI-611 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | HLT 2 -Mechanical - AHU's Not working at correct temperature control & operation. Control of heating and cooling systems to be investigated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633770&prj=263&rqi=4CIj8z8GtbUQeqZjIryw9yKQek
GI-616 | PA12x-1 | N-EMEA | Open | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | General Contractor - Electrical |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Electrical - HLT 2 - AHF 02 & 03 - General warning on both units to be investigated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633781&prj=263&rqi=s08KoiNjJ7taA0mm46f0eZslm4
GI-614 | PA12x-1 | N-EMEA | Closed | P3 Low DCOS | joshw@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | DCOS - HLT 2 Ras_04 deviation alarms - 6,7 13,15,16,17 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633775&prj=263&rqi=EpsI1mnfK7sKHazFlHwdrNNYuo
GI-609 | PA12x-1 | N-EMEA | Closed | P3 Low DCOS | markb@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | LLT - During Fuel Control Panel Controller Failure - DCOS alarm to be changed to red critical alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633764&prj=263&rqi=7B9s9jqZyF7txM16YsAWRtcmT5
GI-612 | PA12x-1 | N-EMEA | Open | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | HLT 2 -Mechanical - All Cool Array panels wiring has been amended with poor install & needs correctly installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633773&prj=263&rqi=eTYCiP05EShQD5hrIJ2tFYlGh9
YT1MECH-671-001 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-08-14 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Documentation Not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | Leak detection - TQ Panel ( Refrigerant) | LEAK - Chilled water system leak detection |  |  | Electrical - Missing Dead cable test results | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633618&prj=263&rqi=PwDSq4sxFggo5hfOJi0JKqgvyh
IST-24-013 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | jayb@straightlineconsulting.co.uk | 2026-08-14 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Complete | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | sounder Head has been removed from wall | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633616&prj=263&rqi=4by7UnEpCo2IeOL42YXz1uUJ8a
GT1MECH-744-001 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-08-14 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Documentation Not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | Leak detection - TQ Panel ( Refrigerant) | LEAK - Chilled water system leak detection |  |  | Electrical - Missing live cable test results | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633617&prj=263&rqi=eGPY9jqmzppwIdxegGnTgAesHr
IST-24-012 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-13 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Component/Equipment Failure | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - During HLT ZDA228 activated 2 times without any smoke present in the area. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633394&prj=263&rqi=vH15IRNoz35k7kAP6miKavUiOr
GI-607 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gabrielsokolowsky@sygna-emea.com | 2026-08-10 04:00:00.000 +0400 | Customer Access |  | Commissioning Issue | Commissioning | [6 empty] | XX | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632883&prj=263&rqi=Rk3aM49YujpkTpWiOxhXjPvcMq
IST-24-010 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-08 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Design Correction Needed | Design |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - A100/Securitas Security panel to be moved. the placement of this panel stops the door holder magnet to align. Door magnet holder cannot be extended as this would then stop clear Security access being granted to the Access control reader and panel. Location: Ground floor FoH entrance to Phase 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632775&prj=263&rqi=nZjsPhZ0aikLL0Msf8qZFcGtYy
IST-23-002 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-08 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Documentation Not issued/ Required | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Design documentation to be submitted to PPA and approved for Sign off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632774&prj=263&rqi=UBjcqJKXFCzvHsWnk5sf2S4cdS
IST-24-011 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-08 04:00:00.000 +0400 | General Contractor | L5 | Installation Damage | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Fire Door damage. Location: ground floor FoH entrace to phase 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632776&prj=263&rqi=tUqVegmCQJy8xN3QEjI68a3TZP
IST-24-009 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-06 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Correct | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Poor workmanship in Riser 1288 and 1289. images sent to Essais SSI whatsapp group | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632569&prj=263&rqi=IlJxR6JmyzxExz2W7KwoHCMKZQ
OPR-1-001 | PA12x-1 | N-EMEA | Closed | Outstanding Paperwork/Documentation | gregb@straightlineconsulting.co.uk | 2026-08-06 04:00:00.000 +0400 | General Contractor - Commissioning |  | Design Correction Needed | Design | [6 empty] | Asset List - Missing assets from Phase 1 construction. Stairwell Smoke Vents Nitrogen System Sprinkler Control panel Life safety remote modules (various locations in riser cupboards) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632572&prj=263&rqi=pJ577Kp7rXangADHx3g6Yp5mXl
IST-24-008 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-05 04:00:00.000 +0400 | General Contractor - Electrical | L5 | General Design issue | Design |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm DCOS - Due to incomplete Phase 2 the trouble signal is constantly active due to Phase 2 Rack being incorporated with Genset rack. Equinix to confirm if DC OPs will accept this constant fault. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632254&prj=263&rqi=8I5G7CnJJ3EVYc8ohsfSrOIEOg
IST-24-007 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-05 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Labelling | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire alarm - Yellow Ex call points have some labelling errors some examples attached. all Yellow Callpoints to be checked with Photo of each call point and location | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632243&prj=263&rqi=7TX5BBjnNOnK5KgA7q4et7jYt0
GI-593 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-07-29 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Damage | Commissioning | [6 empty] | Mechanical - 1CU_M2R1_58 - condenser fan damage. to be replacedÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631220&prj=263&rqi=v0DMRFunD6viCCy9tlnakHXIYU
GI-592 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gabrielsokolowsky@sygna-emea.com | 2026-07-28 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [6 empty] | Emergency floodlights are not well installed in MVTB rooms : the wall plugs in place seem to be a model for concrete/brick wall but not for a hollow wall. The statement has been done in block D but it would be probably the same in all MVTB rooms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631057&prj=263&rqi=AEj825OE0kztpAgQcrofdYjPKF
GI-588 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gabrielsokolowsky@sygna-emea.com | 2026-07-24 04:00:00.000 +0400 | Equinix Project Manager |  | General Design issue | Design | [6 empty] | For LV SCCS (breaker discrimination study - settings control) : 1UDPR_R2-Q29 breaker is used for the needs of the construction site on phase 2. No control possible for the moment. To be deferred to a future verification session dedicated to phase 2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630647&prj=263&rqi=UaDE2fGi1mx3yWgSaFOYbFDioC
GI-589 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gabrielsokolowsky@sygna-emea.com | 2026-07-24 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Component/Equipment Failure | Commissioning | [6 empty] | 1COP_ER2_1-Q07 The MTU buttons for accessing the menu are not working. It needs to be determined whether all or part of the circuit breaker needs to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630648&prj=263&rqi=3vGUFPpvII0sWPANIorYukOrIq
GI-591 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gabrielsokolowsky@sygna-emea.com | 2026-07-24 04:00:00.000 +0400 | Commissioning Authority |  | General Design issue | Design | [6 empty] | NEUTRAL PROTECTION ON BREAKER 1) ALL CALCULATION NOTES ARE NOT YET FULLY VALIDATED 2) ACCORDING TO THESE NOTES, NEUTRAL PROTECTIONS ARE 4P4D ON A LARGE NUMBER OF CIRCUIT BREAKERS 3) FOR EXAMPLE ON BLOCK D, breakers 1COP_DR2_1-Q01 and 1COP_DR2_1-Q02 WERE FOUND WITH NEUTRAL PROTECTION OFF (4P3D) WHEREAS ON THE NOTE IT IS 4P4D | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630650&prj=263&rqi=a0p8yqWCP7Bzlzp8e8vdgfjQHr
GI-587 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gabrielsokolowsky@sygna-emea.com | 2026-07-24 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation Not issued/ Required | Commissioning | [6 empty] | No on-site acceptance specific documentation was found for the installation of the (16A TP+N) MCBs of the fan walls, installed on the cool array's BB. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630646&prj=263&rqi=w9Gi9doCIF8eaiVZYlL2nOUrw6
GI-590 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gabrielsokolowsky@sygna-emea.com | 2026-07-24 04:00:00.000 +0400 | General Contractor - Electrical |  | Component/Equipment Failure | Commissioning | [6 empty] | 1MDSB_M1R1_3-Q13 During SCCS shift for LV breaker control settings, the authorised person was not able to open the chamber door to access the breaker. This breaker has not been yet checked. Control must be done on W31. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630649&prj=263&rqi=E8bPAsyALAdurSs7VKpCk6vNwx
GI-573 | PA12x-1 | N-EMEA | Closed | P3 Low CX | garyd@straightlineconsulting.co.uk | 2026-07-22 04:00:00.000 +0400 | General Contractor - Electrical |  | Cleaning | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_02 | DCOS - HMI Panels |  | SCH - Schneider | mechanical asset need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630276&prj=263&rqi=vMelHpLAejNhQnu1vsWii4765o
GI-539 | PA12x-1 | N-EMEA | Closed | P3 Low CX | garyd@straightlineconsulting.co.uk | 2026-07-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Correct | Commissioning | [6 empty] | mechanical earth cable stuck in cover 1EXFM_M1R1_02 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629908&prj=263&rqi=yVg1tkAPzLFjOZvrQN67oJXwcB
GI-536 | PA12x-1 | N-EMEA | Closed | P1 High CX | daniel.loayza@eu.equinix.com | 2026-07-16 04:00:00.000 +0400 | SCH - Schneider DCOS |  | General Design issue | Design | [6 empty] | During full load testing of chillers, 3 chiller breakers tripped: MSB M2 - Q-06 - Chiller 1-1 Q-10 - Chiller 3-1 MSB R1 Q-09 - Chiller 1-1 Early indication from AERMEC is that chillers have not over-amped, and early trends from DCOS suggest the breakers in the MSB's did see an overly high current. This leads us to suspect a potential AHF issue or breaker issue that needs to be investigated. BYES need to deploy Danfoss to begin trend gathering and analysis and ITEC need to confirm their equipment is functioning correctly. AERMEC need to provide relevant trend data on those chillers for analysis by the group. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629713&prj=263&rqi=SmkKorl65l9zGhknMIVynQ7oDT
GI-537 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-07-16 04:00:00.000 +0400 | REH - Rehlko Gens |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | MOT - Â TTK fuel leak detection system in the pump rooms is now fed from batteries. This change was implemented after IST. Actions required: 1. Provide the intervention report for this change. 2. Provide updated drawings reflecting the new power supply configuration. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629772&prj=263&rqi=aoD6EJlLGlZy6Fo9Ajzu6xKpGI
IST-24-006 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-08 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Complete | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - DCOS connection not completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628298&prj=263&rqi=7pTeNPyLjgOFyYHTUzCmQGuFeo
IST-24-005 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-08 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Correct | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Smoke extract dampers failed to operate correctly. Dampers didnt open activation and/or close on reset. 1SD_NC_0021 1SD_NC_0022 1SD_NC_0023 1SD_NC_0024 1SD_NC_0025 1SD_NC_0026 1SD_NC_0027 1SD_NC_0028 1SD_NC_0029 1SD_NC_0030 1SD_NC_0031 1SD_NC_0032 1SD_NC_0033 1SD_NC_0034 1SD_NC_0035 1SD_NC_0036 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628295&prj=263&rqi=3QF89rlk1PMic3mHy38ALYU0Av
IST-24-004 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-08 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Correct | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - DH1-6 Dampers do not open after fire signal is received. Belimo seems to operate correctly but the damper blades do not open 1SSIRCFD_NO_0159 1SSIRCFD_NO_0160 1SSIRCFD_NO_0161 1SSIRCFD_NO_0162 1SSIRCFD_NO_0163 1SSIRCFD_NO_0164 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628292&prj=263&rqi=5Z19Ohlti8SW5ykwx0vaUHSIrj
GT1FD-80-002 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-07-07 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Design not as Specified | Design | Fire Detection | equipment | SSI_RACK_1 | FACP - Fire Alarm Control Panel |  |  | Electrical - ZDA. PPA stated thresholds differ from the BYES Aspire design calculations. Should PPA values be adhered too in Design for smoke activation levels? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628249&prj=263&rqi=710CUxSedDCVndQekloGsfALo4
GI-504 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-06 04:00:00.000 +0400 | General Contractor - Electrical |  | Cleaning | Commissioning |  | equipment type |  |  |  |  | Fire alarm - All DH1-6 require Vesda pipework to be cleaned. extremely dirty with Dust from construction works in all Halls | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628014&prj=263&rqi=Fy35WVF6o3VsxpWC0ZH73zbLTa
IST-24-003 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-07-05 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Documentation Not issued/ Required | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - All updated drawings/documentation to be submitted to PPA for approval prior to C&E testing. As built drawings, C&E Matrix to show agreed changes to allow Testing and checklist to be signed off against valid documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627945&prj=263&rqi=1qDPccvYD04oxAiAxPKX3jJ52P
IST-24-002 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-05 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Correct | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire alarm - Automatic fire compartment doors are not closing sufficiently to seal the barrier of compartment. Air balance could be the issue stopping doors fully closing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627942&prj=263&rqi=85jeoXNJ3VG9PWFOW4URUtmWjO
GI-502 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-02 04:00:00.000 +0400 | General Contractor - Electrical |  | General Design issue | Design | Fire Detection | system | Fire Detection |  |  |  | ZDA - within all DH's 1-6 , in certain HAC's the smoke extraction ductwork and sprinkler pipework is obstructing the Vesda detection holes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627688&prj=263&rqi=xYcyL3JwOKX69BxMFUg9WyPDv6 | https://equinix.facilitygrid.co.uk/x/project/263/system/14098
GI-610 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Labelling | Commissioning |  | equipment type |  |  |  |  | HLT â€“ Mechanical â€“ Vertiv White Space Sensor Naming Discrepancy The Vertiv White Space (Cold Aisle) sensor naming convention does not align with the naming used in DCOS. In the field, the cold aisle sensors are labelled as White Space 3 & 4, whereas DCOS identifies these same sensors as White Space 5 & 6 for all standard Cold Aisles (with the exception of the Extension Units). This discrepancy creates confusion when comparing field readings with DCOS data and during fault investigation. Vertiv is requested to confirm the correct sensor naming convention and ensure all White Space sensors are clearly labelled in the field to provide consistency between the physical installation and the DCOS interface for operations and maintenance personnel. Evidence: DCOS screenshots for DH05 and DH06 are attached, showing the Cold Aisle sensors identified as White Space 5 & 6, highlighting the discrepancy with the Vertiv field labelling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627523&prj=263&rqi=1pgTD5BVNmNrVKcdGnBDfkstMA
GI-501 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | HLT â€“ Mechanical â€“ DCOS Temperature and Max Cooling Sensor Labelling The DCOS Temperature Sensors and Max Cooling Sensors throughout Data Halls A, B, C, D, E and F have not been labelled as previously agreed with BYES. The absence of clear identification is causing difficulties when validating sensors during commissioning and fault-finding activities. It will also present ongoing challenges for operations and maintenance personnel when identifying and verifying individual sensors in the future. All DCOS Temperature and Max Cooling sensors should be permanently labelled in accordance with the agreed naming convention to ensure clear identification and maintain consistency with the project documentation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627524&prj=263&rqi=BjyLBPpsziY3eOyKVjWx6Q0D0M
GI-500 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Multiple drawing folders have detached and fallen inside the cooling corridors. The folders are not securely fixed and should be re-secured to prevent obstruction, damage, or a potential housekeeping/safety hazard. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627516&prj=263&rqi=dhpQYQEP9vayWUtPMtaPcB7S4j
GI-476 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | Design Correction Needed | Design |  | equipment type |  |  |  |  | MOT - Testing at the Fuel Control panel for loss to individual relays supplying components. Failing one relay inhibits the entire fuel system functionality. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627370&prj=263&rqi=DgFPTx2RmhiWil7AfLOiLMdNNu
GI-471 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | MOT - Testing at the generator panel for loss of power to supply motorized valve in day tank. No alarms received on the BMS when power was cut to the valves. Pumps were shown as unavailable on the FCP panel HMI, which is incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627365&prj=263&rqi=YKLz62MY3xev1SGC0yp0uIFfNo
GI-477 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design |  | equipment type |  |  |  |  | MOT - All 8 SCPs are located in the same fire zone. A loss of all 8 SCPs will start all associated chillers and pumps at 40 Hz. Risks identified: 1. Risk of over pressurizing the loop. 2. Strings that are out of sequence will start and overload the electrical line-ups. 3. Proof that the cooling plant will be able to manage full load without SCPs is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627372&prj=263&rqi=CAWDhI1qsgzvqO031l2b1VJPtX
GI-492 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design |  | equipment type |  |  |  |  | MOT - FCV valves remain at last know when power loss / comm loss and potentially result in the other chiller on the same string going to low flow situation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627392&prj=263&rqi=jFxYTnZfG4yXtmaCM0wuPW3nGx
GI-469 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | MOT - Testing at the Fuel Control panel for loss of external fuel pipe heaters. The alarm on the HMI is not matching the labeling on the unit in the field. The system is not monitored by the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627363&prj=263&rqi=1OpcuySCFmYQZ161IDbYF629CI
GI-473 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Electrical |  | General Design issue | Design |  | equipment type |  |  |  |  | MOT - On the day of testing, it was informed that a fire signal from the fire system stops the generator. Rehlko vendor could not provide further information. The signal wired from the fire system to the generators was not identified. No schematic drawing exists showing how the fire system is connected to the generators. One fire panel sends hard-wired signals to stop the generators in case of fire . A centralizing panel sending a shutdown signal to each generator poses a high availability risk. High availability risk if there is a common dependency with signals wired from the same location to all generators. In addition, a fire curtain was observed in place. No one could explain how the system works and its impact on generator availability. All relevant documentation must be submitted to assess the risk. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627367&prj=263&rqi=yOR7gYqP2sDDUYeRQcxUxnrLGd
GI-490 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning |  | equipment type |  |  |  |  | MOT - 1. There is no wire labeling on the unit. 2. A bad wire connection (exposed wire) was found. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627388&prj=263&rqi=nJnzza09bd7N842XK48zwqlvSZ
GI-463 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | LLT - ,BMS monitoring was observed to be intermittently lost and restored. The vendor confirmed that this is a recurring issue. Schneider attempted to reboot the BMS server on-site; however, the reboot did not restore BMS monitoring. Schneider subsequently conducted an unplanned intervention during the night to restore the system. Actions required: 1. Provide the intervention report for the night activity. 2. Provide RCA for this recurring BMS monitoring loss. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627355&prj=263&rqi=OfOkvbc3jBCAKTrSeTDR4oxtWV
GI-487 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Design Correction Needed | Design |  | equipment type |  |  |  |  | MOT - Gas Leak Detection The panel is considered as a separate asset and did not have any commissioning tag. Some wiring in the panel is not labeled, and the schematic drawing inside the panel has hand-written modifications (updated wiring of what was installed on-site was not in place during the testing day). The panel is not connected to the BMS system. A battery connection was found inside the panel while there were no batteries connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627385&prj=263&rqi=nqJa414IDv2P7Gn9AlvZ5Xlivp
GI-467 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | MOT - Testing Diesel pump for loss of communication from the PLC The way both FCPs are connected to both pump contactors differs between FCP 1 and FCP 2. Having identical systems each wired in a different way makes troubleshooting difficult. Only the Rehlko technician who installed the system is aware of the wiring differences. action to audit the two FCP's and ensure they are wired in the same way as per design intent and provide the as-built drawing (drawing not available on site during testing) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627361&prj=263&rqi=ZJ7Lv2hQtCnpP4NRctWCMbj6t7
GI-648 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR â€“ Chiller M2R1_2_CH_1 tripped, generating a Chiller Fault alarm at 15:48pm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627330&prj=263&rqi=RKdFH2F0eOru4A62HFanscdnLF
GI-643 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR â€“ PDT sensors in DH04 and DH05 were reading 0.0 during testing. This requires further investigation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627312&prj=263&rqi=8MHsE86hY4bAAFe47Dx8OxHtDK
GI-651 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR â€“ Chiller 5_1 HMI recorded multiple alarms between 14:37 and 14:48, including Compressor 2 & 3 Overloads, Turbocor 2 Inverter Temperature Alarm, and Turbocor 1 Offline. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627336&prj=263&rqi=xL0iOcvkNXlFStaf3v3nMaGeIH
GI-649 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR â€“ Chiller M2R1_3_CH_2 tripped, generating a Chiller Fault alarm at 15:48pm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627334&prj=263&rqi=fIHOTuqNd9QhbqZwbozfiHG3y8
GI-641 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR_3_1 â€“ Evaporator Low Alarm received at 12:40 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627309&prj=263&rqi=CMeGkgXSeveehMpgDlbLsP3gyq
GI-642 | PA12x-1 | N-EMEA | Closed | P3 Low DCOS | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | DCOS Comms Issue/Fault | DCOS | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CRAH_ER1_27 Had a communication alarm present during the heat load testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627310&prj=263&rqi=TZ4XYflTZpyGPnEPRpu9lBebZn
GI-647 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ Mechanical â€“ 1MAU_M3R1_02 generated a SAT High Temperature Alarm (34.5Â°C) at 15:55. At the time of the alarm, DX Unit 1 was OFF and DX Unit 2 was ON. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627320&prj=263&rqi=vV6wB9kLy9IjommyfmlTThPy0b
GI-462 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Cleaning | Commissioning |  | equipment type |  |  |  |  | HLT â€“ Mechanical â€“ The cleanliness of the cooling corridors requires review. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627339&prj=263&rqi=RQy8k5mUTBbKjPjqnth8akONo5
GI-466 | PA12x-1 | N-EMEA | Closed | P3 Low CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | M0T - Testing (ER) Circulation fans loss of communication and loss of power Two circulating fans in the UPS room were found not connected to the CRAHs in the same room. Power supply verification testing and operation testing need to be performed on these fans in relation to the CRAHs in the same room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627360&prj=263&rqi=k1qlbFq9r81kDbYatLr40muTsH
GI-470 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | Design Correction Needed | Design |  | equipment type |  |  |  |  | MOT - Testing at the Fuel Control panel for loss of external fuel pipe heaters. The heat tracing units are placed on site in proximity to MV cables, and some other units are installed behind GRMUs in non-accessible, high-risk safety areas. Maintainability and accessibility issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627364&prj=263&rqi=xDowZzBwTC049vjK7ELHEhfSmZ
GI-480 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | MOT - Loss of 24V to out of sequence string SCP (2 chillers in standby) The two pumps of the affected string started and went to 30 Hz. The chillers of the affected string started, then different chillers began to lock on flow. The PCP then started other chillers, creating multiple chiller failures on the cascade. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627375&prj=263&rqi=T5slYkunbaWifr2g25P3n5TlmG
GI-481 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | MOT - Loss of power to running SCP (2 chillers running). The two pumps of the affected string went to 40 Hz. The chillers of the affected string kept running, then later locked on flow. The PCP started the next chillers in the cascade, resulting in multiple chiller failures on flow, while the two pumps kept recycling hot water from return to supply and overpressurizing the loop. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627377&prj=263&rqi=UQvEpKVk7DhHCMfQABoa07Cv3W
GI-491 | PA12x-1 | N-EMEA | Closed | P3 Low CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design |  | equipment type |  |  |  |  | MOT - Gas Leak Detection When the refrigerant leak detection system tripped all operating chillers, after restarting the chillers, PRV valves operated and a huge amount of water was observed in the pressurization unit room. The cooling loop PRV valves operating value tags are not in place and the valves are not sealed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627390&prj=263&rqi=kAdmJOjeaqPFEAV1TinrYOJvtr
GI-496 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | MOT - DPT Riser 3 should also be tested for filtering or scaling behavior. A value jump is noted, but the exact numerical values should be confirmed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627396&prj=263&rqi=7qL9kUuzpweVbuxN57Hxu4Ylwt
GI-646 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR_2_1â€“ Evaporator Low Alarm received at 13:00 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627317&prj=263&rqi=lJT3ECiI7ABvBlz0w4rqQyps5J
GI-499 | PA12x-1 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Component/Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1CHWSTR_M3R1_6_ELC_1 | CP - Control Panel |  |  | Mechanical - found blown fuses during tests today. That requires further investigation as it has happened previously. RCA to be provided for each blown fuse. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627472&prj=263&rqi=WLMd6nxyPyCd4rs0hnK698DiqM
GI-639 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR_5_2 â€“ Evaporator Low Alarm received at 15:05. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627305&prj=263&rqi=vgTUhYqUTjpQI5EoPSuIFkTbmT
GI-650 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR â€“ Chiller M2R1_6_CH_2 tripped, generating a Chiller Fault alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627335&prj=263&rqi=cEleLqqnuBo3Y73RK6ysXWnebb
GI-640 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR_1_2 â€“ Evaporator Low Alarm received at 16:14. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627307&prj=263&rqi=cvpYxxHItpqjDeqZQJVKEy2BDK
YT1DCOS-225-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS | L2B | Installation Damage | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_23 | DCOS - HMI Panels |  | SCH - Schneider | Protective plexiglass broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627329&prj=263&rqi=KepJaRlCTfox1SSTfeL3yO6wN1
GI-474 | PA12x-1 | N-EMEA | Closed | P3 Low CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | General Design issue | Design |  | equipment type |  |  |  |  | MOT - Testing at the generator panel for TTK leak detection on Gen room. The TTK system is now fed from generator starting batteries. This change was done after IST. No schematic drawing exists for this change. Actions required: 1. Provide the intervention report conducted after IST. 2. Provide updated schematic drawings reflecting the new power supply configuration. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627368&prj=263&rqi=wqaVIVhP0tIxQpQtV6E8640jsE
GI-494 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | MOT - DPT Riser 1 should be tested for communication failure. The notes mention a fault with a negative pressure value, approximately -32 Pa. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627395&prj=263&rqi=BFl5DTyN5z45kELOoj2sGdcGu9
GI-493 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | MOT - Chiller flow switch sensitivity target approx 28 L/s which is noted as below AERMEC setting | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627394&prj=263&rqi=pYgJGlVCpIVAguLkSFS1ZExhpY
GI-472 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | MOT - Testing at the generator control panel for daily tank levels No alarm received on the BMS when failing the analog level sensor on the daily tank. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627366&prj=263&rqi=5axTSbv0J3iff2q1nlcFc5CqoW
GI-468 | PA12x-1 | N-EMEA | Closed | P3 Low CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | DCOS - Equinix |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | MOT - Testing Diesel pump for loss of communication from the PLC. A bad/loose connection was found on the pump flow switch and FCP 1. Rehlko technician intervened and corrected the connection. The flow switch is wired back to FCP 1 through a junction box fixed in a location exposed to vibration, making loose connections likely to recur. No alarms are received when losing power or connection to the flow switch, leaving the system in an unhealthy state until a fuel call occurs to initiate troubleshooting. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627362&prj=263&rqi=80nQMBCYPXhEjNjvfj6R2aefLB
GI-478 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | General Design issue | Design |  | equipment type |  |  |  |  | MOT - Multiple strings have buffer tanks in bypass mode during steady-state operation. In case of a utility outage, the buffer tanks will not support the critical load (TT05: below 21.5Â°C). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627373&prj=263&rqi=kKekTfxbeZ45k11MecbB3ZgrHI
GI-489 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | MOT - Simulate Pressure Drop The alarm name on the BMS "Leak detection" does not match the "Pressurization unit in operation" status. The alarm was received on the BMS after a delay of 90 minutes plus expansion tanks dropping below 20% Ã¢â‚¬â€ this is a significant time delay to receive the alarm on the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627387&prj=263&rqi=4exfEhXbtR5IUQR02GhPUTY8Az
GI-644 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Not Correct | Commissioning | HVAC | equipment | Heat Load Test Hall C | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CA_M1R1_41 - White space temperature sensor reading 29.1 (High High Alarm) when 100% Load is applied | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627314&prj=263&rqi=Zctu78b9rgAJ1m6NtcdJQvKzUS
GI-488 | PA12x-1 | N-EMEA | Open | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning |  | equipment type |  |  |  |  | MOT - 1. There is no site schematic electrical drawing for the unit. 2. The valves and sensors on the unit labels are not matching the names shown on the local system HMI. 3. Updated operation manual and system settings need to be shared. 4. Flow meter for the water supply to the pressurization unit is not connected to the BMS (information shared by the vendor). 5. The PRV is not sealed and the bar value tag is not in place. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627386&prj=263&rqi=gyLX3BIRHGHqRf72ticVty3CCJ
GI-645 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Damage | Commissioning | HVAC | equipment | Heat Load Test Hall E | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ Mechanical â€“ A fan fault was identified on 1CA_M1R1_36 (Fan 22) during testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627315&prj=263&rqi=VWcHakZFQ5DUOe4xNh8lUH5DN5
GI-653 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall E | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ Mechanical â€“ 1CA_M1R1_20 generated a Differential Pressure Alarm (DP1 Out of Range). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627338&prj=263&rqi=SuUTmMENVgkOG29xDhtlod5PV5
GI-482 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | MOT - Loss of power to out of sequence SCP (2 chillers in standby). The two pumps of the affected string started and went to 40 Hz. The chillers of the affected string started, then different chillers began to lock on flow. The PCP then started other chillers, creating multiple failures on the cascade. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627378&prj=263&rqi=TPDnKF2LBG0FlgmXew3KgGecQE
GI-475 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | Design Correction Needed | Design |  | equipment type |  |  |  |  | MOT - Testing at the generator panel for TTK leak detection on Gen room. It was informed that triggering fuel leak detection in the Gen room will open the GRMU breaker, which poses a high availability risk. Stepping on the TTK cable resulting in opening the MV GRMU breaker is not an accepted design. Actions required: 1. Provide all details related to this design. 2. Provide a list of alarms that open the GRMU without impacting generator operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627369&prj=263&rqi=l8GTsXuAgW7Q449Q4RLMuqZcoY
GI-483 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | MOT - Loss of flow transmitter FT01 - Evaporator FT on running chiller 1.1. Initial status: Running chillers: CH 1.1, CH 2.1, CH 2.2. Upon failing the FT sensor at CH 1.1: CH 1.2 in the cascade started and CH 1.1 locked at low flow. The bypass valve opened to maximum rapidly due to loss of FT reading. On String 1, with CH 1.2 running: Due to the bypass valve's fast opening reaction, reverse flow occurred from the supply side of the network to the return (dropping the loop pressure). CH 1.2 with pump at 100% could not push water into the supply side loop network. Due to the pressure loss caused by reverse flow, additional chillers started in the cascade. The system took excessive time until the bypass valve closed and the system began dropping the unnecessary chillers. More than -40 L/S reverse flow!!. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627379&prj=263&rqi=WgffHCNLNoKESXkHbVs60vuOKB
GI-652 | PA12x-1 | N-EMEA | Closed | P1 High CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Not Correct | Commissioning |  | equipment type | Data Hall Heat Load Test Phase 2 | Data Hall Heat Load Test Phase 2 |  |  | HLT - Cool Array sensors calibration discrepancies across all halls. HLT â€“ Mechanical â€“ Calibration discrepancy identified between 1CA_M1R1_20, 1CA_M1R1_18 and the Data Hall temperature readings, with deviations of 1.1Â°C and 1.4Â°C. Further investigation - All Vertiv sensors have calibration discrepancies, Sensors have been replaced, software downgrades/upgrades, Factory support on sensors and still issue remains across all halls with calibration discrepancies 3-4+ degrees out | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627337&prj=263&rqi=88RqcemRb4ZB2KvLrtzDRBSE2m
GI-486 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Design Correction Needed | Design | [6 empty] | MOT - Refrigerant leak detection system (centralized system) testing Ã¢â‚¬â€ Refer to schematic drawing "48 points system" page 11. Opening the closed contact on one relay connected to chiller from Relay Board 1. If the relay board is physically damaged, it will result in opening all normally closed contacts of all relays, leading to shutting down all chillers. Same risk: In case of wire damage from the panel (same cable tray) going out from the panel, this will lead to the same result. Note: On the relay board, each relay normally closed contact is connected to one chiller. Once the relay is energized, the normally closed contact opens, opening the wire loop to the chiller and triggering chiller shutdown. Any cause of opening these wires will lead to chillers shutting down. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627384&prj=263&rqi=XzBrF6FRwM2dxYzzchYC1kMEEY
GI-479 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | MOT - Loss of 24V to SCP of string (2 chillers running). The two pumps of the affected string went to 30 Hz. The chillers of the affected string still had the run command but were locked on flow. The PCP started the next chillers on the cascade, resulting in multiple chiller failures on flow, while the two pumps kept recycling hot water from return to supply and overpressurizing the loop. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627374&prj=263&rqi=gKHHJvj2YQB4zjHf4l8xJtDLlj
GI-455 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | LLT - The SWITCHBOARD LOCAL/REMOTE selector switch is not generating an alarm when the MVTB is placed in local mode on either the local HMI or BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627081&prj=263&rqi=szjE0fm1areLwty6hgXLt7cdmP
GT1DCOS-276-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS General Issue | DCOS | Electrical â€“ LV | equipment | 1DCOS_1_OAP_1 | CP - Control Panel (Max Cool Announcement) |  | SCH - Schneider | Disconnecting the hardwired connection between the OAP and ECP did not generate an ECP Panel Fault indication on the OAP. As stated in the MaxCool SOO, Section 4.0 â€“ OAP Panel Description (Page 9), the "ECP Panel Fault" shall indicate when "the connection between both panels has been disconnected." This behaviour was not observed and should be investigated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627078&prj=263&rqi=L8etWag4dxr2mtIEsNOmlpoKR0
GI-459 | PA12x-1 | N-EMEA | Closed | P3 Low CX | markb@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | MOT - Testing Diesel pump for loss of communication from the PLC The way both FCPs are connected to both pump contactors differs between FCP 1 and FCP 2. Having identical systems each wired in a different way makes troubleshooting difficult. Only the Rehlko technician who installed the system is aware of the wiring differences. action to audit the two FCP's and ensure they are wired in the same way as per design intent and provide the as-built drawing (drawing not available on site during testing) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627086&prj=263&rqi=PZREBStiPIkOPkqNFd21WELqeZ
GI-461 | PA12x-1 | N-EMEA | Closed | Outstanding Paperwork/Documentation | markb@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | MOT - Testing at the Fuel Control panel for double skin pipes fuel leak detection The names of pipe leak detection units on the FCP HMI do not match the SLD, making it impossible to identify where the units are located on-site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627089&prj=263&rqi=D3MOG8UBVW9WNiBKqUpUl5LIwk
GT1DCOS-276-002 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS General Issue | DCOS | Electrical â€“ LV | equipment | 1DCOS_1_OAP_1 | CP - Control Panel (Max Cool Announcement) |  | SCH - Schneider | During testing, the ECP panel power supply was switched off. The OAP correctly activated the audible alarm; however, the ECP Panel Fault red indicator did not illuminate and the blue beacon was not activated. As defined in the MaxCool SOO, Section 4.0 â€“ OAP Panel Description (Page 9), the OAP shall indicate an "ECP Panel Fault" when the ECP power supply is unavailable, and the blue strobe light and audible alarm are used to signal that an alarm is pending. This behaviour was not observed and should be investigated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627079&prj=263&rqi=JQGNas7g5clt9ZYwD9dWAyPB9d
GI-460 | PA12x-1 | N-EMEA | Closed | Outstanding Paperwork/Documentation | markb@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation Not issued/ Required | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | MOT - Testing Fuel Control panels for communication cut between FCP and GCP There is no network schematic diagram for all the FCPs and GCPs. The fiber cables connected to FCP 1 are not labeled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627088&prj=263&rqi=HG2TevFH10m8wZ6wCpzFed2rCo
GI-638 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-25 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall C | Data Hall Heat Load Test Phase 2 |  |  | HLT - Issue discovered during 25% heat load testing: The pressure sensor for 1CA_M1R1_47 was observed reading out of range, exceeding 100 Pa, while adjacent pressure sensors remained stable at â‰¤15 Pa. The sensor subsequently dropped to 0 Pa before recovering. As no similar behaviour was observed on neighbouring sensors, this indicates a likely fault with the pressure sensor or its associated signal/wiring rather than an actual pressure condition. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626862&prj=263&rqi=i6pEm22v1WMi0VuxKizqpCwZ2L
GI-450 | PA12x-1 | N-EMEA | Closed | P2 Medium DCOS | kostask@straightlineconsulting.co.uk | 2026-06-24 04:00:00.000 +0400 | AER - Aermec |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | Mechanical - The differential pressure sensor on the chiller evaporator is showing a negative value when there is no flow. The DCOS page indicates that the sensor has failed. The issue is probably be related to scaling on the DCOS side rather than a sensor fault. DCOS team to check and correct the scaling configuration for ALL the chiller evaporator DP sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626705&prj=263&rqi=34E3e1TSWVCVqpmzJT1OfLXXOS
GI-634 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CHWSTR_5_RAS_3 - Input value 3 in alarm - negative reading | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626487&prj=263&rqi=8VhzKe6NTF2Kjy2hSiC0OG337j
GI-629 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1FCU_M1_54 - Alarm active | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626482&prj=263&rqi=oFFbyVP746oNNl9mDYaPoCH1oW
GI-628 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Component/Equipment Failure | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1PSER_M2R1_1 - Leak alarm active | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626481&prj=263&rqi=q0PtCFjUwyi4Ka0KaGoyrJX288
GI-627 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Component/Equipment Failure | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT 2 - Mechanical - 1RAS_04 - Status deviation alarm active | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626480&prj=263&rqi=NJIXcMamumss82QTEAVJwMoNQn
GI-448 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  | system | DCOS System |  |  |  | Heat load test - Full of E & F String in communication alarm. Impact to HLT & deadline for IST | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626496&prj=263&rqi=cFrIwjRhcrThpaRYHuViXDACyA | https://equinix.facilitygrid.co.uk/x/project/263/system/10784
GI-636 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | General Design issue | Design | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - High humidity alarms - DH3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626491&prj=263&rqi=lYBxbA3f24aUn27BXHAOb4N5WE
GI-449 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning | HVAC | system | CHW System |  |  |  | HLT - Cool array corridors build up in large amounts of water from pipe condensation. - Data hall 5 & 6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626499&prj=263&rqi=do0qX3VJ9Fwrro1O9e9qsxr92i | https://equinix.facilitygrid.co.uk/x/project/263/system/9233
GI-635 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CHWSTR_5_RAS_2 - Input value 3 in alarm - negative reading | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626489&prj=263&rqi=kquejDxRJN2oJvFtt5RLCb73cB
GI-630 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | AER - Aermec |  | DCOS General Issue | DCOS | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CHWSTR_M2R1_2_CH_1 - Low evaporator alarm active | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626483&prj=263&rqi=S4Yja4VxDE9zlrTp9sm7EZl90u
GI-633 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1RAS_04 - High high alarm active - 2.3 bar reached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626486&prj=263&rqi=s5tRZT7tRS1SRI0L0b6q5QzHfv
GI-637 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CHWSTR Strings 1,3,5,6,7 RAS deviation Alarms | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626492&prj=263&rqi=a9s6iskgz7bXGYBnByNIBSDuM8
GI-632 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CHWSTR_3_RAS_3 - Input value 2 in alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626485&prj=263&rqi=eBElV7p7nqjFWO1uUJ01u6VHjo
GI-631 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Component/Equipment Failure | Commissioning | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical -both MAU - Major fault & shutdown | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626484&prj=263&rqi=625L8vfRKtOtXhmOW8NzafecvF
IST-23-001 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-06-19 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Correct | Commissioning |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | L4 C&E Testing: 1MVHR_M1R1_01_IHM not confirmed if shutdown was achieved (Mech needed) Lift 3 not connected for shutdown, shown on Matrix. removed from Matrix, agreed by PPA Ground Floor fire curtains not fully closing Event log for Genset testing to be sent to SLC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626226&prj=263&rqi=aLfIMX1uavVHjvlz9TN2kkfiqO
IST-24-001 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-06-19 04:00:00.000 +0400 | General Contractor - Electrical | L5 | General Design issue | Design |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Following issues found on Testing 17/06/2026. Smoke extract dampers in following Zones failed to operated after manual trigger for Phase 1.1 ZDA104 ZDA105 ZDA106 ZDA130 No event log from testing was able to be downloaded from Racks to to internal issue. all areas tested to be re-tested. ZDA001, ZDM039, ZDA106, ZDM049, ZDA101, ZDA104, ZDA108, ZDA105, ZDA112, ZDA130, ZDA121. DH1 HA+CA, DH2 HA+CA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626229&prj=263&rqi=oJLF6Zjo3JdtDBvqcVlGzew8xf
GI-441 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-06-18 04:00:00.000 +0400 | SCH - Schneider MV |  | Installation Not Correct | Commissioning | [6 empty] | #LLT Issue on the MVTB R2 (Test performed on the 17/06/2026) during the LLT test when we switch off the breaker energizing the P5 of the loop 2 and when we switch back on this breaker who feeding this P5 The MVTB R2 calling the Gen start | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625856&prj=263&rqi=geF6JC891P6LmjKUuiAqRTkQ1Y
GT1FD-80-001 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-06-16 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Cleaning | Commissioning | Fire Detection | equipment | SSI_RACK_1 | FACP - Fire Alarm Control Panel |  |  | Cleaning: of Fibre connection /DCOS rack before C&E testing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625421&prj=263&rqi=164n1wBVkL15XDvsBj8lY9fnwo
GI-440 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-06-16 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | LLT issue comms failure we lost all the coms of the site during the test of the BTU A (losing power source ) DCOS server crashing many times after trying to restart DCOS on engineer laptop ( issue need to be resolved asap) please see [picture attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625501&prj=263&rqi=Mj06a6snI9hqBAOUkYXJqT0AEh
GT1FD-80-003 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-06-16 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Cleaning | Commissioning | Fire Detection | equipment type | FACP - Fire Alarm Control Panel | FACP - Fire Alarm Control Panel |  |  | Cleaning: All EAE units require deep cleaning. EAE_1-23 ALL EAE Units to be cleaned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625422&prj=263&rqi=VZ73TJeNCSsw3u5nJfO7iPk6BZ
GI-422 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-03 04:00:00.000 +0400 | AER - Aermec |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | IST1 - CHILLER LEAK DETECTION â€“ NO COMMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623770&prj=263&rqi=XNxapMaZ37QNKFRNXQs73owHpg
GI-428 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-03 04:00:00.000 +0400 | REH - Rehlko Gens |  | General Design issue | Design | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | IST1 - FCP01 FUEL PUMP FAIL ALARM ON DCOS WHEN COMPLETING M1/R1 SWITCHING ON IST TEST 1.0 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623776&prj=263&rqi=hCFTzefXFwHllhdapS4iT75vtp
GI-429 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-03 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | IST1 - LEAKAGE PIPING LDT ALARMS PRESENT FOLLOWING IST TEST 1.0 SWITCHING | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623777&prj=263&rqi=t1WtCOEBGgycNPG8uUKvI6InQL
GI-418 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-06-03 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Damage | Commissioning | [6 empty] | #IST ## CRAH M1R1_10 Elec Switch need to be replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623758&prj=263&rqi=ZlGJ7P0lEQcOe5PSQQHfuo6NgZ
GI-417 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-06-02 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Installation Damage | Commissioning | [6 empty] | IST# Masterpack Q03 FEEDER TO 1COP_AR1_1 cover protection broken need to be replace please see picture attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623645&prj=263&rqi=ErsJmkRPC099ycZxDZrq6OpKOT
GI-626 | PA12x-1 | N-EMEA | Closed | P3 Low DCOS | joshw@straightlineconsulting.co.uk | 2026-05-30 04:00:00.000 +0400 | AER - Aermec |  | DCOS General Issue | DCOS | HVAC | equipment | Heat Load Test Hall D | Data Hall Heat Load Test |  |  | HLT - During fire Test 29.05.25, Multiple communication alarms on CHW Pumps / Chillers. Still gave command feedback/ feedback as correct - DCOS to investigate further whilst remained in purple alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623493&prj=263&rqi=KiuiixoiA0viupUmXQ3r6jcr68
GI-415 | PA12x-1 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-05-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | Cleaning | Commissioning |  | equipment type |  |  |  |  | Mechanical - All condenser coils of the chillers require cleaning. The dirt in the coils will effect chillers performance. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623216&prj=263&rqi=Yl1h2Q7W0RjClLZw9xazuS7fbV
GI-414 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-05-22 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | All Bone tags on All CRAH's Phase 1 have been amended with permanent marker, all incorrect, BYES to change to all correct permanent tags on CRAH ATS Cables both supplies | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622776&prj=263&rqi=6sV6IfFxn8TGjBmjWLpw72BbZV
GI-413 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-05-19 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design | [6 empty] | Mechanical/Safety - Data hall pressure causing entrance Doors to data halls & Cool array corridors to slam and potential injure someone entering or leaving. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622243&prj=263&rqi=CClaUFHiVru3OKNgTsNCpFyaLU
BT1MECH-529-039 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | General Contractor - Mechanical | L4 | Component/Equipment Failure | Commissioning | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | 1CHWSTR_5_RAS_2 - Temperature sensor not reading correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621766&prj=263&rqi=2jBgGtk7gnN3hCFskLKiTwfCek
BT1MECH-529-043 | PA12x-1 | N-EMEA | Closed | P3 Low DCOS | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | Mechanical - Data hall temperature & humidity sensors go into communication alarm when rising above 50 degrees | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621812&prj=263&rqi=DKWPkBLuZUbCAVlfZw4GKEp2NP
BT1MECH-529-038 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | General Contractor - Mechanical | L4 | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | 1CHWSTR_1_RAS_2 - Temperature sensor not reading correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621760&prj=263&rqi=2PNGfYKCB12C3AuoE4jKumppTi
BT1MECH-529-044 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | General Contractor - Mechanical | L4 | Design Correction Needed | Design | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | MECHANICAL - Both MAU'S major fault - to be investigated - Planned commissioning/investigation on 20.05.26 Alarming as low temperature under 15 degrees. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621823&prj=263&rqi=XZrN1nhAtSpvglmjtebCptwxZN
GI-624 | PA12x-1 | N-EMEA | Closed | P3 Low DCOS | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | Mechanical - HLT Test - Fan fault on cool arrays not latching. changes to a Fan communication alarm due to fan spinning in reverse. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621803&prj=263&rqi=xWc1T1WXJGUG5vRmdZysiaX4Ih
BT1MECH-532-046 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall D | Data Hall Heat Load Test |  |  | Mechanical - 1CA_M1R1_08 - White space 5 temperature to be corrected. 1.3 degrees out and coming into alarm reading 28.3 all others are reading approx 27 in same area | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621827&prj=263&rqi=WImbEsOQjn63hKn5CmSsTg2qEF
BT1MECH-529-037 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | 1CHWSTR_M2R1_2_CH_2 - Experienced intermittent issues that recurred throughout the day | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621759&prj=263&rqi=rQzp3CudvGHpEC4omaAxbVjQUT
BT1MECH-529-041 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Component/Equipment Failure | Commissioning | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | 1GEN_M3 â€“ A sensor fault caused an M3 Generator trip. Kohler will investigate the issue and replace the sensor if required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621804&prj=263&rqi=CRss5WOfYzHOnVxYZ1vptpJ3gy
GI-625 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | Mechanical - TEST 7.10 HLT - Valve actuator communication alarm - when re instated the temperature increased above SLA - Suspected Valve closing during communication failure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621805&prj=263&rqi=DSzUXziOdV8Xo8SNLeFX5hRRj1
BT1MECH-529-045 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | Mechanical - RAS04 - Point 17&18 reading -0.34 Installed but not programmed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621831&prj=263&rqi=o3bBY3SnOTJRYfczpl4Dr1Pu1u
GI-411 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | jayb@straightlineconsulting.co.uk | 2026-05-07 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design | HVAC | equipment | MSB_R2 -Room - CRAH | CRAH Switch Room Redundancy Test |  |  | when UPS is on full load the room temp exceeds higher UPS temp limit causing UPs R2 to inhibit battery charging and derating of UPS output occurs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620657&prj=263&rqi=Sf4m1BWsTob46SHzJa6jz9eeAj
YT1DCOS-274-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-29 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Not Correct | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_55 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - CYT. Phase 2 asset fed from Phase 1. Temp cable installed for energisation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619886&prj=263&rqi=fUAvFzWgxFIb1iqbHGvc3f3MpG
YT1DCOS-223-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-29 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Not Correct | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_21 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - no main earth from HMI panel to containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619895&prj=263&rqi=II80lMlfMPXGtBquIy6FGpMes1
YT1DCOS-226-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-29 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Not Correct | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_24 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - no main earth from HMI panel to containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619885&prj=263&rqi=KqMSM7qvtYWk0yjpwNBbIMvsaK
GT1MECH-724-001 | PA12x-1 | N-EMEA | Closed | Outstanding Paperwork/Documentation | emanuelp@straightlineconsulting.co.uk | 2026-04-28 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Documentation Not issued/ Required | Commissioning | Plumbing | equipment | 1PSET_A_03 | CHWP - Cold Water Booster Pump |  | LOW - Lowara-xylem | MECHANICAL - live cable test report required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619710&prj=263&rqi=m3WG7FzH1Wv8fS0I8DBuvRZMTG
YT1MECH-648-731 | PA12x-1 | N-EMEA | Closed | Outstanding Paperwork/Documentation | emanuelp@straightlineconsulting.co.uk | 2026-04-28 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Documentation Not issued/ Required | Commissioning | Plumbing | equipment | 1PSET_A_03 | CHWP - Cold Water Booster Pump |  | LOW - Lowara-xylem | Mechanical - earthing report missing and permanent cable report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619711&prj=263&rqi=G4xdEGQe5TwaZjG9DQxPud8J1A
GI-404 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-04-16 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | During testing of the Vertiv cooling arrays in Data Hall 01 (PA12), the DP to DT changeover time was observed at 40â€“80 seconds, which differs from the 120 seconds specified in the Sequence of Operations. This issue is related to all CRAY units in the Data Hall 1. 1CA_M1R1_01 / 03 / 05 / 07 / 09 / 11 / 13 / 15 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618331&prj=263&rqi=rWRA9KyL66BNqXx7u9LisOzw5Q
GI-403 | PA12x-1 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-04-15 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Mechanical - CRAH's D string - When failing Return sensor, Fans Do not ramp up as per SOO. Vertiv engineer had to simulate by settings after to increase fan speed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618284&prj=263&rqi=0HrqTzPkSuqJW9tdPKVvCOWe86
GI-396 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Missing Valve Tags on the CW flexible hoses 1CA_M1R1_02 1CA_M1R1_04 1CA_M1R1_06 1CA_M1R1_08 1CA_M1R1_10 1CA_M1R1_14 1CA_M1R1_16 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617919&prj=263&rqi=NukBC5zgKZeASyBn5KTn7wxBND
GI-402 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-04-13 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Installation Not Complete | Commissioning | [6 empty] | The layout drawing for Data Hall 2 is incorrect. The CRAY units (shown in red) are positioned on the wrong side of the room, and the DP sensors (shown in blue) are also incorrectly located. Reference to the drawing: PA12-SC-IC-6140-ZZ-DC-BGMS-SCH (R06) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617961&prj=263&rqi=3u3scIakXa7HYmKpJ32QoSkgoZ
GI-400 | PA12x-1 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-04-13 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Damaged folder holder for documents/drawings to be repaired and secured in place. M1R1_15 M1R1_15 Extension M1R1_01 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617923&prj=263&rqi=CxvLuaxIEWIrRPHhn0MEHqooa2
GI-394 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-11 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | Fire Detection | system | Fire Detection |  |  |  | Electrical - Hellerman sleeve not used on cables in the following connection boxes ZDA074 ZDA075 ZDA076 ZDA077 ZDA078 ZDA089 ZDA081 ZDA073 ZDA072 ZDA071 ZDA066 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617869&prj=263&rqi=q1FoXFXRUa4Gfl657V26DBAciR | https://equinix.facilitygrid.co.uk/x/project/263/system/14098
RT1FD-181-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-11 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Installation Not Correct | Commissioning | Fire Detection | equipment | ZDA121/12150 | ASDP - Aspirating Smoke Detection Panel |  |  | Electrical - ZDA121. No hellerman sleeve used in vesda or connection box. Silver pipes covered in paint. Trunking lid doesn't fit properly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617870&prj=263&rqi=2c6bxguHFl8MDLYh2UqH8k7KKG
GI-393 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-11 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | Fire Detection | system | Fire Detection |  |  |  | Electrical - Hellerman sleeve not used on cables in the following connection boxes ZDA090 ZDA084 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617868&prj=263&rqi=gvDGmKf7EobnWkVoJzJ7GzJUZT | https://equinix.facilitygrid.co.uk/x/project/263/system/14098
GI-395 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-04-11 04:00:00.000 +0400 | General Contractor - Electrical |  | Cleaning | Commissioning |  | equipment type |  |  |  |  | Electrical - All Vesda pipes to be cleaned. most are covered in paint | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617873&prj=263&rqi=qvGdEWNsyoRbkLGnUnGLnNc7wj
YT1DCOS-273-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | mirceag@straightlineconsulting.co.uk | 2026-04-11 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Damage | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_54 | DCOS - HMI Panels |  | SCH - Schneider | Small paint chips and minor surface damage observed on the panel door exterior. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617836&prj=263&rqi=pJSWF7iFR6vnBXF2ABbaPuAfX0
SOR-2412-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [6 empty] | no labelling on the main power supply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617673&prj=263&rqi=jTthlkkGuqi48VrE297et6UNzi
SOR-2410-001 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | tayebb@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Electrical |  | Commissioning Issue | Commissioning | [6 empty] | earthing cable not terminated need to be reviewed by electrical vendor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617672&prj=263&rqi=TpoQmgJ9WABe5SKmZKrm2zwqJc
SOR-2412-002 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation Not issued/ Required | Commissioning | [6 empty] | no drawing present in the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617674&prj=263&rqi=GfmxLHUYsLIZfWrWlwpn8ebvmc
GI-390 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-27 04:00:00.000 +0400 | General Contractor - Electrical |  | DCOS Installation Not Complete | DCOS |  | equipment type |  |  |  |  | Electrical - No earth torque marks on DCOS_1_HMI panels between HMI and Door THIS ISSUE APPLIES TO ALL DCOS_1_HMI PANELS 1-50 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616649&prj=263&rqi=6yNo8bPtlhSLarLFYHEx1GTm0m
GI-388 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | stephenturner@sygna-emea.com | 2026-03-24 04:00:00.000 +0400 | Equinix Project Manager |  | Installation Not Correct | Commissioning | [6 empty] | the cables powering up the load banks in data hall 2 are passing through an open door into the data hall, these door are not forced open the door could close on the cables and damage the cables. the data hall is live and multiple door are open on the data hall letting dirt into the hall. this is also a safety issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616287&prj=263&rqi=gCbbU6aXHmAJ4o9yNElrIt4Rfy
BT1MECH-428-035 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-03-20 04:00:00.000 +0400 | Design Professional | L4 | General Design issue | Design | HVAC | equipment | UPS R1 Room - CRAH | CRAH Switch Room Redundancy Test |  |  | Mechanical - CRAH Redundancy testing, Whilst CRAH 8 is failed and running on CRAH 7, With the distance between the UPS & CRAH, the heat coming off the UPS is not reaching back to the return temperature on CRAH 7 and putting demand on. Temperatures on UPS reached in over temperature alarm at 36-37 degrees. No further increase as temperature values but clear indication the circulation in the Ventilation getting back to 'load' the CRAH. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616060&prj=263&rqi=m0AOHil7Qi5TPZBzUGzeMMb5Eb
BT1MECH-428-036 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-03-20 04:00:00.000 +0400 | General Contractor - BMS | L4 | Component/Equipment Failure | Commissioning | HVAC | equipment | UPS R1 Room - CRAH | CRAH Switch Room Redundancy Test |  |  | Mechanical - Whilst testing CRAH Redundancy testing, TT01 sensors were not working correctly. DCOS confirmed they changed parts with phase 2 panels but scaling from 40-50 are different. All TT01 / dcos panels linking to temperature sensors need all retesting and calibrating with a data logger. for this test we will have to rely on Data loggers. if BYES Fail to supply data logger trends a retest under full load will be required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616069&prj=263&rqi=6jKGiOu6Xov3j9kAmdJuyhF5sM
RT1DCOS-272-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-19 04:00:00.000 +0400 | General Contractor - Electrical | L2 | Installation Damage | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_20 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Damaged Perspex screen | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616033&prj=263&rqi=JiTPD3FRKtwQZzCp3jRYGBqDqX
RT1DCOS-265-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-19 04:00:00.000 +0400 | General Contractor - Electrical | L2 | Installation Damage | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_13 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Damaged Perspex screen and damaged internal plastic trunking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616032&prj=263&rqi=wGag6nWWNGcw1uAzzcskbdI3PL
RT1FS-302-010 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-03-18 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Installation Not Complete | Commissioning | Fire Suppression | system | Fire Dampers - Ground Floor |  |  |  | Mechanical- 1SD_NC_0031 - cabling / Conduit to be fixed correctly after floor resin laying | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616371&prj=263&rqi=ng7Lht39hR2XxQmeYUInR632eU | https://equinix.facilitygrid.co.uk/x/project/263/system/11600
GI-386 | PA12x-1 | N-EMEA | Closed | P3 Low CX | stephenturner@sygna-emea.com | 2026-03-18 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | on Facility grid on a weekly basis the numbers change for the Total Activities. these changes for each level of tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615969&prj=263&rqi=xQawtWlBZ2cDIW8U8gVbKxwKlU
GI-389 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-03-18 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | Mechanical- conduit to be re connected correctly after floor resin install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616372&prj=263&rqi=0epHlEoDfxToSkHb9yu4p7vbll
SOR-2317-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | Mechanical 1FCU_M6_158 Drainage not completed Bone tag missing Earthlings missing Cleaning needed Drip tray missing Torque mark missing on the Isolator Labels are missing on the income | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615802&prj=263&rqi=3MdQOVrxVxhLUppQbIVh9ESQuI
SOR-2329-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [6 empty] | Mechanical: Poste 5 Bone tag missing proper support for the cables ID to be visible | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615845&prj=263&rqi=Ct6cZ2qPuAGpDW1BtT6oIhQ9qG
SOR-2322-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | 1FCU_M6_155 Torquin is missing on the isolator Labels are missing on the wiring Labels are missing on the drainage Cleaning needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615807&prj=263&rqi=jBxhQurruyS6SEoUmcCrqQJbb6
SOR-2320-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | 1FCU_R2_157 Bone tag missing The label on the drainage is missing Torque mark missing on the isolator Cleaning needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615805&prj=263&rqi=eFfBJ8rSkzqTHhDS5lKBcuPOKz
GI-381 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Incomplete Connections | Commissioning | [6 empty] | CYT 1DB_M1R1_8_1 Conditional - Conditional yellow tag applied to unit - Issue will ONLY be closed once permanent supplies are installed and all documentation issued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615790&prj=263&rqi=OamgsFh6vcSUDbRi5ZjDHXTVlC
GI-383 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | Mechanical 1FCU_M5_160 Drainage not terminated Bone tag missing Earthlings missing Cleaning needed Torque mark missing on the Isolator Labels are missing on the income to the isolator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615803&prj=263&rqi=vVi9PoRNP3I4CpG09uigKmxc1H
GI-382 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [6 empty] | CYT 1DB_M1R1_13_1 Conditional - Conditional yellow tag applied to unit - Issue will ONLY be closed once permanent supplies are installed and all documentation issued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615791&prj=263&rqi=JsyH9XhVpI16b9UPgQtW4z2eZ1
GI-380 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Incomplete Connections | Commissioning | [6 empty] | CYT 1DB_M1R1_8_1 Conditional - Conditional yellow tag applied to unit - Issue will ONLY be closed once permanent supplies are installed and all documentation issued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615789&prj=263&rqi=Xy5K88SqQ7DC2x8WFXCaNBoAbp
SOR-2328-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [6 empty] | Poste 4 Bone tag missing ID not attached to the pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615844&prj=263&rqi=8vA7NoxTtqEIisHacTDG9VBEun
GI-379 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Incomplete Connections | Commissioning | [6 empty] | 1DB_M1R1_7_1 Conditional - Conditional yellow tag applied to unit - Issue will ONLY be closed once permanent supplies are installed and all documentation issued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615788&prj=263&rqi=QSmshV0RcjnD0zt3nSDSOq3lA6
SOR-2319-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | Mechanical 1FCU_M6_159 Drainage not terminated Bone tag Missing Earthlings missing Cleaning needed Drip tray missing Torque mark missing on the Isolator Labels are missing on the income to the isolator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615804&prj=263&rqi=580aEzC5ESXX26uqF4s3h5AFqX
SOR-2321-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | 1FCU_M6_155 Torquin is missing on the isolator Labels are missing on the wiring Labels are missing on the drainage Cleaning needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615806&prj=263&rqi=zlQCsKX4QE3jgTyn3BdNI9G1uN
SOR-2326-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | [6 empty] | Poste 6 ID tag missing Cable needs proper support Bone tags missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615842&prj=263&rqi=Ye3XW3pevFk95MppxkfSxwN9xn
SOR-2316-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | Mechanical 1FCU_R2_161 Drainage not completed Bone tag missing Earthlings missing Cleaning needed Drip tray missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615801&prj=263&rqi=zxha5Oz8Tnkij4VmfUZXdWtWsr
SOR-2323-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | 1FCU_M4_156 Torque marks are missing on the torque and the insulator Cleaning needed Bone tags missing ID is missing on the drainage and flow direction | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615808&prj=263&rqi=7yzExSbwtrh0mQZ5LlOWtXF2jG
SOR-2327-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [6 empty] | Poste 1 Bone tag missing ID not attached to the pipework | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615843&prj=263&rqi=cYw281UzHEm5ugAiQOacNbY1vq
RT1DCOS-229-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Electrical | L2 | Installation Damage | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_27 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Perspex screen broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615722&prj=263&rqi=unud1MmIxfEga1JM9UBGTpmx6L
YT1DCOS-237-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Not Correct | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_35 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Earth Cable sharing same entry gland as CAT6 cable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615724&prj=263&rqi=JEqqDTdR2A387RvMSFVudI7Xb6
GI-377 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | Mechanical: Bolts are loose on the CHWSTR. Remove the shipping brackets from the chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615719&prj=263&rqi=oRS74ku4jkVT95CReJWjviPAn7
YT1DCOS-228-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Damage | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_26 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Earth bonding incomplete | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615710&prj=263&rqi=V4JnYAjZhlVKBqBvzGMY0zc0lZ
RT1DCOS-224-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Electrical | L2 | Installation Damage | Commissioning | DCIM/DCOS | equipment | 1DCOS_1_HMI_22 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Perspex screen broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615721&prj=263&rqi=IDbRYBnPn5vTCvxcTXIW0KjyGL
GI-378 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [6 empty] | MECHANICAL: The bolts on the CHWSTR system are loose, and an extra bolt should be added. Please remove the delivery brakes from the chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615720&prj=263&rqi=ndSskGgeZOr289k0AZx0VEyIx8
GI-376 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-03-13 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS | [6 empty] | Mechanical- scaling on graphic to be amended 20l/s difference between flow meter and graphic | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615515&prj=263&rqi=lajPlf77ibHxR5dXU9WhOEwPFF
BT1MECH-402-030 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-12 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Installation Not Complete | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Mobile gent set pipework requires a plug/end cap on the valve. The cables and the terminal boxes to be tidied up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615452&prj=263&rqi=EPzbjEkQbaqH4yikV5vejHXS31
GI-375 | PA12x-1 | N-EMEA | Closed | P3 Low CX | stephenturner@sygna-emea.com | 2026-03-11 04:00:00.000 +0400 | Commissioning Authority |  | Installation Not Complete | Commissioning | [6 empty] | During the L4 Fuel testing, on the fuel system HMI Phase 2 equipment is visible and in Fault, at this moment in time works are unfinished in phase 2. this must be noted in the L4 script and rechecked when phase 2 is undergoing L4 testing . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615343&prj=263&rqi=m2XCwET47NYuKipwCe9XIC3rAF
BT1MECH-402-029 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-11 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Component/Equipment Failure | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - The HMI is freezing during L4, KOHLER team is fully aware about the issue but they cannot provide a solution. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615340&prj=263&rqi=jmhG7YmBcq1CU4b9BJ2l74znCh
BT1MECH-402-026 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-10 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | DCOS Graphics Issue | DCOS | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Police valve on HMI appears as Fire Valve Daily Tank --> Gen Set Pompier Valve Â appears on HMI as Fire Valve No1 Tank and Â No2 TankÂ The DCOS has the correct labellingÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615264&prj=263&rqi=yKkJVFIPwLMVTob60LJ8IiEhFg
BT1MECH-402-028 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-10 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | DCOS Graphics Issue | DCOS | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - HMI Graphics to be adjusted with correct labelling. Alarms description should be specific to the equipment: i.e. Alarm Police Valve GS M1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615297&prj=263&rqi=pUefpYVuA3sYxM7AkBgLDrJJZP
BT1MECH-402-027 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-10 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | DCOS Graphics Issue | DCOS | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - No Â alarm on HMI for pompier valve. There is Pompier Alarm on DCOS. Â Graphics issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615266&prj=263&rqi=v7NIYt5DhEcxlkSUdGMMQeChgT
BT1MECH-402-024 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-10 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Component/Equipment Failure | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Bulk tank 3, solenoid valves not responding on manual and close request. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615222&prj=263&rqi=oiyeuyApQ8N9KDSgtlK5SAqz6S
BT1MECH-402-025 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-10 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Cleaning | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - All bulk tanks require cleaning. Bulk tank 1 is used as a storage and bulk tank 2 is flooded from rain water. See attached pictures. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615259&prj=263&rqi=O87xLcl0ShNC41sSPiTernfsdq
BT1MECH-402-023 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-09 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Component/Equipment Failure | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - HMI not responding, issue with time response of HMI between tabs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615143&prj=263&rqi=TiDrvC60LnaApI4alf40LAYgWh
SOR-2284-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-03-06 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Installation Not Correct | Commissioning | [6 empty] | scratch on the front panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614903&prj=263&rqi=Jnk9rkAZGxbLhCRyRBVgYa7Z7z
SOR-2283-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-03-06 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Commissioning Issue | Commissioning | [6 empty] | scratch on the panel inside | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614902&prj=263&rqi=pNX1bXnxHG76N5owXGMZPZ48KM
GI-374 | PA12x-1 | N-EMEA | Closed | P2 Medium DCOS | joshw@straightlineconsulting.co.uk | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | DCOS/MECHANCIAL - TT01 in UPS Room M1 seems to be reading way off actual temperature off the room BYES/DCOS Team to provide document showing all TT's in phase 1 + calibrations commissioning is complete. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614799&prj=263&rqi=Td0oc8RoNgUb5s6ZIG2Bgki1hb
BT1MECH-402-022 | PA12x-1 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-03-04 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Design not as Specified | Design | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Fuel bulk tank set points are not matching the SOO. There is not enough fuel and have been adjusted to allow available tanks during the L4 test. Kohler to revert set points | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614707&prj=263&rqi=NNEoV8i3nqm8aRxxnQdKuroiHn
GT1MECH-729-062 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-03 04:00:00.000 +0400 | REH - Rehlko Gens | L3 | Installation Not Complete | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Ad Blu manifold Flow Sensor Missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614610&prj=263&rqi=NXNzepBt2bQq58hrJFDrkXx1Yi
GI-373 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | emanuelp@straightlineconsulting.co.uk | 2026-02-26 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | [6 empty] | 1CHWP_M1R1 01 Mechanical earthing not terminated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352222&prj=263&rqi=gSqDYbvpaOD8dlBqD3CW4aRhln
GI-372 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-26 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Damage | Commissioning | [6 empty] | Scratches on the pump 1CHWP_M1R1_02 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352221&prj=263&rqi=0Pzm0gB8KyzsOrf6PRP8JaBRpK
SOR-2258-002 | PA12x-1 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-02-25 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | drawing is not up to date as per checks on site picture attached should be Version 6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212868&prj=263&rqi=KY8xkaOWOlZnjkD0u3c9xZ9V9c
SOR-2354-004 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-24 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | Fire Detection | equipment | EAE_22 | EAE Fire Panels |  |  | No bone tags on Cables | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616000&prj=263&rqi=6uaObRuUlRfaAn6w3JDRmhbFju
SOR-2351-004 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | grantw@straightlineconsulting.co.uk | 2026-02-24 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning | Fire Detection | equipment | EAE_11 | EAE Fire Panels |  |  | Damage to panel Bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615999&prj=263&rqi=sHKCLBp9LVgcgvcFOB90eJ62wT
GI-371 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | grantw@straightlineconsulting.co.uk | 2026-02-23 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation Not issued/ Required | Commissioning | [6 empty] | ELECTRICAL L3 LIVE Cable test reports missing for the following cables\\\\\\\; CBL-1UMDSB_M1R2-01 CBL-1UMDSB_M1R2-02 CBL-1UMDSB_M1R2-03 CBL-1UMDSB_M1R2-04 CBL-1UMDSB_M1R2-05 CBL-1UMDSB_M1R2-06 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199773&prj=263&rqi=29MLapqORlqmPy64szQ2Qo2EuW
GI-387 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-18 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning | Fire Detection | equipment | EAE_18 | EAE Fire Panels |  |  | panel has damage to paintwork | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615997&prj=263&rqi=HySTPaTFdJ0afGh22G2JleYO8a
SOR-2340-005 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-18 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning | Fire Detection | equipment | EAE_19 | EAE Fire Panels |  |  | Paintwork damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615998&prj=263&rqi=Tt1IG3eEAmmPL5sBjcv808ed7W
RT1ELEC-634-393 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Installation Not Complete | Commissioning | Electrical â€“ LV | equipment | 1DCOS_1_OAP_1 | CP - Control Panel (Max Cool Announcement) |  | SCH - Schneider | 1DCOS_1_OAP_1 Mechanical: End Caps missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199345&prj=263&rqi=a9yzOXvasH04LTDuW9BIXxx98W
GI-370 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | adamb@straightlineconsulting.co.uk | 2026-02-16 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [6 empty] | Mechanical- flow meter from CHWP 5-2 Incorrect showing 30 l/s with pump running at approx 25 Hz when pump delivering approx 65l/s and running at 50 Hz | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199328&prj=263&rqi=cziBVjKJR9cu9sbmeC0ohtzSxq
GT1MECH-729-059 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-11 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Commissioning Issue | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - fuel level on alarm at 47% and 2minutes later the alarm disappears still at 47% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199062&prj=263&rqi=ztaCGjBLRDEhA2vlQ2s3R10YUc
GT1MECH-729-058 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-11 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Commissioning Issue | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Urea filling request on the HMI remains off during filling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199061&prj=263&rqi=7FRx0GE7DUvKkAyjycLuWfrvEn
GT1MECH-729-061 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-11 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Documentation Not issued/ Required | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Urea SOO L3 carried out based on R05 SOO, the R06 is for review Â at the moment and KOHLER advised that revision 7 (R07) will be the last oneÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199064&prj=263&rqi=DOdR68mdoR6BmHPVfRyzUEbgz6
GT1MECH-729-060 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-11 04:00:00.000 +0400 | REH - Rehlko Gens | L3 | Installation Not Correct | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Urea pump 1 - flexible hose stretch. To be replaced with the correct size | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199063&prj=263&rqi=kQuwN05FBtL5p4izF7xgmPtQrU
SOR-2199-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning | Fire Suppression | system | Sprinkler System |  |  |  | Sprinler fittings need touch-up painting Poste 28 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198925&prj=263&rqi=33mu4TtU6XCWfiEGRZNqr6FJZ6 | https://equinix.facilitygrid.co.uk/x/project/263/system/10985
GT1MECH-729-056 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Commissioning Issue | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - fuel low level alarm in SOO R06 is not matching with HMI setpoints. There is not enough fuel in bulk tanks to be able to have low level alarm at 50% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198927&prj=263&rqi=EB5GbViSsvDvJ1jXxjl18OG430
GI-361 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | Fire Suppression | system | Sprinkler System |  |  |  | Extra support needed and end caps on the bar Poste 28 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198924&prj=263&rqi=ClosnEVRhybBwxe9TmXtTb3NMz | https://equinix.facilitygrid.co.uk/x/project/263/system/10985
GI-360 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical |  | Torque required | Commissioning | Fire Suppression | system | Sprinkler System |  |  |  | Bolts not torqued Poste 28 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198923&prj=263&rqi=MF57Xw7ycTiRFCvCGa7rPkswCL | https://equinix.facilitygrid.co.uk/x/project/263/system/10985
SOR-2199-002 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical |  | Torque required | Commissioning | Fire Suppression | system | Sprinkler System |  |  |  | Sprinkler System Poste 12 Cx L2A 10/02/26 EP torque missing End caps missing Painting | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198926&prj=263&rqi=1ZSM7GlsFcwJguRkyRlLc6rMrK | https://equinix.facilitygrid.co.uk/x/project/263/system/10985
SOR-2196-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1CHWSTR_M3R1_8_ELC_1 | CP - Control Panel |  |  | Income power needs to be torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198882&prj=263&rqi=a5eU6nGh7gjwztCymTMntrCt7a
GT1MECH-729-057 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Commissioning Issue | Commissioning | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - graphics in hmi not matching with SOO and Equinix standards | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198928&prj=263&rqi=B8Ou6HSjxCI8ehRtwkwwauygRY
RT1FS-301-003 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-02-04 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Incomplete Connections | Commissioning | Fire Suppression | system | Smoke Dampers - First Floor |  |  |  | Electrical - 1SD_NC_0025 - exposed wire to be wagoed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198633&prj=263&rqi=lVsgdmvOHigP1gZu2pLdRNDhbV | https://equinix.facilitygrid.co.uk/x/project/263/system/11603
RT1FS-301-002 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Incomplete Connections | Commissioning | Fire Suppression | system | Smoke Dampers - First Floor |  |  |  | electrical_earth not connected or protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198249&prj=263&rqi=XanO71Kbv6Rq4aUFNiEX06WCM2 | https://equinix.facilitygrid.co.uk/x/project/263/system/11603
GI-356 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | stephenturner@sygna-emea.com | 2026-02-03 04:00:00.000 +0400 | Equinix Commissioning Manager |  | Commissioning Issue | Commissioning | [6 empty] | in all data halls permanent light must be on before energisation for PDCs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198246&prj=263&rqi=umy1rs71WVAtJtZ1xVcc8CGMSQ
GI-357 | PA12x-1 | N-EMEA | Closed | P3 Low CX | stephenturner@sygna-emea.com | 2026-02-03 04:00:00.000 +0400 | Equinix Project Manager |  | Installation Not Correct | Commissioning | [6 empty] | Earthing cable next to the transformer to be fixed in a better position see photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198247&prj=263&rqi=XCcrxasLnoZhasM1WS9hIQcWcr
SOR-2150-005 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | Fire Detection | equipment | EAE _06 | EAE Fire Panels |  |  | Electrical No Asset ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198255&prj=263&rqi=WS3eaTrdiBLwfG7Kn1bqSW6s4s
SOR-2150-004 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | Fire Detection | equipment | EAE _06 | EAE Fire Panels |  |  | Electrical i Cable ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198253&prj=263&rqi=8fdcCnTifM27RG66TqGjpV0gn8
SOR-2149-005 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | Fire Detection | equipment | EAE _05 | EAE Fire Panels |  |  | Electrical No Asset ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198252&prj=263&rqi=RAFqInAMmrYrenrIPTFx38fw5y
SOR-2150-006 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | Fire Detection | equipment | EAE _06 | EAE Fire Panels |  |  | Electrical no End caps in Trunking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198256&prj=263&rqi=irAImeSqGIVJLjWsikbO7hJgB4
SOR-2149-004 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | Fire Detection | equipment | EAE _05 | EAE Fire Panels |  |  | Electrical no End caps in trunking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198251&prj=263&rqi=jS14hru7Iuo4t8TAM0D0ZqpABE
SOR-2149-006 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | Fire Detection | equipment | EAE _05 | EAE Fire Panels |  |  | Electrical No Cable ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198254&prj=263&rqi=HttkKxaeiCi1FMe4uEE0rX3JXw
RT1FS-301-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Incomplete Connections | Commissioning | Fire Suppression | system | Smoke Dampers - First Floor |  |  |  | Electrical- earthing cable cut and not protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198248&prj=263&rqi=XTYwKtWLWjmDqs10UHgexSUaa5 | https://equinix.facilitygrid.co.uk/x/project/263/system/11603
GI-353 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | stephenturner@sygna-emea.com | 2026-01-29 04:00:00.000 +0400 | Equinix Project Manager |  | Installation Not Correct | Commissioning | [6 empty] | On all MVTB'S the MV cables have noÂ glandes, this will effect the IP rating and it seams that foreign objects will can enter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197940&prj=263&rqi=rCXB0fK6eAvHWIxdrQYEIFl6DR
GI-352 | PA12x-1 | N-EMEA | Closed | P3 Low CX | stephenturner@sygna-emea.com | 2026-01-29 04:00:00.000 +0400 | Equinix Project Manager |  | Installation Not Complete | Commissioning | [6 empty] | It is imperative that permanent lighting be installed in all data halls when electrical equipment is energized. Unfortunately, this is not currently the case in Data Halls 3, 4, and 5, and this issue requires immediate attention. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197937&prj=263&rqi=jYDvbxL7HstSrkglnplxAnRvBx
GI-355 | PA12x-1 | N-EMEA | Closed | P3 Low CX | stephenturner@sygna-emea.com | 2026-01-29 04:00:00.000 +0400 | Equinix Project Manager |  | Cleaning | Commissioning | [6 empty] | energised data hall are no condition to be energised due to poor house keeping planks of wood and other objects need removing and dust is also an issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197944&prj=263&rqi=VeieAxENNfR2gALo3cB6cDoRST
GI-354 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | stephenturner@sygna-emea.com | 2026-01-29 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | [6 empty] | on all transformers the earth cable is only connected with a cable tie this can fail in the future. there are only 1 torque mark on each tightened bolt 2 marks are needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197941&prj=263&rqi=raZAmVCzDWC34G5FgMxntlPdUE
GI-350 | PA12x-1 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-01-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Not Correct | Commissioning | [6 empty] | Mechanical - glands not in use to be capped off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197801&prj=263&rqi=hiG3Q6195BaBl6qwkCsMsIit0g
GI-349 | PA12x-1 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-01-28 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Correct | Commissioning | [6 empty] | Mechanical - exposed copper on secondary power supply L1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197800&prj=263&rqi=bekqU0wsD0fk5fGSEVYPZ5b32U
GI-351 | PA12x-1 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-01-28 04:00:00.000 +0400 | General Contractor - Mechanical |  | Torque required | Commissioning | [6 empty] | Mechanical - earthing torque marks required in all three panels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197802&prj=263&rqi=wtsF8klfjTGbWB5WN1OtjjA4vb
SOR-2126-002 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-28 04:00:00.000 +0400 | General Contractor - Electrical |  | Cleaning | Commissioning | [6 empty] | Electrical BB requires cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197796&prj=263&rqi=QHrKS6NLNcjT0hQRrmxTh5yNrH
GI-345 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Correct | Commissioning | [6 empty] | Electrical- Conduit to be fitted correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197673&prj=263&rqi=9xqpvaPnnI8UzM5JWgyKPMM9mo
GI-346 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Damage | Commissioning | [6 empty] | Mechanical- Coil Fins to be combed prior to energisation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197674&prj=263&rqi=UxgoyIqY0DdjtPY5geElmSq8ej
GI-347 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [6 empty] | Electrical- No Bone Tag fitted and Conduit to be made good (1CU_M1R1_29) Gen Building Roof | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197676&prj=263&rqi=wG2bfUK5sJsFysxX9d6wvHaTsX
GI-344 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [6 empty] | Electrical- No Bone Tag Fitted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197672&prj=263&rqi=FIbVkEhahVDVXFdvppZnXvbPIk
SOR-2105-005 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [6 empty] | Electrical- Fire cable to be supported by cable tray and conduit to be made good | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197666&prj=263&rqi=yj8El9e9eqWAMeqwAVB3U0yeKL
SOR-2076-004 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-22 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | [6 empty] | Electrical - containment to be re routed to gain access to Fire damper Acuator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197464&prj=263&rqi=zDgVdjTB8jEHCMBw4UpJptgyFM
SOR-2074-004 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-22 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [6 empty] | Electrical- Containment to be extended for Fire Cables | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197462&prj=263&rqi=PSitoCDCplALcqL8tWDoYfFCos
YT1FS-303-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-22 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Cleaning | Commissioning | Fire Suppression | system | Smoke Dampers - Ground Floor |  |  |  | Mechanical - All Data Hall 1 & 2 Low level ductwork behind dampers to be cleaned and to be free of dust and debris before Fan start up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197445&prj=263&rqi=Fx9SfyMXubDkvAWsRMkC3GLfzu | https://equinix.facilitygrid.co.uk/x/project/263/system/11604
YT1FS-305-001 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-21 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Labelling | Commissioning | Fire Suppression | system | Smoke Dampers - Second Floor |  |  |  | Electrical - All Bone Tags to have correct reference in Data Hall5 & Data Hall 6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197352&prj=263&rqi=zeuPfLlLoRNHB39ha5onvGRQJr | https://equinix.facilitygrid.co.uk/x/project/263/system/11605
SOR-2083-005 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-20 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [6 empty] | Life Safety No Asset ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197468&prj=263&rqi=5iBzvsui7c1t8bUKtuszuOJ83P
RT1FS-304-023 | PA12x-1 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-20 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning | Fire Suppression | system | Fire Dampers - Second Floor |  |  |  | Electrical - All bone Tags to Low Level Smoke Dampers in Data Hall 5 have incorrect reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197303&prj=263&rqi=sgpHZ5otDIgnGni107VdDRMGPc | https://equinix.facilitygrid.co.uk/x/project/263/system/11602
GI-342 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-19 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [6 empty] | Electrical Holding down bolt for Rear compartment Section 2 the thread is worn/ Criss threaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197191&prj=263&rqi=p930kRRNcmVvt6WzAU67ezrWSS
GI-340 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-15 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | [6 empty] | Electrical No Ferrels on Earth cables | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197016&prj=263&rqi=ee188Fys6gYCTaJsWLrQKrAVIR
SOR-2049-006 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Cleaning | Commissioning | [6 empty] | Electrical Panel requires repaint/ Cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197015&prj=263&rqi=PZPb2MjkycGGyXdYIt18QZsTgp
SOR-2049-005 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Documentation Not issued/ Required | Commissioning | [6 empty] | Electrical Drawings need to be updated as | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197014&prj=263&rqi=sNA7AnCPu1UtbqE8aKQpGjKu23
GI-339 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [6 empty] | ELECTRICAL Torque on BB messy need to be cleaned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196805&prj=263&rqi=SjbLEJA4QVqW5sPf00ILK4D6ga
SOR-2032-002 | PA12x-1 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | Electrical No Red Tag QR code for Yellow tag to be placed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196808&prj=263&rqi=dewM7vv95awRSfL0IR6SPGFsfI
GI-338 | PA12x-1 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [6 empty] | Mechanical - cable tray earthing missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196486&prj=263&rqi=cL6889VpzHavNqohVmPtLe1XT2
FPT-765-001 | PA13x-2 | N-EMEA | Closed | Outstanding Paperwork/Documentation | gregm@straightlineconsulting.co.uk | 2026-04-14 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation Not issued/ Required | Commissioning | Mechanical â€“ Water | system | PA13.2 Post Sec Chilled Water System Integration Verification Test Script |  |  |  | Mechanical - MER /KES to issue the results from the on site water analysis test taken 18/3/26 of the Sec CHW system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618095&prj=406&rqi=Cc9Y9zLRRDRcPTxqpAdqlB8ALB | https://equinix.facilitygrid.co.uk/x/project/406/system/14161
GT1MECH-450-001 | PA13x-2 | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-03-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Installation Not Complete | DCOS |  | equipment | 1-MVHR-M5-1 |  |  |  | 1-MVHR-M5-1 DCOS and temp checks not carried out by DCOS team and Temperatures to be taken,. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616192&prj=406&rqi=zIItoWU92JFiwSWJ1zyL9OIztu
DCIML4-1-001 | PA13x-2 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-18 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCIM Cooling Zone issue | DCIM | Controls | system | DCIM |  |  |  | Location Vectors missing for Leak detection phase 2 assets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615974&prj=406&rqi=jsobYordxxClYzOr0QVfLTV5TY | https://equinix.facilitygrid.co.uk/x/project/406/system/11776
DCIML3-1-001 | PA13x-2 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-18 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCIM Sync service Issue | DCIM | Controls | system | DCIM |  |  |  | Template Valve not upserted on DCIM | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615972&prj=406&rqi=uHtEJv2BA0tgMBOfZUH1BGzCzK | https://equinix.facilitygrid.co.uk/x/project/406/system/11776
FPT-763-001 | PA13x-2 | N-EMEA | Closed | Outstanding Paperwork/Documentation | gregm@straightlineconsulting.co.uk | 2026-03-05 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation Not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | Cooling String 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12 String Failure | Cooling String 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12 String |  |  | Cooling String 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12 String Failure test - As left settings still to be issued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614794&prj=406&rqi=1LMJHhUniaTGYhVJaQYKX9T6z7
FPT-762-001 | PA13x-2 | N-EMEA | Open | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-02-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS General Issue | DCOS |  | system | Fuel System |  |  |  | Fuel system Â Pressure switches on fuel pumps are sticking and need to be adjusted Pump 2 was alarming momentarily. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199774&prj=406&rqi=BjxyzC2Ir9FMLGCZqQxs25I6O2 | https://equinix.facilitygrid.co.uk/x/project/406/system/7699
GI-282 | PA13x-2 | N-EMEA | Closed | P2 Medium CX | michaeld@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Component/Equipment Failure | Commissioning |  | equipment | 1-ATS-JR2-1 |  |  |  | Electrical - During IST J it was noticed that ATS-JR2-1 was in alarm and not switching to redundant source. A thorough investigation is required by ITEC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197670&prj=406&rqi=1K3uay8eAFFypkBZXvlnfO6TTH
WTIST-15-004 | PA13x-2 | N-EMEA | Closed | P2 Medium CX | seanh@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | SCH - Schneider Electric |  | Commissioning Issue | Commissioning |  | equipment | IST Phase 2A Hall I | Intergrated System Test Phase 2B I |  |  | Electrical - Failure of Utility (Test 1) during transfer to Gen after the Generator start signal was confirmed however the generator breaker failed to remain closed on 2 occasions. 51N was the ansicode that was received at the time of failure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196784&prj=406&rqi=kFFKPdCFgPd7pekgHhL73vMZRt
L3-13-002 | PA13x-2 Mickey | N-EMEA | Open | P3 Low CX | richardw@straightlineconsulting.co.uk | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Documentation Not issued/ Required | Commissioning |  | system | FIRE - Fire detection / Alarm system |  |  |  | Documentation - Latest documentation related to the tests performed for the DH. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631412&prj=554&rqi=bI9n4LgcdD1wio5VMmCeo14PBG | https://equinix.facilitygrid.co.uk/x/project/554/system/13897
RT1MECH-424-001 | PA13x-2 Mickey | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | Fire Suppression | equipment | Fit Out - MFD-3131 | FD - Fire Damper |  |  | Fire suppression Â MFD-3031 Damper label required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627576&prj=554&rqi=qjk7zt16yRmpJCJqJllMC1Z0o5
YT1MECH-439-001 | PA13x-2 Mickey | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Correct | Commissioning | Fire Suppression | equipment | Fit Out - MFD-3131 | FD - Fire Damper |  |  | Fire Suppression - MFD-3031 fire damper access panel in Mickey office badly cut in to ductwork sharp edges - CUT risk | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627572&prj=554&rqi=3YyxJVXR7RXsDh2XnXN9WyPBQB
YT1MECH-439-002 | PA13x-2 Mickey | N-EMEA | Open | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation Not issued/ Required | Commissioning | Fire Suppression | equipment | Fit Out - MFD-3131 | FD - Fire Damper |  |  | MFD-3031 - Chubb Cable test docs missing for MFD | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627578&prj=554&rqi=qlDIof8RFIdXT2XX1ietrS50D5
YT1MECH-438-002 | PA13x-2 Mickey | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation Not issued/ Required | Commissioning | Fire Suppression | equipment | Fit Out - MFD-3130 | FD - Fire Damper |  |  | Fire Suppression MFD-3130 GC YT checklist missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627581&prj=554&rqi=3eWObBAuafIF8zTCgLyO8kn9RM
RT1MECH-423-001 | PA13x-2 Mickey | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | Fire Suppression | equipment | Fit Out - MFD-3130 | FD - Fire Damper |  |  | Fire Suppression - MFD-3030 ID label missing from actuator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626707&prj=554&rqi=99BDpBhakYMd70fWsTo0F0v8Oy
RT1MECH-423-002 | PA13x-2 Mickey | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning | Fire Suppression | equipment | Fit Out - MFD-3130 | FD - Fire Damper |  |  | Fire Suppression - MFD-3030 fire damper access panel in Mickey office badly cut in to ductwork sharp edges - CUT risk | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626710&prj=554&rqi=ZtA27JODceJQDRhENmaXXlB3Ht
YT1MECH-438-001 | PA13x-2 Mickey | N-EMEA | Open | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-06-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation Not issued/ Required | Commissioning | Fire Suppression | equipment | Fit Out - MFD-3130 | FD - Fire Damper |  |  | Fire Supression MFD-3130 Chubb cable test doc required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625340&prj=554&rqi=JSanyTTT3SZ57sDRSU0jJz2lJV
L3-10-001 | PA13x-2 Mickey | N-EMEA | Closed | P3 Low CX | richardw@straightlineconsulting.co.uk | 2026-06-11 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Documentation Not issued/ Required | Commissioning |  | equipment | 3-PA-11 |  |  |  | Mechanical - 3-PA-11 Missing documents ( Updated drawing, System) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624919&prj=554&rqi=XMUQkcqqiQed9JEEAFCWfjLFA9
GI-236 | PA13x-2 Mickey | N-EMEA | Closed | P3 Low CX | richardw@straightlineconsulting.co.uk | 2026-06-10 04:00:00.000 +0400 | General Contractor - Electrical |  | Commissioning Issue | Commissioning | [6 empty] | Electrical - Missing Arc Flash label for DB, STS and UDP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624754&prj=554&rqi=gudmHHcNxWEdKA03J6WwbGSMj8
GT1ELEC-510-002 | PA13x-2 Mickey | N-EMEA | Open | P2 Medium CX | richardw@straightlineconsulting.co.uk | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | Electrical | equipment | Fit Out - Lighting / Emergency Lighting | LITE - Lighting Control |  |  | Electrical - Confirm LUX levels have been checked against global standards (normal lighting). Lux levels not achieved - Minimum 500 lux | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622452&prj=554&rqi=QTIFXtP7XBygAU6jGoFk6V8q1q
GT1ELEC-510-001 | PA13x-2 Mickey | N-EMEA | Open | P3 Low CX | richardw@straightlineconsulting.co.uk | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | Electrical | equipment | Fit Out - Lighting / Emergency Lighting | LITE - Lighting Control |  |  | Electrical - Confirm all associated distribution panels for lighting controls and power have been level 3 commissioned and signed off accordingly. DALI system needs to be reviewed and handed to OPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622449&prj=554&rqi=g1BCM0641W3LdTmy41FCbWDeG2
L3-13-001 | PA13x-2 Mickey | N-EMEA | Open | P2 Medium CX | richardw@straightlineconsulting.co.uk | 2026-05-19 04:00:00.000 +0400 | Equinix Commissioning Manager | L3 | Commissioning Issue | Commissioning |  | system | FIRE - Fire detection / Alarm system |  |  |  | Confirm that battery back-up autonomy meets specification (isolate mains supply for â€˜24â€™ hours then operate fire detection and ensure sounders operate for specified time) Battery needs to be replaced and test needs to be re-done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622265&prj=554&rqi=G9dURdRtwWuJUtKo5s1kBLqiLb | https://equinix.facilitygrid.co.uk/x/project/554/system/13897
GI-235 | PA13x-2 Mickey | N-EMEA | Closed | P3 Low CX | richardw@straightlineconsulting.co.uk | 2026-05-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | [6 empty] | Electrical - Missing labels on all busbars | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620116&prj=554&rqi=UmE2mg9pAvK7vBXxxRvcZLtXPi
GI-021 | PA13x-SWGR | N-EMEA | Closed | P2 Medium CX | Iuliant@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | VER - Vertiv Electrical |  | Comms Issue/Fault | DCOS | Electrical | equipment | 1-COP-D2 | COP - Customer Operating Panel |  |  | Circuit breakers B12;C2;C3;C4 show issues/fault on DCOS trip status . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198862&prj=526&rqi=0jG50o9CK43cp5KTmK0gir9S3J
SOR-52-003 | PA13x-SWGR | N-EMEA | Open | P3 Low CX | Iuliant@straightlineconsulting.co.uk | 2026-01-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS not Complete | DCOS | Electrical | equipment | 1-COP-D1 | COP - Customer Operating Panel |  |  | Confirmation is required regarding the current status of the MCB for COP-D1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196646&prj=526&rqi=9WRcyogLsywuS5ng8VztL5ARKf
SOR-72-004 | PA13x-SWGR | N-EMEA | Closed | P3 Low CX | Iuliant@straightlineconsulting.co.uk | 2026-01-09 04:00:00.000 +0400 | VER - Vertiv Electrical |  | Labelling | Commissioning | Electrical | equipment | MSB-D | MSB- Main Input Switchboard |  |  | MSB-D Bus-bar Phase Sequence Label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196647&prj=526&rqi=4Rm6ptqb5a4IuvdOPdmfFuDlnk
SOR-413-001 | PA14-1 | N-EMEA | Open | P2 Medium CX | emanuelp@straightlineconsulting.co.uk | 2026-09-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation not complete | Commissioning | [6 empty] | AFIRE_A_01_DMP_03 Hoses were routed through the damper, preventing verification that it could close fully and operate correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638494&prj=553&rqi=7FPFn4Cwp6MpDzFgyA2wEPjh9S
L2L3 Sun-166-001 | PA14-1 | N-EMEA | Open | P3 Low CX | steved@straightlineconsulting.co.uk | 2026-08-14 04:00:00.000 +0400 | General Contractor - Electrical |  | Incomplete Connections | Commissioning | Electrical â€“ MV | equipment | 1HMTX_1 | HMTX - Primary Substation Transformers |  |  | Thermal Relay fed by temporary power, needs a permanent supply, and has a temporary label, plus has a few scratches on the door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633621&prj=553&rqi=occcyUHaJTfqC8greiClf4dz1a
GI-017 | PA14-1 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [6 empty] | 1PCP_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625301&prj=553&rqi=oyl8tobPhIA1cDV8J40ixJDweH
GI-018 | PA14-1 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [6 empty] | 1PCP_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625302&prj=553&rqi=yBctStcsI543b7cFg6S7n921qp
GI-019 | PA14-1 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [6 empty] | 1PCP_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625303&prj=553&rqi=LYNfjXnKZIhv6oc2bpY1XR9bNz
GI-016 | PA14-1 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [6 empty] | 1PCP_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625300&prj=553&rqi=wl8fRBjGWuCeyL5sZgbtk2qJLX
GI-015 | PA14-1 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-14 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [6 empty] | 1PCP_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625293&prj=553&rqi=WE1QIZ8msMUDG5bOXgyOoaD3zm
GI-012 | PA14-1 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-09 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Commissioning Issue | Commissioning | [6 empty] | 1UDP_C2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624695&prj=553&rqi=5OqtReLKfFsHNiwLikhE0cCXLS
GI-011 | PA14-1 | N-EMEA | Open | P3 Low CX | hajar.banan@spie.com | 2026-06-04 04:00:00.000 +0400 | SOC - Socomec |  | Commissioning Issue | Commissioning | [6 empty] | 1STS_C2R_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623938&prj=553&rqi=cEVfdEWURQt2ar0z5b6Fh74Oel
RT1ELEC-12-001 | PA14-1 | N-EMEA | Closed | P3 Low CX | steved@straightlineconsulting.co.uk | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider MV | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1GRMU_B | GRMU - Generator Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme. Missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623599&prj=553&rqi=NuRAAH9NgekWfJHp3VvcujGWdp
RT1ELEC-11-001 | PA14-1 | N-EMEA | Closed | P3 Low CX | steved@straightlineconsulting.co.uk | 2026-05-26 04:00:00.000 +0400 | SCH - Schneider MV | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1GRMU_A | GRMU - Generator Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme, labels missing for breakers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623136&prj=553&rqi=qxIeKjK9UTTMK6199MefEfIvoU
RT1ELEC-11-002 | PA14-1 | N-EMEA | Open | P3 Low CX | steved@straightlineconsulting.co.uk | 2026-05-26 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning | Electrical â€“ MV | equipment | 1GRMU_A | GRMU - Generator Ring Main Unit |  |  | Verify the switchgear tool board is secured to a wall. Missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623137&prj=553&rqi=XdOvbjoNa0OqJKZsmuVczcUzlQ
GI-010 | PA14-1 | N-EMEA | Closed | P2 Medium CX | simonm@straightlineconsulting.co.uk | 2026-03-26 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | system | CWTR |  |  |  | Installation in progress without approved test packs/QA process in place. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616658&prj=553&rqi=9ZqGBkra1fGyOoENWVNhlhzM75 | https://equinix.facilitygrid.co.uk/x/project/553/system/12491
GI-008 | PA14-1 | N-EMEA | Open | P3 Low CX | simonm@straightlineconsulting.co.uk | 2026-02-25 04:00:00.000 +0400 | Project Manager |  | Design not as specified | Design | [6 empty] | Mechanical - Technical Submittal of TW240. The approved tech sub has a statement on page 13 stating that the CHW return temperature must be reduced to from 28Deg C to 27.4Deg C, achieved by increasing the flow through the balancing valves. And on page 15 the return air temperature to be increased from 37Deg C to 37.5Deg C This means that all the assets withing the CHW system will need to have recalculated specification to accommodate this, but there doesn't seem to be addressed anywhere. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221135&prj=553&rqi=YqhFQ9E8l1S9MGZCV80NsEBiBR
GI-002 | PA14-1 | N-EMEA | Open | P3 Low CX | steved@straightlineconsulting.co.uk | 2026-01-19 04:00:00.000 +0400 | SCH - Schneider MV |  | Documentation not issued/ Required | Commissioning | [6 empty] | Electrical - Issue found during FWT of PUSP Panel :- â€¢ Schneider: To update the nameplate of each cubicle according to SPIE instructions and Equipment naming to be added to each panel like : 1PUSP_1 / 1PUSP_2 â€¢ Schneider: To add the cell serial number to the PUSP schematics to avoid errors during assembly â€¢ Schneider: Key number: R1T to be differentiated between the 2 stations according to SPIE's instructions (R1T_1 / R1T_2) â€¢ Schneider must provide the connection recommendations (Cable heads, etc.) â€¢ Schneider: Place a warning label on the emergency stop button of each PUSP panel. â€¢ Schneider: To update the schematics by taking into account the various issues raised. â€¢ Schneider: must submit to SPIE a control/monitoring cable schedule (eg. P643 cabinetâ€¦) following the same method implemented by Schneider MCE. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197156&prj=553&rqi=JsiC7HbXON9tcFU7UpfOgoO2JO
BT1MECH-1-006 | PA3-DH7 Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-30 04:00:00.000 +0400 | Equinix Project Manager | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | EPIVE 07,02,06 - Glycol Concentration 60% compared to other valves at 24% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616876&prj=676&rqi=jQondOlcDmSwggabbG7ZlD24zO | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
BT1MECH-1-005 | PA3-DH7 Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-29 04:00:00.000 +0400 | Equinix Project Manager | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | CDU status not changing to 'Tank filling' during pump fill process. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616804&prj=676&rqi=imYVxqglIxcOVsKC03357hYtcU | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
BT1MECH-1-004 | PA3-DH7 Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-27 04:00:00.000 +0400 | Equinix Project Manager | L4 | Labelling | Commissioning | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | All valves to be labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616705&prj=676&rqi=0dVdyXfIxf2bT4XkDeaYObOzr8 | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
BT1MECH-1-002 | PA3-DH7 Liquid Cooling | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-27 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Commissioning Issue | Commissioning | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | CDU-01 HMI not responding to some setpoint changes. Changes are reverting back to original settings after a few seconds. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616661&prj=676&rqi=mmLiX2oLyyvakAl7W6ySxr10Nd | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
BT1MECH-1-001 | PA3-DH7 Liquid Cooling | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-27 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Installation not correct | Commissioning | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | All CDU airvents installed with PTFE tape, some o-rings appear damaged/mishapen and some airvent caps are missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616660&prj=676&rqi=FWPW4VEGcMPPu6sUoJmr83HNxZ | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
BT1MECH-1-003 | PA3-DH7 Liquid Cooling | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-27 04:00:00.000 +0400 | Equinix Project Manager | L4 | Installation not correct | Commissioning | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | PTFE tape and brass/galvanised steel connections used on temporary connections to Manifold. All materials used must comply with wetted materials list and a suitable anaerobic sealant used instead of PTFE tape. PTFE tape can disintegrate and contaminate TCS/SFN causing blockages to filters and equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616663&prj=676&rqi=7QPBNPihib0qBbwzKVelPiETAf | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
GI-025 | RJ03-2 | AMER | Open | P3 Low CX | jesse.oliveira@b2dc.com | 2026-09-15 04:00:00.000 +0400 | Subcontractor |  | Installation not complete | Commissioning | [6 empty] | missing teamwork | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638235&prj=651&rqi=jtuT0rIndH9uPQsQLIdCQolF8c
GI-023 | RJ03-2 | AMER | Open | P3 Low CX | jesse.oliveira@b2dc.com | 2026-09-15 04:00:00.000 +0400 | Subcontractor |  | Missing Components | Commissioning | [6 empty] | Conduit box without cover | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638233&prj=651&rqi=Gu5maiTyFvRgkzJKuzOUorJBC8
GI-024 | RJ03-2 | AMER | Open | P3 Low CX | jesse.oliveira@b2dc.com | 2026-09-15 04:00:00.000 +0400 | Subcontractor |  | Installation not complete | Commissioning | [6 empty] | missing the support for the hydraulic line | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638234&prj=651&rqi=jRv3jYPSjqRAaB06t9AGFmMrcd
GI-022 | RJ03-2 | AMER | Open | P3 Low CX | jesse.oliveira@b2dc.com | 2026-09-10 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning | [6 empty] | The arc flash sticker was not found on the equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637624&prj=651&rqi=E0bciqBO4aDHkRqGqUhT5EuQ6r
GI-016 | RJ03-2 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-22 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Drawings are out of date within panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634807&prj=651&rqi=ZpUlcMDx89HGNcjwT8CVjobwdr
GI-018 | RJ03-2 | AMER | Open | P2 Medium CX | mt.uchoa.eng@gmail.com | 2026-08-22 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | VESDAs - Asbuilted and approved ASPIRE hydraulic calculation and isometrics not delivered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634809&prj=651&rqi=e9cXkzZ5GFM6q1lpxJ18knXh0U
GI-017 | RJ03-2 | AMER | Open | P2 Medium CX | mt.uchoa.eng@gmail.com | 2026-08-22 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Vesdas VEU-15 and VEU-16 installed in previous Phase 1: Existing pipes have not been removed. New pipes in circulation have not been installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634808&prj=651&rqi=rpOhV4hTtBBGwiEBMLFVLK7NvM
GI-015 | RJ03-2 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-22 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Drawings are out of date within panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634805&prj=651&rqi=sB0uqWCLFkYHiPNjcwjwW1ysSF
GI-006 | RJ03-2 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-20 04:00:00.000 +0400 | General Contractor |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | VESDAs - Batteries not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634527&prj=651&rqi=fxIv3C5X3prWuUA6zBxkvGjV6G
GI-007 | RJ03-2 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-20 04:00:00.000 +0400 | General Contractor |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | There are some loose clamps in sampling pipes - VES-03; VES-014; VEU-07; VEU-08; VEU-09; VEU-17 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634534&prj=651&rqi=MAxjDdJ5YydWEGTQ5U3zG2GHQN
GI-012 | RJ03-2 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-20 04:00:00.000 +0400 | General Contractor |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | VESDAS Model VES - Quick connect benchmark fiiting specified in design are not installed in endpoints. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634541&prj=651&rqi=V85YM4ibTrblD6qJBIq5YKN0cd
GI-013 | RJ03-2 | AMER | Closed | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-20 04:00:00.000 +0400 | General Contractor |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | VESDAs - Quick connect benchmark fittings specified in design are not installed in testpoints. -- Issue closed (repeated) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634542&prj=651&rqi=heAKtAWn44kg93xZ1gWTxlaEkN
GI-008 | RJ03-2 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-20 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | VESDAs - L2A GC checklist signed-off not presented. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634535&prj=651&rqi=XaRfe61xtDpFwtM3nJap2yAq8Y
GI-004 | RJ03-2 | AMER | Ready for Verification | P3 Low CX | Julio@b2dc.com | 2026-08-15 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | The LOTO procedure complete with organogram structure are not available on Sharepoint The LOTO procedure posted on SharePoint does not mention the equipment in Blocks B and C or how to lock them out | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633851&prj=651&rqi=BQPEmXWVk4sigrh1bYETtB5z4G
YT1ELEC-163-001 | RJ03-2 | AMER | Closed | P2 Medium CX | Julio@b2dc.com | 2026-07-30 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment type | TX - 480v-208/120 Transformer | TX - 480v-208/120 Transformer |  |  | The L2B documentation is not available on SharePoint for analysis and inspection of the equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631615&prj=651&rqi=OxxVGt3tnLMmEkXp8ukQxmNv8w
GI-002 | RJ03-2 | AMER | Open | P3 Low CX | cassiano.ferreira@b2dc.com | 2026-07-24 04:00:00.000 +0400 | SCH - Schneider Electric |  | Documentation not issued/ Required | Commissioning | [6 empty] | An analysis of the available documentation was conducted, and it was found that the documents listed below were missing, MSB, UDP e RMU-BTU. The torque wrench calibration certificate was not found on Asite The approved technical documentation (description) was not found on the Project Portal MCE was unable to find the electrical panel installation and operation manual on the Project Portal | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630749&prj=651&rqi=so8zMQ7MTsRrZyu1FguJkqyn9c
GI-001 | RJ03-2 | AMER | Ready for Verification | P3 Low CX | bruno@b2dc.com | 2026-05-22 04:00:00.000 +0400 | VER - Vertiv |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Actual Submittal evaluated from projects ""PW161 (AAN).pdf"" to CRAH Vertiv equipment requires additional specification described below: 1) Specification of the CRAH outlet air deflectors. This issue requires the aprooval from design for the specification of the air deflectors to be closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622830&prj=651&rqi=Zx3HkY0GGgpvSB91FFSzCBSpz2
L2L3 Sun-238-001 | SG03-P4 | APAC | Open | P2 Medium CX | MarcusGoh@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-5 | CPR2 - UPS |  |  | HMI OS and APP version for UPS-R-CPR2-5 differs from the approved setting list. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636549&prj=615&rqi=bMYA24HxbZIik0i4DYbY2VIf0J
GI-042 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-31 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical | equipment | DB MP-R-CPR2-02 | CPR2 - Mech DB |  |  | [Power Meter Test with PQMS]: During the test, the power factor readings for power meters F01 and F02 were displayed incorrectly on PQMS. In addition, the THD-V and THD-I readings for F02 were also not displayed correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636080&prj=615&rqi=HWWgrNangFEe2VtetnRsEITymc
GI-037 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | Redundant alarm notifications were observed in the BMS alarm log. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633599&prj=615&rqi=1Wq9eBm0Wu9Y6KLRAoAKsDAFWL
GI-041 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | No approved UPS setting list was available at the time of testing. Testing was initially conducted based on the UPS settings proposed by Eaton. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633603&prj=615&rqi=GZl5QAJO05LdTkMEuK3kVgmEXh
GI-034 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | Upon simulating high-level communication loss by disconnecting the CAT6 communication cable, no SMS notification was generated to AlertOps. As a result, Operations may not be aware of the communication loss. However, the BMS interface at the respective UPS displayed â€œ?â€ indicators against the affected AI points, indicating the loss of communication. BMS vendor to configure SMS notification as an alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633592&prj=615&rqi=ciJRIbM33ndLLa5DEvIBPGDbbw
GI-036 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | Battery remaining runtime was not displayed on the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633598&prj=615&rqi=tJfJDHgRbBp4TvPmviwJ0kyx2e
GI-035 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | The UPS has separate Overload and Output Overload alarms. When the Output Overload alarm was triggered, the corresponding Output Overload alarm was correctly received by the BMS. However, when the Overload alarm was triggered, the BMS continued to display Output Overload instead of the corresponding Overload alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633597&prj=615&rqi=vryAnuv6Y0EICmXh4guF8b9iK7
GI-040 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | SMS notification to AlertOps was not ready for testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633602&prj=615&rqi=m7bDrSaVA6PtNYPRgTao2Tr19s
GI-039 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | During Overload Stage 1 (110%â€“125% load), the inverter transferred to Static Bypass after 7 minutes 40 seconds instead of the required 10 minutes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633601&prj=615&rqi=AHKl7X7y2Ky1RHgFP9R8ZrCfbf
GI-038 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | During the battery discharge test, the BMS received a Low Battery alarm; however, the corresponding Low Battery alarm was not displayed on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633600&prj=615&rqi=rixtdD5e3IikqDvM9m7buMuFBT
GI-033 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | PLC-R-CPR2-01 | CPR2 - BMS |  |  | Revealed during Cx3 FCU with BMS: It was observed that the BMS graphics only display the FCU tag/name without indicating the corresponding room layout or the specific room served by each FCU. As the approved GUI was not available during the inspection, the BMS team shall update the graphics to include the room location served by each FCU. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630924&prj=615&rqi=E5826OrAPCwLW4NOSulXA4hkuS
GI-032 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | [CHSB Breaker Modification Works]: The BMS team shall update the GUI (SLD) in accordance with the approved naming convention and SLD. It was observed that CHSB CPR2 still shows an outgoing feeder to CP-CHWP. Therefore, the team shall ensure that the BMS SLD is updated prior to conducting the CHSB breaker modification works. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630921&prj=615&rqi=KUlKL2wtrS4TA9ObraAudbk4dd
GI-030 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Electrical | equipment | CP-FCU-R-CPR2-04 | CPR2 - FCU CP |  |  | There was no approved setting for overload thermal relay for both MV fans and FCU visible during inspection. WL to confirm with design consultant/LEW. This issue applicable to all 12 nos of FCU and 12 nos of MV Fan at CPR2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624675&prj=615&rqi=7yx6Xk3dqK8praDDhLfa2tddpg
GI-029 | SG03-P4 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | PLC-R-CPR2-01 | CPR2 - BMS |  |  | Few issues revealed during Cx2A for PLC panel: 1) Vendor to provide and submit the SLD/control diagram drawing for design consultant's approval. This drawing was not visible during inspection. 2) To update GA drawing as per built on-site. 3) There were two different MCB type installed for both PLC panels. One panel was equipped with Type B 6A while another one was equipped with Type C 6A MCB. To confirm with design consultant. 4) To install earth bonding between panel door and panel 5) To put component's sticker labelling for clarity | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623900&prj=615&rqi=qoAallBZ572mMosXxvWtL2oXEN
FPT-49-001 | SG04-4A | APAC | Closed | P2 Medium CX | MarcusGoh@commtechasia.com | 2026-08-09 04:00:00.000 +0400 | General Contractor | L4 | Installation not correct | Commissioning | Multi-Discipline | system | Heat Load Test (DH 5-2) |  |  |  | DH5-2 cold aisle temperature increased to 26.8Â°C at RLE Sensors 11 and 18 when the CHW ring valves between CRAC Units 9 and 10 were closed. It was also observed that one of the CHW ring valves between CRAC Units 8 and 9 was not fully opened. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632815&prj=663&rqi=1YtJBzJA7kh4Gxw5VDW9KcYf3g | https://equinix.facilitygrid.co.uk/x/project/663/system/14481
FPT-16-002 | SG04-4A | APAC | Closed | P2 Medium CX | MarcusGoh@commtechasia.com | 2026-08-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Installation not correct | Commissioning |  | equipment type |  |  |  |  | After the CRAC unit restarted following a power failure, the EBIV failed to open to Vmax as specified in the SoO. Instead, the valve returned to 0% open and resumed modulating based on the Supply Air Temperature (SAT) control logic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632816&prj=663&rqi=pv9LzVm20v72rhCcgMygxmFGnF
GI-050 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | CRAC did not fall back to local unit SAT setpoint when signal from Granular Control is lost. CRAC will be running based on last SAT setpoint commanded by Granular System. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629922&prj=663&rqi=RefhiHGWTNKl48KYVzMnw8yL4N
GI-048 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | 1. There are questions mark on top of all the faceplate in granular control overview page.Granular control 2. PLC connection status on graphic not ready, to be configured. 3. Existing Prosoft Gateway for RLE manger keeps showing alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629920&prj=663&rqi=hSWwfXCmYPskZiedG1lzKvZlg9
GI-049 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-19 04:00:00.000 +0400 | General Contractor |  | Component/ Equipment Failure | Commissioning | [6 empty] | RLE-24 temperature and humidity readings different with other sensors. The sensor was unable to recover back after RLE Wing Manager power failure test. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629921&prj=663&rqi=EKxgsYzJ5JCNi0vanZhefMdikp
GI-047 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Comms Issue/ Fault | DCOS |  | equipment type |  |  |  |  | When CU loss of power and communication loss with DCOS, there is no loss comm alarm at DCOS. Parameters loss comm but communication alarm still show inactive. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628312&prj=663&rqi=KgZnvnUmsSKhzEccQHkPS19Djy
GI-046 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Fire Mimic panel needs to reflect the latest battery room layout 5A and 5B. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628311&prj=663&rqi=BhVgyAQl3olWuonGGzBRVvW6Yd
GI-045 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | DCOS summary and face plate naming need to be changed from 5_BATTR_A_1_PREACT to 1-GSCP BATTR 5A and 1-GSCP BATTR 5B. Applicable for all gas suppression panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628310&prj=663&rqi=VD5ZGzNlCNMNhrvQZcnMGvhuCg
GI-044 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | To provide LEW endorsed drawing and place inside the LCP. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628136&prj=663&rqi=eoZZfoIBOWW4RumZSyx1bDdSWz
GI-042 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | 1. Rockwell is required to check whether the RLE sensor will still be included in the calculation when it is placed in maintenance mode. 2. Rockwell is required to check the meaning of the triangle with a question mark symbol shown on the RLE sensor graphic. 3. Two parameters are missing from the Machine Learning faceplate. Rockwell is required to add these parameters. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627195&prj=663&rqi=zqry6eN4SaMISFrVZ9WKmLhozg
GI-038 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | 1. The layout of the ProSoft and FiberTek communication gateways differs from the drawing. 2. The labeling of the ProSoft gateway does not match the drawing. 3. The quantity of the TB-24V1 fuses does not tally with the drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627098&prj=663&rqi=QZm36m2nHAEZJUx7bR1jrIJWuJ
GI-035 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | There is no labeling for smoke detector signal cables inside the unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626875&prj=663&rqi=VW2aBIPiqABe1oszQHmbullTrC
GI-031 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-21 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | 1. The installed manual release and abort switch for GSS are different with approved layout. 2. The installed Pre-action pipe and sprinkler head quantity/location are different with approved layout. 3. Location of pre-action sprinkler pipe drain point are different with approved layout. 4. The location of fireman intercom panel is different with approved layout. 5. There is no drawing placed inside the GSS panel. 6. The height of GSS panel installed is different with approved drawing. 7. There is no breathing apparatus installed outside the battery room. 8. There is no zone chart installed. 9. The painting of trunking and conduit need to touch up. 10. There is no zone chart installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626329&prj=663&rqi=Wq8cRneIERSZDVboSQhqDL1nm8
GI-032 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-21 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | 1. External fire modules are not labeled. 2. There is no labeling of all the cables inside the GSS panel. 3. There is no labeling of all pipes, conduit and trunking. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626330&prj=663&rqi=AG2hpEG74vTt7pq0jiXQlf9Oxj
GI-028 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-21 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | 1. Table of primary and secondary source need to be updated in LCP SLD as per site installation. 2. Battery room 5A equipment layout is different with the drawing. 3. The rating of fuse for LCP cooling fan is not tally with SLD, update in SLD is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626313&prj=663&rqi=zEYzFQyR2j8REUXS6bzM1mC68U
GI-029 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-21 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | 1. The name of LCP need to reflect actual room name "5A" and "5B". 2. MCB for damper, control and 230V XFMR inside the LCP are not labeled. 3. Fuse for cooling fan and power sensing "NSF", "ESF" are not labeled. 4. To provide labeling for incoming power cables. 5. Labeling of LCP trunking and conduit are inadequate and some are not labeled. 6. The fan isolators, hydrogen and methane sensor are not labeled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626314&prj=663&rqi=VKbfxDZp83UT51zRtsEQSYE3C3
GI-023 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | 1. There is no equipment labeling for condenser unit. 2. There is no circuit labeling for power isolator. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625562&prj=663&rqi=3pVQ6bHRRhajfV7rpHJkutKGtq
GI-024 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | 1. The gradient of condensate drain pipe has been lift up by power conduit, to rectify. 2. The condensate drain pipe armaflex insulation is incomplete and not properly sealed. 3. There is no equipment labeling on DxFCU and its thermostat. 4. There is no labeling on condensate drain pipe and trunking. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625566&prj=663&rqi=NgDVpdJCa7dpwsmuMPj4RdKGIt
GI-022 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | 1. All the labeling of outgoing cables terminal blocks are not tally with the circuit number. 2. The labeling of relay is not tally with the outgoing circuit. Refer to the photo attached. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621850&prj=663&rqi=eLEu6TNq89aPlN3HSQSBp5yMa4
DCOS-1-002 | SG04-4A | APAC | Closed | P2 Medium DCOS | MarcusGoh@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L1 | DCOS Template Issue | DCOS | [6 empty] | ERCS/QA required to raise RFI regarding the alarm severity that is not stated in SPL â€‚â€‚â€‚ UPS: - Blower fan failure 850 - Emergency power off 850 CRAC: - Loss of air flow 450 - Loss of power 650 - Supply air RH high / low 650 - Return air RH high / low 650 - Return air temp high / low 650 - SAT sensor failure 650 - RAT sensor failure 650 - RH sensor failure 650 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621310&prj=663&rqi=wN9Q6qEXACLiceG2pCmBjxnGQw
DCOS-1-001 | SG04-4A | APAC | Closed | P2 Medium DCOS | MarcusGoh@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L1 | DCOS Graphics Issue | DCOS | [6 empty] | DCOS SFAT Issues and Observations: 1. UPS "load on bypass" and "low battery alarm" alarm severity to change from critical 950 to urgent 850 as per SPL 1.0. 2. The summary page of UPS did not show any alarm when the alarm was triggered. 3. Static text for UPS tagging needs to be corrected and the text â€œtemplateâ€ shall be removed. 4. UPS high limit and low limit alarm thresholds shall be user-editable. 5. All equipment Maximo IDs have already been provided by ERCS. DCOS is required to deploy and update the IDs in the graphics. 6. ERCS is required to request the location vector from EQIX and provide it to DCOS for updating. 7. Equipment naming in DCOS shall follow the UIUX naming format. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621309&prj=663&rqi=97ocNQ7XVtGu1tGxWpbTqFaPQZ
GI-017 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Kindly provide sticker labeling for the breaker settings, in accordance with the approved discrimination study, for all new SUDP and PDU. Including Arc Flash sticker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620702&prj=663&rqi=PSNN7peCGOqhPMvGjFD42LLB1D
GI-013 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | When the unit stops due to loss of air flow, there is no loss of air flow alarm showing at the unit HMI. The unit only shows fan failure alarm, Stulz to check and clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619992&prj=663&rqi=gbstNYhr6pwmMVZJeVwhXSHsZ6
GI-014 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | To provide drawing pocket and attach LEW endorsed drawings for SUDP and PDU. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619994&prj=663&rqi=E0TnLkQ2M65z858HaLyNHbRWWe
GI-015 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | 1. Missing cable labeling for CAT6 cables as per photo attached. 2. To provide drawing pocket and attach LEW endorsed drawings for SUDP. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619995&prj=663&rqi=SelYefKvDhCX60NhSvLNrUoT2D
GI-009 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | To provide labelling for signal cables at E2 controller terminals J14. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619397&prj=663&rqi=2j7LEj7f7AnsolFtrCZSDwFgUI
GI-006 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | The Armaflex insulation for CHW pipes inside the units is not properly wrapped and has come loose, to rectify accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617415&prj=663&rqi=xfxx32oDlOpDZFfuYwm6cbfT0W
GI-004 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | 1. The fuse F02 rating of "6A" does not tally with the approved drawing, which specifies "4A". To update the drawing. 2. The overload contactor F31 range of "26Aâ€“32A" does not tally with the approved drawing, which specifies "2.5Aâ€“32A". To update the drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617413&prj=663&rqi=Odr94kmHhVg50LHvAMm47GHCaU
GI-003 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | To provide labelling for signal cables at E2 controller terminals J10 and J4. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617412&prj=663&rqi=Bfc4s5aq5QWC5zZEAHJuACmtWe
GI-002 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Torque required | Commissioning |  | equipment type |  |  |  |  | To provide torque markings on all earth cable terminations. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617411&prj=663&rqi=CaknDmys067yiPmlcFoYyxhUpg
GI-007 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Condensate drain pipes after passing through the units are not properly secured, to secure accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617416&prj=663&rqi=dwU9xXE5XbEckUfnofXWTLUqtY
GI-005 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | To cap off the cooling coil drain point. Applicable to all CRAC units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617414&prj=663&rqi=2CbrYCvdEw6NeJyvx3tYcpyhYk
GI-008 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | To standardize the SAT sensors under the raised floor to face toward the CRAC units, except where obstructed by other services. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617417&prj=663&rqi=q5FisNc2EhoYzbJuzZm50ek71h
GI-001 | SG04-4A | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | All the CAT 6 cables connecting between Adapter Board and MCMS Port are not labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617001&prj=663&rqi=7iSxSwsbfQqOs6k9bJ0btgxGrp
GT1SEC-2-005 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-11-09 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not complete | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx3: Level 5 : D137 no BG D153 no KCU D147 cannot test door cannot close D152 cannot test door cannot close D148 cannot test door cannot close | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637847&prj=618&rqi=TVya3a8xcGK1IX5I1JqThSHeb3 | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GT1DCOS-13-001 | SG06-1 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-09-16 04:00:00.000 +0400 | General Contractor - BMS | L3 | General Design Issue | Design | Controls | equipment | 1CPOS_RIO_01 | DCOS - Control Panels |  |  | It was observed that the Power Supply Common Alarm refers to the PSU failure alarm. During the simulation of Primary Source and Secondary Source failures individually, no alarm was triggered to provide notification. (Apply to all CPOS Panels) Based on the control wiring, the two sources are combined to supply the two PSUs. Therefore, a failure of only Source 1 or Source 2 will not trigger the PSU failure alarm. The PSU alarm will only be triggered when both the primary and secondary sources fail, resulting in a loss of supply to the PSUs. Kindly clarify with the EoR to confirm the design intent and verify whether the current alarm logic is in accordance with the approved design. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638239&prj=618&rqi=DlZDfYYOA6SLzRRx1hX3n6eIs6
GI-512 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-09-16 04:00:00.000 +0400 | Electronic Safety and Security Contractor |  | Commissioning Issue | Commissioning | Security | system | Security - Card Access System |  |  |  | L8 CX Issues - D224 DC always open - D222 DC always open | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638425&prj=618&rqi=Ka48Uxp2Cp0nIc2xESofpGmpx2 | https://equinix.facilitygrid.co.uk/x/project/618/system/14513
GI-511 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-09-15 04:00:00.000 +0400 | Electronic Safety and Security Contractor |  | Commissioning Issue | Commissioning | Security | system | Security - Card Access System |  |  |  | L7 CX - D197 DC always open - D211 DC always close - D212 EL no power - D210 no BG - D208 DC always open | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638424&prj=618&rqi=PnenUqbYBBBtqH4nJrZrvIJP6m | https://equinix.facilitygrid.co.uk/x/project/618/system/14513
GT1SEC-2-006 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-09-14 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not complete | Commissioning | Security | system | Security - CCTV System |  |  |  | L6 CX3 Issues - D172 DC always close - D173 EL Issue - D169 no BG - D714 EL Issue - DR181 no BG - D184 DC always close - D184 no BG - D180 DC always close | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637903&prj=618&rqi=hJUupqLmboh4lMGfqEZze3BudG | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
RT1ELEC-552-001 | SG06-1 | APAC | Open | P3 Low CX | KeeLeongLee@commtechasia.com | 2026-09-14 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | For Level 8 IT busduct, please rectify the following: 1. To replace label for J-21,56,67, 2. To ensure the joint label is installed properly for J-043 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637901&prj=618&rqi=7F384iySUxLbc3zpqaF2zkDbng | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GT1SEC-2-004 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-09-10 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not correct | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx3: Level 4 Issues D108 No REX MC1 No Siren D119 No REX D121 DC always open MC3 No Siren | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637587&prj=618&rqi=0ohiAikiH6GkWd39O724MAZmea | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-504 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Electronic Safety and Security Contractor |  | Installation not complete | Commissioning | Security | system | Security - CCTV System |  |  |  | L3 CX Issues - D85 DC always closed - D81 DC always open - D94 DC always closed - D96 open without scanning card | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637450&prj=618&rqi=XzQZwQELprFJ8aKW4Z6TrqTXVJ | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GT1SEC-2-002 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not correct | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx3: CCTV CX3 : Cam 153 : View is partially obstructed by the exit light | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637399&prj=618&rqi=wKSTJy9BsSn652uTNT73gVFcf1 | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GT1SEC-2-003 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not correct | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx3: Level 2 to 9: 1.Fire fighting lobby 2A to ext corridoor biometric reader need to shift 2. Level 2 TER Room A door access have issues 3. E wall A door access have issue 4. Door 65 Cool spine 1 has issues Camera: 1. L1 to L9 (Staircase 1 to 4) CCTV is removed as per SCDf comments , thus the view of the respective cameras is blanked out during the CX3 test | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637400&prj=618&rqi=KLPS43wW8A5Iw1LthRvdL5W43q | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-500 | SG06-1 | APAC | Ready for Verification | P2 Medium CX | jessyong@commtechasia.com | 2026-09-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General Design Issue | Design |  | equipment type |  |  |  |  | Observed incorrect voltage readings and negative kw readings at the ACB micrologic for STSSB. Socomec to rectify for all STSSB. Dcos has feedback when load test with s2, no negative values observed and voltage readings are normal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637058&prj=618&rqi=wOPTnaIGVjL9oD4lsYtWCGN3b8
GI-497 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2 A/ B: General Defects : 1SF Z 18, 1SF Z 5, 1EF M1 3 , 1EF M1 2 , 1FCU A 05 , 1FCU A 06 1. Document pocket to be affixed on all FCU / SF 2. Ducting needs to be labelled 3. Drawing needs to be updated as per components installed on the panel 4. Trunking to be sealed properly 1FCU A 06 (incoming earth not terminated) 1. Document pocket to be affixed on all FCU / SF 2. Ducting needs to be labelled 3. Drawing needs to be updated as per components installed on the panel 4. Trunking to be sealed properly 1SF A 12 1. Document pocket to be affixed on all FCU / SF 2. Ducting needs to be labelled 3. Drawing needs to be updated as per components installed on the panel 4. Trunking to be sealed properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636505&prj=618&rqi=E56P1jJGuaBsNVXMBp6LTFHsd4
GI-496 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx L2A - General Issues for FCU / EF / SF 1. Please ensure that there are permanent labels affixed to the Equipment / Control Panels 2. Ensure that there is a document pocket affixed to the control panel 3. FCU - Ensure that permanent labels are affixed to the thermostats of the FCU when they are installed 4. FCU name plate is installed on to the Control panel as per GA drawing 5. Ensure that the earthing cable (Trunking) is terminated 6. Unit strut needs to be shortened with end caps installed on them 7. The Ducting needs to have label applied to them | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636499&prj=618&rqi=pWQLQawWcAydeM84XYaEFhGZw2
GT1SEC-2-001 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not complete | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx3 : L1 to L9 (Staircase 1 to 4) CCTV is removed as per SCDf comments , awaiting waiver from scdf if it would be reinstalled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636413&prj=618&rqi=HDUPrWXJ8DlhZpKRWZbzjdWhQ3 | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
RT1ELEC-553-001 | SG06-1 | APAC | Open | P3 Low CX | RyanWu@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Component/Equipment Failure | Commissioning | Electrical â€“ LV | system | Mechanical Busduct System |  |  |  | To replace torn off tags for: Lvl 2 joint 20 Lvl 5 joint 14 Lvl 8 joint 64 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636226&prj=618&rqi=eaDO1TDgW04Dt42RGkYNM7FtA2 | https://equinix.facilitygrid.co.uk/x/project/618/system/14864
GI-491 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CX2 - White glove : 1USP_C1R1_2_1 1USP_C1R1_2_2 1USP_C2R1_3_1 1USP_C2R1_3_2 1USP_C2R1_4_1 1USP_C2R1_4_2 1USP_C1R1_2_3 1USP_C2R1_3_4 1USP_C2R1_4_4 1RPP_C1R1_2_1_3 1RPP_C1R1_2_1_4 1RPP_C2R1_3_2_3 1RPP_C2R1_3_2_4 1RPP_C2R1_4_2_3 1RPP_C2R1_4_2_4 1RPP_C1R1_2_3_3 1RPP_C1R1_2_3_4 1RPP_C2R1_3_4_3 1RPP_C2R1_3_4_4 1RPP_C2R1_4_4_3 1RPP_C2R1_4_4_4 1. USP Name plate to which RPP spare need to indicate on the panel 2. Engie needs to update USP outgoing circuit 3. Overall schematic needs to be made available in the room and to be attached to a visible place Assigned to woh hup / Engie / SMBE - Please update with responses here | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636305&prj=618&rqi=q1PywFYxKhxtC5H6UhG7Xg8tCN
GT1DCOS-17-003 | SG06-1 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-31 04:00:00.000 +0400 | General Contractor - BMS | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1CPOS_RIO_05 | DCOS - Control Panels |  |  | Requires fine-tuning of the CHWP PID settings, bypass valve opening, and timer. When both CHWP are running, the system repeatedly triggers a CHW low-flow alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636035&prj=618&rqi=mCep5RpqNjNrjxomYdDo9axTDt
GT1DCOS-16-001 | SG06-1 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-31 04:00:00.000 +0400 | General Contractor - BMS | L3 | Documentation not issued/ Required | Commissioning | Controls | equipment | 1CPOS_RIO_04 | DCOS - Control Panels |  |  | Observed that when the operating string fails, the next available string is automatically called to run. However, the failed string is commanded to stop immediately, and the pumps will stop after a 60-second time delay based on the current timer settings. This occurs before the next available string has successfully started and achieved a proven run status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636037&prj=618&rqi=F71YjcsEHSjb7hPlrFVBhFEWGK
GT1DCOS-19-006 | SG06-1 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-31 04:00:00.000 +0400 | General Contractor - BMS | L3 | General Design Issue | Design | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | Observed that only one CT is running to support two CWPs during string rotation. Kindly confirm with the design consultant/EoR the design intent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636034&prj=618&rqi=zA7iehwwF5HfZ06OwL8nABFeM7
GT1DCOS-19-007 | SG06-1 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-31 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | Observed that CWP 4 starts running before CT 4 FCV-01 valve opens during the stage-up sequence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636036&prj=618&rqi=P0zQRBYMY8S7skR4CXoNx2cACk
GI-484 | SG06-1 | APAC | Ready for Verification | P2 Medium CX | RyanWu@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not correct | Commissioning | Electrical â€“ LV | system | Mechanical Busduct System |  |  |  | To move the unistruts and obstructions away from the joints of the mechanical busducts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635241&prj=618&rqi=Pfk07ZgaADne6211mpyHT6CEcw | https://equinix.facilitygrid.co.uk/x/project/618/system/14864
GT1DCOS-19-005 | SG06-1 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor - BMS | L3 | General Design Issue | Design | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | As per SoO, initial chiller start sequence, one cooling tower will run . Observed that chiller string still able to stage in although after sequentially reset the faulted latching alarms and attempt to start the towers one at a time for three times maximum and "insufficient devices available to run" activated. Kindly confirm with the design consultant/EoR the design intent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635218&prj=618&rqi=z16z4jN1mc8gjlGuW9YCTAtkWv
GT1DCOS-17-002 | SG06-1 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning | Controls | equipment | 1CPOS_RIO_05 | DCOS - Control Panels |  |  | Observed that during string rotation, while CH was still in VSD precharge, CPOS considered String 2 as already run and stopped String 4. Kindly check with the JCI chiller team whether the system can take the chiller run status as the run point signal to CPOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635216&prj=618&rqi=qPsQGJbNdje9TejJNgmuONZlIb
GI-483 | SG06-1 | APAC | Ready for Verification | P2 Medium CX | RyanWu@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not correct | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | To move unistruts and other obstructions away from the joints of the IT busducts as shown in the screenshots | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635236&prj=618&rqi=V8jAd2Uaxm5w2MLSMnJlXERoy0 | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-471 | SG06-1 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | PACV 1 when doing the trip and flow test of PACV 1 the pipe was found to a loud sound and have excessive vibration that lead to bits and pieces of the wall and ceiling came out and sprinkler pipe leak . Please find out whatâ€™s the cause and rectify 31/08/2026(Updated): Please note that a similar incident happened on PACV 11 (level4) trip test on the 31/08/2026 , where a loud sound was heard at the corridor here the trip test is occurring | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634303&prj=618&rqi=c6vee8kz98ZAxGdZpHtVYk3FZf
GI-467 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-08-18 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Cx3: 1. Flood light outside e- wall 3 A is found to be yellowish , to find out is it the same model of light that is installed or its a different kind that is installed 2. Chilled water riser (LC) Light is not installed yet 3. It riser 3A-1 Light is not installed yet / might have been removed from the vendor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634118&prj=618&rqi=bfdYBGAaBiv7eccBTh88wQMOhB
GI-462 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-08-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | To update submittal 6211 lv schematic diagram z swing, to include secondary circuit to 1mdsb_z2 source 2 from 1mdsb_r1_2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633910&prj=618&rqi=XkTUf1jkplU0T647T2Oou377gS
GI-459 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-08-14 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not correct | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | BUSDT cx2A observation 1.GA dwg to update, sld to upload in FG(incorrect dwg indicating the placement of the components) 2. earth bond to install at panel door 3. to install labels on equipment as per approved maximo list 4. Missing otdr passing critieria in mos and testing wavelength. (vendor mentioned is 850nm and less than 3db/km) 5. To install labels the incoming source to the thermal monitoring panel on the power socket 6. Unable to find patching panel in equipment layout | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633586&prj=618&rqi=YNw30FTPEeSl6oSEgyii7aby4j | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-458 | SG06-1 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Observed signs of possible water/moisture ingress and including discoloration/rust-like staining within the loadbank enclosure. Engie to investigate the condition of the enclosure seals, joints, cable glands and other potential entry points, and implement the necessary corrective action to prevent recurrence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633389&prj=618&rqi=MvzdralQlExRRanLyH8AxxIDTp
GI-455 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | CX3: SAP Test N2L06D037 N2L06D032 - Labels need to be updated N2L05D07 - Label need to check N2L05D073 - RP / SAP panel update N5L01D077 - Needs to be updated N2L02D062 - Label is wrong and needs to be updated N2L02D064 - Label is wrong and needs to be updated N5L02D065 - Location needs to update N5L02D056 - Location needs to update | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633139&prj=618&rqi=kWATXROZeoStVkQXvCfWMtgsqK
GT1DCOS-23-004 | SG06-1 | APAC | Closed | P2 Medium CX | hemendrrajeganathan@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning | Controls | equipment | 2CPOS_RIO_04 | DCOS - Control Panels |  |  | Cx3 2CPOS_RIO_04 Temperature readings during sensor verification and current status are out of range. To check the condition of temperature sensors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633145&prj=618&rqi=WEq5HRbEdBchRvSbn4d9JxphYa
GT1DCOS-23-001 | SG06-1 | APAC | Open | P3 Low DCOS | siakhongneogh@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS | Controls | equipment | 2CPOS_RIO_04 | DCOS - Control Panels |  |  | Vendor to cross-check all alarm names and alarm descriptions to ensure they accurately reflect the corresponding alarms. Apply to all strings. Including Bypass valves and Temperature/DP/ flow sensors in Chiller Plant Room 2 (South), all indicated wrong location in faceplate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632971&prj=618&rqi=cYzeB19gbGg2UWvTkxvVRor2j9
GT1DCOS-18-001 | SG06-1 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS | Controls | equipment | 1CPOS_RIO_06 | DCOS - Control Panels |  |  | Observed that FCV01 will automatically open when Cooling tower and Valve Control Panel are in Auto mode, while the VFD is manually commanded to run via DCOS. Kindly confirm with the EoR the intended design philosophy and sequence of operation during manual override. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632958&prj=618&rqi=ODFD7PzxUgUQxkof05IkoNDukM
GT1DCOS-23-003 | SG06-1 | APAC | Open | P3 Low CX | siakhongneogh@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS | Controls | equipment | 2CPOS_RIO_04 | DCOS - Control Panels |  |  | Observed that was a command of 30% speed command during DCOS manually override to command run. Vendor to investigate and cross check the logic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632973&prj=618&rqi=aSPWMkTs8U4cI59EOWc9Tx19vS
GT1DCOS-23-002 | SG06-1 | APAC | Open | P3 Low CX | siakhongneogh@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS | Controls | equipment | 2CPOS_RIO_04 | DCOS - Control Panels |  |  | Vendor to cross-check and ensure all alarm shall reflect corresponding alarms correctly on the CPOS HMI. Apply to all strings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632972&prj=618&rqi=9bqOdeVpJTvaAenbVCzN6WDoqs
GT1DCOS-26-001 | SG06-1 | APAC | Closed | P3 Low CX | hemendrrajeganathan@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning | Controls | equipment | 2CPOS_RIO_05 | DCOS - Control Panels |  |  | Cx3 2CPOS_RIO_05 TT-14 sensor is out of tolerance limit (more than 12 deg difference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632399&prj=618&rqi=lZjKWL8RWbACdZnsXD5vK6uAVh
GT1DCOS-17-001 | SG06-1 | APAC | Closed | P3 Low CX | hemendrrajeganathan@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning | Controls | equipment | 1CPOS_RIO_05 | DCOS - Control Panels |  |  | Cx3 1CPOS_RIO_05 TT-17 sensor is out of tolerance limit (more than 12 deg difference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632401&prj=618&rqi=XT1x2kUiMOhjOV8tzL05KZQD0q
GI-442 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-08-04 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | Cx3: Level 9 : Temperature Sensor HMI and DCOS / Sensor While performing the sensor verifications of the temperature sensors , the following below was observed : Sensor 1 reading is out by 1 degrees Celsius Sensor 8 Reading is out by 0.57degrees Celsius Sensor 15 reading is out by 0.5 Degrees Celsius Sensor 14 reading is out by 0.6 Degrees Celsius Sensor 7 reading is out by 3.5 Degrees Celsius The allowed tolerance is +/- 0.5 degrees Celsius Please refer to the table attached to this Issue for your reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632158&prj=618&rqi=q9eIajadFUJ96P3wJmm4cmK1oP
GI-430 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Cx3: JF with DCOS 1JF_Z_1 DCOS 1JF_Z_2 DCOS 1. 1JF_Z_2 DCOS - Stop button is damaged , as its slightly chipped and need to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631462&prj=618&rqi=tEOX18eL5Z34YZu4ss1uPnjEvf
GI-431 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Cx3: 1JF_Z_2 DCOS, 1JF_Z_1 DCOS 1. Graphics showed that for JF there is no name on the graphics that would state what is the name of the jet fan , only when it is being hovered above when / where the name of the jet fan can be seen 2. Observed that there is no status that tells if the JF is in high or low speed on the graphics 3. When fire alarm is triggered , the Jet Fan unit would stop and not automatically resume after the fire alarm is reset (Remains off) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631463&prj=618&rqi=doT3fg1WBEBLk2gETpfjARrQyJ
GI-423 | SG06-1 | APAC | Ready for Verification | P2 Medium CX | jessyong@commtechasia.com | 2026-07-29 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | To update mech ATS/socomec settings and SOO and submit to EOR for review and approval, unable to set as per approved settings during cx3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631121&prj=618&rqi=YqAaTYssLIE8i49z6CPJMhWfMK
GI-422 | SG06-1 | APAC | Open | P3 Low CX | jessyong@commtechasia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | To install labels as per approved maximo list and/or sld. Observed at 1RMU_A, Q01 and Q02 installed labels do not align with approved mv sld. ABB to rectify and attach photos of all RMU and BTU showing correct labels installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631119&prj=618&rqi=uXxVfdDgl0xNWGvo03jRTbPuwa
GI-424 | SG06-1 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | To update ATS settings for 3914 and 3904 voltage imbalance only able to set minimum at 0.02s instead of 0s. To resubmit the revise settings to EOR for review and approval. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631122&prj=618&rqi=MyQXhhjtufroKdNRhtEWo5qjrV
GI-425 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-07-28 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Cx3: Jet Fan (JF) When the JF is started in high speed mode , the JF would jerk and move in violent manner | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631142&prj=618&rqi=PNW7t73ozDq9y6EMK4nPILFxJM
GT1DCOS-19-004 | SG06-1 | APAC | Closed | P3 Low DCOS | siakhongneogh@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | General Contractor - BMS | L3 | Labelling | Commissioning | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | On the CH DCOS faceplate, the refrigerant temperature displayed refers to the saturation temperature. To confirm that this is correctly labeled or revise the display if necessary to avoid misinterpretation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630640&prj=618&rqi=iPsYTo3kyPLUI0y75UbVroYp7g
GT1DCOS-19-003 | SG06-1 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | The CHWP and CWP cannot be ramped up or down from the CPOS HMI. To investigate and enable this functionality. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630639&prj=618&rqi=Zmz0Hc0nPPZ4Y0hhCggtDucwei
GI-420 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Cx3: All Battery Container Battery container FCU Supply / return pressure gauge needs to be changed to a bigger capacity pressure gauge as the current one is out of range and could not take any readings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630488&prj=618&rqi=GE9vbZ5qAFpj7A02SYiUegtqys
GI-413 | SG06-1 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: To upload the compile picture file for hard to access joint for level 2 for MECH, IT and LB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630048&prj=618&rqi=vUdCGQ27HyMR2PjSHZoJ8Qjslr | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
YT1DCOS-18-001 | SG06-1 | APAC | Open | P3 Low CX | hemendrrajeganathan@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - BMS | L2B | Documentation not issued/ Required | Commissioning | Controls | equipment | 1CPOS_RIO_06 | DCOS - Control Panels |  |  | Cx2B 1CPOS_RIO_06 To revise schematic and panel drawing and upload into checklist once completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630058&prj=618&rqi=HSAzYjEw9DgzBt7iNPJIV0ZWHw
GT1DCOS-19-001 | SG06-1 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | DCOS is unable to execute manual ramp-up and ramp-down commands for the CWP and CHWP because the control is being overridden/ affected by CPOS although HMI in Remote mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630045&prj=618&rqi=k4tITFkcqAhgjodJBITwAeT1rC
GT1DCOS-19-002 | SG06-1 | APAC | Open | P3 Low CX | siakhongneogh@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | The CPOS HMI and DCOS are unable to identify or indicate which system currently has manual control overriden. There is no clear status or indication to distinguish whether the equipment is in CPOS Manual Mode or DCOS Manual Mode, resulting in ambiguity over the active control source. Attached D2SD screenshot was during Local panel in Auto mode, CPOS HMI in Local mode and DCOS in auto mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630046&prj=618&rqi=wvdbjWhYycjYhx9agackouLvEA
RT1SEC-2-005 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L2A | Installation not correct | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx2a: Level 9 : DR216: FIRE FIGHTING LOBBY 1 BIOMETRIC SCANNER IS DISLODGED | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630112&prj=618&rqi=YiHQZEWtnFesj7UFDyRLRybFwc | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-417 | SG06-1 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: To upload the compile picture file for hard to access joint for level 9 for MECH, IT and LB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630052&prj=618&rqi=ol6TaXm48WHZZSYpU1GkT1pybQ | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-416 | SG06-1 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: To upload the compile picture file for hard to access joint for level 8 for MECH, IT and LB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630051&prj=618&rqi=CSpaf54JFJRiIEAVj9cRAQFnar | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-414 | SG06-1 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: To upload the compile picture file for hard to access joint for level 5 for MECH, IT and LB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630049&prj=618&rqi=bQeAjEHrEFQ3039xCsiV4iVgpz | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-415 | SG06-1 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: To upload the compile picture file for hard to access joint for level 7 for MECH, IT and LB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630050&prj=618&rqi=NKZrdpkUtPW1UMmSqQidX0HaH8 | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-410 | SG06-1 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-18 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: Load Bank busduct During inspection it was found that some busduct is unaligned and the jointing was block but Unistrut support. To rectify and upload proof of rectification Unaligned joints - LB-L5-J-028, LB-L5-J-027, LB-L5-J-026, LB-L5-J-020, LB-L5-J-019. Blocked by Unistrut - LB-L5-J-018, LB-L5-J-007, LB-L5-J-003 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629894&prj=618&rqi=aMMYZzaYrsSYWFFjgeuwWmOdrJ | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-409 | SG06-1 | APAC | Closed | P2 Medium CX | alifasyraf@commtechasia.com | 2026-07-18 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: Load bank busduct At Level 9 the joints of LB-L9-008 was not installed to rectify and upload the proof of works | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629893&prj=618&rqi=B67tiT1V1PPliUJIABHA9PHiHv | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-406 | SG06-1 | APAC | Closed | P3 Low CX | RyanWu@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | To update routing of bus ductors on drawing where necessary, as there are changes to the locations to some of the panels where the ductors are supposed to go | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629350&prj=618&rqi=4550XI0mKtmrLW4qKuJ6hVBwmf | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-407 | SG06-1 | APAC | Open | P3 Low CX | jessyong@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | To update the hv power study for the curve characteristic for RMU Z, C, A, R1, M1 and D hi set settings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629351&prj=618&rqi=FnULqCcYNNkOfnHa1XlWAE1Amo
GI-403 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | CxL2A 1FCU_M1_07 1FCU_M1_08 - FCU is missing the equipment label that is supposed to be affixed onto the FCU - FCU Control panel is also missing an equipment label on top of its run stop trip light - Document pocket needs to be attached to the FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629299&prj=618&rqi=aZG0uNx8VNeuuMn9Qo6gaZTuke
GI-400 | SG06-1 | APAC | Closed | P2 Medium CX | RyanWu@commtechasia.com | 2026-07-14 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Observed misalignment in the IT busduct installed in sts room 2A from joint IT-L2-J008 to J009. Engie to rectify and recall for reinspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629133&prj=618&rqi=rZu3gBNeheIG7jhzbpbnAlg1Ir | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-401 | SG06-1 | APAC | Closed | P2 Medium CX | RyanWu@commtechasia.com | 2026-07-14 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning | Electrical â€“ LV | system | IT Busduct System |  |  |  | Observed misalignment in the IT busduct installed in the STS RM D, from joint IT-L5-J-72 to IT-L5-J-77. Engie to rectify and call for reinspection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629134&prj=618&rqi=YUwOSIJzHUIroDzTuRX4ZyJoVA | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-396 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-11 04:00:00.000 +0400 | Electronic Safety and Security Contractor |  | Labelling | Commissioning | Security | system | Security - CCTV System |  |  |  | C2A: Level 5 Security System Labels wrong for some security camera in E- wall room A side need to be rectified Some camera alignment appears to be slanted and needs to be rectified | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628769&prj=618&rqi=qryFVgIzwXXn8LZ5mRyp5lWlHb | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-389 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2a / Cx2b: 1JF_Z_1 1JF_Z_2 1. Document pocket not affixed to the panel 2. 1JF_Z_1 button gasket need to be adjusted / fixed 3. 1JF_Z2 stop button is slightly damaged and need to be fixed 4. Please confirm on site , the OL Relay model is stated as LRD07 , while the other OL Relay model is LRD12 , please also confirm the overload setting 5. DCOS cable is not terminated for 1JF_Z_1,, 1JF_Z_26 6. Please update the drawing where there are components installed in the panel , but is not reflected in the drawing : - Fuse F7/ F8 is missing in drawing - Power supply converter is missing from the drawing -Relay position is swapped in the drawing 7. JF Terminal block for thermostat has two more blocks cable in it , drawing to be updated (Terminal Block 09/10) This defect is applicable to all other jet fans at other levels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628457&prj=618&rqi=sgiL7XCtWStnzfco92x7FlClvc
GI-388 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2a/Cx2b: 1JF D 1 Drawing to be updated Trunking to be sealed Document pocket to be included in panel 1JF D 2 Drawing to be updated Document pocket to be included in panel 1. Please confirm on site , the OL Relay model is stated as LRD07 , while the other OL Relay model is LRD12 , please also confirm the overload setting 2. DCOS cable is not terminated 3. Please update the drawing where there are components installed in the panel , but is not reflected in the drawing : - Fuse F7/ F8 is missing in drawing - Power supply converter is missing from the drawing -Relay position is swapped in the drawing 4. JF Terminal block for thermostat has two more blocks cable in it , drawing to be updated (Terminal Block 09/10) This defect is applicable to all other jet fans at other levels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628238&prj=618&rqi=UDAXkupuBMi7BpyT5jKhsQoHhw
GI-386 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3: Fireman intercom Testing : L8: Genset B / E - Wall B Handset call quality was found not be to clear L8 Cool Spine 8-2 / Level 7 Genset B there is significant feedback occurring while using having the call at the same time Notes: 1. When having 1 way communication , the one way light does not light up and appears in 2 way 2. Sometimes when having a 3 way communication , the 3 way communication light does not light up Hand Sets with physical issues: 1.L9-E-WALL 9B HANDSET Missing Glass 2.L9-FFL 9B HANDSET Missing Glass / this handset is also missing in the drawing 3.L9- Goods lift HANDSET Missing Glass - label to be updated in full - Goods Lift Lobby 4.L8- Goods lift should be rename as goods lift lobby 5.L7- Goods lift should be rename as goods lift lobby 6.L7-Cool spine 7-2 - Break glass needs to be changed 7.L6- Goods lift should be rename as goods lift lobby 8.L6-FFL 8B HANDSET Missing Glass 9.L5-STS 5B HANDSET Missing Glass 10.L8 STS 6A HANDSET Missing Glass 11.L6 Cool spine 6-2 HANDSET Broken Glass 12.L1 Security Room HANDSET Missing Glass 13.L6 - E- Wall 6A HANDSET Broken Glass 14.L1 Battery Container 1A HANDSET Missing Glass 15.L5- FFL 5A HANDSET Missing Glass 16.L1 SPK PUMP Room - HANDSET Break glass needs to be changed - label spelt wrongly 17.L5- STS 5A - HANDSET Missing Glass 18.L3- Goods lift should be rename as goods lift lobby 19.L5- cool spine 5-1 - HANDSET Missing Glass 20.L1- Good Lift - HANDSET Missing Glass / should be rename as goods lift lobby 21.L4- cool spine 5-1 - HANDSET Missing Glass 22.L6 FFL 6a - Handset missing glass 23.L5- E Wall 5A - HANDSET Missing Glass Suggest that L1-L8 goods lift lobby the label to be changed to full Goods lift Lobby Label Handset issues : 24.L6-Cool spine 5-1 Handset - LED light is not working 25.L4-FFL Handset - LED light is not working | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628051&prj=618&rqi=FJfJlQOC9oQ8IwdPndM8cjr3C2
GI-384 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CX3 : Fire Level 7 N12L03D015 and N12L04D012 RP mimic LED wrong Mimic drawing to be updated, riser 7A medium voltage is L7-Z87 Mimic drawing need to change the zone name for the following zones: L7-Z44 (change to 5A) L7-Z45 (change to 4A) L7-Z46 (change to 3A) Trouble detectors: N12L04D016 N12L03D021 N12L04D050 N12L03D018 N12L04D015 label on detector wrong N12L03D040 image very dark, unable to check label N12L04D045 changed to exposed for panels and fire PC N12L03D044 change label sticker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627950&prj=618&rqi=gDjpqOk5wpIfNvZPoWLszACdN0
GI-385 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | L8 CX3 SAP : 1. Drawing needs to be updated on the location of the bell / strobes as they are missing 2. Handicap toilet missing strobe light in the drawings 3. Genset missing strobe light in the drawings 4. Positions of some strobe lights need to be Changed on the drawings L8 Data Hall 1 1. Detector found wrapped with plastic : N15L01DD014 2. Mimic panel diagram / zone of the DH8-1 and cool spine needs to be updated as those two separate zones have been merged into one zone L8 Data hall 2 : Detector Sticker label was found and need to change: N15L04D007 N15L03D014 N15L04D020 N15L03D027 N15L04D033 N15L03D034 N15L04D014 N15L03D008 N15L04D021 N15L03D028 N15L04D034 N15L03D039 Mimic panel data hall number need to change. Should be DATAHALL 14 (DH8-1) and DATAHALL 15 (DH8-2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628050&prj=618&rqi=wTS04Rvx3Jv3C2mY7A90vTbW2b
GI-383 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | 1SF A 3 - drawing to be replaced with lew approved drawing 1 SF A 6 - drawing to be replaced with lew approved drawing 1 SF A 5 - drawing to be replaced with lew approved drawing 1SF A 4 - drawing to be replaced with lew approved drawing 1SF C 3 - sticker to be paste on the fan unit 1SF Z 25 - fan no label All SF to have document pocket affixed to the panel All SF drawings ducting should have labels attached to them | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627949&prj=618&rqi=gtdOi7JpRC9zSyYzUs52y50Mc4
GI-382 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CX3: Level 7 Smoke Detector Testing Strobe light location on drawing to be updated. (Markup on drawing) N12L04D024 and N12L04D034 wrong location name & zone on panels and fire PC N12L04D035 panels, fire PC and mimic drawing need to change to 5B Mimic drawing need to change the zone name for L7-Z70 (should be 5B) and L7-Z71 (should be 3B) N12L03D010 change new sticker label (cause the current sticker label roll up a bit) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627748&prj=618&rqi=euuKXlLCJOFWfO91kcTGTw4DeB
GI-381 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx3: Level 8 NER Room 1FCU_A_22 1FCU_M1_19 - No label installed on the thermostat - thermostat temperature is out by 1 degrees celcius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627591&prj=618&rqi=cKItQ7Q2f2vH9Ym6dmO1yUNwnH
GI-380 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3: Level 6 fire protection 1. extra call point in the system N10L05M003 2. Call point N10L04M008 label need to change 3.DH6-1 HR call point RP zone number wrong Level 7 fire protection Strobe light need to update on drawing (placement wrong/missing) N13L01D001 label need to change N13L01D025 label need to change N13L01D021 and N13L01D015 fire PC and panels need to change to exposed Drawing need to update: N13L01D046 and N13L02D046 swap location N13L01D044 and N13L02D044 swap location Mimic panel drawing need to update to latest version N13L01D034 zone number wrong | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627439&prj=618&rqi=pelWrzl3iDmWwzQUme0U9R7JrC
GI-378 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2a/ 2B: 1SF Z1 30 1SF Z1 31 nameplate to be change to the correct name drawing to be updated isolator to be installed phase label to be installed trunking to be sealed excess cable to be terminated dcos cable to be terminated Labels to be attached to the equipment 1SF Z1 29 1SF Z1 28 nameplate to be change to the correct name incoming and outgoing cable to be terminated to isolator drawing to be updated dcos cable to be terminated trunking to be sealed excess cable to be terminated Labels to be attached to the equipment 1JF A 1 1JF A 2 drawing to be updated trunking to be sealed trunking earth missing For 1JF A 1, fuse is rusty dcos cable not yet terminated Labels to be attached to the equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627436&prj=618&rqi=M7rJpQCQXynKES9cApE3UNanwp
GI-377 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2a / Cx2B : 1FCU M1 07 1FCU M1 08 1) drawing to be updated 2) trunking to be sealed 3) redundancy cable is not connected 4) Thermostat to be installed and labelled 5) Document pocket to be affixed to the panel 6)Labels to be affixed to the FCU 7) Labels is missing on the ducting | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627429&prj=618&rqi=1bwqWin8eboBeachyCFAAoDxvm
GI-375 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Level 6 Cx3: Mimic drawing need to change the E-WALL no.A and E-WALL no.B to the same as the drawing. N10L03D011 detectorâ€™s label need to change N10L04D019 has issue - detector failed to trigger | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627166&prj=618&rqi=w9qOz24bS0vHTSP16aWayUIW1Z
GI-371 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Observed the lamp test at the gen annunciator, does not light up the low coolant level alarm. Rehlko to rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626882&prj=618&rqi=pq3yHCUOfPQXYzM6k0Bo7hSX2b
GI-372 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A/Cx2B 1FCU Z 08 drawing to be updated thermostat label missing 1FCU Z 09 drawing to be updated thermostat label missing trunking earth missing ducting label missing 1 JF M1 1 missing incoming cables (engie side) missing isolator label drawing to be updated trunking to be sealed trunking earth missing Missing Labels on the JF 1 JF M1 2 missing incoming cables (engie side) missing isolator label drawing to be updated trunking to be sealed trunking earth missing all 6 amps fuse rusty Missing labels on the JF | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626928&prj=618&rqi=6JL41qIuk1KvE9d0vwbXQWvYz1
GI-370 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A/Cx2B: 1SF M1 3 : drawing to be updated trunking to be sealed incoming cable missing incoming phase label missing isolator missing phase label missing from outgoing cable Cx3: 1FCU Z 22 and 1FCU Z 23 drawing to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626733&prj=618&rqi=eGZLr4pJwwVK0SsnS3x8cnt7j4
RT1DCOS-1-002 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment type |  | DCOS - Control Panels |  |  | Cx2B: 1DCOS CP 01 cable not terminated due to a module needs replacement 1DCOS CP 02 Drawing holder did not stick on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626929&prj=618&rqi=L21FubpXRIReUrhHpH9woD1lER
GI-369 | SG06-1 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | FCU: Cx3 CSR Room A: 1FCU_Z_22 1FCU_Z_23 1. Damper opening and feed back of the actuator needs to be adjusted / fined tuned so that the damper opening and feed back would be correct 2. FCU : Type 1 FCU / it has damper opening and closing controls , which is not monitored on the DCOS side , Access tech and DCOS to check why is that so , and only local trip can be seen 3. There is No SOO mentioning of what should be the behavior of the damper in the SOO 4. When the damper fails ( Fail To open ) the alarm comes on and the fan stops running 5. when the unit is trip the fan would stop running and then the damper would remain open , which deviates from the check list which says when the unit trip the damper should close and the PICV is closed (manual mode) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626724&prj=618&rqi=4NTsrkV4n1t0k78bhmPILMjrHe
GI-365 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3 : Level 6 Detector N10L04D008 pic only able to see the 8 as they were unable to take clear photo but the panels etc shows correct number Mimic drawing need to update (including panel): 1. L6-Z14 missing on drawing (data hall lobby 6A) 2. Both data hall HR zone labels are wrong N11L05D010 mimic panel shows 2 LED (should only be 1) N11L05D004 and N11L06D004 detectors label unclear N10L04D010 label on detector missing RP mimic panel canâ€™t see the word L6-Z54 on it Drawing needs to be updated: Data hall 1 HR location should be 6A-4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626533&prj=618&rqi=hz3JMOJanaPR6QsJoEFu1qrRO1
GI-366 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Cx3 : 1FCU_C_10 1) when normalizing thermostat, PICV will close then open. 2) During auto mode, DCOS summary alarm and supply fan cmd mismatched lights up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626537&prj=618&rqi=NACXIGE5catvayfOWMlSqXEYMY
GI-362 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | FCU Cx3: 1FCU_Z_27 1FCU_Z_06 1FCU_M1_54 1FCU_M1_50 1FCU_M1_49 Observations 1FCU_M1_50: - Unit keep tripping spontaneously through the overload relay - need to check if the overload settings are too sensitive - That only happened after the dirty filter alarm is triggered manually at the unit - Setting is 250 - DPS - Find out why the PICV Valve feedback takes some time to come after the actual PIVC Valve is closed at the panel (Measured at feedback) - Unable to access unit to attach TA scope to check flow - When thermostat of the FCU fails ,the PICV is supposed to remain at last position / however what happened was the valve closed instead of remaining fully opened | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626378&prj=618&rqi=K5RojAOuhi8gkUutAx5nBkK9FG
RT1DCOS-13-002 | SG06-1 | APAC | Open | P3 Low CX | Weihaolim@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1CPOS_RIO_01 | DCOS - Control Panels |  |  | During the Cx2A inspection, the following observations were noted (apply to all PCP and RIO panels): To update network architecture and earthing connection diagram, connection on site don't tally with drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626336&prj=618&rqi=BD7xbsz8jy1NiHK88Ucx2VSDxt
GI-359 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3: Level 6 Fire protection Drawing needs to be updated. Such as strobe light location, smoke detectors location and labelling. Smoke detectors (physical) needs to change the label N11L01D033 N11L01D016 Data hall number needs to be updated on mimic drawing, fire PC and all the panels. From DATA HALL 6 (wrong) to DATA HALL 10 (correct) From DATA HALL 7 (wrong) to DATA HALL 11 (correct) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626279&prj=618&rqi=QK1Tva6WoN09lQ4tr3QPYJ4OuX
GI-361 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | FCU Cx3: 1FCU_M1_33 Find out why the PICV Valve feedback takes some time to come after the actual PIVC Valve is closed at the panel (Measured at feedback) - Unable to access unit to attach TA scope to check flow - When thermostat of the FCU fails ,the PICV is supposed to remain at last position / however what happened was the valve closed instead of remaining fully opened | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626374&prj=618&rqi=jc1kAADgMInVsVivSJoqCYxU0l
GI-358 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | CX3: Find out why the PICV Valve feedback takes some time to come after the actual PIVC Valve is closed at the panel (Measured at feedback) - Unable to access unit to attach TA scope to check flow - When thermostat of the FCU fails ,the PICV is supposed to remain at last position / however what happened was the valve closed instead of remaining fully opened Applicable to levels FCU . Level 1: 1FCU_Z_06 - PICV valve operation not aligned as per SoO 1FCU_M1_54 1. Moxa switch/ BMS card issue, unable to comms DCOS, PICV valve operation not aligned as per SoO, MOXA card needs to be replaced / Fixed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626277&prj=618&rqi=tWj8BKp3XHZ7iAoRkkgRibO6iJ
GI-351 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | CX3: 1FCU_C_13 - Sponteneous tripping of the unit for no apparent cause , and it happened 3 times - Find out why the PICV Valve feedback takes some time to come after the actual PIVC Valve is closed at the panel (Measured at feedback) - Unable to access unit to attach TA scope to check flow - When thermostat of the FCU fails ,the PICV is supposed to remain at last position / however what happened was the valve closed instead of remaining fully opened 1FCU_M1_35 Find out why the PICV Valve feedback takes some time to come after the actual PIVC Valve is closed at the panel (Measured at feedback) - Unable to access unit to attach TA scope to check flow - When thermostat of the FCU fails ,the PICV is supposed to remain at last position / however what happened was the valve closed instead of remaining fully opened 1FCU_C_12 Find out why the PICV Valve feedback takes some time to come after the actual PIVC Valve is closed at the panel (Measured at feedback) - Unable to access unit to attach TA scope to check flow - When thermostat of the FCU fails ,the PICV is supposed to remain at last position / however what happened was the valve closed instead of remaining fully opened - Find out why after i did the thermostat failure for the unit , this unit is an AHU / but is classified as an FCU , and it has two EC fans , after failure of the thermostat and its reinstatement , only one fan is found to be working while the other fan remained off , it was confirmed to be off after measuring the fan feedback | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625867&prj=618&rqi=zqxiBSenG4nYFQgtOgKPat217H
GI-353 | SG06-1 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2 A/ B: General Defects : 1SF Z 18, 1SF Z 5, 1EF M1 3 , 1EF M1 2 , 1FCU A 05 , 1FCU A 06 1. Document pocket to be affixed on all FCU / SF 2. Ducting needs to be labelled 3. Drawing needs to be updated as per components installed on the panel 4. Trunking to be sealed properly 1FCU A 06 (incoming earth not terminated) Condensate tray and label outstanding on fcu need to be installed - P2 issue 1. Document pocket to be affixed on all FCU / SF 2. Ducting needs to be labelled 3. Drawing needs to be updated as per components installed on the panel 4. Trunking to be sealed properly 1SF A 12 1. Document pocket to be affixed on all FCU / SF 2. Ducting needs to be labelled 3. Drawing needs to be updated as per components installed on the panel 4. Trunking to be sealed properly 5. incoming cable yet to be terminated - P2 issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625869&prj=618&rqi=4AtNFhdX4fArwgf7isBp7CnJQE
GI-350 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A : 1FCU_A_04 1FCU_Z_07 1SF_A_04 1. thermostat to be installed 2. Document pocket to be affixed to the panel 3. trunking to be closed up and sealed 4. 2A fused to be replaced (rusty) 5. Ducting to be labelled with stickers stuck to it 6. Drawing to be updated as per components installed on site 1SF_A_04: 1. trunking to be sealed 2. Ducting to be labelled with stickers stuck to it 3.. Drawing to be updated as per components installed on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625683&prj=618&rqi=qCPT19itmHkmJDPvCdNINvrmi6
GI-349 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3: Fire Level 5 Point to Point testing : Mimic drawing need to update on locations such as: 1. Data Hall lobby 2. â L5-Z16 need to update to L5-Z18 3. â corridor 5A zone update to L5-Z25 Corridor 5A on mimic panel (physical) need to update to latest drawing then test the zoning LED again For detector N8L03D031, mimic LED light up at wrong place | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625682&prj=618&rqi=OgiW8jVhRChxxuIiRWCw6lSIaI
GI-348 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Cx3: Fire Pump Panel 1. Fire pump panel date and time is not set yet on the HMI 2. Fire Pump panel please check why is there a battery mode on the pump panel 3. Please check if data such as voltage / ampere / trending records can be extracted / down loaded from the pump 4. record / wrote firm ware version up here | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625554&prj=618&rqi=tpyeH2VTOtaM5j6VIiJLGIcphr
GI-343 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A 1EF_Z_8 1. Document pocket need to be affixed to the EF 2. Labels need to be attached to the EF / Ducting 3. Grilles need to be installed in its correct location 1FCU_Z_46 1FCU_Z_58 1FCU_Z_59 1FCU_C_07 1FCU_D_07 1FCU_C_03 1FCU_D_03 1FCU_Z_47 1) drawing to be updated due to incorrect position/wire label. 2) thermostat missing for all FCU/ to be installed 3) trunking to be sealed off for act and dcos (light can pass through) 4) wires to be terminated. 5) Document pocket to be installed for the FCU 6) Labels to be attached onto the drain pan | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625336&prj=618&rqi=PSu2JSIDQQ4pZhgfQSKk6jh2Yq
GI-344 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3: LEVEL 5 : Label on detector is wrong: N8L04D040 N8L03D040 N8L04D031 Please update the detector and attach photos here Drawing label wrong N11L01D047 (on drawing) change to N9L01D047 N11L02D049 (on drawing) change to N9L02D049 N8L04D040 (on drawing) change to N9L04D040 N8L03D040 (on drawing) change to N9L03D040 Please update drawing and attach here Mimic Panel issues N8L04D032 mimic LED did not light up when triggered | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625338&prj=618&rqi=0SC0LoHn6dPNegcDV9GYou5p6f
GI-341 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3 Fire : Level 5 SAP 08, 09: Drawing : Drawing missing strobe light at the genset area (5A / B) Detector Label on the following detector is wrong: N9L04D026 N9L04D033 N0L04D008 N9L01D026 N9L01D032 N9L02D025 N9L01D010 N9L02D047 (drawing need to update to N9L02D048 + need to change label on detector) N9L02D001 N9L01D008 Please update Bell strobe Data hall 1 near N9 L01 D008 is left hanging and not installed properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625193&prj=618&rqi=egBqScSblD1ZEEbuDNfdxFHH3P
RT1SEC-2-004 | SG06-1 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L2A | Documentation not issued/ Required | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx2A: L7 Card Access Panel ACP-13 and ACP-14 L8 Card Access Panel ACP-15 and ACP-16 L4 Card Access Panel ACP-07 and ACP-08 L6 Card Access Panel ACP-11 and ACP-12 1. PSU needs to be labeled to show where /what devices it is connected to 2. Battery needs to be labelled (Installation / Start using date) 3. Earth cable within the PSU units need to be attached / installed 4. Panel earth needs to be installed on the door 5. Internal wiring needs to be terminated with proper labelling 6. Applicable to all ACP units 7. There needs to be a GA drawing of the main ACP unit so that people can identify the components within 8. In the drawing , label the PSU units 01- 07 as shown on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625189&prj=618&rqi=71GehT0hZI5UYZQagYrzIzGlRg | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-336 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2a: 1SF_Z_4 1SF_Z_8 1SF_Z_9 1SF_Z_16 1. Document pocket needs to be installed on the SF 2. Labels are missing on the SF as well as on the ducting itself | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624952&prj=618&rqi=Es3YPkS29zzsVl32fXwbDHfBCB
RT1DCOS-28-002 | SG06-1 | APAC | Closed | P3 Low CX | siakhongneogh@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 2CPOS_GWP_01 | DCOS - Control Panels |  |  | During the Cx2A inspection, the following observations were noted (apply to 1CPOS_GWP-01 and 2CPOS_GWP-01): 1. The equipment layout plan / setting-out drawings have not been updated to reflect the current site conditions. 2. General housekeeping and cleaning works are required. 3. To install flexible conduit/ trunking for the incoming cables 4. Pending power earthing details explanation 5. Drawings to be in place 6. Permanent labelling shall be properly installed for incoming cables and screw terminal 7. To retighten and torque as per manufacturers guildelines | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624889&prj=618&rqi=jRs59LNYWqJWXsS8GGVtoiybbR
RT1DCOS-28-001 | SG06-1 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - BMS | L2A | Installation not correct | Commissioning | Controls | equipment | 2CPOS_GWP_01 | DCOS - Control Panels |  |  | Onsite 1Q2 , 1Q3 and 1Q4 MCB model was not tally with the bill of materials. Onsite was model A9F84110, however BOM indicate A9F84106 (apply to 1CPOS_GWP-01 and 2CPOS_GWP-01) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624885&prj=618&rqi=GhXwaaHJ9MzYW1T3aCfa2Kb5aM
GI-337 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2a: 1FCU_Z_20 1FCU_Z_21 1FCU_Z_29 1FCU_Z_30 1FCU_Z_34 1FCU_Z_35 1FCU_Z_32 1FCU_Z_33 1. Document pocket to be affixed to the units 2. Ducting labels should be installed 3. Labels missing on the FCU 4. Drawings to be updated 5. Thermostat missing and not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624953&prj=618&rqi=Ae2aBXBnn55a6jkEYN6NbESljx
GI-335 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3: SF : 1SF_D_02 - overload settings issue 1. Overload settings may be wrong as when i tried to measure the amperes i did not get a reading and only got 0 amps, Please check 2. When fire alarm is triggered / fan is supposed to resume last status when the fire signal is triggered / - It did not do so in local mode , the unit shut down , however in auto mode , the unit restarted after the alarm is cleared | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624951&prj=618&rqi=pluIx24KtZCvUdsecLQYNcJEkm
RT1DCOS-28-003 | SG06-1 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - BMS | L2A | Installation not correct | Commissioning | Controls | equipment | 2CPOS_GWP_01 | DCOS - Control Panels |  |  | Onsite the input card/ multiplexer quantity was not tally with the bill of materials. Onsite was only 1 set of input card and secrew terminal, however BOM indicated 2 sets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624890&prj=618&rqi=JRWw1Lg6U8VvV0Fvwodnf3PuKz
RT1SEC-2-003 | SG06-1 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L2A | Documentation not issued/ Required | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx2a: L4 Card Access Panel ACP-07 L4 Card Access Panel ACP-08 L6 Card Access Panel ACP-11 L6 Card Access Panel ACP-12 1. PSU needs to be labeled to show where /what devices it is connected to 2. Battery needs to be labelled (Installation / Start using date) 3. Earth cable within the PSU units need to be attached / installed 4. Panel earth needs to be installed on the door 5. Internal wiring needs to be terminated with proper labelling 6. Applicable to all ACP units 7. There needs to be a GA drawing of the main ACP unit so that people can identify the components within 8. In the drawing , label the PSU units 01- 07 as shown on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624520&prj=618&rqi=kJlKTeRSdjI8mqP10iBiqPDuV9 | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-333 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2a: 1FCU_Z_35: 1) INCOMING LIGHT missing white plastic cover/ It should be replaced 2) SLD to be update/remedied 1FCU_Z_34: 1) SLD to be updated/remedied 1FCU_Z_33: 1) SLD to be updated/remedied 1FCU_Z_30: 1) SLD to be updated/remedied All panels must have document pocket to be included Labels should be affixed to the FCU Ducting labels should be affixed to the duct Thermostat should be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624518&prj=618&rqi=gR2aXPTvYIlu1he9Nm6HzetrIr
GI-332 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor - Mechanical |  | General Design Issue | Design |  | equipment type |  |  |  |  | FCU Cx3: Observations: 1. SOO states that when FCU in shut down or off mode the PICV valve should return to close state (0% position) 2. When tested on site the FCU shuts down or go into Off mode , in local / Auto / The PICV valve remains as open 3. Accesstech to confirm if the valve should remain open / close when the unit is shut down 4. Dirty Filter alarm , when it is in local mode , it stays on , but when its in auto mode , it switches off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624516&prj=618&rqi=oQbqBIHyewTbPA7yYakZUktwAh
GI-331 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx3: Level 1 SAP Point to Graphics test: Strobe missing at the following locations: 1. Janitor Room 2. Shipping and recieving room 3. need to update in drawing that a bell / strobe was relocated near inventory storage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624341&prj=618&rqi=bClaSMaz9gNFKUbHyf61e0n7Vn
GI-330 | SG06-1 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | To update the approved settings to include the change in the PT100 sensor setpoints change and excitation current limit change from 23% to 40%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624010&prj=618&rqi=ITUNyVSDkvAUnMX0Rbx4lVNUyO
RT1SEC-2-002 | SG06-1 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L2A | Documentation not issued/ Required | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx2A: L2 Card Access Panel ACP-03 L2 Card Access Panel ACP-04 L3 Card Access Panel ACP-05 L3 Card Access Panel ACP-06 1. PSU needs to be labeled to show where /what devices it is connected to 2. Battery needs to be labelled (Installation / Start using date) 3. Earth cable within the PSU units need to be attached / installed 4. Panel earth needs to be installed on the door 5. Internal wiring needs to be terminated with proper labelling 6. Applicable to all ACP units 7. There needs to be a GA drawing of the main ACP unit so that people can identify the components within 7. In the drawing , label the PSU units 01- 07 as shown on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624008&prj=618&rqi=L7SLsXrcsbmpZzt3Zr3wfyvP8D | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-329 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A: Cx2a: 1FCU_M1_05 1FCU_M1_06 P2 Issues: 1. Condensate tray is not installed on the FCU 2. BMS cabling has not been terminated yet / finished terminating 3. Equipmment tag is missing on the FCU 4. Pipe flow direction / labelling is missing 5. Isolators is not installed yet 6. FCU thermostat is not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624009&prj=618&rqi=arTW9YtKHefc5VpklmjBatFkv6
RT1DCOS-9-001 | SG06-1 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-05-29 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1CPOS_PCP_1_CPU | DCOS - Control Panels |  |  | Onsite PCP Prosoft model was not tally with the drawing. Onsite was PLX31-EIP-MBTCP, however Drawing indicate PLX32-EIP-MBTCP (apply to all PCP panels) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623462&prj=618&rqi=LyhoqLlTNjXYfUeLuXHhePqf9u
RT1SEC-2-001 | SG06-1 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-05-29 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L2A | Documentation not issued/ Required | Commissioning | Security | system | Security - CCTV System |  |  |  | Cx2A: ACP_1 and ACP_2 ACP_9 and ACP_10 1. PSU needs to be labeled to show where /what devices it is connected to 2. Battery needs to be labelled (Installation / Start using date) 3. Earth cable within the PSU units need to be attached / installed 4. Panel earth needs to be installed on the door 5. Internal wiring needs to be terminated with proper labelling 6. Applicable to all ACP units 7. There needs to be a GA drawing of the main ACP unit so that people can identify the components within 7. In the drawing , label the PSU units 01- 07 as shown on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623494&prj=618&rqi=hzHWFmTX1s5qyNU9jQo0deggWF | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-322 | SG06-1 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2B: 1CHWSTR_1_CHWBT_1 1CHWSTR_3_CHWBT_1 2CHWSTR_1_CHWBT_1 1. Labels missing from the buffer tank , a label identifying the buffer tank needs to be installed 2. Bolts are missing from the legs of the buffer tank - where it is connected to the i beam 3. Temperature sensors are not installed on the buffer tank 4. Auto Air vents needs to be installed 5. Water directional flow needs to be added onto the pipings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623354&prj=618&rqi=4qqjWS6gNr3RAOth93jGGoSX0r
GI-321 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A: 1SF_Z_1 1EF_Z_1 Cx2A : 1SF_D_1,1SF_D_2,, 1SF_C_1 , 1SF_C_2 1SF_D_1, 1SF_D_2, 1SF_C_1 , 1SF_C_2 1. Missing document pocket 2. SF missing the tag on the equipment 3. Ducting missing the tag 4. All equipment tag must be update to the latest equipment naming 5. Drawing needs to be updated for the missing tag that is not indicated in the drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623174&prj=618&rqi=pvdHBLUECk405ExLFehu7RbdqR
GI-320 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A: 1FCU_Z_24 1FCU_Z_31 1FCU_Z_76 1. Labelling missing from the control panel 2. Document pocket is missing and not attached 3.Fuse layout in the drawing missing F3,F4,F5 4.MCI and over load relay position need to be updated in the drawing 5.TS must be removed from the drawing as it does not exist 6.Relay THR1 / DFR1 relay in the drawing is switched , and needs to be updated 7.FCU missing equipment tag 8. FCU CHW supply and return do not have their directional / flow ,markings yet on the pipe 9 . All equipment tag must be update to the latest equipment naming 10. Drawing needs to be updated 11. FCU thermostat is not installed 12. Ducting Missing tags that need to be included 13. gaps between the trunking etc needs to be sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623173&prj=618&rqi=5QHAQY1Foj9jScKIqLBQ9HAeEW
GI-317 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jessyong@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | SMBE to ensure all labels installed are as per the revised approved dwg and in addition breaker ratings AT/AF should follow as per approved studies. Please ensure the dwg indicated breaker ratings follows the approved power studies. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622958&prj=618&rqi=4ump9XneFstTlRbbANbp0vPxT8
GI-316 | SG06-1 | APAC | Open | P3 Low CX | jessyong@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | SMBE to ensure all DPM settings are set as per approved DPM alarm setpoints. Observed all levels DPM during DCOS cx3 inspection alarm setpoints are not as per approved settings. Please submit the approved settings DPM, crompton relay settings, sync check relay settings, UOVR in procore for EOR review and approval | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622957&prj=618&rqi=tPwriVljk7quMRywSiCaNodEnP
GI-314 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2a 1FCU_C_06 ,1FCU_D_06,1FCU_C_02 ,1FCU_D_02 1. Labelling missing from the control panel 2. Document pocket is missing and not attached 3.Fuse layout in the drawing missing F3,F4,F5 4.MCI and over load relay position need to be updated in the drawing 5.TS must be removed from the drawing as it does not exist 6.Relay THR1 / DFR1 relay in the drawing is switched , and needs to be updated 7.FCU missing equipment tag 8. FCU CHW supply and return do not have their directional / flow ,markings yet on the pipe 9 . All equipment tag must be update to the latest equipment naming 10. Drawing needs to be updated 11. FCU thermostat is not installed 12. Ducting Missing tags that need to be included 13. gaps between the trunking etc needs to be sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622888&prj=618&rqi=MRs4aKdK6FKcEC2vnfmArhXhq2
GI-315 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A : 1SF_D_1,1SF_D_2,, 1SF_C_1 , 1SF_C_2 1SF_D_1, 1SF_D_2, 1SF_C_1 , 1SF_C_2 1. Missing document pocket 2. SF missing the tag on the equipment 3. Ducting missing the tag 4. All equipment tag must be update to the latest equipment naming 5. Drawing needs to be updated for the missing tag that is not indicated in the drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622889&prj=618&rqi=HeRkjHEiNUKtpCdpVjP7b3KLj7
GI-308 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A: SG6-1PACV_27,26,28,29 Nitrogen panel :SG6-1NG_16,SG6-1NG_17, 1. Ensure that the condensate drain is installed 2. Document pocket needs to be affixed to the panel 3.Permanent labels to be installed 4. Wires need to be labeled Piping 1.PSV-D is not installed on the pipings 2.Ensure that the piping have its flow markings and direction as well as its permanent labels 3. Ensure that the drain pipe has drain markings affixed to it 4. Permanent labels to be installed 5. Ensure that SCV/ PACV pipings have its labels affixed on to it SAP SG6-1SAP_16,19 1. Wires need to be labeled PACP : SG6-1PACP_16 3. Wires need to be labeled Isolators for PACP / ING / SAP not installed yet at that time of the inspection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622572&prj=618&rqi=VrcojtCXxOh6RlHLNjhC921E8F
GI-311 | SG06-1 | APAC | Closed | P2 Medium CX | ericchong@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A: 2CHWSTR_M1R1_CTSF_2 1CHWSTR_M1R1_CTSF_1 1CHWSTR_M1R1_CTSF_2 1CHWSTR_M1R1_CTSF_3 1CHWSTR_M1R1_CTSF_4 1CHWSTR_M1R1_CTSF_8 1CHWSTR_M1R1_CTSF_9 1. SLD & Panel GA to be amended to reflect the correct set up. ACT to call for reinspection upon drawings approval. 2. Vessel to be cleaned prior to sand filling. 3. Missing equipment labels. 4. Typo on control panel indications 5. Missing isolation valves before the skid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622615&prj=618&rqi=3pghBGZMv1MpJ32tCsSc3St2cx
RT1DCOS-17-001 | SG06-1 | APAC | Open | P3 Low CX | siakhongneogh@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - BMS | L2A | Installation Damage | Commissioning | Controls | equipment | 1CPOS_RIO_05 | DCOS - Control Panels |  |  | Observed that the HMI has been scratched. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622408&prj=618&rqi=GR1axKD6KcWcUCZpuA6JcA8nrp
RT1DCOS-13-001 | SG06-1 | APAC | Closed | P3 Low CX | siakhongneogh@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1CPOS_RIO_01 | DCOS - Control Panels |  |  | During the Cx2A inspection, the following observations were noted (apply to all panels): 1. The equipment layout plan / setting-out drawings have not been updated to reflect the current site conditions. 2. General housekeeping and cleaning works are required. 3. To install flexible conduit/ trunking for the incoming cables 4. Pending incoming feed earth stud to loop on earth bar 5. Drawings to be in place 6. Permanent labelling shall be properly installed for incoming cables 7. To retighten and torque as per manufacturers guildelines | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622407&prj=618&rqi=DpXw34jCre25dClTDkDCUoq58x
GI-304 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2a 1FCU_z_57 , 1FCU_z_57 1. Labelling missing from the control panel 2. Document pocket is missing and not attached 3.Fuse layout in the drawing missing F3,F4,F5 4.MCI and over load relay position need to be updated in the drawibng 5.TS must be removed from the drawing as it doe snot exist 6.Relay THR1 / DFR1 relay in the drawing is switched , and needs to be updated 7.FCU missing equipment tag 8. FCU thermostat is not installed 10. Ducting Missing tags that need to be included 11. gaps between the trunking etc needs to be sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622304&prj=618&rqi=sUspkdEpZJalNncIScSqbiUwU8
GI-301 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | CX2B: Jockey pump missing its flow direction arrows , it needs to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621892&prj=618&rqi=OaVE0WQXXyAbmY3UeT2GBW7c2F
GI-300 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Cx2 A : L9 Domestic water tank 1. Tank / pump plinth at the corners need to be touched up 2. Water direction/ flow markings need to be installed 3.Anti Mosquito netting is not installed 4. Pipe overflow marking sis not indicated on the pipe yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621674&prj=618&rqi=3Af7gN8kW2egGP86ZwZBaQHpXo
GI-293 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A: SG6-1PACV_27,26,28,29 Nitrogen panel :SG6-1NG_14,SG6-1NG_15, 1.Ensure that incomming wires from isolator to panel is installed 2. Ensure that the condensate drain is installed 2. Document pocket needs to be affixed to the panel 4.Permanent labels to be installed 5. Missing ethernet module - need to check if it needs to be installed 6. Wires need to be labeled Piping 1.PSV-D is not installed on the pipings 2.Ensure that the piping have its flow markings and direction as well as its permanent labels 3. Ensure that the drain pipe has drain markings affixed to it 4. Permanent labels to be installed 5. Ensure that SCV/ PACV pipings have its labels affixed on to it SAP SG6-1SAP_14,15 1. Please ensure that batteries are installed at the sap panels 2. This defect applies to all sap panels in the building 3. Wires need to be labeled PACP : SG6-1PACP_14,15 1. Please ensure that PACP panels have batteries installed in them 2. This defect is applicable to all PACP panels 3. Wires need to be labeled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620403&prj=618&rqi=6zVSJBNRjQ9YlDDkoTCVvq7dze
GI-290 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A: SG6-1PACV_19,18,20,21,23,22,24,25 Nitrogen panel :SG6-1NG_10,SG6-1NG_11, SG6-1NG_12, SG6-1NG_12 1.Ensure that incomming wires from isolator to panel is installed 2. Ensure that the condensate drain is installed 2. Document pocket needs to be affixed to the panel 4.Permanent labels to be installed 5. Missing ethernet module - need to check if it needs to be installed 6. Wires need to be labeled Piping 1.PSV-D is not installed on the pipings 2.Ensure that the piping have its flow markings and direction as well as its permanent labels 3. Ensure that the drain pipe has drain markings affixed to it 4. Permanent labels to be installed 5. Ensure that SCV/ PACV pipings have its labels affixed on to it SAP SG6-1SAP_10, 11,12,23 1. Please ensure that batteries are installed at the sap panels 2. This defect applies to all sap panels in the building 3. Wires need to be labeled PACP : SG6-1PACP_10,11,12,23 1. Please ensure that PACP panels have batteries installed in them 2. This defect is applicable to all PACP panels 3.Wires need to be labeled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620260&prj=618&rqi=zqSMIusxQOTVHGPlfRVp5Xvo5k
GI-285 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A : UG make up water tank & accessories (All 4 Tanks) in underground room 1. Please check the tank capacity and ensure that the volume and etc is correct 2. Please ensure the electrode height is correct and accurate for all tanks 3. Net for the overflow is not installed (anti Mosquito Netting) / waring pipe also 4:Drain overflow label needs to be attached to the pipe Domestic water Tank 1. Please affix the water flow indicator on the pipe 2. Net for the overflow is not installed (anti Mosquito Netting) / warning pipe also 3. Please ensure the electrode height is correct and accurate for domestic water tank 4.Drain overflow label needs to be attached to the pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619869&prj=618&rqi=pWu0yC0nIUr16cHQ9bSVyTYLeY
GI-287 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Cx2B: NER Room: 1 FCU_Z_75 1 FCU_Z_13 Isolators installed is not the correct one , please check | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619916&prj=618&rqi=4osh1pDtjUDkGStaGzG95gppnG
GI-288 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A : Sprinkler water tank / Pipe 1.Sprinkler water tank have not spray painted the sprinkler tank capacity onto the tank / walls yet 2.The discharge pipe should be labelled 3.The water directional flow markings should be installed / affixed to the pipes | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620150&prj=618&rqi=xuS9roISjHivABNBVkVEM1L2fG
GI-284 | SG06-1 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CX2A: 1FCU_Z_75, 1FCU_M1_13, 1MAU_C_2, 1MAU_M1_07, 1MAU_D_2 & 1MAU_M1_08 In the General Lay out drawing , the position of the relays do not follow as per the as GA drawings , please check and update the position of the relay in the GA drawings , as per what that is in the panel Please also trace and check the wiring of the fuse before updating the drawings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619677&prj=618&rqi=jWY7BqrIgcwqQjsBeN29wEbePi
RT1DCOS-7-001 | SG06-1 | APAC | Closed | P2 Medium CX | RyanWu@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - BMS | L2A | Installation not complete | Commissioning | Controls | equipment | 1DCOS_CP_7 | DCOS - Control Panels |  |  | put a missing 50mA fuse at compartment 13 for 2x1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618995&prj=618&rqi=1GMkDzZItpwcUdpL6eB7mQp1cg
RT1DCOS-5-001 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_CP_5 | DCOS - Control Panels |  |  | To provide updated dwg in panel pocket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618324&prj=618&rqi=cKTGUa65u0sY2i0oUp6fbP6jZT
RT1DCOS-6-001 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_CP_6 | DCOS - Control Panels |  |  | To provide updated dwg in panel pocket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618325&prj=618&rqi=r5YOPy8QxOY0ks2G2f3EtxPRT3
RT1DCOS-4-001 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_CP_4 | DCOS - Control Panels |  |  | To provide updated dwg in panel pocket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618323&prj=618&rqi=jOpWzSV9o6XCNBVzMftr4ljTBI
RT1DCOS-3-001 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_CP_3 | DCOS - Control Panels |  |  | To provide updated dwg in panel pocket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618321&prj=618&rqi=Plg3im8Qh4941dDbs1iPsC16zE
GI-266 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A : MAP : 1. MAP drawing , needs to be updated , please insert and resubmit the drawings for review 2. Batteries need to be installed in the PACP / SAP/ MAP , with the date of installation affixed to the battery 3. Permanent labels to be installed PACP : 1. PACP GA drawing , needs to be updated , as total power failure module is not included in the GA drawing , please insert and resubmit the drawings for review 2. PACP GA drawing : Patent CP - the module needs to be named in the GA drawing 3. Permanent labels to be installed PACP / SAP: 1. Batteries need to be installed in the PACP / SAP , with the date of installation affixed to the battery This general defect is applicable to all PACP / SAP panels MAP / SAP / RP / Mimic Panels 1. Please ensure that the incoming power cables are terminated prior to CX2B inspections 2. Permanent labels to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618261&prj=618&rqi=KuBEPqs0IXXe6ZJhV8FwYqqmzk
GI-264 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor - BMS |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | CX2A visual inspection conducted for 1DCOS_CP_3,4,5,6, observed the following issues 1. Cable sheath to reinstall at enclosure, not at gland plate once trunking is installed 2. Missing danger sign 3. Missing engraved sign for PE and TH1 4. Incorrect PLC part number in dwg 5. To update dwg on IE grounding 6. Provide additional 50mA fuse within the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618201&prj=618&rqi=Jp60FU1s5pyTbp4X5KdHMfNuPo
GI-263 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General Design Issue | Design |  | equipment type |  |  |  |  | LVSB SOO to include transferring system to maintenance bypass procedures and the panels involved in the transfer process, including but not limited to ups system, udp/umdsb/or any associated panels and MSBs. Update soo to submit to procore for EOR review and approval. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618105&prj=618&rqi=ZiSTCfThSlIlgA2vkhwkKTK18a
GI-262 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A SG6-1SCV_10,12,11 1.Ensure that the piping have its flow markings and direction as well as its permanent labels 2. Ensure that the drain pipe has drain markings affixed to it 3. Flow meter for SCV is not installed yet 4. Permanent labels to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617960&prj=618&rqi=VroJK8fC8hEsrkn593O3l5jBLx
GI-261 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A: SG6-1PACV_13,12,17,16,15,14 Nitrogen panel :SG6-1NG_07 ,SG6-1NG_09 , SG6-1NG_08 1. Missing labels within the nitrogen panel 2. Requires SLD / GA drawing to be placed / affixed in panel / sent to HDR for approval 3. Ensure that incomming wires from isolator to panel is installed 4. Ensure that the condensate drain is installed 5.Document pocket needs to be affixed to the panel 6.Permanent labels to be installed 7. Missing ethernet module - need to check if it needs to be installed 8. Wires need to be labeled Piping 1.PSV-D is not installed on the pipings 2.Ensure that the piping have its flow markings and direction as well as its permanent labels 3. Ensure that the drain pipe has drain markings affixed to it 4. Permanent labels to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617959&prj=618&rqi=02ZXlC51xUIvzkA2YPHA4ApEjZ
GI-254 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A: SG6-1PACV_11,10,07,06,09,08 Nitrogen panel :SG6-1NG_06 ,SG6-1NG_04 , SG6-1NG_05 1. Missing labels within the nitrogen panel 2. Requires SLD / GA drawing to be placed / affixed in panel / sent to HDR for approval 3. Ensure that incomming wires from isolator to panel is installed 4. Ensure that the condensate drain is installed 5.Document pocket needs to be affixed to the panel 6. Permanent labels to be installed 7. Missing ethernet module - need to check if it needs to be instaled 8. Wires need to be labeled Piping 1.PSV-D is not installed on the pipings 2.Ensure that the piping have its flow markings and direction as well as its permanent labels 3. Ensure that the drain pipe has drain markings affixed to it | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617834&prj=618&rqi=spYtq5ZAYEdQqgfv7OqCQlLAmv
GI-248 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A SCV 05,06 1.Ensure that the piping have its flow markings and direction as well as its permanent labels 2. Ensure that the drain pipe has drain markings affixed to it 3. Flow meter for SCV is not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617728&prj=618&rqi=tEI0pyZhxzFiGVq5gLLOwjoNt0
GI-255 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A SCV 09,07,08 1.Ensure that the piping have its flow markings and direction as well as its permanent labels 2. Ensure that the drain pipe has drain markings affixed to it 3. Flow meter for SCV is not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617835&prj=618&rqi=8U4tq5Ehy26VMwF7yiibhVDIP8
GI-247 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A: SG6-1PACV_02,0304,05 Nitrogen panel : SG6-1NG_02, SG6-1NG_03 1. Missing labels within the nitrogen panel 2. Requires SLD / GA drawing to be placed / affixed in panel / sent to HDR for approval 3. Ensure that incomming wires from isolator to panel is installed 4. Ensure that the condensate drain is installed 5.Document pocket needs to be affixed to the panel 6. PSV-D is not installed on the pipings 7. Permanent labels to be installed on panels 8. Missing ethernet module - need to check if it needs to be installed 9. Wires need to be labeled Nitrogen panel :SG6-1NG_03 1. Panel has scratches on it that needs to be buffed out 2. Panel wording below has been damaged , please touch up 3. Permanent labels to be installed on panels 4. Missing ethernet module - need to check if it needs to be installed 5. Wires need to be labeled Piping: 1.PSV-D is not installed on the pipings 2.Ensure that the piping have its flow markings and direction as well as its permanent labels 3. Ensure that the drain pipe has drain markings affixed to it 4. Permanent labels to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617676&prj=618&rqi=PEWRCYSjaKTbkAQKO4DkbgCHqB
GI-243 | SG06-1 | APAC | Closed | P2 Medium CX | RyanWu@commtechasia.com | 2026-04-08 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Replace the earth cable "FROM MFEB ELEC RISER 5B-2" at level 5 FEB STS 5B as insulation is scratched to the point can see copper inside | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617515&prj=618&rqi=OMpwWw11kW0DjEkBDaplBcLIiX
GI-245 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A SCV 1,2,34 1.Ensure that the piping have its flow markings and direction as well as its permanent labels 2. Ensure that the drain pipe has drain markings affixed to it 3. Flow meter for SCV is not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617540&prj=618&rqi=xreupxcXiw01TTv7TxfAypNe2n
GI-246 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2A Mimic Panel / Repeater panel 1. SLD and GA is required of the mimic / repeater panel pending submission and approval from HDR 2. Permanent labels to be installed on panels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617546&prj=618&rqi=2a8hcysUZMok5TY3fJeE6jYj4S
RT1DCOS-2-001 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-02 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_CP_2 | DCOS - Control Panels |  |  | Cx2A : DCOS_CP_02: 1. Cable entry edge needs to be protected by a rubber sleeve to prevent the sharp edge from cutting / damaging the cable 2. Light needs to be indicated in the GA drawing 3. the door panel earth needs to be checked its the approved type 4. Danger stickers to be affixed to panel before energization 5. Document pocket needs to be affixed to panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617168&prj=618&rqi=sENiKtVYazMjm1Iy6MBc1g3e9u
RT1DCOS-1-001 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-02 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_CP_1 | DCOS - Control Panels |  |  | Cx2A : DCOS_CP_01: 1. Cable entry edge needs to be protected by a rubber sleeve to prevent the sharp edge from cutting / damaging the cable 2. Light needs to be indicated in the GA drawing 3. The door panel earth needs to be checked its the approved type 4. Danger stickers to be affixed to panel before energization 5. Document pocket needs to be affixed to panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617166&prj=618&rqi=lWUqt8JX2Zw8Yw5CNK0FflK2eh
GI-234 | SG06-1 | APAC | Closed | P3 Low CX | KeeLeongLee@commtechasia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Observed during Cx2B earthing inspection, all the earth bar is not labelled. Affected earth bar as below: 1. MFEB ELEC RISER 9A-2 2. FEB-1-E-WALL-9A 3. FEB-2-E-WALL-9A 4. FEB UG MUWP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616629&prj=618&rqi=e7h5MTjIBuslCMKg2ojMmF4O8P
GI-231 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2a 1CHWSTR_03_HX 1CHWSTR_02_HX 1CHWSTR_04_HX 1CHWSTR_09_HX 1CHWSTR_10_HX 1. The hex is missing a equipment label to be affixed to the hex 2. The name on the nameplates need to be updated to the newest naming 3. 1CHWSTR_02_HX - there is a dent that needs to be combed on the hex -CLOSED 4 . The chilled water / condenser water pipes need to have label on where is supply and return 5., Pipe flow arrows / naming is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616361&prj=618&rqi=RFzxr53TsplkxFpFiaU041bcfV
GI-229 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-23 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CxL2a: LV MFEB B for LV to MFEB ELEC RISER 5B-2 Drawing needs to be updated on the position if the Note one ( Cable Tray Earth) , as well as the position of the Incomming earth wire from LV MFEB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616167&prj=618&rqi=8JlsXKcvEUv6twdnYt8f1jLxRQ
GI-228 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-23 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Cx2a LV MFEB B to FEB UG MUWP Room : 1, Label on the earth wires ( 1/2 ) in the MUWP underground room needs to be changed From LV MFEB 1B -(1) ( L1 CSR 1B) / From LV MFEB 1B -(1) ( L1 CSR 1B) " 1" Prefix in front of the B is advised to be removed . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616166&prj=618&rqi=H2MzE9Bc8pZCZSgyvYaaLLvegy
GI-226 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-20 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx L2 A : 1FCU_Z_73 / 1FCU_7_74 /1FCU_C_04 /1FCU_D_04 /1FCU_A_15, 1FCU_A_16 1. Label tag is missing on the FCU panel 2. Thermostat is not installed on the FCU 3. There is no TS in the panel , but there TS shown and indicated on the drawings 4. The relay THRI / DFR1 position in the GA is shown as swapped , GA needs to be updated 5. Location of the MC1 needs to be shifted down in the GA drawing 6.OL1 - Model in the panel is shown as LRD06 , drawing shows as LRD08 , drawing needs to be updated 7. Dirty Filter Status of the field device X1.3 , X1.4 - needs to change to 13/A / 14 /A 8. Fan Speed Command needs to change X3.18 to 21 B 9. Document pocket is not attached to the panel 11. Label on FCU needs to be affixed 12 . Labels need to be attached to the ducting 13. gaps between the trunking etc needs to be sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616122&prj=618&rqi=OBUVHP2vDZtYSWIBrXF1bSIhGe
GI-209 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx L2 A : 1FCU_C_09 / 1FCU_D_09 /1FCU_D_10 /1FCU_C_10 /1FCU_M1_29 1. Label tag is missing on the FCU panel 2. Thermostat is not installed on the FCU 3. There is no TS in the panel , but there TS shown and indicated on the drawings 4. The relay THRI / DFR1 position in the GA is shown as swapped , GA needs to be updated 5. Location of the MC1 needs to be shifted down in the GA drawing 6.OL1 - Model in the panel is shown as LRD06 , drawing shows as LRD08 , drawing needs to be updated 7. Terminal block for field device should be shown as X1, X2 - safety provision switch /- needs to be updated in the drawing 8. Common alarm status wire U13/14 appears to be swapped 9. PICV Feed back X3.21 - Missing Cable and cable is not attached 10. Document pocket is not attached to the panel 11. Label on FCU needs to be affixed 12. Ducting Missing tags that need to be included 13. gaps between the trunking etc needs to be sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615450&prj=618&rqi=XtW0aUtm5zQqC9jP64CuYvMu6h
GI-208 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CxL2a 1 SF _Z_6 , 1 SF _Z_7 1. Please ensure that plastic wrapping for the SF are removed 2. Please ensure that there is a big visible label for the SF 3. Please ensure that the earth cable is labelled 4. Please update the GA to show that the transformer is installed at the bottom of the panel and not at the top 5. Please check if the FIRE SIGNAL is labelled as 15/A , 16 A ( drawing ) or 13 / 14 A ( installed on site ) 6. Terminal block is missing its label , in the panel , please install the label 7. Please update the General Arrangement drawing the FCU - Fuses Behide door , should be fuses behind door 8. Document pocket is missing and is not added to the panel 9. Ensure that the fuses behind the door is has a label affixed to it 10. In the GA , fuses behide the door should be updated 11. Unit strut needs to be shortened with end caps installed on them 12. Ducting Missing tags that need to be included 13. gaps between the trunking etc needs to be sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615448&prj=618&rqi=rICoy0Z8ErOcEQOY6xK2Ivpigr
GI-206 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx L2 A : 1 FCU_D_08, 1 FCU_C_08,1 FCU_Z_61, 1 FCU_Z_62 1. Label tag is missing on the FCU panel 2. Thermostat is not installed on the FCU 3. There is no TS in the panel , but there TS shown and indicated on the drawings 4. The relay THRI / DFR1 position in the GA is shown as swapped , GA needs to be updated 5. Location of the MC1 needs to be shifted down in the GA drawing 6.OL1 - Model in the panel is shown as LRD06 , drawing shows as LRD08 , drawing needs to be updated 7. Terminal block for field device should be shown as X1, X2 - safety provision switch /- needs to be updated in the drawing 8. Common alarm status wire U13/14 appears to be swapped 9. PICV Feed back X3.21 - Missing Cable and cable is not attached 10. 1 FCU_Z_61 - cable came off during the inspection , and needs to be tightened 11. Document pocket is not attached to the panel 12. Label on FCU needs to be affixed 13. Ducting Missing tags that need to be included 14. gaps between the trunking etc needs to be sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615342&prj=618&rqi=C6JEALXigwAfTE0lQQDeIRVbWg
GI-205 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CX2A 1SF_Z_10, 1SF_Z_11, 1SF_Z_14,1SF_Z_15 1. Fuses behind the door spelling in the GA is wrong 2. Transformer location in the GA is also wrong and needs to be updated in the GA drawing 3. OL Settings need to be confirmed 4. Labels need to be attached on the Supply Fan it self 5. Labels also need to be attached to the ducting 6. Document pocket is not attached to the panel 7. Unit strut needs to be shortened with end caps installed on them | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615341&prj=618&rqi=Z7oJDdAK5KzPBFlO4zaEGumqpY
GI-203 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A, 1 FCU _Z_ 43 , 1 FCU _M1_49 , 1 FCU _Z,49 , 1 FCU _Z_50 1. FCU thermostat is not installed 2. FCU Control panel missing the equipment tag 3. There is no TS in the panel , but it is shown in the drawing 4. Location of the MC1 needs to be updated in the General Arrangement Drawing 5. F5 needs to be added into the General Arrangement Drawing 6. Relays THRI / DFRI position in the general arrangement is swapped 7. Terminal block X1 ( Provision safety switch ) / (EC Fan Fault Signal) / Dirty Filter Alarm status needs to be updated in the drawing as the naming does not tally on site and also at the drawing 8.Document pocket is missing and is not added to the panel 9. Label on FCU needs to be affixed 10. Ducting Missing tags that need to be included 11. gaps between the trunking etc needs to be sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615198&prj=618&rqi=qebd84GLGh1xdo6qbuSPIGTpCy
GI-201 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CxL2a 1 SF _Z_10 , 1 SF _Z_11, 1 SF _Z_14, 1 SF _Z_15 1. Please ensure that plastic wrapping for the SF are removed 2. Please ensure that there is a big visible label for the SF 3. Please ensure that the earth cable is labelled 4. Please update the GA to show that the transformer is installed at the bottom of the panel and not at the top 5. Please check if the FIRE SIGNAL is labelled as 15/A , 16 A ( drawing ) or 13 / 14 A ( installed on site ) 6. Terminal block is missing its label , in the panel , please install the label 7. Please update the General Arrangement drawing the FCU - Fuses Behide door , should be fuses behind door 8. Document pocket is missing and is not added to the panel 9. Ensure that the fuses behind the door is has a label affixed to it 10. In the GA , fuses behide the door should be updated 11. Unit strut needs to be shortened with end caps installed on them | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615116&prj=618&rqi=6moZMZJW6t2n7k39uCPdffzjTT
GI-200 | SG06-1 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | CX2A MV Fan: 1EF_Z_4 1EF_Z_5 1. Missing label on the ducting. 2. Debris to clean. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615048&prj=618&rqi=evATnppMMQKkyMqOcdT7b2KFSo
GI-193 | SG06-1 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-03-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Earthing Cx2A Earthing from MV FEB B / A to CSS ( RMU ) 12 way Earth bar type and dimensions installed on site in the RMU differ from type / dimension shown in the drawing The 12 way EB shown in the drawing is split into two and has a test link connected to it where else on site the bar is just straight, without a test link and is different from the one that is installed Please check and advise on the dimensions on which one is correct | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614805&prj=618&rqi=pDVI3cfHyB66UDagIDZspv1haO
GI-191 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A : During CX2a visual inspection it was observed that the STS enclosure IP rating ,does not match approved drawing 1. Please refer to the email thread attached 2. Please also include pictures of the rectified enclosure as reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614765&prj=618&rqi=HubwM7TSpTl3yZyeOFP7IH0BKd
GI-192 | SG06-1 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CX2A Buffer tank: 1. 2CHWSTR_2_CHWBT_1 has damaged insulation and dented. 2. All three Buffer Tanks 1CHWSTR_01_CHWBT_1, 2CHWSTR_2_CHWBT_1 & 1CHWSTR_02_CHWBT_1 leg insulation below the base is incomplete and not fully covered. 3. Issue with 1CHWSTR_02_CHWBT_1 and 1CHWSTR_04_CHWBT_1, on the approved drawing 1CHWSTR02_CHWBT_1, have "1CHWSTR_04_CHWBT_1" on its name plate and 1CHWSTR_04_CHWBT_1 have "1CHWSTR02_CHWBT_1". AccessTech to check approved drawings and change name plates. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614789&prj=618&rqi=5k9BrIAz8k21HLxKCC5x6249QB
GI-189 | SG06-1 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CX2A Issue FCU_M40 & FCU_Z60 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Only FCU Panels have labels, No Labelling for FCU itself. 3. Temperature Thermostat to be installed in all FCU rooms. 4. Approved drawing, general arrangement discrepancy of components. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. PSU 50W is also in the incorrect area. Drawing to be updated and approved. 5. Incoming Terminal for FCU Panel, termination is incomplete 6. Dirty Filter Alarm Status, X1.3 & X1.4, drawing indicates 1B & 13/A, on site shows 13/A & 14A. 7. Fan Speed Command, X3.18, drawing indicates 6/B, on site shows 2/B. 8. Control Circuit Diagram 1 Drawing indicates OL1 LRD16 (9 ~ 13), onsite shows LRD08 (2.5 ~ 4) 9. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 10. Drawing Pocket to be installed in FCU panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614688&prj=618&rqi=PYwfm4Hau3pI1HBZRX1G3ig8gP
GI-188 | SG06-1 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | CX2A Issues FCU_Z53, FCU_Z54 & FCU_Z55 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Only FCU Panels have labels, No Labelling for the FCU itself. 3. Temperature Thermostat to be installed in all FCU rooms. 4. Approved drawing, general arrangement discrepancy of components. Magnetic Contactor (MC1) and Overload (OL) Relay is in the incorrect area. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. TS Relay to be remove in drawing. Drawing to be updated and approved. 5. Incoming Terminal for FCU Panel, termination is incomplete 6. Dirty Filter Alarm Status, X1.3 & X1.4, drawing indicates L1B & 13/A, on site shows 13/A & 14A. 7. Fan Speed Command, X3.18, drawing indicates 6/B, on site shows 2/B. 8. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 9. Drawing pocket for panel to be installed 10. FCU_Z53 location to be update in the floor plan layout 11. FCU_Z54 cable pulling test failed. 1FCU_Z_54_CP_LCP_UI1 cable is broken during the cable pull test. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614687&prj=618&rqi=GCudhXiSmqjP4nevX3AjTWL0kd
GI-190 | SG06-1 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A Issues FCU_M56 & FCU_Z27 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Only FCU Panels have labels, No Labelling for the FCU itself. 3. Temperature Thermostat to be installed in all FCU rooms. 4. Approved drawing, general arrangement discrepancy of components. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. PSU 50W is also in the incorrect area. Drawing to be updated and approved. 5. Incoming Terminal for FCU Panel, termination is incomplete 6. Dirty Filter Alarm Status, X1.3 & X1.4, drawing indicates 1B & 13/A, on site shows 13/A & 14A. 7. Fan Speed Command, X3.18, drawing indicates 6/B, on site shows 2/B. 8. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 9. Drawing Pocket to be installed in FCU panel 10. Not able to tally FCU S/N due to inaccessibility. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614690&prj=618&rqi=PzBdRq9JfIMDEK75KO53CoGTwY
GI-185 | SG06-1 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A Issue 1FCU_M1_33, 1FCU_C_12, 1FCU_M1_34, 1FCU_D_13 in STS ROOM A & STS ROOM B 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Only FCU Panels have labels, No Labelling for the FCU itself. 3. Temperature Thermostat to be installed in all FCU rooms. 4. Approved drawing, general arrangement discrepancy of components. Magnetic Contactor (MC1) and Overload (OL) Relay is in the incorrect area. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. PSU 50W is also in the incorrect area. Drawing to be updated and approved. 5. Incoming Terminal for FCU Panel, termination is incomplete 6. Dirty Filter Alarm Status, X1.3 & X1.4, drawing indicates 1B & 13/A, on site shows 13/A & 14A. 7. Auto Mode & Common Alarm, drawing indicates U12 & COM respectively, on site it is swapped COM & U12. 8. Fan Speed Command, X3.18, drawing indicates 6/B, on site shows 2/B. 9. Control Circuit Diagram 1 Drawing indicates OL1 LRD16 (9 ~ 13), onsite shows LRD10 (4 ~ 6) 10. STS ROOM A & B, unable to check the S/N of FCU Units 11. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 12. Drawing Pocket to be installed in FCU panel 13. Not able to tally FCU S/N due to inaccessibility. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483507&prj=618&rqi=b8HW8qcGqZLg470bncjZPRo6ds
GI-186 | SG06-1 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A Issue 1FCU_C_11, 1FCU_D_11 & 1FCU_D_12 in TER 5A & TER 5B2 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Only FCU Panels have labels, No Labelling for the FCU itself. 3. Temperature Thermostat to be installed in all FCU rooms. 4. Approved drawing, general arrangement discrepancy of components. Magnetic Contactor (MC1) and Overload (OL) Relay is in the incorrect area. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. TS Relay is missing in drawing. Drawing to be updated and approved. 5. Incoming Terminal for FCU Panel, termination is incomplete 6. Dirty Filter Alarm Status, X1.3 & X1.4, drawing indicates L1B & 13/A, on site shows 13/A & 14A. 7. Fan Speed Command, X3.18, drawing indicates 6/B, on site shows 2/B. 8. Control Circuit Diagram 1 Drawing does not indicate OL1 Model and Range 9. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 10. Drawing pocket for panel to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483508&prj=618&rqi=OoovIsqi91Z8OK6sKUknDkPNqC
GI-187 | SG06-1 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A Issues 1FCU_M1_55_CP & 1FCU_Z_26_CP 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Temperature Thermostat to be installed in all FCU rooms. 3. Approved drawing, general arrangement discrepancy of components. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. Drawing to be updated and approved. 4. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 5. Drawing Pocket to be installed 6. For 1FCU_M1_55_CP, earth cable is not terminated to the panel earth bar. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483511&prj=618&rqi=Iw0ZOnvpbE42iJefPQV2IXbXyP
GI-217 | SG06-1 | APAC | Closed | P3 Low CX | ericchong@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - BMS |  | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_CP_7 | DCOS - Control Panels |  |  | Cx1 FWT: 1DCOS_CP_07: 1. Danger sign not pasted during FWT. RVS to paste on site after confirming the sign design. 2. Incoming/outgoing cable management to be done onsite. 3. To add label on trunking lid adjacent to respective terminal block. Missing label are GWP_01, 1XO and 2XO. 4. To change the wire tagging of DI terminal blocks connected to Extension PLC module, to tally with latest as-built drawing. 5. Drawing: DO relays (1XO, 2XO) to be updated in the drawing, tally with existing panel. 6. Drawing: To change the incoming cable labelling to â€œTBX:L / TBX:Nâ€, tally with existing wire tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615696&prj=618&rqi=OZPpNkjRDQXJU44unaV0RNGy2f
GI-216 | SG06-1 | APAC | Closed | P3 Low CX | ericchong@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - BMS |  | Documentation not issued/ Required | Commissioning | Controls | equipment | 1DCOS_CP_3 | DCOS - Control Panels |  |  | Cx1 FWT: 1DCOS_CP_03, 1DCOS_CP_04, 1DCOS_CP_05, 1DCOS_CP_06 1. Danger sign not pasted during FWT. RVS to paste on site after confirming the sign design. 2. Incoming/outgoing cable management to be done onsite. 3. Drawing: DO relays (1XO, 2XO) to be updated in the drawing, tally with existing panel. 4. Drawing: To change the incoming cable labelling to â€œTBX:L / TBX:Nâ€, tally with existing wire tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615692&prj=618&rqi=Gnd1FZpOKxZRmobIyC43gbl9fP
GI-184 | SG06-1 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-02-26 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | As per HDR comment, for OPSFLEX Rm, STS Rm and Ewall Rm to install 50x6mm2 earth bar. Engie to rectify as per HDR comment and submit the revise dwg to procore for official approval. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483397&prj=618&rqi=KAbGmMmBfAHOBqnBhfcVOA7JS2
GI-183 | SG06-1 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Engie to update the following, 1. Earthing overall SLD to update FEB EWALL 2A-1 and 2 cables connection, including incorrect location installed as per the approved layout, submittal 1502. 2. MFEB elec riser 2A to update in overall SLD, current earthing cables connection does not align with the approved SLD 3. Missing main label for all earthing bar 4. Observed earthing cable sleeve installed at cable tray. Engie to replace. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483396&prj=618&rqi=HgMrZUsKwU0Fj30Mw1ANuBYNB4
GI-176 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-02-22 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A - 1FCU_Z_05, 1FCU_Z_65, 1FCU_Z_66,1FCU_Z_67 1. Labelling not installed on the FCU 2. Thermostat is not installed yet 3. Ensure that the earthing cable (Trunking ) is terminated 4. FCU name plate is installed on to the Control panel as per GA drawing 5. Relay THRI / DFRI location is swapped in the drawing and needs to be updated in the GA drawing 6. There is no TS relay in the panel , please check and update the drawing 7. Incoming cable needs to be terminated and labelled 8. Fuse F3 needs to be updated in the SLD , F3 / F4 should be labelled as F4 / F5 respectively in the SLD | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199740&prj=618&rqi=lpUaOhxPVCbuXh1N6y2Ptf2KIT
GI-182 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-02-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Observed incorrect cable size installed for all UMDSB panels. Drawing indicated internal power cables size as 50 sqmm but on site/actual installation measured 35sqmm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199753&prj=618&rqi=gY3w1SHUONhVHjc1pQnArsobJv
GI-177 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-02-22 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A - 1FCU_Z_72,1FCU_M1_45, 1FCU_C_13, 1FCU_Z_26, 1FCU_M1_35 1. Labelling not installed on the FCU 2. Thermostat is not installed yet 3. Ensure that the earthing cable (Panel) is terminated 4. FCU name plate is installed on to the Control panel as per GA drawing 5. Relay THRI / DFRI location is swapped in the drawing and needs to be updated in the GA drawing 6. Incoming cable needs to be terminated and labelled 7. Fuse F3 needs to be updated in the SLD , F3 / F4 should be labelled as F4 / F5 respectively in the SLD | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199741&prj=618&rqi=xHUw1aWYWgZbtvMvz79RWjHgI9
GI-181 | SG06-1 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-02-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Incorrect heater watt installed for all LVSB panels. As per dwg is 55W. 1UDP_C1, 1UDP_C2, 1UDP_D1, 1UDP_D2, 1MDSB_C, 1UMDSB_C, 1UMDSB_D, 1MDSB_Z2, 1MDSB_Z3, 1MDSB_R1_2, 1MSB_Z 1LBSB_ZR1_2, 1MDSB_M1_1_1_5, 1UDP_Z, 1 MDSB_Z1, 1LBSB_ZR1_1, 1LBSB_ZR1_2 To update for all LVSB panels and insert the updated approved dwg in the panel pocket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199750&prj=618&rqi=L4Heb6nALJIpOOo2x6SwxDZfBY
GI-173 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx L2A - General Issues for FCU / EF / SF 1. Please ensure that there are permanent labels affixed to the Equipment / Control Panels 2. Ensure that there is a document pocket affixed to the control panel 3. FCU - Ensure that permanent labels are affixed to the thermostats of the FCU when they are installed 4. FCU name plate is installed on to the Control panel as per GA drawing 5. Ensure that the earthing cable (Trunking) is terminated 6. Unit strut needs to be shortened with end caps installed on them 7. The Ducting needs to have label applied to them | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199135&prj=618&rqi=y4qX9jCI4CxPHO0WTYOBwMR4nb
GI-171 | SG06-1 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-02-11 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Cx2A General Issues for all FCUs 1. Thermostat for FCU only installed in Rooms FER B-2 and TER B-2 for mockup, before Cx2B testing all thermostat to be installed -CLOSED 2. Only FCU Panels have labels, the FCUs itself do not have labelling, all FCUs to have labels before Cx2B. -CLOSED 3. Unable to check the fan coils and identify the sensors/components inside the FCU due to either inaccessibility or already joint with duct, arrangement to be made to verify condition of coil and any components such as sensors or dampers (if applicable). -CLOSED 4. 1FCU_Z_65, 1FCU_Z_66, 1FCU_Z_67, 1FCU_Z_72, 1FCU_M1_45, 1FCU_C_13, 1FCU_M1_35 signaling and power cable not terminated, unable to do Cx2A. -CLOSED 5. 1FCU_Z_05 Unable to do Cx2A, because FER ROOM 1B-2 not accessible. -CLOSED 6. 1FCU_Z_06_CP, 1FCU_M1_54_CP, 1FCU_Z_48_CP, 1FCU_M1_50_CP, Typical panels. Approved drawing, general arrangement discrepancy of components. Magnetic Contactor (MC1) and Thermal Overload Relay is in the incorrect area. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. PSU 50W is also in the incorrect area. Drawing to be updated and approved 7. 1FCU_Z_03_CP, 1FCU_Z_04_CP, 1FCU_Z_40_CP, 1FCU_Z_41_CP, 1FCU_Z_42_CP Typical Panels. Approved drawing, general arrangement discrepancy of components. Magnetic Contactor (MC1) and Thermal Overload Relay is in the incorrect area. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. TS Relay is not shown in the approved drawing but is present inside the panel on site. Drawing to be updated and approved. 8. Second Labelling above the R/S/T Light on panel missing, However GA Drawing shows Labelling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199127&prj=618&rqi=bOzPjmmiVxaQwBLgkE0cyOv72t
GI-166 | SG06-1 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-02-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | CxL2A : 1.Pump label to be updated as label to be updated as per latest approved naming. 2. Document pocket is missing and is not added to the panel Issue is applicable also to hose reel pump and jockey pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199044&prj=618&rqi=UrTT8CnsD9ulPmKWCjgbIVkXXU
GI-139 | SG06-1 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | For All STS panels Observed the following issues 1. IP21, however there is no cover at the bottom of the panel 2. No GA, no fuse breaker/rating, no PCBs (QB540S1/2, QB120.4, QB102.1, QB102S1/2, ST630 S1/2 etc) labels indicated in approved drawing. 3. Incorrect fuse numbering on approved dwg 3. no phase labels installed at busbar 4. to install on/off label at isolator Q51 5. missing label for key exchange box and key lock 6. to check if busbar mimic label can be installed on panel door 7. Poor adhesion observed on heatshrink(bubbling on heat shrink tubing) 8. socomec to check as per IEC on the minimum distance between phase busbar and ensure design comply Socomec to rectify before Cx2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198100&prj=618&rqi=GpJoxqmsAna3oVB630Eo6fEMui
GI-138 | SG06-1 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | For ALL STSSB observed the following issues 1. Incorrect fuse installed at F18, instead of 20A, 10A was installed instead - CLOSED 2. no fuse rating label install for F18, 18A, 18B, 18C, 18D - CLOSED 3. install label for MOXA - CLOSED 4. Missing terminal numbering on 1X2, to include control drawing for 1X2 circuit in drawing - CLOSED 5. Missing phase label indication on busbar - CLOSED 6. Missing busbar mimic label on panel - CLOSED | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198099&prj=618&rqi=gFcKa2UWWGGDePwqRrC0AVMeYm
GI-068 | SG06-1 | APAC | Closed | P2 Medium CX | ericchong@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | Cx1 DCOS SFAT2 (19-20 Jan) Refer to issue tracker in attachment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197213&prj=618&rqi=hbjZV4DQDN26NwmXoJKMM12iAU
GI-067 | SG06-1 | APAC | Closed | P1 High DCOS | ericchong@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | General Contractor - BMS |  | Documentation not issued/ Required | Commissioning | Controls | equipment | 1CPOS_PCP_1_CPU | DCOS - Control Panels |  |  | Cx1 CPOS SFAT (19-Jan): Refer to issue tracker in attachment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197212&prj=618&rqi=q4lQ3Z6HwarMhkRGeIkLkclAFW
GI-064 | SG06-1 | APAC | Closed | P3 Low CX | YenBinChai@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Equipment: 1UMDSB_R1_7, 1UMDSB_M1_2_1, 1DB_Z2_1_01, 1DB_Z2_2, 1DB_Z1_1, 1DB_Z2_2_03 Issue: The outgoing label is currently missing because the existing SLD does not indicate any outgoing feeders. It will be finalized based on the approved naming convention and updated SLD. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196922&prj=618&rqi=VyoYskIZM4URz2oMIRFezicYPh
GI-061 | SG06-1 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-01-09 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | CxL1 Rehlko KD-3500-E FWT DCOS Issues DCOS(Action from DCOS Team, to update the deviation in the elec points list and coordinate with WH to submit for approval) â€¢ Incorrect Genset command status in faceplate â€¢ Incorrect gen operating status(status remained in gen fault) in faceplate â€¢ Incorrect gen run status(running emergency service/running non-emergency service) in faceplate â€¢ Alarm severity not as per dcos elec points list rev.4 â€¢ Incorrect load capacity % status on summary page â€¢ SMS/Alertops to test during Cx2/3 (not available during FWT) â€¢ Load current, kVAR shown out of limits range during load test with DCOS â€¢ To enquire low coolant level alarm on alarms page. (As per Rehlko, GEN only has low coolant level shutdown) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196654&prj=618&rqi=uwSuTWKx5n9y9CEiiJoaUmPCj2
WTELEC-3-002 | SL02x-2 | APAC | Closed | P3 Low CX | youngjinkim@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | Multi-Discipline | system | Electrical system |  |  |  | (Cx-Elec-L5) 1ATS_M3R2_75 common alarm observed during M3 block's dead bus test. During the ATS transfer for VRFOD, a common alarm was observed temporarily. While the ATS transfered successfully, the feedback received by ATS controller was otherwise, leading to the common alarm. The alarm normalized automatically in a few min. Please check the ATS condition on site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615742&prj=450&rqi=e9yafQALWdV6gFKmG33jo7fw6j | https://equinix.facilitygrid.co.uk/x/project/450/system/13552
WTMECH-9-002 | SL02x-2 | APAC | Closed | P3 Low CX | donghunsong@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | General Contractor | L5 | Missing Components | Commissioning | Multi-Discipline | system | Mechanical system |  |  |  | ( CxA-L5-MECH IST(4F)) During the UPS Room N-condition test, one SLA temperature in the UPS room exceeded 35Â°C. Therefore, the airflow limit of the relevant CRAH was increased from 80% to 100%, after which the UPS room temperature was maintained at or below 35Â°C. Confirmation from the design team is considered necessary regarding this temperature exceedance. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615105&prj=450&rqi=SRiiKKfzJ6EZ0GjVY1PYc5nItQ | https://equinix.facilitygrid.co.uk/x/project/450/system/13553
WTELEC-2-001 | SL02x-2 | APAC | Closed | P3 Low DCOS | junghohan@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Subcontractor |  | DCOS General Issue | DCOS | Multi-Discipline | system | Electrical system |  |  |  | (L5-CxA-DCOS) PUE and total IT load cannot be monitored on the DCOS dashboard graphics. The Tranche 2 IT load is not combined with the Tranche 1 value. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197512&prj=450&rqi=wJIytIjq4uk6t9RLphpPYtxlVp | https://equinix.facilitygrid.co.uk/x/project/450/system/13552
GI-103 | SL02x-2 | APAC | Closed | P3 Low DCOS | youngtaekkim@commtechasia.com | 2026-01-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | (L4-CxA-MECH) During the ICOM failure test process, a Temperature High-High alarm is being triggered due to a fault value, although it should not occur under this test condition. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196628&prj=450&rqi=ZztAg6l3f4VAzmkCIa79MECUD2
GI-102 | SL02x-2 | APAC | Closed | P3 Low DCOS | seungdeokseo@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | (L4-CxA-Elec) The circuit breaker status is not displayed correctly after server integration during LIB test During the Battery L4 discharge test conducted after server integration, it was observed that the UDP_E2_OUT_3 circuit breaker was closed and supplying load, but its status was not displayed correctly. After correction, it appears necessary to perform the test again to verify proper operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196320&prj=450&rqi=jCTsUy10oS0xHZXTDiizjOwdQq
GI-050 | SL2x-F2 | APAC | Closed | P3 Low CX | youngtaekkim@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | (CxA-MECH-L3) The 4F STS RM text on DCOS is hidden by overlapping SIM text, making it unreadable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196415&prj=509&rqi=US2UQ9tSu3WIcoInRx11xT4xN0
RT1ELEC-35-001 | SP03-P2 | AMER | Open | Outstanding Paperwork/Documentation | celso.okuyama@lzaengenharia.com.br | 2026-08-26 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | TX-PG-AUX-1.1 | TX - 480v-208/120 Transformer |  |  | GC Inspection checklist is approved on Project Portal and appended to the document section of this checklist | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635335&prj=693&rqi=pP011VSr5X9EnnrJKniUgqd8hC
SOR-4-001 | SV11-P2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-03-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs BMS) Fan status not working correctly at the BMS. Confirmed by Delta that the Modbus point for Fan Status (Binary) is not functioning correctly. Will need to be resolved and potentially applied to new projects as a software / firmware update. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615862&prj=624&rqi=rguBKrgs4CURXYYa9OnehsaKIr
GI-135 | SV11-P2 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Incomplete Connections | Commissioning | [6 empty] | UDP-C-2 breakers C-4, 5, 6 Micrologic screens are not energized. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614731&prj=624&rqi=0fHTxFNR27uEVX4ySBn4PpQpDD
GI-134 | SV11-P2 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Incomplete Connections | Commissioning | [6 empty] | UDP-C-1 breakers C-4, 5, 6 Micrologic screens are not energized. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614729&prj=624&rqi=Cz2eLqWsDVpaQpHvMdSV3DnsTI
GI-132 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-26 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (Both Chillers C-04 and D-05 BMS) L4 Cooling Tower Bypass does not properly increment open when it's setpoint is not met. Timer counts down but the valve never get's the incremented command. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352250&prj=624&rqi=maH2FdsMdY643CMnsDxCHka73F
GI-130 | SV11-P2 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-26 04:00:00.000 +0400 | Design Professional |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (Both Chillers C-04 and D-05) L4 If the JCI Chillers go into "Cycling Shutdown" due to leaving liquid low temperature - Full Free Cooling, while the Skid is in the process of proving, the proving process will get interrupted and the Skid will "Fail to Start". JCI Chillers always start when receiving an enable (regardless of current CHW temps), and will shut down if their CHW supply is low. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352248&prj=624&rqi=gDi9h4jCrr6XCvgBjGcgcWYvnr
GI-129 | SV11-P2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-02-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | (All Delta CRAHs BMS) L4 Fan status not working correctly at the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352245&prj=624&rqi=td4RhLbQ0yythlDt0vS74kkX7j
GI-128 | SV11-P2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-02-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | (All Delta CRAHs BMS) L4 CHWV mismatch alarm not working correctly at the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352244&prj=624&rqi=CIjNA7oywobVG7le7STbK3CwsR
GI-126 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-25 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (BMS general) L5 Trending graphs for Chiller Skid sensors and Delta CRAHs do not track to the specified value, no data appears. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221115&prj=624&rqi=BQLkEwt84Rb9D8hxMgW47lpvra
GI-127 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-25 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (Both Chiller Skids BMS) L5 No communication alarm comes in when comms are lost to the JCI Chiller control panel (or the Chiller is completely de-energized) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221117&prj=624&rqi=NRqqoadzY14eHHlTlpShFuxKXO
GI-125 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-25 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | (All Chiller Skid BMS) Remove the following points at the chiller skid module on the "Chiller" layout screen on the BMS: - CHWDP - Chiller Cap | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221112&prj=624&rqi=Ce2MCEXyKso2EmLBsJcBB84ceH
GI-122 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-24 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | (All Chillers BMS) When accessing the Chiller faceplate in the skid pop up from the Chiller layout button, it shows updated information. However, when accessing the skid pop up from anywhere else (Equipment control, roof layout, etc), there is information missing (DT value) and several points not matched/updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199969&prj=624&rqi=Yu5X9fqSqpTrPhP3MpMzgTz0UX
GI-121 | SV11-P2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (All Chiller Skids) CWP VFD would fault on overcurrent during fast restart. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199968&prj=624&rqi=d1HmJ4gq8AFazxFZtdLSpIx4qE
GI-114 | SV11-P2 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-21 04:00:00.000 +0400 | Design Professional |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (Both Chiller Skids C-04 and D-05) L4 The categorization of multiple abnormal conditions as "Cycling Shutdowns" (0 on HOA, 0 on hardwired fault, 1 on hardwired cycling shutdown) by the JCI Chillers causes various system PLC integration issues in the following scenarios: Full Free Cooling: - Full free cooling is not available, will remove Skid from rotation - Unless loss of HOA is supplemented by the "Cycling Shutdown" bit Any other "Cycling Shutdown" condition, including loss of suction pressure transducer, loss of condenser flow, and loss of evaporator flow: - Will stay in Cycling shutdown indefinitely and not be removed from rotation - If loss of HOA is supplemented by the "Cycling Shutdown" bit to allow for full free cooling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199717&prj=624&rqi=fTY5rcQZZecmlQRyoN0YYz1T6J
GI-104 | SV11-P2 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-20 04:00:00.000 +0400 | Design Professional |  | General Design Issue | Design |  | equipment type |  |  |  |  | (All Chillers C-04 and D-05) L4 Allowing the Chiller to cycle off of it's compressor for the purpose of full free cooling (Cycling Shutdown) does not send the expected signals (HOA status) to the BMS to allow it to stay in the CHW plant rotation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199684&prj=624&rqi=1uPCKghuBgC5gAAUcXHpsQbRxo
GI-107 | SV11-P2 | AMER | Closed | P3 Low DCOS | alec.dughi@veolia.com | 2026-02-20 04:00:00.000 +0400 | Design Professional |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Chiller Skids) L4 TST mode change center point does not track Chiller supply temperature setpoint. Currently acts based on a hard coded value written in each PLC (inaccessible). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199702&prj=624&rqi=fLC1W9rsra2jqXGwDC4xTzIrJb
GI-105 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-20 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | (All Chillers CH-C-04 and D-05 BMS) L4 Chiller block graphics on the BMS display a nuisance "Warning" message even when the Chiller does not present any warnings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199686&prj=624&rqi=LNIMt2NRVK2Ez2eM390TRgoY3B
GI-109 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-20 04:00:00.000 +0400 | Design Professional |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | (Both Chiller Skids C-04 and D-05 BMS) L4 The System bypass valve will continue to climb open when flow through the skids is below minimum in the following states: - There is no run status from the CHWP - The Skid is performing an initial start-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199706&prj=624&rqi=vTI6uXSkulyFLUalGmfPIe0wVI
GI-108 | SV11-P2 | AMER | Closed | P3 Low DCOS | alec.dughi@veolia.com | 2026-02-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Chillers C-04 and D-05) L4 When values become negative (ex. evaporator / condenser approach temps) the Modbus data from Chiller to BMS goes high >6000F even though the Chiller HMI correctly displays the negative value (ex. -0.5 deg F) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199705&prj=624&rqi=l09sDczhDGfXc9FZEKgYtwUXJx
GI-110 | SV11-P2 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-20 04:00:00.000 +0400 | Design Professional |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | (Both Chiller Skids C-04 and D-05) L4 Failing the CHWP on a running JCI Chiller Skid will not cause a hardwired fault status from the Chiller, so the Chiller Skid will not be faulted and removed from the rotation until the debounce timers count down (3 min total, 1 min for CHWP, 2 min for Skid). During this time, the System Bypass Valve will continue to open, eventually reaching 100% with N-1 pumps running, causing an unrecoverable building DP crash. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199707&prj=624&rqi=yDqSj4vWJJRZ4lKv0fSRISkL1q
GI-112 | SV11-P2 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-20 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (Both Chiller Skids C-04 and D-05 BMS) L4 Faulting a running Chiller does not create the proper latching fault status in the BMS to allow for it to be successfully rotated off of. Causes the Skid enable to be constantly opened and closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199710&prj=624&rqi=mnPaSazww5N5yqeIufNI1g3aHJ
GI-102 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-19 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs) L3 Valve mismatch alarm is missing from alarm summary page | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199624&prj=624&rqi=vVsaAQLENEvzw6Ns1ig0VzdbuC
GI-100 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-18 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (Both Chiller Skids BMS) L3 Cooling Tower Bypass needs it's setpoint adjust added to front end BMS graphics. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199497&prj=624&rqi=MLaEtvhD1uwOfRgEEL4nk3bigw
GI-099 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | (All Chiller Skid BMS) CV-02 and CV-07 graphically are colored green indicating that the valves are open but physically they are not. Those should be grey on the Chiller Skid graphics. See attached. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199383&prj=624&rqi=5LglX8iViVnAe0DSfaeK2lpQDp
GI-098 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-12 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | (All Chiller Skids BMS) Current (Amps) value for CWP and CHWP display as off by a factor of 10. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199145&prj=624&rqi=TKi1PpyOj8Cr6KTeJWdvGrg3hZ
GI-093 | SV11-P2 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-11 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Chiller Skids BMS) L3 The Chiller cycling off it's compressor due to low CHWST is treated as a hard fault by the BMS, which will remove it from the rotation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199095&prj=624&rqi=EOIN3XeX4K8AGwEvXxQaWayElG
GI-095 | SV11-P2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-02-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Design not as specified | Design |  | equipment type |  |  |  |  | (All Chillers C-04 and D-05) L4 Chillers are throttled due to over amperage when at 90-100% load. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199097&prj=624&rqi=XVFbYh4f9Fqdinz8bFb3DHzFhR
GI-091 | SV11-P2 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-11 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Chiller Skids BMS) L3 When the entire Skid has it's enable removed, the Cooling Tower enable stays activated and it continues to run, even when all other components have shut off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199093&prj=624&rqi=CQ0aJk4hAXfQcIw59iXulB3rJ3
GI-090 | SV11-P2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | (MSB-C) MSB-C did not have appropriate UL certification stickers installed on any of the switchboard panels. Issue was identified during an external inspection and not noted during Cx testing *LESSON LEARNED* | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198935&prj=624&rqi=g68iNgiRZDc0h8colKnYCgYXcp
GI-081 | SV11-P2 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (All Chillers) L3 Modbus data unable to be received from JCI control panel. BMS communication established, but no register data able to be pulled in. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198713&prj=624&rqi=5OkGcEEF5aHgnLToCUrEe75Dqz
GI-084 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (All Chiller Skids BMS) L3 Graphics and control for CV-03 do not function from the BMS, works from local HMI | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198716&prj=624&rqi=fnsJQo5Aci9bh75PiI1XzOtW6F
GI-083 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (All Chiller Skids BMS) L3 BMS graphics show blank (% open) boxes for two-position valves. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198715&prj=624&rqi=RoUUiOhyZnAjBqsp7WhpTD0asy
GI-082 | SV11-P2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Design correction needed | Design |  | equipment type |  |  |  |  | (All Chillers) L3 Head pressure control not functioning, signal sent to valves from JCI panel does not correspond to minimum open percentage setpoint during Chiller operation, unit always faults on "No Condenser Flow". | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198714&prj=624&rqi=j5ZomFdORl9qegWueumbQELoTy
GI-085 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (All Chiller Skids BMS) L3 CV-09 (CHWP isolation) has associated graphics even though it does not exist as a control valve | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198717&prj=624&rqi=b7LAWTnhp3hgBtyzCOjGefT6Op
GI-080 | SV11-P2 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs) L3 Re-arrange required to alarm summary page graphics, should neatly represent reduced quantity of alarms that are available from the Delta CRAHs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198711&prj=624&rqi=JGVot5GlYrq3BdsPEALg5Wzjh0
GI-074 | SV11-P2 | AMER | Closed | P3 Low DCOS | alec.dughi@veolia.com | 2026-02-03 04:00:00.000 +0400 | Controls Contractor |  | DCOS Template Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs BMS) L3 Entering water temperature and leaving water temperature are switched in BMS faceplate. Leaving water temperature on BMS seems to be monitoring entering water temp of the CRAH (70F). Entering water temp on BMS seems to be tracking supply air temperature of the CRAH. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198259&prj=624&rqi=BCiKfOFsMAss7xznXbeEtTAz9u
GI-075 | SV11-P2 | AMER | Closed | P3 Low DCOS | alec.dughi@veolia.com | 2026-02-03 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs) (BMS) L3 Chilled water valve mismatch alarm is missing from Alarms page on BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198260&prj=624&rqi=OtlYjRsmJcknGnLZVCKw5LpRCS
GI-071 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs) L3 Data Points to add: - Supply fan command (%) - Supply fan feedback (yes/no) Alarm Points to add: - Communication alarm - CHW Valve mismatch alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198155&prj=624&rqi=NfYVLa0mSUHIOkgXr6OebUr8Dg
GI-068 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS Template Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs) L3 Duct static pressure is not needed on CRAH faceplate. (+scaled incorrectly and incorrect units) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198152&prj=624&rqi=urGX3NrpFbq8I7WsJV0U49X41R
GI-069 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs) L3 Return Temp and Supply Temp in BMS seem to be tracking Return and Supply humidity of the actual CRAH, respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198153&prj=624&rqi=lFKGKjcibBAcJKKL5RhSl8DoYb
GI-070 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | (All Delta CRAHs) Graphics for Chilled Water Valve command are monitoring Fan Speed command. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198154&prj=624&rqi=WYlMYwUCZAL6x1x7B6DjGeoW9t
GI-065 | SV11-P2 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-01-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | (Chiller Skid C-04 and D-05) L2B Wires terminated between load side A and B phase lugs do not allow 1" clearance over air and no barrier is present. Per UL580A c 10.2, 1" clearance over air is required for 480V applications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197700&prj=624&rqi=SqseNGMb9yKynVOOJuZbYsRALg
GI-063 | SV11-P2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-01-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning | [6 empty] | (CH-C-04) Refrigerant monitor exterior alert light bracket has broken off. Replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197590&prj=624&rqi=Jp8rYApREM3dFiiE52pW3FUZGA
GI-062 | SV11-P2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Component/Equipment Failure | Commissioning | [6 empty] | (Electrical SKID-C) A badge reader has been knocked off its housing and is dangling by a small clip and some wires. The badge reader needs to be reinstalled correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196897&prj=624&rqi=WIuz4ZsYULiRMc1JvBWjtwdJZz
GI-060 | SV11-P2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-01-13 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (All Delta CRAH's) Delta CRAHs do not have grouping mode. Please remove the following from the BMS faceplate graphic: Lead unit status, grouping mode status, grouping unitary demand status, group hot aisle SP, group hot aisle temp, group A/M slider. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196818&prj=624&rqi=6lexvlyLyghh2YKFB28Sa2tM1V
GI-056 | SV11-P2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-01-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | (All Chiller Skids) L3 Permant labels for CHWP breaker is currently labeled as spare. New permanent label is needed to depict the new termination. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196664&prj=624&rqi=mVTAVeZPMSgT4lOdN4icvsAI9W
SOR-272-001 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | 1MAU_R1_01 & 1MAU_B_02 CMS investigated the issue with the previously reported low flow to the Heating cooling and Dehumidifiers Hx's, found both units locked out on cooling and dehumidification modes, due to Low Pressure switch activation on the DX system, opened the liquid solenoid and checked the saturated refrigerant pressure against the pressure temperature chart using ambient temperature and the charges are found to be low in both units. CMS to schedule a resource to leak test and repair the leaks and tope up the refrigerant levels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638418&prj=479&rqi=8j1V7xl6nhclAi15Bm1TppeTFY
SOR-271-003 | SV18-1 | AMER | Open | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | After adding the control wires, the Maintenance bypass breaker on the mimic for UPS_A3/B3/C3/D3/E3/F3/R1_3 should be added. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638021&prj=479&rqi=D0Y1XLBMrLrni5MqvpxAeiQ01C
SOR-271-001 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-09-14 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | MEGA CRAH Automatic Transfer Switch Timers If the Reserve S2 fails and the utility power is available on S1 ... Currently sequence is Immediate Design requirement is a 3 second delay switching back from Reserve S2 to Utility Power S1, aligned with the intention of a minimum of 3 second break before make timer, can this be achieved with a late break auxiliary contact on a contactor, if deemed acceptable? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638018&prj=479&rqi=MbX6u4O4x47Y287gcOLN2BA3Li
SOR-270-005 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-09-10 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | To provide cap for all exposed terminal for power supply 24VDC at MDSB to prevent shorting and trip the control breaker. Note: Applicable for all MDSB at Skid A/E/F/B/C/D | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637589&prj=479&rqi=r826QppR3Zdfr6QrO5Lagr3c4y
SOR-270-001 | SV18-1 | AMER | Open | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-09-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | To upgrade the STS, 800AMPS firmware for UM1 Control card to V7.0 as per the Equinix approved Firmware release Aug. 26. Applicable for block A/B/C/D/E/F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637285&prj=479&rqi=R4Dydv4rs7MOOIkZStnU8rN8vc
SOR-269-001 | SV18-1 | AMER | Ready for Verification | P1 High CX | jordan_dubose@fsttechnical.com | 2026-09-02 04:00:00.000 +0400 | Controls Contractor |  | DCIM BCM Issue | DCIM |  | equipment type |  |  |  |  | Equinix Operations is not able to see the programmed 44 (A/E/F) 1RPP_X2s on Level 2. This prevents FST from starting the primary injection testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636628&prj=479&rqi=uuXIIOoAPnw2wiaunUwdcCZ2Ae
SOR-267-001 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Vertiv Control Panel wiring needs to be cleaned up the large coils of wiring is putting strain on the points of connection, which will lead to component failure. This has already manifested itself on 1CRAH_D_07 HMI THIS APPLIES TO ALL 36 UNITS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635881&prj=479&rqi=c956wkULITPs8tA0koQLtcXi7h
SOR-267-002 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-08-28 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | FST observed that the 1RPP panels in Data Hall B & Data Hall F are in different locations than what is in the E130.2A & E130.2B drawings. 1RPP_F2_1_3 1RPP_F2_2_3 1RPP_F2_1_4 1RPP_F2_2_4 1RPP_F2_1_6 1RPP_F2_2_6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635912&prj=479&rqi=e7GCAtDkpLJ9wCwrRgVTROuhbj
SOR-266-001 | SV18-1 | AMER | Ready for Verification | P1 High DCOS | jordan_dubose@fsttechnical.com | 2026-08-27 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | The breaker frame sizes in the all the blocks (A-Z and also the 2nd phase) MSB One-Lines were changed to all be 4000A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635745&prj=479&rqi=meZWskdsh66vAFnJmGjmCBIGM1
SOR-264-004 | SV18-1 | AMER | Open | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | The SCR at Gen A was found faulted and didn't run when the GEN A was running with 1.4MW load. The fuse 4Amps at the control panel is randomly busted during the lost of utility and transfer to Generator source. Note: This is happening on Gen E and F. Cummins to revisit the size of the fuse if that is the correct size. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635098&prj=479&rqi=bUMWRnpIIN1atV0f1cUKe5YDWC
SOR-264-003 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-08-24 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | The labeling of the 1STS_A2's are incorrect in Oneline_A_UDP_PDU as it should go 1STS_A2_1, 1STS_A2_2, 1STS_A2_3, and 1STS_A2_4 from left to right to match E603.05 Drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634979&prj=479&rqi=pivtGEVANa8EI8qxH1lungoZIK
SOR-263-005 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Align all Vertiv MEGA CRAH - Transfer Time from S2 to S1 per agreement, reference Matrix attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634826&prj=479&rqi=2zU7JVTLsXSQY3hizt86YLkIfP
SOR-263-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | As found condition - buzzer active no alarms on HMI, this issue applies to units: 1CRAH_B_07 1CRAH_B_09 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634825&prj=479&rqi=lqSNfxks7msrmLWxjr4JXb0v9m
SOR-263-007 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | The 30 second-time delay is not deployed for the loss of utility power S1, transfer to reserve power S2, it needs to be to protect the fan motors. This applies to all Vertiv CRAH units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634847&prj=479&rqi=9COO22TS4CuPycDg5d7fYzXxEb
SOR-263-002 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Air Flow Sensor - not alarming when tubes are disconnected, this applies to the following units: 1CRAH_B_01 1CRAH_C_01 1CRAH_C_08 1CRAH_B_09 1CRAH_D_06 1CRAH_D_09 1CRAH_D_10 1CRAH_D_12 airflow sensor only works when one tube is connected. . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634823&prj=479&rqi=3oJ7baNQ621dxVe8PM8XWveIgm
SOR-263-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Vertiv MEGA CRAHs not transferring back from S2 to S1 when utility power is reinstated, thus applies to the following units 1CRAH_C_06 1CRAH_D_08 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634822&prj=479&rqi=xLy6JO8qPg9YIae958tNl02RAO
SOR-263-003 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Fan rubbing noise coming from the fan section of the Vertiv MEGA CRAHs, this issue applies to: 1CRAH_C_06 1CRAH_C_10 1CRAH_D_12 THE FIX APPLIES TO ALL VERTIV CRAHs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634824&prj=479&rqi=DUwoqHQqBAV0IqzN5iWGpjmwYq
SOR-262-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-21 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning | [6 empty] | The following Flow transmitters are generating repeater status deviation alarms on flow CWR_FT_C1 CWR_FT_C5 CWR_FT_C10 Thais needs to be investigated to determine root cause. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634673&prj=479&rqi=aUPHOJLbg9TTGB3JzDzTKYmfuA
SOR-262-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-21 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | Chiller 1ACC_A_03 & 1ACC_A_04, there is an issue with the auto alarm reset function, after three unsuccessful try's the loop goes into a lock down scenario. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634679&prj=479&rqi=Lpd5QjqDRLnYOKEk8OFaUB1Ewc
SOR-261-003 | SV18-1 | AMER | Open | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Investigate the ON and OFF battery low alarm in the UPS_X3 Note: Applicable for 1UPS_A3/E3/F3/D3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634438&prj=479&rqi=Jk195fqc5J5zRAtdGHljp8BnLC
SOR-261-001 | SV18-1 | AMER | Open | P3 Low DCOS | jordan_dubose@fsttechnical.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | The 1STSs are missing a general alarm in DCOS. This was shown when 1STS_E2_4 had abnormal fan alarm locally but not in DCOS detailed in Issue 1092. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634295&prj=479&rqi=0Gfv95gFsWDqkly9cJpCUMoU4T
SOR-260-001 | SV18-1 | AMER | Open | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-18 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [6 empty] | During the event, the 20 A breaker (1UPNL_E3, L1#1) feeding the secondary source of the DMARC was found in a tripped condition. At the same time, the primary source was unavailable due to the loss of 1MSB_A during the pre-IST condition, resulting in a complete loss of communications for all equipment associated with Skid A, including MLTX_A, GEN A, and 1RMU_A. Need to re-evaluate the proper size of the breaker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634163&prj=479&rqi=jAzWKXFoX6no4hECfQDQLR7DLI
GI-104 | SV18-1 | AMER | Open | P2 Medium CX | daniel_chavez@fsttechnical.com | 2026-08-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | UPS_X3 (Mechanical UPS's) for the below skids require an expansion card in order for the MSB interface to be integrated. UPS_B_3 UPS_C_3 UPS_D_3 UPS_R1_3 UPS_A3 UPS_E3 UPS_F3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634136&prj=479&rqi=CgGa8wsOuPrcnRU4iwBIRri2to
SOR-257-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Investigate/troubleshoot and rectify the On and Off low battery alarm for 1UPS_F3 that is showing at DCOS. The actual battery readings at HMI are normal and not showing low battery alarm at the UPS unit. However, in the DCOS is showing battery alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633723&prj=479&rqi=x7cCES4urCxQ1rFRCFS0KDpZXg
SOR-258-001 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | The MAUs Roof FOH, 1MAU_R1_1 & 1MAU_B_2 have had numerous alarms on low chilled water flow, inhibiting the dehumidification and heating modes of operation, Suspect the chilled water strainer to units is blocked. Issue Raised on Facility Grid to investigate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633741&prj=479&rqi=q5EOus2oMStkVXDnXpb91AM0CT
SOR-257-002 | SV18-1 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-13 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Hanley to provide the missing terminal block for breaker auxiliary contact for 1UPS_X3 Breaker input at 1MDSB_X. The breaker auxiliary contact will provide information to the UPS_X3. The missing terminal block is applicable for 1MDSB_R1/B/C/D | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633580&prj=479&rqi=MttVOUz6cab5FTagxbi5b6RrCR
SOR-257-001 | SV18-1 | AMER | Open | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Investigate the missing battery voltage readings at DCOS. The reason might be the modbus register from the UPS wasn't the same with the DCOS. Note: The issue is also the same with 1UPS_A3/E3/F3/D3.- Delta needs to resolve the issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633434&prj=479&rqi=lSk2Fh8tJEEJmx4Jh9l3i73oD3
SOR-255-007 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | The modification you rightly completed to the units to avoid drawing in FOG into the OSA air section, since this air is heated in the first section with an electric heater. The eliminator (photo for clarity is attached) is now clogging up with air borne dust. Can you please have one of your guys tidy this up so the filter can be easily removed for cleaning and/or replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632365&prj=479&rqi=ssUwKKdZniW5LvnYkNdfIUbtLz
SOR-255-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-31 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Check the loss of PM3 PQM communication with the DCOS in 1MSB_F | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631730&prj=479&rqi=lHrKyncvNtz4J0a1C0c7HFWNJn
SOR-255-004 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-31 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Missing Auto/Manual label at the HMI for the following. 1. 1MSB_Z 2. 1MSB_A 3. 1MSB_E Replace the phenolic label that will include the missing Auto/Manual. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631734&prj=479&rqi=pokRKKc6DxSe2s25JHY5nJoN5D
SOR-255-005 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-31 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Replace the defective Phase sequence relay at 1MSB_F | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631735&prj=479&rqi=91mQkURYygk4W5d5p3zbLo3GoU
SOR-255-006 | SV18-1 | AMER | Ready for Verification | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-31 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | CMS humidifier has been attributed to High water consumption, please review the current design with a view to improve water consumption. This applies to all units | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631845&prj=479&rqi=JGfVO2hcZL6bmZ38sgbuYFZWOZ
SOR-255-002 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-31 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | The maintenance mode illuminated selector switch doesn't work at IOB breaker for 1UPS_A2 and Q09 OUT TO 1LBSB at 1MSB_A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631729&prj=479&rqi=UBc9GCwS70YRf5kvcUiltGTgxZ
SOR-254-004 | SV18-1 | AMER | Closed | P2 Medium CX | Jessie_Salita@fsttechnical.com | 2026-07-29 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Side cover canâ€™t fix at 1UDP_A1_1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631336&prj=479&rqi=6GZNC3Gkm8go8qO8wASD5f4fhn
SOR-250-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | All of the TRANE heat pumps Condensate Pumps in areas A, E & F , condensate pumps discharge connection leaked on start-up- Therma repaired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630601&prj=479&rqi=hDJNEVR9w5IzRFA3Wb8mH6sxfH
SOR-249-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-21 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [6 empty] | Request of information on missing indication at DCOS for input, output and MBB breaker status for 1UPS_X3. Applicable for all 1UPS_A3/E3/F3. Note: Phase 1 doesn't have also the Breaker status at 1UPS_X. It might also, apply as well. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630209&prj=479&rqi=cM6UHJ9Mi1mYyV4j4PHbTTZeri
SOR-248-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | Powerhouse A "VESDA system" the UPS side of the PH: the orifice on the sniffer Pipe EOL is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630040&prj=479&rqi=M9aAyJyfVlMi3imWP1QMCYNA7E
SOR-246-005 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-07-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | The cover 1RPP_E1_2_5 are the incorrect size resulting in the exposure of the breakers for the branch circuits 69 and 71. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629799&prj=479&rqi=Lc94iU4biZPFua60vzu3USRtMA
SOR-246-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-16 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | PDU voltage monitoring to be changed: From: Phase to Neutral To: Phase to Phase. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629796&prj=479&rqi=RQmI5lBQYLBBGWkFClqujtSecm
SOR-242-006 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-12 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [6 empty] | 1MTS_Z2_C was added recently at 1MDSB_C. In order to accommodate 1MTS_Z2_C breaker required which is 250AT, Redwood took the 250AT from 1MAU_C_3 and used to 1MTS_Z2_C. The 1MAU_C_3 transferred to 150AT breaker which was spare breaker before. It satisfies the Overload settings for 1MAU_C_3 but the short circuit and Instantaneous canâ€™t set to 2500AT which is the required setting. The minimum setting is 1500Amps only. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628783&prj=479&rqi=fKriA5jq3yasxJu2teQiMgWmfb
SOR-242-007 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-12 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [6 empty] | In MPS interconnection wiring between 1MSB_X and 1UPS_X3, there was a control cable for input to PLC for 1MBB signal for 1UPS_X3. The 1MBB breakers are located in 1MDSB and 1UMDSB_X. There's no cabling between these two switchboards to 1UPS_X3 for 1MBB indication to UPS. Please advise how we can get the 1MBB input signal to PLC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628790&prj=479&rqi=QXXvrccblbnQXbeZcjWDYwrCHL
SOR-242-004 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | The 1MAU_Z_01, Q11 at 1MDSB_Z1 breaker can't set the Overload Protection, to 60Amps per the Protection coordination study. The breaker was 250Amps and the minimum to set was 100Amps. Need to replace the CB to 150Amps. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628781&prj=479&rqi=Dn10oL3176KxzxkfaEWn9i7HIt
SOR-242-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | 1MTS_Z2B breaker at 1MDSB_B can't set the Overload protection to 225Amps as per Protection Coordination. The trip unit was 600AT and the minimum to set the Overload protection was 240Amps. We might replace the trip unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628780&prj=479&rqi=TRPR0F93DmQ9bSousq89fwxCva
SOR-242-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Generators All Generators vibration isolators - the bushings are damaged and needs replacing on the guide associated with this assembly. Cummins have agreed to replace all of them. Issue raised to trace to closure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628773&prj=479&rqi=MyE0DSnGKco4tdea8nzxjQjp3v
SOR-241-001 | SV18-1 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Replace the failed rectifier for 1UPS_A2 that was found during the load banking. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628756&prj=479&rqi=yG3ByFvsMKN6iEvChgP5bKguTt
SOR-239-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment | Fire Alarm |  |  |  | 1. VESDA unit started and air flow-maintained constant, but unit did not normalize- programming required. 2. Install of VESDA piping at PH door diagonal to VESDA equipment is incomplete, variety of deficiencies noted: a. Pipe not glued to valve, b. Missing air cap, c. Missing valve, There is a deadline of 7/17 for the completion of this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628438&prj=479&rqi=cIQzAt2BRJjkfOkqx67VNwL0vc
SOR-239-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment | Fire Alarm |  |  |  | 1. VESDA unit started and air flow-maintained constant, but unit did not normalize- programming required. 2. Install of VESDA piping at PH door diagonal to VESDA equipment is incomplete, variety of deficiencies noted: a. Pipe not glued to valve, b. Missing air cap, c. Missing valve, There is a deadline of 7/17 for the completion of this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628435&prj=479&rqi=f36RjHR7dntQky1ypRubltQPSB
SOR-239-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment | Fire Alarm |  |  |  | 1. VESDA unit started and air flow-maintained constant, but unit did not normalize- programming required. 2. Install of VESDA piping at PH door diagonal to VESDA equipment is incomplete, variety of deficiencies noted: a. Pipe not glued to valve, b. Missing air cap, c. Missing valve, There is a deadline of 7/17 for the completion of this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628440&prj=479&rqi=dPF0oDA7iEsVeOjgoSffbsZWxd
SOR-238-001 | SV18-1 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Investigate and rectify the SCR abnormal fault alarm. Note: Applicable for the following. 1. 1STS_A2_1 2. 1STS_A2_2 3. 1STS_A2_3 4. 1STS_A2_4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628205&prj=479&rqi=hJSQzzEsCmdGIpIooCyydb5uAf
SOR-236-003 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | The labels for phases are incorrect and will need to be replaced for RPP's. The labels should show A-B-C from left to right. Note: This issue is applicable to the additional 28 RPP panels added after Bulletin 1. 18 in Block C 10 in Block F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627616&prj=479&rqi=4HdlvJXiQVR8Vri2kBLvSN3SwC
SOR-235-002 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | To transfer the cables from 1MSB_X external status of the RIB breaker to 1MDSB for 1UPS_A3/E3/F3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627571&prj=479&rqi=LOrZ88ERlfRHplLwfSf69NfLtc
SOR-236-004 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | The motherboards in the A2/E2/F2 RPP panels on Level 2 have screws of incorrect lengths. The screws in the 44 1RPP_X2_X _X blocks below have this issue A Block: 22 E Block: 2 F Block: 20 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627627&prj=479&rqi=93iTTXY0oRFzEWzfftqBF9Msia
SOR-235-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Current at Phase A is not showing readings while Ig showing current which is not correct.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627455&prj=479&rqi=Y4Uvh5RNZ905x0AUr4xJIVFHwi
SOR-233-002 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-28 04:00:00.000 +0400 | TRN - Trane |  | Installation not complete | Commissioning | [6 empty] | Warning sticker missing from heat trace j-Box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627185&prj=479&rqi=3y4NfNbo1nZs1isKYPj1cm2QPY
SOR-233-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-27 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [6 empty] | Chiller 1ACC_A_04 Chiller Pump Non-Drive Bearing noise, and today when we ran it at low RPM, we realized it has deteriorated to a point where the bearing will need to be replaced. Trane have taken to bearing details from the pump nameplate and have ordered a replacement. The work to change the bearing can be completed with the pump in situ. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627184&prj=479&rqi=C0W2z4QZVozlFwHOR6hW44iW8L
SOR-230-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Breaker status at DCOS is not changing when breaker is Open or Closed. Note: Applicable for Gen A & E. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626834&prj=479&rqi=WL8KD0REo6KWgegkk1blZqTw5E
SOR-230-004 | SV18-1 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-24 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | When simulating the Emergency Stop, the Phase Overcurrent alarm & Shutdown alarm were also initiated, and those alarms shouldn't be activated. We expect Emergency Stop to be activated. Note: Applicable for Gen A & E | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626837&prj=479&rqi=9eFTCXkHQN3IL0qpd8WJLVrWJ6
SOR-229-005 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-24 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | When simulating Emergency Stop, the Phase Overcurrent alarm & Shutdown alarm are also initiated and should not be the case. Note: Applicable for Gen A & E. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626836&prj=479&rqi=H3LphJASWUpUm8ywsZo18mbtXW
SOR-228-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-23 04:00:00.000 +0400 | Design Professional |  | General Design Issue | Design | [6 empty] | Potential issue with the Chilled water make-up station: The check valve resides on the discharge after the bypass line on the chilled water make-up station, if it did stick closed situation may be difficult to recover. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626547&prj=479&rqi=18oScdeTblUN5j9V1RgaDupJVz
SOR-229-002 | SV18-1 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Replace the defective CT for Phase A in 1UPS_F1. Note: The defective CT was originally found in 1UPS_A1. The replacement was taken from 1UPS_F1 and installed to 1UPS_A1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626629&prj=479&rqi=CEgHbfDWfG8jICrSq5DLma7oz5
SOR-225-004 | SV18-1 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Replace the defective MCU card for 1UPS_A2. In order to troubleshoot and rectify the issue. Delta took MCU card the 1UPS_F2 and installed in 1UPS_A2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625698&prj=479&rqi=EAGpBZuHwKnWAJH0KCtueNsGwq
SOR-225-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Investigate the fluctuating voltage reading from 476V to 482V from 1UDPR_C2 breaker which should be stable voltage from 1UPS_R1_01 & R1_02. The breaker voltage sensor might be an issue. The voltage IOB from 1UPS_R1_1 & 1UPS_R1_2 are stable with voltage reading of 479VAC and the voltage should be the same with 1UDPR_C2. The voltage reading at 1UDPR_C1 is the same with 1UPS_R1_1 & R1_2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625695&prj=479&rqi=i619rL3VsEjmCuC9F9kkAxkhFx
SOR-222-003 | SV18-1 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Troubleshoot and rectify the SCR 1 SRC OVER TEMP WARNING during load banking and the load is around 780amp at 1STS_D1_4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625198&prj=479&rqi=DxmXPkUVIgr0HBXnZBwIfM8nam
SOR-222-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-13 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | This week we had to split the chilled water system to facilitate chiller load bank testing. Part of the test we had to valve the headers feeding the 1CRAH_D_01 THRU 1CRAH_D_12. Since it's an open space, we left the units running to help cool down the areas. When we reinstated the chilled water system back to normal configuration, the Vertiv CRAH alarm for "loss of Cooling" alarm had to be manually reset before the units returned to normal cooling operation mode. FST think this alarm should be an auto reset. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625201&prj=479&rqi=UtqbpMVQjltbyEObTL8I6SPk9O
SOR-221-007 | SV18-1 | AMER | Open | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-06-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | 1STS_A2_1, 1STS_A2_2, 1STS_A2_3 are missing knobs on top of the A2 sets in the top hats and 1STS_ E2_3 has the missing hardware detailed below. -13 screws missing meant to secure back cover. - 8 top hats knobs either missing entirely or is missing the screw that mounts it inside the knob. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625173&prj=479&rqi=ldkjit8vAIwHhl3yyf1SN8n4Ue
SOR-220-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Replace the breaker from 20AT to 15AT for Heat Pump at 1PNL_R1_1_H1 feeding HP_A , E and F according to the manufacturer recommendations. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625039&prj=479&rqi=j1gbhac3GVtGpZGn1GoeomELKH
SOR-217-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Provide missing power two (2) units module for 400KW for 1UPS_A3, 1UPS_E3 and F3. The installed modules are good for 300KW. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624353&prj=479&rqi=c6Ff3AGWgDLI6lvGGZDukCfqBe
SOR-215-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | To find the missing wire for SKRU release signal. The wire 2015 & 2016 are terminated at 1MSB but on UPS terminal, the wires can't be found. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624192&prj=479&rqi=HlcbLweiSEaQhSl9tySnmdPiwg
GI-102 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-05 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [6 empty] | p3E-Tech surveyed leak Detection tape located in PHs A, E, F: MPS-installed leak tape is missing the EOL (â€œEnd of Lineâ€) terminators for all of the sense lines in these PHs. Issue raised on facility Grid to Track to completion. E-Tech can install when parts are received from MPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624162&prj=479&rqi=cjiUvysfNmwQLjZ1Mncwd05mhW
SOR-213-002 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-04 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [6 empty] | Provide missing settings for 1UDP's_A1_1/2; 1UDP_E1_1/2; 1UDP_F1_1/2.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623877&prj=479&rqi=vnviGJxyyKKnlTK6o2nKi8VkHr
SOR-214-001 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-06-04 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | The LTD settings of the PRX10 LSI trip units in the Eaton breakers in 1UDP_A1_1., 1UDP_A1_2, 1UDP_E1_1, 1UDP_E1_2, 1UDP_F1_1, and 1UDP_F1_2 are fixed and cannot be adjusted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623970&prj=479&rqi=AOk0IPObB31XPr96JSqomLn0xz
SOR-213-001 | SV18-1 | AMER | Closed | P2 Medium CX | jordan_dubose@fsttechnical.com | 2026-06-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1RPP_F2_1_2 | RPP - Remote Power Panel |  | RPP-208-250-60 | The 1RPP_F2_1_2 is missing the lug cover. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623861&prj=479&rqi=qQopPQZx7944wbP6NbLz9qoALg
SOR-212-001 | SV18-1 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | The door is difficult to open at skid R1 front left door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623713&prj=479&rqi=1K88YXxrgXBFGHq8da5q0gBorT
SOR-211-006 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-02 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Replace the defective CAT6 cable for gateway 2 to switch at 1MSB_A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623581&prj=479&rqi=emLbjlXlrjlEhCSj3spjJn5nPJ
SOR-211-002 | SV18-1 | AMER | Open | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-06-01 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Labelling | Commissioning |  | equipment type |  |  |  |  | The labelling for the Q#'s of 1MSB_A/E/F is different in the SV18-2 submittal than in the engineering drawings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623567&prj=479&rqi=QHMAkvP8YTAz2qufkZwYaFKtZ6
SOR-256-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-01 04:00:00.000 +0400 | TRN - Trane |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Minor damage to Armaflex Insulation Damage, Needs Patched. Applies to Chillers 1ACC_E_19 1ACC_E_20 1ACC_F_22 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623540&prj=479&rqi=trg1Zqns60Ha07AFa9vwDvqEba
SOR-211-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-01 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [6 empty] | Powerhouse F: 1CRAH_F_15 SV18.1RLEM_F_LEAK_15 Leak Detected - Leak detection in alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623577&prj=479&rqi=rp5GHcKKzwBG3mGY5HoaedPGra
SOR-211-003 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-06-01 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Engine hours at the local HMI are not the same with the DCOS. Information for both should match. This is applicable for the following. 1. GEN B 2. GEN C 3. GEN D 4. GEN R1 5. GEN Z | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623572&prj=479&rqi=WiWEsrlbjuvSRMAsWkbajdcW4Q
SOR-211-001 | SV18-1 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | The door is difficult to open at skid D front left door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623554&prj=479&rqi=vBrR5gSEGVPPUJiTDfGzBnp7nG
SOR-210-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Provide the connecting bar for Transformer tap 4-5 to compensate the voltage drop on Transformer output. Provide- 48 pieces. 1PDU_B2_4 1PDU_C1_4 1PDU_D1_4 1PDU_D2_4 1PDU_E1_1 1PDU_E1_2 1PDU_E1_3 1PDU_E1_4 1PDU_F1_1 1PDU_F1_2 1PDU_F1_3 1PDU_F1_4 1PDU_A1_1 1PDU_A1_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623488&prj=479&rqi=yOhTEpcs6ofiC1CevDaIr76LbD
SOR-209-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Provide the missing Ethernet cable for the following. 1. 1HP_A_1 and 2 2. 1HP_E_1 and 2 3. 1HP_F_1 and 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623393&prj=479&rqi=aV4TQBgxHipqtmcQov0lNjXJBH
SOR-208-001 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1RPP_C2_2_2 | RPP - Remote Power Panel |  | RPP-208-250-60 | There is a damaged door in RPP_C2_2_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623240&prj=479&rqi=trxju2xeaBFxMgko6V3C9ECszi
SOR-207-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | The clearance of 1â€ phase to phase wasn't maintain for B & C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623150&prj=479&rqi=vF7vOGRkOG8VFvTISj2h50s0I0
SOR-206-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-25 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [6 empty] | To provide new updated setting to reflect the breaker model Square D instead of ABB for the following PDU's 1. 1PDU_A1_1. 2. 1PDU_ A1_2, 3. 1PDU_A1_3 4. 1PDU_ A1_4. 5. 1PDU_E1_1 6. 1PDU_E1_2 7. 1PDU_E1_3 8. 1PDU_E1_4 9. 1PDU_F1_3 10. 1PDU_F1_4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623058&prj=479&rqi=9wqTMbbXFkHoMtTqhBVyK6WBEp
SOR-206-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-22 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [6 empty] | Provide missing protection settings for the following. 1PDU_B2_4 1STS_B2_4 1STS_C1_4 1PDU_C1_4 1STS_D1_4 1PDU_D1_4 1STS_D2_4 1PDU_D2_4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622857&prj=479&rqi=nvn4dMVIjZaAgzVvh6DrxF0bmR
SOR-206-002 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-22 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [6 empty] | Provide missing protection settings for the following. 1UTX-F3-L1 1UTX_A3_L1 1UTX_E3_L1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622879&prj=479&rqi=46kaK6VgaGb4KAE11D3oZRA1RK
SOR-201-002 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-05-16 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  | system | CHW System |  |  |  | The following Chilled Water Riser, Onicon flowmeters need to be replaced FT401 FT601 FT903 As they are reading outside of the 10% range. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622028&prj=479&rqi=cFkqpXTad855e0MA3bZD4GBrJE | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-200-001 | SV18-1 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-14 04:00:00.000 +0400 | Equinix Ops |  | DCIM BCM Issue | DCIM | [6 empty] | Tested all the CTs (100% with 72 CT's) for each panel and found sensor 37 to 42 doesn't show current readings in BCM. This is consistent to all 18 panels. Completed as follow's 1RPP_B1_1_1 1RPP_B1_1_2 1RPP_B1_1_3 1RPP_B1_1_5 1RPP_B1_1_6 1RPP_B1_1_7 1RPP_B1_2_1 1RPP_B1_2_2 1RPP_B1_2_3 1RPP_B1_2_4 1RPP_B1_2_5 1RPP_B1_2_6 1RPP_B1_2_7 1RPP_B1_3_1 1RPP_B1_3_2 1RPP_B1_3_3 1RPP_B1_3_5 1RPP_B1_3_6 1RPP_B1_3_7 1RPP_C2_1_1 1RPP_C2_1_2 1RPP_C2_1_3 1RPP_C2_1_4 1RPP_C2_1_5 1RPP_C2_1_6 1RPP_C2_2_1 1RPP_C2_2_2 1RPP_C2_2_3 1RPP_C2_2_4 1RPP_C2_2_5 1RPP_C2_2_6 1RPP_C2_3_1 1RPP_C2_3_2 1RPP_C2_3_3 1RPP_C2_3_4 1RPP_C2_3_5 1RPP_C2_3_6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621917&prj=479&rqi=fTeqB6Nb3Ta8DLzj59n0i8TXgN
SOR-195-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-08 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Replace the breaker 2/0 to 350 lugs to 14 to 1/0 lugs to fit the 2AWG that was pulled for 1UTX load at 1UMDSB_A3/E3/F3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621010&prj=479&rqi=jt3lTiY1Fs6IrF78E6yvceMReW
SOR-193-002 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | FST observed that they are several screws in the different 1PDUs that are stripped. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620627&prj=479&rqi=zc9iV8jXkYScmbT37hA5DBw5AF
GI-094 | SV18-1 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-04-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Generator Output Breaker is missing the K1 kirk key and cylinder. K1 Serial Number is 64393. This is applicable to GEN_A, GEN_E, & GEN_F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619964&prj=479&rqi=uhNoj8fUOwvxHFoY09FjgSmPP7
SOR-187-004 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Incomplete Connections | Commissioning |  | equipment type |  |  |  |  | Perform neutral connection modifications to all STS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619816&prj=479&rqi=Si552PsOnSE13istwCoTt22aeP
SOR-187-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Provide missing parts for breaker key interlock. 1. Missing TABS for breaker drum kirk key Gen A/E/F 2. To provide whole set of kirk key for Gen A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619793&prj=479&rqi=wVMz1k6C1U6erbJqLKDEWqUxXs
SOR-187-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Bolts missing on the following units: 1CRAH_D_12 1CRAH_D_10 1CRAH_D_09 1CRAH_D_05 1CRAH_D_04 1CRAH_D_02 1CRAH_C_10 1CRAH_C_09 1CRAH_C_08 1CRAH_C_07 1CRAH_C_04 1CRAH_C_03 1CRAH_B_01 1CRAH_B_02 1CRAH_B_03 1CRAH_B_04 1CRAH_B_07 1CRAH_B_08 1CRAH_B_09 1CRAH_B_10 1CRAH_B_11 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619805&prj=479&rqi=kiMe3xaBslZk3kgcUAalMHcIo4
SOR-186-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-27 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Power Houses A, E & F - Trane Heat Pumps Trane representative reviewed the panel wiring and discovered the units have been set up for BACnet so they will need a gateway to change the protocol, issue raised in facility grid to track this to closure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619646&prj=479&rqi=NaLjHIpSzrzt1DB6GciZJT1HkS
SOR-186-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Power Houses A, E & F Heat Pump - Smoke Detector Circuit: The power wire at the smoke detectors at the Trane WSHPs has not been pulled. Currently they have only pulled the control wiring that shuts the units down. See Attached Photo's for clarity | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619586&prj=479&rqi=kW3x20Prxpr7hu7M954PMu9lpc
SOR-186-003 | SV18-1 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | To perform the neutral modification for STS to meet Equinix standard. Applicable for all STS for Block A/E/F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619661&prj=479&rqi=wJoJEKxMThvH3btCpgXWCtcy5j
SOR-183-002 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | Two ceiling junction boxes in Skid K are incomplete and/or not labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619421&prj=479&rqi=l4CAXp5w9zodMNjLDnx8xT2UzK
SOR-183-001 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | In 1MSB_K there are missing bonding cables to ground the top hats in the sections 05A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619372&prj=479&rqi=eLf1OVou9G1ihxpntYfw1XWQE5
SOR-181-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1RPP_C2_3_2 | RPP - Remote Power Panel |  | RPP-208-250-60 | To provide the missing bar and bolts connecting to the main incoming cable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619258&prj=479&rqi=XHyDRdhiFiBhbeMZcFvWMe4BcU
SOR-182-001 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-23 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning | [6 empty] | In 1MDSB_K the lugs are not correct for the 1PNL_K_HP_BKR & 1UPS_K3_BKR terminations. Hanley to send (3) lugs for #1/0awg to support the 1PNL_K_HP_BKR and (6) lugs for 3 #500kcmil to support the 1UPS_K3_BKR | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619274&prj=479&rqi=HyX1jK8xUabYwLAxTqcoska3qo
SOR-182-002 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-23 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not complete | Commissioning | [6 empty] | In 1UDP_K2 the lugs for the termination to 1STS_K2_3 in BKR#4 are incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619277&prj=479&rqi=msmcNYjIjGcUDDvegW80xt8unO
SOR-180-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-22 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Provide missing SKRU key (K3) at 1UMDSB_A3/E3/F3 for UPS_A3/E3/F3. K3 Serial Number is 6440 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619148&prj=479&rqi=epqxDn9x1FHVlqtNPjKr50JKPj
SOR-180-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-22 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Provide missing SKRU key (K7 & K8) for 1MSB_A for 1UPS's. 1. 1UPS_A1- 3 pieces 2. 1UPS_A2- 3 pieces K7 Serial Number is 64155. K8 Serial Number is 64156. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619146&prj=479&rqi=S2QHW7THbyWDaFKkNjZASlWnO8
GI-091 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-04-22 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS | [6 empty] | aalogmonitor is still showing errors and warnings in the platform | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619141&prj=479&rqi=5G4nE8kp0HKy1yum1aOTjzOJIc
GI-092 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-04-22 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS | [6 empty] | topserver is reflecting several errors & warnings & hundreds of connections | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619142&prj=479&rqi=KxuIrzbqF4ZqCcXN20PkXrlxTf
GI-090 | SV18-1 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | On Power Skid E; the Mortise/Cassette has a short/blown security panel fuse. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618919&prj=479&rqi=iecrGOVHUvof3THgYONf6aQbkT
SOR-179-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-21 04:00:00.000 +0400 | TRN - Trane |  | Installation Damage | Commissioning | [6 empty] | Armaflex insultation on chiller pumps, needs protection from UV light, it would need to be covered/Jacketed or painted. see attached photo the damage is already occurring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618915&prj=479&rqi=k4bP99vfnGT2S1nx8lNrBYkpVz
SOR-179-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-21 04:00:00.000 +0400 | TRN - Trane |  | Installation not complete | Commissioning | [6 empty] | Chiller ball valve plugs missing issue raised on Facility Grid. Chiller C_12 Supply BV Drain Plug Missing. Chiller D_18 _ 2 X Pump & Suction Diffuser drain Plugs. Chiller R1_01 Suction Diffuser Drain Plug Missing. Chiller R1_01 Supply BV Drain Plug Missing. Chiller R1_02 Supply BV Drain Plug Missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618913&prj=479&rqi=wcEYJqtG5xu6ZG03QUqP2wLMnJ
GI-089 | SV18-1 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | On Powerhouse Skid A; Door D does not fully close/latch. Furthermore, the door is not level. The door contact was removed to prevent further damage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618918&prj=479&rqi=Z6IKYIYxfmsOSREzXuqluAyO3i
GI-088 | SV18-1 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | On Powerhouse Skid A; Door B does not fully close/latch. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618917&prj=479&rqi=IrtRJ3SmL7jOT4kP75vUjd0mkf
SOR-178-003 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning | [6 empty] | The mechanical lugs for 1UMDSB_X3 terminations to Q09 in the 1MDSB_X are incorrect in skids A, E, & F. Six (6) lugs are for the (2) #500kcmil wiring. Six (6) lugs are for the needed for (2) #2/0 ground. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618778&prj=479&rqi=nWszevbrlAC7sFgx0XoS2ckAWy
SOR-178-002 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning | [6 empty] | The mechanical lugs for 1PNL_GEN_X terminations to Q04 in the 1MDSB_X are incorrect in skids A, E, & F. Nine (9) lugs are needed for the #4 wiring. Three (3) lugs are needed to support the #8 ground. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618777&prj=479&rqi=Ve8HosGabFhTJ7kXZfA7wvsyok
SOR-178-004 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | [6 empty] | The current 1PNL_X_HP_BKR in the 1MDSBs in Blocks A, E & F has only LSG ground protection and not the LSIG ground protection required in both the Hanley submittal and engineering drawings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618779&prj=479&rqi=OlCJLfiHJMNHqKJ1D5WWhwIqjy
SOR-178-006 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [6 empty] | Chiller 1ACC_D_18 Chiller failed on phase loss during IST. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618781&prj=479&rqi=KcSvZ7xAhSWecWpuXBe2QDDy7E
SOR-178-001 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning | [6 empty] | 1UMDSB_A3 has mismatching lugs as they have 3/0 - 350kcmil lugs installed but need lugs to support 3 #2 & 1 #8G, 1-1/4"C wiring for the 1UMDSB_A3 to the 1UTX_A3_L1 breaker. Three (3) lugs are needed for the #2 wiring. One (1) lug is needed for the #8 ground. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618776&prj=479&rqi=ACrpNgPnIgaudrCuBm8YGUiTwQ
SOR-178-005 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [6 empty] | Chiller 1ACC_C_12 failed following UPS power loss testing. Both control fuses located in the harmonic filter housing and fuses feed the main controls circuit; they blew with the inrush current. there are two sets in series 15 amps in the harmonic filter & 10amp in the power panel. TRANE have agreed to upgrade the 10-amp fuses to 15amp. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618780&prj=479&rqi=kqd7ZEGD1OKNz0BR4y7RsxL38b
SOR-170-004 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-04-19 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | To remove the "Heat Traced" alarm from the General alarm through the hardwire from Chiller control to RIO panel. This is preventing the Chiller lockout every time there was a momentarily loss of supply voltage to the "Heat Traced" circuit which is non-UPS source. Separate the Heat Traced alarm by pulling new cable from Chiller control panel to I/O input at the RIO panel. Etech will program the additional input for DCOS. Note: Applicable for all Chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618674&prj=479&rqi=9dNCZrNGRqYlbT0v0NCoB4u61p
SOR-176-013 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [6 empty] | MV-1 & MV-2 Power Houses - Air conditioning units Graphic need to be deployed. This issue applies to the following units: 1SUDB3_AC_1: MV-1 North Yard. 1SUDB3_AC_1: MV-1 North Yard. 1SUDB1_AC_1: MV-2 South Yard. 1SUDB1_AC_2: MV-2 South Yard. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618615&prj=479&rqi=O19vYSCjA9DFtEfyMZZjHw06S5
SOR-176-012 | SV18-1 | AMER | Closed | P2 Medium CX | James_Kenny@fsttechnical.com | 2026-04-18 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | This one applies to all TRANE chillers The location of the Thermal Dispersion is not ideal as these switches respond better to laminar flow as opposed to turbulent flow. Chiller manufacturers use Tube Grooving to Improve Heat Transfer The use of grooved copper tubes in chiller systems is a method to enhance heat transfer efficiency. Grooves can induce a swirling motion in the fluid, which helps to displace the fluid and increase the heat transfer rate. This technique is effective when the Reynolds number is between 500 and 5000, as it can lead to a significant increase in heat transfer capacity. The grooved design is particularly beneficial in heat exchangers where the goal is to maximize thermal energy transfer between fluids. The thermal dispersion switch is installed right at the end of the tube bundle, this switch is sensitive the turbulence, please review. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618604&prj=479&rqi=BL9bBEUfih3Hvgpdw0tlMgFm7m
SOR-176-009 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-04-17 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [6 empty] | The SF6 alarms for Breakers and other compartment wasn't able to get the alarms in DCOS at 1SUDB_2. Schneider will need to verify the Modbus register to match with DCOS. The SF6 alarms is assumed to be the same issue in 1SUDB_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618599&prj=479&rqi=2jRtCpNajea4JL5Yy2xn4bn5XM
SOR-176-010 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-17 04:00:00.000 +0400 | Subcontractor |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | MPS to resolve why Skid D Heat Pumps are not responding to their corresponding room thermostats | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618601&prj=479&rqi=tyVDOQocEzYWqujNeo8jwXYyUn
SOR-174-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | To investigate the current harmonic on B-phase of Rectifier input is high in comparison with phase A & C. The 9.09% current harmonic in phase B is the total for two units of UPS. Phase A & C have almost the same harmonic value of 1.5% average. Take note that we applied 1100KW each UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618587&prj=479&rqi=LaFJh5COWMOC4RUh8jG4OjRJpy
GI-087 | SV18-1 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | Provide the materials the was taken from STS _F2_1 for the replacement of damaged components for 1STS_D2_3. As follow's. 1. Control cables. 2. Set of control breakers strip. 3. Electronic Modules (Oumar from Delta knows the model. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618602&prj=479&rqi=xU7RAKtmW8FkjhML3wdv2qmIBG
SOR-176-011 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | MAU_D_4 Smoke detection alarm test | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618603&prj=479&rqi=PpkU6t3IjRKUVF1YRl2F3QV41q
SOR-174-002 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | The humidifier sump has gone numerous times into drain down mode, since these units are fed by softened water so the conductivity probe may not be readying reliably, please have your technician check this out to verify the proper functionality. This applies to MAU_R1_01, MAU_B_2, MAU_C_3, & MAU_D_4. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618293&prj=479&rqi=pwd52CGoN6kO3GBX9c2Y83fqFz
SOR-173-002 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [6 empty] | Investigate the tripped occurred on the breaker 60AT feeding 1TX_R1_2_R1 at SKID R1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618265&prj=479&rqi=OFdAylmw05Bxdl89OiOI8jRbQD
SOR-173-001 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [6 empty] | 1ACC_R1_02 Compressor 3 Fault - Compressor failed The compressor failed the bearing levitation recalibration tests. The chiller sub cooler circuit the liquid solenoid valve & EXV were creating a lot of noise/hammer, it was found the chillers number 3 compressor was running with the suction isolation valve closed, due to an actuator fault. Tech support asked the Trane service engineer to isolate the compressor for troubleshooting tomorrow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618182&prj=479&rqi=hscuDzqwrXWBs59AAaIX0p3PYr
SOR-172-004 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning | [6 empty] | Skid D Heat Pumps are not responding to the thermostats. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618007&prj=479&rqi=f5FfxD5IIi1aB4JlfR3g4r1LBS
GI-086 | SV18-1 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-04-11 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning | [6 empty] | Control board was taken from one of the 1st floor MEGA CRAH units. Note that the asset nomenclature has not yet been identified for this unit, but the serial number for this unit is T26C006449. This was to resolve Issue #762. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617874&prj=479&rqi=FHVd7sK5YUopbBFcuRMKNptKsh
SOR-169-003 | SV18-1 | AMER | Closed | P2 Medium CX | James_Kenny@fsttechnical.com | 2026-04-10 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | A T3C A78 General Heaters Protection Alarm notification associated with loss of Heat Trace activated during power transfers for the following units: ACC_B_07 ACC_D_17 ACC_R1_01 ACC_R1_02 If the chiller is in idle mode, this alarm caused the chillers to lock out on DCOS. To avoid a reoccurrence of this issue this point need to be changed to a monitored point. TRANE to provide information on how they recommend the points to be managed, this is required for the associated RFI | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617786&prj=479&rqi=yC8ZIUsk51QyxbsvdiiC8lyltq
SOR-170-001 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-10 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS | [6 empty] | In DCOS the "Electrical" screen cuts off the kW values for the PDUs on the right side of the screen. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617828&prj=479&rqi=ECjAXNyO0fx0qvNBXiw0oGEnoV
SOR-168-006 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-09 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [6 empty] | PRE-IST TESTING CHILLER 1ACC_C_11 FAILED ON LOW FLOW | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617631&prj=479&rqi=yoo3BL61mmQVsGLymzZO4Dvtlh
SOR-168-007 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-09 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [6 empty] | PRE-IST 1ACC_R1_02 FAILED ON MOTOR BEARING ALARM | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617632&prj=479&rqi=FCuj4B9WHLDcjeQUhPQ3ojA2bL
SOR-166-008 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [6 empty] | PRE IST TESTING Chiller 1ACC_B_08 FAILED ON LOW FLOW FOLLOWING BEING RESET AND RESTARTED & THROUGH BEING SEQUENCED ONLINE | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617527&prj=479&rqi=zsbxJgb34BeneScXsmbMmubRbc
SOR-166-010 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | MAU's depict wrongly 2 supply fans There is one supply and one return Fan | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617564&prj=479&rqi=IIJaWkLFJroYGyvP0zSt1DYfyT
SOR-166-007 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning | [6 empty] | PRE IST TESTING Chiller 1ACC_B_08 CHILLER PLANT MANAGER DIDNT RESET IT | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617526&prj=479&rqi=if5a66aAs60Oej1bc3ccykFBWx
SOR-166-009 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | PRE-IST TESTING Chiller plant manager dialed up to the sequencer all 18 chillers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617528&prj=479&rqi=97GgantSQnMyudf5L7fIql8lY6
SOR-166-005 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | TRN - Trane |  | Commissioning Issue | Commissioning | [6 empty] | PRE IST TESTING Chiller 1ACC_C_12 FAILED ON LOW FLOW THROUGH BEING SEQUENCED ONLINE | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617524&prj=479&rqi=j4qWUGGwXvno34UzeQG37pddNe
SOR-166-006 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [6 empty] | PRE IST TESTING Chiller 1ACC_B_08 FAILED ON LOW FLOW THROUGH NORMAL OPERATION | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617525&prj=479&rqi=mKKLeZTN3FdM12QjRUK8bDM1z9
SOR-166-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [6 empty] | PRE-IST TESTING Chiller 1ACC_R1_02 FAILED ON LOW FLOW DURING BLOCK R UTILITY POWER TRANSFER TO GENERATOR | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617522&prj=479&rqi=hBNoVrWAYzgTXyxw3o2VLwfSZY
SOR-166-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [6 empty] | PRE IST TESTING Chiller 1ACC_C_11 FAILED ON LOW FLOW THROUGH BEING SEQUENCED ONLINE | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617523&prj=479&rqi=gcCEkTN3IqKGCAVLxR8ebZm07y
GI-085 | SV18-1 | AMER | Closed | P1 High CX | daniel_chavez@fsttechnical.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1RPP_B1_2_5 | RPP - Remote Power Panel |  | RPP-208-250-60 | A hot spot was discovered during load bank testing on RPP_B1_2_5 panel bussing. Refer to attach photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617460&prj=479&rqi=WVTWbuWbmJfEDVBsZqedse4Gn1
SOR-166-002 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | 1UPS_D3 is not communicating with the DCOS/BMS. Delta will need to investigate as E Tech confirmed they are not able to ping it. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617475&prj=479&rqi=pXZx0RyTHMa6vWqIegmgS3UaYg
SOR-165-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Alarm Screen Shots for DH D and associated Mega CRAH units | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617383&prj=479&rqi=YoO1DE7cXtAAw8ehkLAVSsgxQC
SOR-165-006 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Alarm Screen Shots for the Chilled Water System | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617386&prj=479&rqi=Xx7nZ6ayuYbgKzxiJGqmYwSvnf
SOR-165-008 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Delta CRAHs - Powerhouse Issues | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617389&prj=479&rqi=nGQ09KZaNjxNVg3XJdHBc0zj88
SOR-165-007 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | The Block A, E, & F 1BATT cabinets are missing batteries. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617388&prj=479&rqi=D01BI8vv229vzOQVnh6SMad6Ed
SOR-165-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Alarm Screen shots for Data Hall B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617364&prj=479&rqi=zv95unkGNKVgljE9rH7XML776V
SOR-165-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Alarm Screen Shots for Data Hall H including Mega CRAHs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617382&prj=479&rqi=TInnzgSmYQOL3B8TZMkacETtzf
SOR-165-005 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [6 empty] | Alarm screen shots for DATA HALL F + Mega CRAHs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617384&prj=479&rqi=VwGcnbFXuPVusxs1mMKKaKepJU
SOR-163-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | 1MAU_C_3 Alarm on Low Pressure Limit Switch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617245&prj=479&rqi=ZTQFs7xDWuOPfULf56pyUFPn6d
SOR-162-001 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-04-02 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Clear alarms for GEN R1, Z and B. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617157&prj=479&rqi=ka5hRll4iYIOvhTTiGdttIEo8Z
SOR-158-010 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-01 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [6 empty] | Freeze Protect valve on chiller 1ACC_R1_02, appeared to respond slower that the valves on the other chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617099&prj=479&rqi=iSy47rbmAlQgJhnqql1Xxcn5ed
SOR-161-001 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-01 04:00:00.000 +0400 | Design Professional |  | General Design Issue | Design | [6 empty] | There was no information where to get the UPS source for 1MSB_A/E/F feeding the controls as per Hanley submittal. DLB should provide direction what 1STS to use for feeding the 1MSB_A/E/F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617095&prj=479&rqi=AM4NDoHYKizyKEi1LqBfFfib5m
SOR-158-009 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Leak Detector LD2100 RLE controller from MPS found not communicating to BMS/DCOS and needs to be replaced. Powerhouse D | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616984&prj=479&rqi=wMZY2X1WmsP2p9QQBmL2VEv1D4
SOR-158-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  | system | CHW System |  |  |  | Chiller Transfer from Utility Power to Generator Power testing 1ACC_R1_01 & 1ACC_R1_02 failed on DCOS as the plc did not capture the power loss event and apply the 30 seconds delay on the external chiller alarm for phase loss. Without phase loss event capture the plc thinks it's in normal mode and will alarm and latch any alarm from external source. Trane troubleshooted the issue with tech support and lessons learned from DC22, they found that the phase loss relay was wired incorrectly to the normally closed contact on the phase loss relay. Trane corrected this and set the voltage to 480V. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616914&prj=479&rqi=LufCbsrhka60yUDtmGVUvmW5sY | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-158-004 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS | [6 empty] | E-Tech to include the Bard Units in the DCOS at MV1 and MV2 for monitoring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616960&prj=479&rqi=o0m16LQmp6QMATupJDykOl9dRa
GI-081 | SV18-1 | AMER | Closed | P1 High CX | daniel_chavez@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Washer discovered in MSB_A lineup, located in the 1BB_LB cabinet, far back against the bussing. Refer to attached photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616985&prj=479&rqi=vV33nYpJNZE1qtatbIhmweJs7j
SOR-158-007 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | I noticed that every day we are losing communication for all the equipment and come back in. Then your need to come back for each equipment's to clear the alarms. Could you please investigate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616971&prj=479&rqi=9W7yxwBI2ZTfVbnumS1WPzLgy8
SOR-158-008 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | All energized Equipment should have While Line background to indicate that were energized. This is applicable for all 1MSB's.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616973&prj=479&rqi=hijM92pB1qbZJ1iwpul5qRvkp0
SOR-156-002 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-03-28 04:00:00.000 +0400 | Subcontractor |  | Installation not correct | Commissioning | [6 empty] | Rectify the loss of communication for Leak Detection for the following. 2. Clear all the alarms. 3. Level 1 & 2 FOH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616760&prj=479&rqi=dvMjSVb3S7cWe4ESlgybbxKzSb
SOR-156-003 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-03-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | The SCR Common Alarm is active on 1GEN_B, 1GEN_R1 & 1GEN_Z. E Tech is to troubleshoot and resolve. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616762&prj=479&rqi=zgKjuJailszvoGrBnaZ0xEAkbw
SOR-155-002 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-03-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Duplicate of issues 661-677. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616632&prj=479&rqi=AdBqGabt2xnZtDG9QzfvNIWlbv
SOR-155-001 | SV18-1 | AMER | Open | P2 Medium CX | jordan_dubose@fsttechnical.com | 2026-03-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | The Carrier Heat Pumps natively speak BAC-NET communications to the BMS system at Equinixâ€™s SV18 facility. However these units will require BAC-NET gateways to allow proper communication to this BMS system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616631&prj=479&rqi=rgpsYqUhjDOyq2GzGGw9OnZVmI
SOR-154-004 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-03-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | The exhaust fan didn't energize, and damper didn't open during the simulation of battery temperature rise for UPS's for PH D and R1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616472&prj=479&rqi=DLmBj9JEEvflesPcvKfIShLdUG
SOR-151-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-24 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not complete | Commissioning |  | system | CHW System |  |  |  | Riser 1 & 6 was using 600 gpm cooling; issue raised on facility grid to track to closure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616270&prj=479&rqi=wWldbh1R9AB9J4GMmhCC3SDXg8 | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-151-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-24 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not correct | Commissioning |  | system | CHW System |  |  |  | Riser 4 and riser 9, when all other risers were closed, we had a no flow condition on the riser suggesting the bypass is closed, needs to be cracked open for corrosion protection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616272&prj=479&rqi=NSoPjNsvjVHjoxyBJU5E9tN95b | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-149-002 | SV18-1 | AMER | Closed | P2 Medium CX | James_Kenny@fsttechnical.com | 2026-03-22 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning |  | system | CHW System |  |  |  | Chilled water - Chiller flowmeter to riser flowmeter alignment - CDU risers 1 & 6, 4 & 9 Pressure control valves, not available to view or operate on the DCOS graphic, | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616136&prj=479&rqi=V78syQXgCmiTxx7qpCMHhHZ5KX | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-149-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-21 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Issues with Utility Power Loss and transfer to generator for all Trane Chillers, Issue raised on facility Grid and Trane contacted in this regard. See attached report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616135&prj=479&rqi=V3ZIyxlpsrfLZC0bjftQPa1awG
SOR-148-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Humidifier Piping, from pump to humidifier needs to be supported. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616058&prj=479&rqi=Sk0tf6ZwV5Ncw4EaV3DeWwSEPQ
SOR-147-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [6 empty] | Currently the chiller sequencer does not react appropriately staging down and there have been a number of chiller failures as a result. When the load on HVAC equipment associated with the chilled water distribution loop drops off the sequencer doesn't react quickly enough as the valve close so does the flow path the chillers run at minimum flow and fail when flow is reduced further. This issue can be resolved by implementing the low flow control strategy, where the recharge valve is brought online to maintain minimum flow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615992&prj=479&rqi=dONtk3MoNGfzmycbVgA0YGAB4r
SOR-147-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Equinix engineering and design team, need us to isolate one riser and one chiller at a time run the chiller into the riser, the reason for this exercise is to match the chiller flow to the riser flowmeter as it seems there is a very large error between the two. This procedure will take place when Leo is finished load banking. Detail to follow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616013&prj=479&rqi=vrOV3Spwj8ti19IE2YhVuMrnRH
GI-078 | SV18-1 | AMER | Closed | P3 Low CX | Rangsiya_Faihin@fsttechnical.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | The internal connection cable labeling for the battery cabinets is not consistent with the MPS.322 submittal. As shown on the attached page, the red boxes highlight the field-observed conditions. Please re-assign this item to the appropriate responsible party if needed. UPS_R2_2 & UPS_R2_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615834&prj=479&rqi=16RCMzojJ4eQzzChbLtfJE8aDh
GI-077 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Buttons without filler color once they are selected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615774&prj=479&rqi=gtzU6gkmk59J4G3wbm5pA5a8Tt
SOR-139-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | All Make-up Air handling units need to have droplet eliminators installed after on the inlet air hood of the unit, to deal with ambient fog conditions outside. Applies to the following: 1MAU_R1_01 1MAU_B_02 1MAU_C_03 1MAU_D_04 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615320&prj=479&rqi=z6u9fus8a4efnSivrAWxvmhGJX
SOR-138-006 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS |  | equipment type |  |  |  |  | The soft point "Logic Failure" per 2.16 DCOS Table of the Record - Delta STS 800A Submittal 480v V2 is not visible for the 1STSs to the customer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615190&prj=479&rqi=Qm7BSCLODy5qDkf1khO2IW5H7E
SOR-101-008 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-09 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [6 empty] | RESULTS OF SURVEY CONDUCTED BY THERMA TAB ON ALL OF THE CHILLED WATER PRESSURE TRANSMITTERS THE FOLLOWING TRANSMITTERS WERE READING OUT OF RANGE: DCOS Input numbers 1, 2, 5, 6, 7 & 8. See attached Table for reference, pressure readings were taken with a calibrated meter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615145&prj=479&rqi=P4xXRDRYLzSMJ3DOwM39ZNHqbg
SOR-138-005 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Carrier Heat Pumps: The TCV within the unit is limited to 2.5 to 13 GPM, design flow for this unit is 18 GPM, this applies to the following units: HP_R1_01, HP_R1_02, HP_B_01, HP_B_02, HP_C_01, HP_C_02, HP_D_01, HP_D_02 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615178&prj=479&rqi=SbvBTXx3BgdR1aNhSyMEsBZ2U8
SOR-137-008 | SV18-1 | AMER | Closed | P1 High CX | James_Kenny@fsttechnical.com | 2026-03-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Condensate Pump not activating on Delta CRAH unit located in the Power House Skids | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614986&prj=479&rqi=EWqorzyMEMkgTK40rLMkPDNWMz
SOR-137-009 | SV18-1 | AMER | Closed | P1 High CX | James_Kenny@fsttechnical.com | 2026-03-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Delta CRAH units located in the Power house Skids, do not transfer back from Reserve power to Primary power following power reinstatement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614987&prj=479&rqi=zNqKp3N3LBKlSnt0Suo5kZikTj
SOR-137-007 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Delta CRAH Units located in the Powerhouse Skid: R1 A B C D E F Units do Not shut down on smoke detector activation when the units operate in manual. In automatic the units will only work when the Fire Shutdown is enabled "ON". This is not acceptable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614985&prj=479&rqi=x9o5SovCVXoQuqg6RvGXdx18DD
SOR-137-010 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | VESDA CONTROLLER Units located in the Power house Skids & the MV-1 & 2 Power houses are in constant alarm. Relating to: R1, B, C, D, MV-1 & MV-2. WE NEED A REPRESENTATIVE FROM VESDA HERE ON SITE TO RECTIFY THE ISSUES WE ARE ENCOUNTERING. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614988&prj=479&rqi=9LAeIO9Vu1hZBf7P8y8yroGrsa
GI-076 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | PDUs are not reflecting the output CB in the onelines | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614921&prj=479&rqi=67AbLyK5RKmVH5qtVIaQseD82o
SOR-135-004 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Condensate Hi level switch interlock with the unit's compressor works but the unit's points integration to DCOS is not complete and this alarm needs to be verified once communications are established. This applies to the following units: make repairs necessary. 1HP_R1_1 1HP_R1_2 1HP_B_1 1HP_B_2 1HP_C_1 1HP_C_2 1HP_D_1 1HP_D_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614853&prj=479&rqi=L6Ozp7UNV3o7tNKJgpd9uNDulT
SOR-135-003 | SV18-1 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Smoke Detector is shutting the unit down locally but the unit's points integration to DCOS is not completed and this alarm needs to be verified once communications are established. This applies to the following units: HP_R1_2 Â HP_B_1 1HP_B_2 1HP_C_1 1HP_C_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614852&prj=479&rqi=7OtdR1uJPTAVomTLHNNoJ1UuB1
GI-073 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Risers are displayed in the detail view but missing in the overall floor plan view. Riser labels do not show which data halls each riser supports (operational context is missing). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614742&prj=479&rqi=NHyT5rpXMoOSuAysvTmtk77QC2
GI-068 | SV18-1 | AMER | Closed | P2 Medium DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS | [6 empty] | DP sensors are reading a wide variety of numbers, suggesting are missing scaling or not reading well | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614737&prj=479&rqi=vT9lUXbIA58uzrXqkqfyAq1DdZ
GI-064 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS | [6 empty] | 1. Chiller Flow Low Alarm Logic Incorrect Category: DCOS Design Issue (Alarm logic implemented incorrectly â†’ design/config logic error) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614733&prj=479&rqi=2UvT5AGKtMUiIaFJNo91Rvd8As
GI-069 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | The CRAHs overviews are not setup yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614738&prj=479&rqi=0v62nte0slTAVJDwx9K65qpSSS
GI-067 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [6 empty] | PQM data shows incorrect voltage and PF due to negative incoming power; polarity must be corrected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614736&prj=479&rqi=0P5A7e0ZHUp7ICCwmChTtg2qAz
GI-072 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Floorplan does not visually show which element is currently selected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614741&prj=479&rqi=0USfzYAw3EZrEZBpBYvygzgzmV
GI-066 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS | [6 empty] | SPARE and FUTUREâ€‘SPARE breakers must not be monitored or ingested. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614735&prj=479&rqi=x1q01tpdRQVVwidBvyG55TGl1L
GI-071 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Hot/cold aisle selection is reversed; cold selects hot and viceâ€‘versa. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614740&prj=479&rqi=IzXaaKU6kmfeqNGkiFDwjJMDmQ
GI-075 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS | [6 empty] | Battery Time Remaining is missing for all UPSs on the graphics/monitoring views. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614744&prj=479&rqi=JpVjDPMDZZamJbttfyMXJMaCB2
GI-065 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [6 empty] | Need confirmation whether these meters are the first monitoring point upstream of the SUSPs; if yes, Utility digital assets must be created per Appendix 7. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614734&prj=479&rqi=eI8bsbgJfx9yNFfBlrTKKubtoe
SOR-134-002 | SV18-1 | AMER | Closed | Outstanding Paperwork/Documentation | jordan_dubose@fsttechnical.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | Missing BMS/ ENMS signed documentation (Point to point check sheet and fibre results) for SV18-1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614722&prj=479&rqi=DjzCaBIm9pDHgRvw6MfwPkR0XH
GI-070 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | The UI does not highlight the selected item, making it unclear which item is currently active. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614739&prj=479&rqi=q0xON7W2xKXYQnY5pnU5CePV4C
GI-074 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Missing weblinks/deep links for assets (CRAHs, UPSs, etc.) from graphics to their detail/faceplate pages. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614743&prj=479&rqi=ntz9ocbC6TPCWagi7mMaBoivzr
SOR-132-006 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Some DCOS issues uncovered during our Powerhouse Skid CRAHs -Smoke detection testing. Skid B 1CRAH_B_13 - Successful Test - Not Depicted on the unit's faceplate in DCOS - E-Tech notified Skid C 1CRAH_C_13 - Successful Test - Not Depicted on the unit's faceplate in DCOS - E-Tech notified. 1CRAH_C_15 - Successful Test - Not Depicted on the unit's faceplate in DCOS - E-Tech notified. Skid D 1CRAH_D_14 - Successful Test - Not Depicted on the unit's faceplate in DCOS - E-Tech notified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614632&prj=479&rqi=OxY3vKos8oetvFWKWu5Xm3g9wN
SOR-133-003 | SV18-1 | AMER | Closed | P1 High CX | daniel_chavez@fsttechnical.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | The transformer for the VESDA system on Power House Skid B doesn't provide output voltage on the secondary side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614659&prj=479&rqi=sMQx4M1YOsXy4r01rdPSSht4Gs
SOR-132-007 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Skid C & D CRAH fan speed control All units were placed in automatic during testing, chillers and associated pumps were started and rooms cooled down to temperature set point. All fans continued to run at full speed, the expectation is the fan speed reduces as the temperature comes within range of setpoint. Suspect issue with the CRAHs Units remote temperature transmitter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614633&prj=479&rqi=vlmTzv1zWCl7PlckOTwO6uVPSU
SOR-132-005 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | PID pop-up settings are not working well: -scale is bad -name on buttons is wrong - EU range is wrong In GENERAL all pop-up settings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483499&prj=479&rqi=rQNjlhfankm09DBIJHW6FJlvLk
SOR-132-004 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS |  | equipment type |  |  |  |  | Gateways for the RPPs (BCM) connection can be move 2-3 Us above the current position so the cables won't be curved like now, which will affect the comms in the future | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483495&prj=479&rqi=D9lr9z0wUYi3XSmz8zJfphSW0M
SOR-117-005 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-27 04:00:00.000 +0400 | Owner |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | 1ACC_R1_01 - rode through the test and alarms reset thereafter, all UPS circuits were healthy during the test. 1ACC_R1_02 - House 120V UPS power was removed and the alarms didn't reset. The reason it didn't ride through is the Trane UPS in their control panel is programmed to provide power for a 3 second drop in power An extension of this timer from 3 seconds to 12 seconds would get us through the transition to Gen power. Trane Panel UPS is an Emerson Sola-HD 300w and backs up the chiller controller only. During test of the generator back up circuits on Saturday, Chillers 1ACC_B_07 & Chillers 1ACC_B_07 Phase Loss alarm activated and latched. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483373&prj=479&rqi=bxGwdp0lDizweGQVk4xSe9JqR0
SOR-127-005 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-27 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Discharge Valve oriented, there is a risk with the operation of the valve the mechanism may loosen up, and the handle would drop and disengaged from the actuator in its current position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483372&prj=479&rqi=ll6nESjOZIu8bJpHpu3jbRnqAU
SOR-130-004 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1RPP_F2_2_6 | RPP - Remote Power Panel |  | RPP-208-250-60 | 1RPP_F2_2_6 is missing two CT sticks due to them being used to replace the damaged CTs in 1RPP_B1_3_1 and 1RPP_B1_3_6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352262&prj=479&rqi=HLKDZfacgxOWTq6qQ66WTv69VI
SOR-130-003 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1RPP_B1_3_1 | RPP - Remote Power Panel |  | RPP-208-250-60 | During the PEI FST found a CT Senser had been damage possibly from installation on 1RPP_B1_3_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352261&prj=479&rqi=vpDJ8MKg9YvBt3YjWtea2NMZGa
SOR-131-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Fan spring isolators to be replaced on all units | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483382&prj=479&rqi=Kkl1HhxQvX9xAY2KniJQn6GLJ9
GI-060 | SV18-1 | AMER | Closed | P3 Low CX | adrian_brown@fsttechnical.com | 2026-02-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1RPP_B1_1_3 | RPP - Remote Power Panel |  | RPP-208-250-60 | During the PEI we found a missing cover for the small terminal under the main terminal | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352240&prj=479&rqi=kFKt5R3X8gtRoKiRBVKBzDeGzR
SOR-130-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-26 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [6 empty] | CONDUIT CONNECTIONS Covers missing on the conduit leading to the field devices on TST_B_07, See attached Photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352246&prj=479&rqi=okJqGvUg6yFUAHWPSIu3TiQjLl
GI-061 | SV18-1 | AMER | Closed | P3 Low CX | adrian_brown@fsttechnical.com | 2026-02-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | Electrical â€“ LV | equipment | 1RPP_B1_3_6 | RPP - Remote Power Panel |  | RPP-208-250-60 | During the PEI we found a CT Sencer had been damage possibly from installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352241&prj=479&rqi=SV2bOpeIrAZu7x5WTicnb7D7IL
GI-059 | SV18-1 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-02-24 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | Dummy Issue for JTM requested by Pat. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204066&prj=479&rqi=YDP4uLKb8K68umMPz1IPde1Mlf
SOR-122-017 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | [6 empty] | The mechanical lugs for 1PNL_X_HP terminations to Q06 in the 1MDSB_X are incorrect in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199681&prj=479&rqi=YXe74tQ2qaaxz0ZNT5UErwrcGT
SOR-122-008 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Mechanical Contractor |  | Missing Components | Commissioning | [6 empty] | The 1WSHPs in skids A, E, & F are missing drain pans underneath them per the request of Equinix. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199640&prj=479&rqi=qWchqAs7m2H7XkD0pfAjQKI26O
SOR-122-001 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design | [6 empty] | The positions of 1WSHP_X_1 & 1WSHP_X_2 in skids A, E and F in E403 are different from latest approved MPS submittal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199627&prj=479&rqi=SVUCVCx7pAfOH7UkLUonNPzipr
SOR-122-004 | SV18-1 | AMER | Closed | P2 Medium CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | The external small green stub in between the condensate piping and the light shown in MPS.000 is not installed in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199636&prj=479&rqi=Y0RE7BxJ20pupRJBJGLjEDQlqc
SOR-122-003 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | The top external tabs shown in MPS.000 are not installed in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199635&prj=479&rqi=NDBZtCAEjLG5RWmmKLaEJnB2os
SOR-122-002 | SV18-1 | AMER | Open | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design correction needed | Design | [6 empty] | 1MDSB_X Q01 in SV18-2 Hanley Submittal should be Spare. Refer to DLB Engineering Drawing Single Line Drawings E602.05, E602.009 & E602.10. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199633&prj=479&rqi=xZ8E2uVIe5IqV90GGRHoQ6gvVM
SOR-122-006 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | The ethernet connection from 1UPS_X_3 to DMARK shown in MPS.521 were not installed in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199638&prj=479&rqi=LsbiWvATVuhDJeCIShaUo7MkdL
SOR-122-007 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | [6 empty] | The mechanical lugs for 1UPS_X_3 terminations to Q07 in the 1MDSB_X are incorrect in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199639&prj=479&rqi=7O1hJbG51eLo8ZPS4PMbWkrgc1
SOR-122-015 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning | [6 empty] | 1MSB_E sections 5, 6, 11, 12, and 13 each had a screw that was screwed into the ground bus bar. MPS successfully removed the screws in the 5 sections of 1MSB_E. This has resulted in the ground bus bar plates in the 1MSB_E sections 5, 6, 11, 12, and 13 each having a hole in them. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199647&prj=479&rqi=wf2S0qF7l0obBvdaEP8QLCvFrV
SOR-122-009 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | FST observed that a third branch junction box above the 1BTUs in skids A, E, & F shown in MPS.400 was not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199641&prj=479&rqi=bYaEQYYDBKWdQFSEQa74NymAPw
SOR-122-011 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | The ball valve is missing from the section 2 VESDA conduit in front of 1CRAH_A3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199643&prj=479&rqi=OLs0n0kAiIG97iSCAad6qpg251
SOR-122-005 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | The three pulling gutters shown in MPS.301 were not installed in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199637&prj=479&rqi=sn4LiyNtJR6eox90U5GzsrweEV
SOR-122-016 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [6 empty] | The ball valve is missing from the section 2 VESDA conduit in front of 1CRAH_E3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199648&prj=479&rqi=54nWJik9uYAZte8mcjXNAfshWf
SOR-117-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-18 04:00:00.000 +0400 | Owner |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | Soft Points that are not available from the chiller: Flow switch COP Condenser Fan Fault Condenser Fan Summary Fault Evap. Approach Temperature Evap. DP Sensor. TXV 1 TXV 2 Free Cooling mode enable Free Cooling valve % Hot Gas 1 Hot Gas 2 Liquid Level 1 Liquid Level 2 Liquid Refrigerant Temperature Ambient Temperature Lockout. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199503&prj=479&rqi=KPv7Ul4ixcgWZR4vKQee5L4V4S
SOR-119-004 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [6 empty] | Chilled water make-up skid - Pressure transmitter needs to be wired and represented on the DCOS graphic. The flow switch is not on the graphics either, this needs to be tested to ensure an alarm is posted to the DCOS alarm page. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199502&prj=479&rqi=auzKBwyUeEM9OR72pRKUEru4IG
GI-056 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | The alarm border is overlapping the objects in different dashboards. The objects need more spacing between them to show correctly the alarm border | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199401&prj=479&rqi=Fpl6A6AKeHYMb7LM9LrJ7pJGhB
SOR-118-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Remove lifting eyes from all Generators on site: | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199378&prj=479&rqi=fbCz0zxsP4okVZP7Qwi9O3ThUY
GI-055 | SV18-1 | AMER | Closed | P3 Low CX | manuel.gomez@eu.equinix.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | The Alarm border overlaps multiple objects. The objects need more spacing between them so they can be reflected correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199400&prj=479&rqi=xD8suZ0nHjaOZelGXKAsDvjpCb
GI-057 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | STS faceplate issues with : - power factor not communicating - overview content not available - lines in the hierarchy are not showing the right flow, you can see on source one there is a piece of line at the top right corner that is not white. - The voltage in the table is not showing all the values as per the object (kwh, Vab, Vbc are different) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199402&prj=479&rqi=GFHzMMKFLqooMRP8zqqJ0fzBvs
SOR-118-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Clean debris and rust off all generator roofs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199379&prj=479&rqi=JGtfwP0bMQhX49VYPy960rJC07
GI-053 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [6 empty] | Autolunch of OMI app is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199397&prj=479&rqi=87nErhGYYMwJm67Vnwe8GWNyvK
GI-054 | SV18-1 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS | [6 empty] | The statistics alarms app is not properly configured, furthermore, not working | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199399&prj=479&rqi=9jxilv0Uha1cWLNpv0JvgbpVA9
GI-049 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | The Overviews for each MSB are inconsistent, leading to a graphical issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199280&prj=479&rqi=7GX153ri3MTs3fRKp1RAEt9tkP
GI-044 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | On Chiller ACC Overview the headers are repeated on each row, per DCOS Configuration Guide this is not acceptable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199275&prj=479&rqi=BdjbaLbQ9BM4eusBbzORYMuYtR
GI-050 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Template Issue | DCOS | [6 empty] | Fire in the footer are not clickable, so we can not go to the respective faceplace/object page | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199281&prj=479&rqi=3cPYZlzmkPfVUEQzLoJYErKD91
GI-052 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Missing name of the data halls (floorplan and tooltip) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199283&prj=479&rqi=A7i79PMs3nJReoyYjBIOVs5vLH
GI-045 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | The CWST screen appears to have overlapping issues; this screen needs to be revisited once we have more value. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199276&prj=479&rqi=d5JWrAnPo77PcE4BDfB39w5eeo
GI-046 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Chilled water overview graphics have several issues as the sensors are misplaced or not located with dashes or pipping leads to nothing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199277&prj=479&rqi=bD5cCukvSUSZnxV1DGyGo6cS3B
GI-047 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | Chiller Overview has no arrows, and the pump is not in the right direction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199278&prj=479&rqi=8L1x0M5FeGCagUv7ops0P6cWPA
GI-048 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | On the Data Hall Overviews, there is not a trace for the Leak Detection, this is against the DCOS configuration guide. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199279&prj=479&rqi=1I8Z6AeDZGmXhI27VN464hdr4B
GI-051 | SV18-1 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | I understand the previous apps bring the oversize for the "csv export," but let's standardize now across the alarm apps | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199282&prj=479&rqi=cgYQJexDsdt2TlurkmnZrEs74g
GI-043 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [6 empty] | This is a dummy issue to confirm that JTM is receiving email notifications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199223&prj=479&rqi=C9feNwafgPtT5Ve0iY8icsI2wG
SOR-110-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-09 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  | system | CHW System |  |  |  | Issues with the Chiller RIO Panel wiring to be addressed, applies to the following RIO Cabinets: CHILLER-RIO-01 CHILLER-RIO-02 CHILLER-RIO-07 CHILLER-RIO-08 CHILLER-RIO-11 CHILLER-RIO-12 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198827&prj=479&rqi=hsAUm6i8epVkwJJFsW1B67ZIYk | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-110-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-09 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | Scaling to be addressed on all Chillers & Pumps, this applies to the following chillers: 1ACC_R1_01 1ACC_R1_02 1ACC_B_07 1ACC_B_08 1ACC_C_11 1ACC_C_12 1ACC_D_17 1ACC_D_18 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198826&prj=479&rqi=ZL8uTTNTI8aeByOxpFV9qmnzQj
SOR-109-001 | SV18-1 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-02-09 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | 1SUDB 1 & 2 are not communicating at DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198753&prj=479&rqi=S8iF4HbZ8HHo8oChtL4po466XD
SOR-109-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-02-09 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | 1MSB_Z is not communicating with the DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198755&prj=479&rqi=fFnTUCJdCSvaixG7GxcSaGlZMG
SOR-109-002 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-02-09 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [6 empty] | 1RMU_R1/B/C/D/Z are not communicating with DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198754&prj=479&rqi=qm4iBOOxdb6BS0cVs0G7aUpTGD
SOR-108-003 | SV18-1 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-02-07 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS |  | equipment type |  |  |  |  | FST observed during testing that Soft Points listed below requested by Equinix are not available in the DCOS system for the different 1UPS's. -Battery Cycle Buffer Full -Battery Time Remaining Status -Battery Time Remaining -Control Power Failure -DC Bus Voltage -DC Cap Fuse -Emergency Power Off -Input Current Unbalance -Output Voltage AN -Output Voltage BN -Output Voltage CN -Rectifier Fuse -Static Switch Disable -kWh | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198729&prj=479&rqi=jxSXlrktUQfaRBeGxTuYbK3FVg
SOR-108-002 | SV18-1 | AMER | Closed | P1 High DCOS | jordan_dubose@fsttechnical.com | 2026-02-07 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | During 1UPS's battery drain testing FST observed that the "Low Battery Alarm" did not turn on in DCOS system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198728&prj=479&rqi=JjWBnBgrQzPY5BHmFOeAVISYxl
GI-038 | SV18-1 | AMER | Closed | P3 Low CX | adrian_brown@fsttechnical.com | 2026-02-05 04:00:00.000 +0400 | General Contractor |  | Installation Damage | Commissioning | [6 empty] | Mega CRAH cosmetic issues Observed Issues / Damage: â€¢ CRAH C-06: Front grille is discolored with visible damage. Deep scratches were observed on the left-side panel. â€¢ CRAH C-04: Front grille shows visible damage, discoloration, and scratches. â€¢ CRAH C-03: Front grille has similar damage and discoloration as C-04, though less severe. â€¢ CRAH C-12: Front grille is damaged and discolored. â€¢ CRAH C-10: Significant dent and scratches on the front panel, consistent with possible impact from a lift. â€¢ CRAH C-11: T2 sensor wiring is damaged and stripped. Therma has been notified of this issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198645&prj=479&rqi=TbNnDjyDoWKUPzKm8KuOkYSf4c
SOR-104-003 | SV18-1 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [6 empty] | Incomplete leak detection cable installation for all Skids. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198185&prj=479&rqi=P0s4qwncVfs1Bxxe96ye33ITUO
GI-035 | SV18-1 | AMER | Closed | P3 Low CX | baron_brown@fsttechnical.com | 2026-01-31 04:00:00.000 +0400 | Owner |  | Commissioning Issue | Commissioning | [6 empty] | Verify interfaces and interlocks with EMS / Generator control / HV & LV switches Confirm alarms and indicators are operable Confirm CxA Level 4 (Blue Tag) Functional Performance test script available and approved Complete DCOS/ ENMS signed documentation is attached as a document to this checklist. (Point to point check sheet) DCOS Point to Point check complete 100% DCOS status/ alarming verified to ENMS workstation DCOS Point to Point check complete. 100% DCOS status/ alarming verified to DCOS workstation. 100% SCADA status/ alarming verified to DCOS workstation Local Alarms/ statuses are proven to HMI 1HMI SCADA 1MSB Input checklist these items are open and checked NO at this time. FST will verify during Level 4 Testing . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198071&prj=479&rqi=QFdv3sjomAzRhybKAaVCQiXE4d
SOR-102-006 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Power to the Smoke detectors is not installed from the Fire Alarm panel to the smoke detector, in this case the Carrier representative could not complete his scheduled start-up for the equipment. 1WSHP_C_01 1WSHP_C_02 1WSHP_D_01 1WSHP_D_02 Inline plugs for fans and pressure switches found unplugged in the unit, increasing the time troubleshooting. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198072&prj=479&rqi=9mlTeuZt9INdx8OogtJ0eVYNJz
SOR-102-001 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning |  | equipment type |  |  |  |  | Powerhouse Skids CRAH's All panels appear to have been tightened up with a cordless drill and the captive nut broken from its anchor, or threads have been damaged, this has caused significant delay on the commissioning of the Equipment. MPS to better manage the QA Process in their shop, issue raised on Facility Grid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198058&prj=479&rqi=amOneJMzn39QHUkg5GH7E9G7vo
SOR-102-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  | equipment type |  |  |  |  | 3 x Supply air sensors are missing from the Powerhouse Skid CRAHs. Delta is swapping the sensors to enable their commissioning process. Parts on order. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198059&prj=479&rqi=F5kWEWrA3r3L73gEn9EVqEWbVv
SOR-101-006 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | Raceway ran in the way of access panels for the Air filter section on 1CRAH_ C_14, needs to be moved. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197961&prj=479&rqi=jC4f9koJmOmxVFDn4feW8JFZe5
SOR-101-002 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-29 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design |  | equipment type |  |  |  |  | FST observed that labeling of the Skid Heat Pumps in the field, engineering drawings and approved MPS submittals did not match. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197956&prj=479&rqi=i3BUY6CfjYfjL2DNeZCqBxmOO4
SOR-101-004 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | FST observed that the labeling of conduits and junction boxes for the panel sources of the Heat Pumps in Skid R1 are not accurate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197959&prj=479&rqi=4MZoeyJrIlvvgM4ZzCU79hOR4f
SOR-101-003 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-29 04:00:00.000 +0400 | Design Professional |  | Design not as specified | Design |  | equipment type |  |  |  |  | FST observed that source of the Skid Heat Pumps in the field, and engineering drawings did not match. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197957&prj=479&rqi=d7o7dFgdykpONwC8xsWLYAXQIF
SOR-101-005 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | equipment type |  |  |  |  | FST observed that the labeling of conduits and junction boxes for the panel sources of the Heat Pumps in Skid B are not accurate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197960&prj=479&rqi=jxipaYskTBRZpjU3vqowXYaIWs
SOR-97-002 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-24 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | IP addresses to be uploaded into the chiller Pumps, Danfoss VFD: 1ACC_R1_01 1ACC_R1_02 1ACC_B_07 1ACC_B_08 To be done following start-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197545&prj=479&rqi=sw7aR94zYwpXW3yh4i5eO2aubd
SOR-96-011 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-24 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | In the absence of reliable Chiller flowmeters, Cx & Trane representative made the call to install Pete's plugs on the inlet and outlet of the chiller evaporator. This way Trane can connect a pressure differential meter to the petes plugs and determine the actual differential using the manufacturers chart for the evaporator Flow plotted against differential pressure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197542&prj=479&rqi=5aZjEYvJFZsorkA9dGtLZOgN7g
SOR-95-008 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-23 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [6 empty] | Chiller Return flowmeter was not operating - screen was not illuminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197527&prj=479&rqi=kNFdSnlXmq5HwGLYgAswzA1joe
SOR-96-003 | SV18-1 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-23 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [6 empty] | Chiller condenser fan junction boxes had water ingress, blew fuses on start-up on chiller circuit 3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197530&prj=479&rqi=897QwdRWZNrKGQZNDkAYkXI3iH
SOR-91-009 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-20 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1-EGB-Z-2-2 | BUS - Busbar |  |  | FST observed on 1TGB-Z-2-2 that the cables for connections to 1TBG-Z-2-3 and the ladder rack are thin wires instead of #4/0 AWG CU identified in E604.01-SINGLE-LINE-DIAGRAMS---GROUNDING-Rev.7. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197269&prj=479&rqi=fnncv1jZKJzbzas7vKuUBhjq0F
SOR-91-002 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-16 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design | [6 empty] | In the latest R3 coordination study, E709 panel schedule and in the field both 1UPNL_B1_H1 & 1UPNL_C1_4_H1 have one 125A and three 80A circuit breakers but those panels have one 125A and three 100A breakers in the E603.06 & E603.07 UPS_DISTRIBUTION Single Lines from Bulletin 2 & 3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197068&prj=479&rqi=GVw4GVW1k8RJLhQTNZmu4avgCf
SOR-86-001 | SV18-1 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-10 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design | [6 empty] | FST observed that the E602.03-E602.14 Single Line Block Diagrams incorrectly state that only the 1MSB_Xs, 1MSB_X Remote HMIs, 1UPS_X1s, 1UPS_X2s, 1BATT_UPS_X1s, and 1BATT_UPS_X2s are pre-wired by the skid Manufacturer as it also lists the 1MDSB_Xs, 1UPS_X3s, and 1BATT_UPS_X3s as well. Attached are the Single Line Block Diagrams for blocks installed in the current phase but is applicable to every block. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196677&prj=479&rqi=p6WYnCevAdXYH4sJzb4hBy5z1G
SOR-83-004 | SV18-1 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-01-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | Missing communication ethernet cable for 1MSB_D at Dmark. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196537&prj=479&rqi=1D8I7th8waZ1lwACc0qkrF30uw
BT1MECH-15-001 | SV18-2 | AMER | Open | P2 Medium DCOS | nick.shawger@veolia.com | 2026-09-17 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1ACC_G_15 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers) Chillerâ€™s with miscellaneous alarms are not available to run in rotation Details Due to the above â€œFaultingâ€ sequence, Chillers that are physically available to run but have an alarm that triggers the HW fault signal will never prove in the CHW Plant sequence The combination of the HW fault signal and the initial lack of â€œRunning Statusâ€ will trigger a â€œFaultâ€ and removal from rotation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638614&prj=684&rqi=TyhWpFg8YAH1kaWDLUw9BvDqPW
BT1MECH-15-005 | SV18-2 | AMER | Open | P2 Medium DCOS | nick.shawger@veolia.com | 2026-09-17 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1ACC_G_15 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers) Compressor Not Required (Low Load) does not have a robust implementation Details Current implementation of the â€œCompressor Not Required Bitâ€ does not allow a Chiller start and prove in the rotation under low load Only works to prevent a low load Chiller from â€œFaultingâ€ if it is already proven in the rotation before going to low load mode, also only if the debounce timer is set to > 120s Therefore CHW Plant stage-ups due to flow (as opposed to load) are unstable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638619&prj=684&rqi=IunaiGDAibOoF6SZYGisKCKhK8
BT1MECH-6-001 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-09-17 04:00:00.000 +0400 | TRN - Trane | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1ACC_H_14 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_H_14) L4 Compressor 3 constant fault | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638626&prj=684&rqi=cEfI5Z6qLVwBhpNTZdpCy4vED4
BT1MECH-2-001 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-09-17 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1ACC_R2_05 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_R2_06) L4 Constant Heat Trace warning alarm even though heat trace breaker is closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638623&prj=684&rqi=EaVbgWbYbo2ZplDVhJyjysQTBq
BT1MECH-15-004 | SV18-2 | AMER | Open | P3 Low DCOS | nick.shawger@veolia.com | 2026-09-17 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1ACC_G_15 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers) Setting the Chillerâ€™s setpoint from the BMS is currently not functional on all SV18-2 Chillers, scaling is way off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638618&prj=684&rqi=aC7pmgLPxyhKOLatfPCikrOO3R
BT1MECH-15-003 | SV18-2 | AMER | Open | P2 Medium CX | nick.shawger@veolia.com | 2026-09-17 04:00:00.000 +0400 | TRN - Trane | L4 | General Design Issue | Design | Mechanical â€“ Water | equipment | 1ACC_G_15 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers) Failing the Chillerâ€™s main controller will not â€œFaultâ€ the Chiller Details Chiller will shutdown Values communicated to the BMS will â€œfreezeâ€ such that: HW fault signal will not be present â€œRunning Statusâ€ will remain ON Resolution Accept behavior and rely on Operator intervention OR code a patch to remove Chillerâ€™s from rotation due to not meeting setpoint | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638616&prj=684&rqi=ESeYceFEpYyYube93wnAUi8kIy
BT1MECH-3-001 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-09-17 04:00:00.000 +0400 | TRN - Trane | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1ACC_R2_06 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_R2_06) L4 Modbus communication is showing all 0's. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638622&prj=684&rqi=9iz3uqj3oG7qwj7jqZQqd55fPS
BT1MECH-2-002 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-09-17 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1ACC_R2_05 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_R2_05) L4 Constant Heat Trace warning alarm even though heat trace breaker is closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638625&prj=684&rqi=WwYYUE4xdFdp75sEjgiS7D1fAo
BT1MECH-65-005 | SV18-2 | AMER | Open | P3 Low DCOS | nick.shawger@veolia.com | 2026-09-17 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1CRAH_G_13 | CRAH - Computer room air handler (Skid) |  |  | (All Skid CRAHs) Changing the SAT / DT Setpoint at the HMI doesnâ€™t update the value on the BMS faceplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638620&prj=684&rqi=nQByDpyYOlfbyQWQww2FSJaEQc
BT1MECH-15-002 | SV18-2 | AMER | Open | P2 Medium CX | nick.shawger@veolia.com | 2026-09-17 04:00:00.000 +0400 | TRN - Trane | L4 | Design correction needed | Design | Mechanical â€“ Water | equipment | 1ACC_G_15 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers) Loss of minimum flow switch feedback will not â€œFaultâ€ the Chiller Details Chiller will shutdown HW fault signal will not be present Chiller will continuously attempt to restart â€œRunning Statusâ€ will flip back and forth Therefore debounce timer will never fully count down | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638615&prj=684&rqi=W1SxPeQSmxXO2ypLQR4fxDOFHp
GT1ELEC-347-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UPS_H_1 | UPS - Uninterrupted Power Supply |  |  | (1UPS_H1) HMI failed to turn on when energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638407&prj=684&rqi=CYcTgS3fpBWqjA3yt8OQiz57T2
GT1ELEC-350-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UPS_J_1 | UPS - Uninterrupted Power Supply |  |  | (1UPS_J1) HMI failed to turn on when energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638409&prj=684&rqi=2OlhRPWmBdK1Rs6BgmjhohLrBX
GT1ELEC-348-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UPS_H_2 | UPS - Uninterrupted Power Supply |  |  | (1UPS_H2) HMI failed to turn on when energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638408&prj=684&rqi=AoEDpBqSVm4YKz7L4CnyXVXkeB
GT1ELEC-357-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_2 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_2)Â HMI on UPS failed to turn on when energizing.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638387&prj=684&rqi=WtCQbh1zeDtqanc4h7Radxlztv
GT1ELEC-356-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_1 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_1) HMI on UPS failed to turn on upon energization.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638388&prj=684&rqi=HqoQgpPXQe91fLuTGGUNrIXefM
GT1ELEC-344-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-09-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1UPS_G_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G1 L3 Several failed components identified during startup of the equipment. Issues include the inverter assembly, power supply module, and several cards. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638187&prj=684&rqi=mOPsDGgameAbkDMlV5vAirwJ2m
GT1ELEC-254-001 | SV18-2 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-09-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1RPP_K1_2_6 | RPP - Remote Power Panel |  |  | Top hinge for door came off and door was falling out of placement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638237&prj=684&rqi=Ap6Jj29baFS4t5Tq9I580dDvXP
GT1ELEC-106-001 | SV18-2 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-09-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1PDU_G1_1 | PDU - Power Distribution Unit |  |  | Sub feed 4 has a communication alarm inÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638236&prj=684&rqi=cBKoPFsKAEchelO3vmH96usgOs
GT1ELEC-183-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1RPP_E1_2_2 | RPP - Remote Power Panel |  |  | 1RPP_E1_2_2 L4 During HLT, a thermal deficiency was noted and the equipment was shut off. After further inspection, a bolt on the bus bar was found not properly installed or torqued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638038&prj=684&rqi=pzSpv7fqEkAoXQMGaw7jtJdHGo
GT1ELEC-126-002 | SV18-2 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1PDU_J2_2 | PDU - Power Distribution Unit |  |  | Missing disconnect for HMI power supplyÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638027&prj=684&rqi=fZ8PnCLwRQ4g3aBum0E6u83nC4
GT1ELEC-101-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1PDU_E1_4 | PDU - Power Distribution Unit |  |  | (PDU E1_4): HMI failure. HMI is not showing subfeeds.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638005&prj=684&rqi=axhmoVQyxGW1Fk5LPFxzKvLCJa
GT1ELEC-126-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1PDU_J2_2 | PDU - Power Distribution Unit |  |  | (1PDU_J2_2) HMI displays aux power fail.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638026&prj=684&rqi=nSJCEtkVFDnhje2qN79JokF307
BT1MECH-41-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | alec.dughi@veolia.com | 2026-09-11 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Comms Issue/ Fault | DCOS | Mechanical â€“ Water | equipment | 1CRAH_H_01 | CRAH - Computer room air handler |  |  | (All H-fed Data Hall CRAHs) L4 None of the H CRAHs are viewable on BMS, check if the MOH Network cabinet is up and working correctly? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637824&prj=684&rqi=xD6NIPXXmQaMnU3cb92kxbjEy8
BT1MECH-80-002 | SV18-2 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-09-11 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (HP_G_01) L4 BMS Graphic is switched in Aveva. HP-G-01 is showing data from HP-G-02 and vice versa. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637823&prj=684&rqi=LKDy4vI2Pxt8TE8OWt8khJbNAd
BT1MECH-80-001 | SV18-2 | AMER | Open | P2 Medium CX | alec.dughi@veolia.com | 2026-09-11 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Comms Issue/ Fault | DCOS | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (HP_G_1) L4 HP_G_ 1 port at network switch in D mark panel suspected to be bad. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637813&prj=684&rqi=HzOt0WVvvNkzL2U3csDqNc0amk
BT1MECH-64-001 | SV18-2 | AMER | Open | P2 Medium CX | ethan.hang@veolia.com | 2026-09-09 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_12 | CRAH - Computer room air handler |  |  | (1CRAH_K_12) L4 Two EC fans were taken and given to K_02 and K_04. New fans are needed for K_12. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637551&prj=684&rqi=e3wvUq6s2WBTS0xlI8LtHy5u7f
BT1MECH-56-002 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-09 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_04 | CRAH - Computer room air handler |  |  | (1CRAH_K_04) L4 Unit produces significantly lower airflow than all other units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637509&prj=684&rqi=72FH3RrFV0VdXTSO12bQo6GU6V
GT1MECH-42-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-09-08 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1CRAH_G_01 | CRAH - Computer room air handler |  |  | (All K CRAHs) L3 At the BMS floor layout, all K CRAHs are labeled as J CRAHs. Etech relabeled to K. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637287&prj=684&rqi=FIPIvyxY9EWQ9OLecAV74rCMuz
BT1MECH-54-003 | SV18-2 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-09-08 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (CRAH-K-02) L4 Condensate pump discharge copper piping has a leak that sprays water during pump operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637323&prj=684&rqi=Ald4jufHZbKFuBRocAGjLTVwUR
BT1MECH-56-001 | SV18-2 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-09-08 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Incomplete Connections | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_04 | CRAH - Computer room air handler |  |  | (CRAH-K-04) L4 Condensate pump discharge copper piping has a leak at brass fitting that sprays water during pump operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637327&prj=684&rqi=AU5M1aRwjIxEpnHomqxqJynklj
BT1MECH-55-002 | SV18-2 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-09-04 04:00:00.000 +0400 | Mechanical Contractor | L4 | Incomplete Connections | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_03 | CRAH - Computer room air handler |  |  | (CRAH-K-03) L4 Leak detection module is wired incorrectly. Not using the correct 2 out of 3 wires in both power and signal bundles going into the module itself. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636922&prj=684&rqi=bGXqVIUycTkllvLbrYNDVTTIFa
BT1MECH-37-002 | SV18-2 | AMER | Ready for Verification | P3 Low CX | alec.dughi@veolia.com | 2026-09-03 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_09 | CRAH - Computer room air handler |  |  | (CRAH-G-09) L4 Condensate pump discharge copper piping has a leak that sprays water during pump operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636755&prj=684&rqi=ASjrCddVd9eTdFtgly7GeTze3a
BT1MECH-55-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_03 | CRAH - Computer room air handler |  |  | (1CRAH_K_03) L4 Failing RAT sensor does not make the fan speed go to 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636596&prj=684&rqi=iu30m5WReZLCh37e6CuTSnVbiy
BT1MECH-54-002 | SV18-2 | AMER | Open | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (1CRAH_K_02) L4 K10 contactor is defective, preventing the correct operation of the ATS function. Replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636593&prj=684&rqi=UYDvjxckugsKVGQLqIbXnPXrwK
BT1MECH-54-001 | SV18-2 | AMER | Closed | P1 High CX | alec.dughi@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Incomplete Connections | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (1CRAH_K_02) L4 CHW valve 2 has no power. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636568&prj=684&rqi=25eV7lL2PM9vPp2bdEvsvIjsKK
BT1MECH-37-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_09 | CRAH - Computer room air handler |  |  | (1CRAH_G_09) L4 Failing RAT sensor does not make the fan speed go to 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636600&prj=684&rqi=B185g7nyrXWdpWldGQ0qNkXws1
BT1MECH-35-003 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (1CRAH_G_07) L4 Failing RAT sensor does not make the fan speed go to 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636597&prj=684&rqi=fM3hsUO7aSf7CcNlJOi943blgz
BT1MECH-57-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_05 | CRAH - Computer room air handler |  |  | (1CRAH_K_05) L4 Failing RAT sensor does not make the fan speed go to 100%. EDIT 9.9.26: Hidden setting "Sensor Fail Fanspeed" found. Units require firmware update PA2.08.17R Build 20260303-185731 for this setting to be active. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636594&prj=684&rqi=xzda9tbboGOZNUokOPyR4rhXw6
BT1MECH-36-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_08 | CRAH - Computer room air handler |  |  | (1CRAH_G_08) L4 Failing RAT sensor does not make the fan speed go to 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636599&prj=684&rqi=n1dmbpojxm5LTzsqpPWGCjIwqe
YT1ELEC-155-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1RPP_A1_1_1 | RPP - Remote Power Panel |  |  | All RPPs L2B A single screw on all 4 corners of the panel board is too long and requires replacement. AMG is tracking this issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636356&prj=684&rqi=pkLUIB6xLD2r0mlM0y8yVUGbv0
BT1MECH-35-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-31 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (DH CRAH) L4 Supply fan speed command is 1 input behind at the BMS. ex: default starts at 50%, inputting 60%, fans go to 60% but BMS stays at 50%, inputting 70%, fans go to 70% but BMS goes to 60%, etc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636164&prj=684&rqi=naL4YEONvMqSrPo0Qbhz1BvkdT
GT1MECH-18-001 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-08-31 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_01 | CRAH - Computer room air handler |  |  | (1CRAH_G_1) L3 Source 2 50A fuse bracket was found to be broken during L3. Replacement bracket and fuse needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636119&prj=684&rqi=d0URjpWfnLvfIjEqGVtpUukmpO
BT1MECH-35-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-31 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (DH CRAH) L4 Supply fan speed command is not showing correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636165&prj=684&rqi=5q0LSYNyWMMLlODc8Dme8Q374m
GT1MECH-38-001 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-08-27 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_09 | CRAH - Computer room air handler |  |  | (1CRAH_H_09) L3 Control board was donated to higher priority CRAH_K_04. CRAH_H_09 needs new control board. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635759&prj=684&rqi=odQyfCc8496Z79sGcjOvOik7Xm
YT1ELEC-355-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_J3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_J3 L2B Broken Dry Contact Card that requires replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635695&prj=684&rqi=HRFad3v0EEisuFD1dokraw7dxi
BT1MECH-61-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-27 04:00:00.000 +0400 | Controls Contractor | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_09 | CRAH - Computer room air handler |  |  | (1CRAH_K_09) L3 Upper CAT6 port is not sending data to the Moxa switch for U2U communications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635758&prj=684&rqi=K8xqdZyMsvJlBzaolzqG5wn8ik
GT1ELEC-92-002 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | UPS_K_1 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635470&prj=684&rqi=G9UTnvun9A4z1qk39lCwsrKLew
GT1ELEC-93-002 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | UPS_R2_2 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635473&prj=684&rqi=WJyRKo3ty2UxfiSMDQbeZOdDk4
GT1ELEC-383-001 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_R2_3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | UPS_R2_3 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635478&prj=684&rqi=mXIqUMElwHsRwnB7ZHXUCzQZKU
GT1ELEC-90-003 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | UPS_H_2 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635465&prj=684&rqi=8pOBYeKIX8mpi280ZbevLs2bQd
GT1ELEC-380-001 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_H3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | UPS_H3 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635475&prj=684&rqi=M2cIJajHQXsdpO0C7MnRk0Wp6y
GT1ELEC-90-002 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | UPS_H_1 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635464&prj=684&rqi=aYZDSbjwbJD2PeY90HFB79XCjO
GT1ELEC-381-001 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_J3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | UPS_J3 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635476&prj=684&rqi=zjDUYvAdOcMjURbTVlvgpa9iG8
BT1MECH-65-004 | SV18-2 | AMER | Closed | P3 Low CX | abdul-qadeer.bilal@veolia.com | 2026-08-26 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS General Issue | DCOS | Mechanical â€“ Water | equipment | 1CRAH_G_13 | CRAH - Computer room air handler (Skid) |  |  | (All Skid CRAHs) L4 Supply air temperature on CRAH BMS faceplate is not actually tracking the SAT that the valve controls to. Please use address 0x0017 dec 23. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635452&prj=684&rqi=rR1S5YGNKZSwEunpr6YJNGD4kG
GT1ELEC-382-001 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_K3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | UPS_K3 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635477&prj=684&rqi=ssYWEBOMAPFv1mnYAz8sDfJlLW
YT1ELEC-237-001 | SV18-2 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-08-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1RPP_H2_2_5 | RPP - Remote Power Panel |  |  | Found a broken/damaged connector piece during normal inspection of RPP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635337&prj=684&rqi=W63FT3h9D1Yvzgh7QW2XfsY710
GT1ELEC-89-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | UPS_G_1 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635461&prj=684&rqi=c8YrvPTJKzNFQkHvWqTjWfZ4X2
GT1ELEC-89-002 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | UPS_G_2 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635462&prj=684&rqi=PH1yNnEufcHdyfv6lcdYBOW7nC
GT1ELEC-379-002 | SV18-2 | AMER | Work Completed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | UPS_G3 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635474&prj=684&rqi=AzfLcJnF52XhdLSyvdM5HYMUXr
GT1ELEC-91-002 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | UPS_J_2 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635468&prj=684&rqi=zkK38y3JgSouHdnVMP0yWDaXk7
GT1ELEC-92-003 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | UPS_K_2 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635471&prj=684&rqi=7HsN242iBzSlTZHOgzXbURaMXv
GT1ELEC-91-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | UPS_J_1 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635466&prj=684&rqi=KEDzUI17xCUQJxFSWRcY01MvZw
GT1ELEC-93-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | UPS_R2_1 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635472&prj=684&rqi=OSuOPSrnmddptHWx4aEeYClhiO
BT1MECH-73-001 | SV18-2 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-08-25 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1CRAH_J_15 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_J_15) L4 Unit is mapped to J_13 on the floor layout, and J_13 is mapped to J_15 on the floor layout. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635191&prj=684&rqi=fCdsrE3P8If08Rfq9Z9A4vapqr
BT1MECH-65-003 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-25 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Comms Issue/ Fault | DCOS | Mechanical â€“ Water | equipment | 1CRAH_G_13 | CRAH - Computer room air handler (Skid) |  |  | (All Skid CRAHs) L4 Writing SAT and DT setpoint from the HMI does not update at the BMS. If a new number is then written from the BMS, it overrides the HMI as usual. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635131&prj=684&rqi=nGfmh4qXKCcA0i2nr8bHeoAPXY
BT1MECH-65-001 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-08-21 04:00:00.000 +0400 | Owner | L4 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1CRAH_G_13 | CRAH - Computer room air handler (Skid) |  |  | (All Skid CRAH's) L4 Fan command to both supply fans is 1 signal. Separate supply fan commands for each fan exist on the BMS faceplate and 1 is always stuck at 0%. This prevents proper fan command mismatch alarming. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634681&prj=684&rqi=V9eM3Tkzu3dfjqCdfxaEouPYoF
GT1ELEC-346-002 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_G3) L3: MBB does not indicate position on UPS HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634553&prj=684&rqi=7W7z76bZ9B85WteR1vYUsSe6aL
GT1MECH-82-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L3 Trane FSR found Bellimo Valve to not be functioning correctly. Trane has contacted MPS and they will work on getting a replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634485&prj=684&rqi=UzGwEruB9aVUJnJ7tZzUfZYE6F
GT1MECH-76-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (HP-H-1) L3 Thermostat damaged during startup procedures, needs replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634443&prj=684&rqi=ZlmmBQwT33fc5mxPFGSv8UH122
GT1ELEC-379-001 | SV18-2 | AMER | Work Completed | P3 Low CX | chase.negich@veolia.com | 2026-08-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | (1UMDSB_G) L3: Kirk key interlock does not provide indication on UPS or UMDSB.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634554&prj=684&rqi=PjFgX0zsRtTASIScjey4nVUsig
GT1ELEC-346-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_G3) L3: Battery breaker status on HMI is backwards. When breaker is shut, it indicates open.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634552&prj=684&rqi=H3kytySAOOmOWD1ike9UcFduLB
GT1MECH-69-001 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“Air | equipment | 1EF_G_1 | EF - Exhaust Fan |  |  | (Skid Leak Detection) L3 Etech has found a bad leak detection cable section on the DMARK wall. New replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634236&prj=684&rqi=IIPwpUcIaXrYzHZDshHhIUH2U2
YT1MECH-90-004 | SV18-2 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-08-19 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (HP-R2-1) L2B Phenolic circuit labeling (circled in red) is incorrect (labels are swapped between HP-R2-1 and HP-R2-2). To clarify, east-most HPs are HP-X-1 and west-most units are HP-X-2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634293&prj=684&rqi=c3VsMIbw2Zqp5MdqNoEwWkme8W
YT1ELEC-358-002 | SV18-2 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-08-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_K3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_K3 L2B:Â Torn door filter on cabinet panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634144&prj=684&rqi=EGqKbVtmTKLfENL5DlxQ1BVY60
BT1ELEC-3-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1GEN_J | GENL - Generator (LV) |  |  | 1GEN_J L4 Failed speed indication in 1GEN_J during testing. Warning came in early into testing labeled '689 ECM.C3 Crankshaft Speed Error'. This did not stop the test from completing but needs to be resolved. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634005&prj=684&rqi=CBtz4qZS90UOaUivmLgiyOH8RR
BT1ELEC-4-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1GEN_K | GENL - Generator (LV) |  |  | 1GEN_K L4 Failed pneumericator motherboard for 1GEN_K. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634012&prj=684&rqi=mfcTDhXLg284ei0Rt1oAOSADo5
GT1MECH-75-001 | SV18-2 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-08-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (HP_G_2) L3 Thermostat control wiring insulation is damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633996&prj=684&rqi=okFZfVyEhI2FyHOubMlh0YRQc1
YT1ELEC-349-002 | SV18-2 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G3 L2B Torn filter on UPS enclosure door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633730&prj=684&rqi=Xso0dZ30dmJNEBFxBqkHyXTyS4
GT1MECH-83-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (1HP_R2_2) L3 Trane FSR found Bellimo Valve to not be functioning correctly. Trane has contacted MPS and they will work on getting a replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633727&prj=684&rqi=41AXFbHETvZ7OU9vPObzYbjdDU
GT1MECH-76-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (1HP_H_1) L3 BMS skid floor layout labelled incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633456&prj=684&rqi=b9ZUcdAoFK2vxJdcXO5lfyXcKy
GT1MECH-78-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (1HP_J_1) L3 BMS skid floor layout labelled incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633457&prj=684&rqi=5anZNV4EMg62orfVz9rvqsPuXl
YT1MECH-80-005 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_K_1 | EF - Exhaust Fan |  |  | (Skid K leak detection) L3 CAT6 cable is too short to be terminated at the leak detection panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633532&prj=684&rqi=64oVLtrsV6IbfJemLhIvNhVyS0
GT1MECH-80-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (1HP_K_1) L3 BMS skid floor layout labelled incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633458&prj=684&rqi=0cgaXSoNoyR6HCWdBd1gSlWYq5
GT1MECH-82-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L3 BMS skid floor layout labelled incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633460&prj=684&rqi=UKTn1Y8Dv8uiWPxAVxNXz4ncxx
GT1MECH-74-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (1HP_G_1) L3 HP_1 and HP_2 objects are flipped on the floor layout at the BMS. See attached electrical bulletin #2 for correct asset tags. Typical for all skids. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633453&prj=684&rqi=RI2mksZnCpyLosUO3TxVay9jlp
RT1ELEC-247-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1RPP_K1_1_1 | RPP - Remote Power Panel |  |  | 1RPP_K1_1_1 L2A FST cannabalized a set of screws for one lug kit inside of this RPP. Creating this case to track the replacement of these screws and the lug cover. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633384&prj=684&rqi=DzIA1CZScpYqHGNxOYl9VrD3BM
GT1ELEC-90-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | 1MSB_H L3 1MSB_H Breaker Q15 control panel has a failed motherboard that requires a replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633267&prj=684&rqi=fxlqk2uyy2NgrIIs1deeCzj6PT
RT1MECH-85-005 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (1HP_H_2) L2A Heat pump missing thermostat. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633268&prj=684&rqi=qsjJqThaqVipf52kWcnFPmn87y
GT1ELEC-92-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | 1MSB_K Tracking Purposes FST has cannabalized the Phase Sequence Relay off of 1MSB_K for installation on 1MSB_F. Please provide an update on the schedule for delivery and replacement in 1MSB_K | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633278&prj=684&rqi=196vtjh8jYjKgz2K40t5OyLpPh
RT1ELEC-190-001 | SV18-2 | AMER | Open | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-08-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1RPP_E1_2_5 | RPP - Remote Power Panel |  |  | (1RPP_E1_2_5) The cover is incorrectly sized by the manufacturer resulting in the exposure of the breakers for the branch circuits 69 and 71. The serial number of the panel is F1251024EQX00647. This issue was entered originally as issue #1048 in SV18-1 before the clarification that the 1st floor 1RPPs are part of Veolia's scope. Anord Mardix Group (AMG) is already aware of this issue and needs to provide estimated date of when the replacement cover can arrive to SV18. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633137&prj=684&rqi=KlTj3gJVpF3mzbRGgD5TpbTeQ0
GT1MECH-43-001 | SV18-2 | AMER | Closed | P1 High CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (1CRAH_K_02) L3 Fan 8 replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633075&prj=684&rqi=sp5z3EemubmZO4b9bDNcoBjDro
GT1MECH-45-001 | SV18-2 | AMER | Closed | P1 High CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_04 | CRAH - Computer room air handler |  |  | (1CRAH_K_04) L3 Fan 1 replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633078&prj=684&rqi=k5OQPL76hSV6K4FxuXkMPg8d9U
GT1MECH-44-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_03 | CRAH - Computer room air handler |  |  | (1CRAH_K_03) L3 Unable to put the unit into manual mode | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633076&prj=684&rqi=SdSH0q0UUK7nNczhwJ7tfq9J3E
GT1MECH-24-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (1CRAH_G_07) L3 Constant loss of airflow alarm present on the unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633071&prj=684&rqi=fyUW2rcarLl2fcxPz1NMJsrl93
GT1MECH-27-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_10 | CRAH - Computer room air handler |  |  | (1CRAH_G_10) L3 Constant motor overload/EC fan fault alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633072&prj=684&rqi=xfUg4TnmxAECf9GXJyDQC54G4r
GT1MECH-28-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_11 | CRAH - Computer room air handler |  |  | (1CRAH_G_11) L3 Constant loss of airflow alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633073&prj=684&rqi=E0MjL3ZtglQfmx1cgKQVReUbcL
BT1MECH-1-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | TRN - Trane | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1ACC_J_09 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_J_09) L4 DC/DC converter for compressor 2 communications failed on R2_06 during 4 hour HLT. Part cannibalized from J_09. Replacement delivered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633088&prj=684&rqi=uXywWusOc4PJYPv73aUhVWuGRG
GT1MECH-46-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_05 | CRAH - Computer room air handler |  |  | (1CRAH_K_05) L3 Unit unable to be put into manual mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633080&prj=684&rqi=iq13dpIYK8rDKKnuDaljJ8mIwW
GT1ELEC-370-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | chase.negich@veolia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_R2 | GENL - Generator (LV) |  |  | 1Gen_R2 (L3): E-STOP did not open Gen output breaker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632951&prj=684&rqi=JoPhMpnRRTUyUCn5bcyzMUPwcJ
GT1MECH-85-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-05 04:00:00.000 +0400 | TRN - Trane | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1ACC_R2_05 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_R2_05) L3 Compressor 2 communication module was found to be faulty. Trane had a new one on hand and replaced. Adding as a closed issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632327&prj=684&rqi=gPl3BubQcNcHGXVxrN8bLn1q2j
YT1MECH-31-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-04 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2B | Incomplete Connections | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_06 | CRAH - Computer room air handler |  |  | (1CRAH_G_06) L2B Ground wire disconnected. Re-crimping needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632217&prj=684&rqi=gFvrhOmKNGD6neMIL5bBGk7fZ0
GT1MECH-84-001 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-08-04 04:00:00.000 +0400 | TRN - Trane | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1ACC_J_09 | ACC - Chiller â€“ Air Cooled |  |  | (ACC-J-09) L3 During startup, CHWP VFD disconnect failed. Need new part. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632142&prj=684&rqi=MMTiTnctayQGXHU7ZHE4Xpp1k2
GT1MECH-87-001 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-08-04 04:00:00.000 +0400 | TRN - Trane | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1ACC_J_10 | ACC - Chiller â€“ Air Cooled |  |  | (ACC-J-10) L3 CHW leak was found on return side of chiller piping, right before CHW pump. Leak has been narrowed down to the gasket betweeen Victaulic T fitting and black coupling on CHW pipe, gasket to be replaced before running pump. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632144&prj=684&rqi=llJd52GlNuAxpyxEwA76hLW9Ci
YT1ELEC-95-006 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-07-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | 1MSB_K L2B Section 02A had factory installed ferrules from MPS that were too large. The ferrules installed were for gauge 14 wires but the wires are gauge 16, so the wires were pulling out of their pins with little force. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631866&prj=684&rqi=KEzWRqdwi70arANP3aEX8wrq42
YT1ELEC-72-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_1_2 | LIBATT - UPS Battery |  |  | 1BATT_R2_1_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631646&prj=684&rqi=2JoWIJRp1Oz9GMGlFrQ4nLfGqf
YT1ELEC-63-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K1_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K1_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631522&prj=684&rqi=f7hwGMxc0JZV97UuafrJCuGq5D
YT1ELEC-76-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_2_2 | LIBATT - UPS Battery |  |  | 1BATT_R2_2_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631654&prj=684&rqi=4A7vBp9QPLP26fMQf7W4yTS4kF
YT1ELEC-65-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K1_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K1_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631636&prj=684&rqi=B39EPTwNQ9EUhE00MrV4uDTRX5
GI-005 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | Common to all RPPs RPP incoming termination points labeled CBA vice ABC. RPP subfeeds labeled CBA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631642&prj=684&rqi=sSglawavAltlVf4dUGEuZJETSv
YT1ELEC-62-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K1_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K1_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631517&prj=684&rqi=lIsRprM9fyVzZbFqsonKxE3Sdn
YT1ELEC-79-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_R2_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_R2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631657&prj=684&rqi=NeOjCHMmwBCZO5xQZe7QdOKFxb
YT1ELEC-75-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_2_1 | LIBATT - UPS Battery |  |  | 1BATT_R2_2_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631650&prj=684&rqi=IGLmhrrkD3jEjKBoi0Bs4QVwdt
YT1ELEC-60-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J2_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J2_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631515&prj=684&rqi=wgkIAKxjpMKr7dBEe6JZxk9X8D
YT1ELEC-78-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_2_4 | LIBATT - UPS Battery |  |  | 1BATT_R2_2_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631656&prj=684&rqi=CpaGAYFLJywc2rSw7tD4aBYNxl
YT1ELEC-54-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J1_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J1_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631509&prj=684&rqi=Inpuzl3ydGOLNKIdsLTXSQoxlM
BT1MECH-8-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | ethan.hang@veolia.com | 2026-07-30 04:00:00.000 +0400 | TRN - Trane | L4 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1ACC_H_13 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_H_13) L4 For tracking purposes, during a fast restart test while the chiller was at 100% capacity, the CB218 relay intermittently failed. Trane is working on sending a replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631542&prj=684&rqi=MJfCwRtOzPEot2AJxlYzEIWI9n
YT1ELEC-55-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J1_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J1_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631510&prj=684&rqi=xQoKU81RxhrU4juwv7icuLAjWV
YT1ELEC-53-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J1_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J1_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631453&prj=684&rqi=kZc4f1PQ5hbrlFwdq0ipeNEbWk
GT1MECH-12-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-30 04:00:00.000 +0400 | TRN - Trane | L3 | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CHWP_J_09 | CHWP - Chilled water pump |  |  | (1CHWP_J_09) L3 During start up, Trane found that the CHWP disconnect had failed. Trane is working on shipping a replacement part. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631547&prj=684&rqi=i3d83IUzuR70TV94FxgnuibiPu
YT1ELEC-70-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631643&prj=684&rqi=p4phbWIMIKmKnT1lAFY6j6VaVD
YT1ELEC-68-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K2_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631639&prj=684&rqi=axyUPN8WViWYtjS3WZPTqJqS7F
YT1ELEC-58-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J2_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J2_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631513&prj=684&rqi=qPhYICwmqFFlhK5lSN1RPkYO2t
YT1ELEC-69-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K2_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K2_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631641&prj=684&rqi=Zd5xsOqZmW7oNNdNhOvvm5zhNx
YT1ELEC-64-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K1_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K1_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631632&prj=684&rqi=kYKOOlQSBiiFrrx6jcTU5lXdM5
YT1ELEC-56-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J1_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J1_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631511&prj=684&rqi=BoJmttOj3OJsC6vvVyOEEmlNhu
YT1ELEC-73-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_1_3 | LIBATT - UPS Battery |  |  | 1BATT_R2_1_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631648&prj=684&rqi=H0e4PxjN29D93dzbD3NnxS601x
YT1ELEC-57-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J2_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J2_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631512&prj=684&rqi=mNRItTnwIIk57eS8LGEowaq3bb
YT1ELEC-77-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_2_3 | LIBATT - UPS Battery |  |  | 1BATT_R2_2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631655&prj=684&rqi=9z3b8utbt8xUYGGYLXHcVi6mDg
YT1ELEC-67-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K2_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K2_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631638&prj=684&rqi=fJAa1ctuNxdsbACpQ4CkpuTAOk
YT1ELEC-59-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J2_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631514&prj=684&rqi=ESrZkTQxiLstnxuPc4vMPZEKxP
YT1ELEC-66-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K2_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K2_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631637&prj=684&rqi=OefQfzzZ2aNBU5nzF0mYkVexmK
YT1ELEC-74-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_1_4 | LIBATT - UPS Battery |  |  | 1BATT_R2_1_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631649&prj=684&rqi=ED3IMBar9myUA1nMhH8TVNAoYk
YT1ELEC-61-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631516&prj=684&rqi=NrGotqkzpv4FTsMnjXWG6jdU5X
YT1ELEC-71-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_1_1 | LIBATT - UPS Battery |  |  | 1BATT_R2_1_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631645&prj=684&rqi=jz3AWWYaMI4IJ2DjcfXCwKtJJP
YT1ELEC-347-003 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_G_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G1 L2B Several components have been cannabalized for repair on Phase-1 SKIDs by the Delta team. Equipment that was taken is as follows: 1 M-board 2 P-boards 1 H-board 2 Fans | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631592&prj=684&rqi=YjOoyHc2KCYEbYDip0EJsVt3dE
YT1ELEC-52-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631327&prj=684&rqi=Q0ulmJPi4Ogv4wK0Yjj9OpW62N
YT1ELEC-383-001 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_H3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_H3 UPS_H_3 MBB breaker Q03 is missing its second set of aux contacts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631311&prj=684&rqi=pwoaoL4x5XNOB5AhEsB39xTVvP
YT1ELEC-48-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H2_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H2_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631320&prj=684&rqi=fWlAH2ydKD7tn2a2I82EcZCSdz
YT1ELEC-35-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G1_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G1_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631298&prj=684&rqi=g8rpTEDl2hZmw6gb0TC6lkbKcw
YT1ELEC-95-004 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2B MSB HMI has 4 key-actuated selector switches, and only 3 are required. Per Hanley submittal drawing #HSU-5478FO-ELC-DWG02, this switch should be removed and blanked off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631208&prj=684&rqi=dswagLFS6gUKgwjrUNePl9KiMI
YT1ELEC-95-005 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2B The key-actuated selector switches on the MSB HMI lock the keys when not in the center position. The selector switches should not lock the keys in any position. Sheet 2 of Hanley Submittal Drawing #HSU-5478FO-ELC-DWG02 specifies this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631209&prj=684&rqi=oawZOU8sf2K09bgOgy90GAZ1OR
YT1ELEC-356-001 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_K_1 | UPS - Uninterrupted Power Supply |  |  | Exhaust fan control wire from UPS_K_1/2/3 not correctly landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631290&prj=684&rqi=cxkHgqbj36UpplBDFx1k2dqClJ
GT1ELEC-367-002 | SV18-2 | AMER | Ready for Verification | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Comms Issue/ Fault | DCOS | Electrical â€“ LV | equipment | 1GEN_H | GENL - Generator (LV) |  |  | 1GEN_H L4 P2P Testing - Identified discrepancy with the GCB breaker status sending inverted status signals to the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631267&prj=684&rqi=6Jb9MVZXmAmNEOhTc0s0eDwkLD
YT1ELEC-50-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H2_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631322&prj=684&rqi=tZyARGTMzEDels1kUj3RIQxFCQ
YT1ELEC-356-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_K_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_K1 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631289&prj=684&rqi=lGTRKHuAM68fZJrgeTroZoHgXQ
YT1ELEC-45-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H1_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H1_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631317&prj=684&rqi=e0GZf1bdItaG9mxYPQdsvejgXT
YT1ELEC-43-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631307&prj=684&rqi=ssYZCOcFizURepqULqTn9ngTVO
YT1ELEC-36-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G1_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G1_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631299&prj=684&rqi=XWDUNYpBcIgs9aBGBELhA1PE7j
YT1ELEC-348-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_G_2 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G2 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631282&prj=684&rqi=bN05vQs3ZG9YxTnmXsA0qmhf2I
YT1ELEC-385-002 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_K3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_K3 UPS_K_3 MBB breaker Q03 is missing its second set of aux contacts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631313&prj=684&rqi=cLnSUKCP3k5VPBD61rV0yhrgVg
YT1ELEC-42-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G2_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G2_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631306&prj=684&rqi=rHTHkqliXwmY7rhsjQ8LQCZ5AP
YT1ELEC-38-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G1_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G1_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631302&prj=684&rqi=Ux2Z8z7LhB91eV46TO6wj2TS69
YT1ELEC-354-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_J_2 | UPS - Uninterrupted Power Supply |  |  | 1UPS_J2 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631287&prj=684&rqi=ZHvQfd4TnxxnUbqZU0nKH9jxPx
YT1ELEC-39-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G2_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G2_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631303&prj=684&rqi=R55it8YhHQLHnBUZd0bW61rrkO
YT1ELEC-382-002 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_G3 UPS_G_3 MBB breaker Q03 is missing its second set of aux contacts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631310&prj=684&rqi=navyz00itJgvduf7yihiaH1gBt
YT1ELEC-41-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G2_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631305&prj=684&rqi=ilf0uYnQwC5lFT0ohNoZzrMSgd
YT1ELEC-347-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_G_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G1 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631278&prj=684&rqi=3IhjRyhOCikxZKobSJYNaXEgu7
YT1ELEC-347-002 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_G_1 | UPS - Uninterrupted Power Supply |  |  | Exhaust fan control wire from UPS_G_1/2/3 not correctly landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631281&prj=684&rqi=5C4cP8itNPt9Eedhj9hzLoPajX
YT1ELEC-350-002 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_H_1 | UPS - Uninterrupted Power Supply |  |  | Exhaust fan control wire from UPS_H_1/2/3 not correctly landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631286&prj=684&rqi=540MBVFDSOvpobPPc4bRHo0hxD
YT1ELEC-350-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_H_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_H1 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631283&prj=684&rqi=brA0tqtt6DFZWeP2FFF8PgQbj7
YT1ELEC-359-001 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_1 | UPS - Uninterrupted Power Supply |  |  | Exhaust fan control wire from UPS_R_1/2/3 not correctly landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631295&prj=684&rqi=oemOy7yua8iY4WoQjz4UWfLNrM
YT1ELEC-359-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_R2_1 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631296&prj=684&rqi=wvlyZQmOdBV9VlO0ulrrwYMEdx
YT1ELEC-384-001 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_J3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_J3 UPS_J_3 MBB breaker Q03 is missing its second set of aux contacts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631312&prj=684&rqi=mCuxhEu8OpXBUgH6Swchf9SnaU
YT1ELEC-151-001 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1PNL_R2_1_HP | DB - Distribution Boards |  |  | 1PNL_R2_1_HP 1CRAH_R2_13 (SKID CRAH_H_1) landed at 7,9,11 vice 1,3,5 1CRAH_R2_15 (SKID CRAH_H_2) landed at 1,3,5 vice 7,9,11 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631300&prj=684&rqi=hDBDIhRsd6A85pRRRIrHBwzsKQ
GT1ELEC-366-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Comms Issue/ Fault | DCOS | Electrical â€“ LV | equipment | 1GEN_G | GENL - Generator (LV) |  |  | 1GEN_G L4 P2P Testing - Identified discrepancy with the GCB breaker status sending inverted status signals to the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631260&prj=684&rqi=tRdfbgt9SyFKhr59TMHBytXZ4h
RT1ELEC-154-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Design Professional | L2A | Design correction needed | Design | Electrical â€“ LV | equipment | 1PNL_R2_2_H2 | DB - Distribution Boards |  |  | 1PNL_R2_2_H2 L2B SCCS lists all breakers as having fixed trip setpoints at 50A, however the EATON breakers installed, which are the correct breakers, have variable trip settings that need to be identified and adjusted on the breaker to ensure proper coordination and protection. The SCCS will need to be updated to reflect this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631235&prj=684&rqi=Oz5k1Jzu8h8LQQPc9OzIFdCxHT
YT1ELEC-351-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_H_2 | UPS - Uninterrupted Power Supply |  |  | 1UPS_H2 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631284&prj=684&rqi=aPy1UOe6vZHyrn1MkUi7LxNkm9
YT1ELEC-40-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G2_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G2_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631304&prj=684&rqi=JEgpuonVVb6Wqm94XGF1Cv4Ptj
YT1ELEC-353-002 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_J_1 | UPS - Uninterrupted Power Supply |  |  | Exhaust fan control wire from UPS_J_1/2/3 not correctly landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631288&prj=684&rqi=JfGk1qOhTd0OfYAJXCTUZW5MOq
YT1ELEC-44-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H1_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H1_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631309&prj=684&rqi=IPZSnR5nSBmp9CHxh6WskbQe8I
YT1ELEC-47-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H1_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H1_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631319&prj=684&rqi=f6deOwUiVP7kZudgLC3PPi1S72
RT1ELEC-153-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Design Professional | L2A | Design correction needed | Design | Electrical â€“ LV | equipment | 1PNL_R2_2_H1 | DB - Distribution Boards |  |  | 1PNL_R2_2_H1 L2B SCCS lists all breakers as having fixed trip setpoints at 50A, however the EATON breakers installed, which are the correct breakers, have variable trip settings that need to be identified and adjusted on the breaker to ensure proper coordination and protection. The SCCS will need to be updated to reflect this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631222&prj=684&rqi=jRW5SbcIXoOcKUa05DrAuiOwkB
RT1ELEC-155-002 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Design Professional | L2A | Design correction needed | Design | Electrical â€“ LV | equipment | 1PNL_R2_2_H3 | DB - Distribution Boards |  |  | 1PNL_R2_2_H3 L2B SCCS lists all breakers as having fixed trip setpoints at 50A, however the EATON breakers installed, which are the correct breakers, have variable trip settings that need to be identified and adjusted on the breaker to ensure proper coordination and protection. The SCCS will need to be updated to reflect this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631236&prj=684&rqi=x2wLCos67nKuvMAX2x57vUae7I
YT1ELEC-360-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_2 | UPS - Uninterrupted Power Supply |  |  | 1UPS_R2_2 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631297&prj=684&rqi=VMzt3bK29iBluDmu4ceDaZsH9n
YT1ELEC-49-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H2_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H2_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631321&prj=684&rqi=8TG4na1ZoxXfSGtZGjAtrlPZWI
YT1ELEC-353-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_J_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_J1 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631285&prj=684&rqi=5MioxoOqPRCXJgfKpLMnFyvFmE
YT1ELEC-357-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_K_2 | UPS - Uninterrupted Power Supply |  |  | 1UPS_K2 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631294&prj=684&rqi=QMGiidJoLLmFWbn1VmTbjvGe1J
YT1ELEC-46-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H1_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H1_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631318&prj=684&rqi=DMDTNPRwf16XF7O04vQ1hjmqzG
YT1ELEC-37-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G1_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G1_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631301&prj=684&rqi=nsoeGwExjm5RujXrVJLuYP2AEj
YT1ELEC-51-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H2_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H2_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631326&prj=684&rqi=NWwXGoov5u62QGaW2eADlvRnzU
YT1ELEC-386-002 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_R2_3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_R2_3 UPS_R2_3 MBB breaker Q03 is missing its second set of aux contacts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631314&prj=684&rqi=TRtNHs1OAuGMmjTlwOfjyCzwR1
YT1ELEC-142-001 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1PNL_GEN_G | DB - Distribution Boards |  |  | 1PNL_GEN_G TRIP/CLOSE switch installed on all phase 2 generator panels. Close feature not operable IAW design. Switch not installed on phase 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631094&prj=684&rqi=owgd3XkVAWUaOYEOseM6xICMm0
YT1ELEC-143-001 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1PNL_GEN_H | DB - Distribution Boards |  |  | 1PNL_GEN_H TRIP/CLOSE switch installed on all phase 2 generator panels. Close feature not operable IAW design. Switch not installed on phase 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631095&prj=684&rqi=SVTjnnGrdkTDUiUlD7W26iLhpA
YT1ELEC-147-001 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1PNL_GEN_R2 | DB - Distribution Boards |  |  | 1PNL_GEN_R2 TRIP/CLOSE switch installed on all phase 2 generator panels. Close feature not operable IAW design. Switch not installed on phase 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631098&prj=684&rqi=qIQN2OcdLQ1jasKRiRrsIDTJVb
YT1ELEC-149-001 | SV18-2 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1PNL_J_HP | DB - Distribution Boards |  |  | (1PNL_J_HP) L2B: Panel schedule does not match the wire tag. Verified that wire tag is correct.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631100&prj=684&rqi=0Hg3xTMYEi9vpYs4f3mRwaOEo0
YT1ELEC-145-001 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1PNL_GEN_K | DB - Distribution Boards |  |  | 1PNL_GEN_K TRIP/CLOSE switch installed on all phase 2 generator panels. Close feature not operable IAW design. Switch not installed on phase 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631097&prj=684&rqi=WTZEgY8T3TEdTdcebVUdGzhiqG
YT1ELEC-144-001 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1PNL_GEN_J | DB - Distribution Boards |  |  | 1PNL_GEN_J TRIP/CLOSE switch installed on all phase 2 generator panels. Close feature not operable IAW design. Switch not installed on phase 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631096&prj=684&rqi=dVeXztHEDNtzPMBcy9QwCmRQL7
YT1ELEC-385-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_K3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_K3 L2B K3 Kirk Key (64400) is missing for this UMDSB. Hanley has spare key and will expedite a shipment to site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630750&prj=684&rqi=vZGI0PmP89XqFMwnyxg6vBpedC
GI-004 | SV18-2 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design | [6 empty] | Various issue and in consistantcies found in rev 2 of SCCS: UNPL and PNL breakers listed as fixed. Breakers are adjustable. ABB breakers do not allow for S and Int setpoint to be the same value. S must be smaller than INT | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630773&prj=684&rqi=qgR31BkWbag7udhqBZYxmRcxjH
YT1ELEC-386-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_R2_3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_R2_3 L2B K3 Kirk Key (64400) is missing for this UMDSB. Hanley has spare key and will expedite a shipment to site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630751&prj=684&rqi=yiu4AUbTs92patHVieTPXm18Qe
YT1ELEC-93-004 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | 1MSB_H HMI Label plate does not show all switch positions listed in the submittal. Switch label should show all three positions (Auto/Auto, Auto/Man, Man/Man). See attach example. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630760&prj=684&rqi=qMW8DQ6G7OBqIgZkBW7ED4Gzcp
YT1ELEC-92-002 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | 1MSB_G HMI Label plate does not show all switch positions listed in the submittal. Switch label should show all three positions (Auto/Auto, Auto/Man, Man/Man). See attach example. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630761&prj=684&rqi=wevxSDDGsq9UCKrbxpPltURXaH
YT1ELEC-95-003 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | 1MSB_K HMI Label plate does not show all switch positions listed in the submittal. Switch label should show all three positions (Auto/Auto, Auto/Man, Man/Man). See attach example. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630757&prj=684&rqi=wdEAiGETkf8SAvIReqIQOn6HR7
YT1ELEC-94-002 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | 1MSB_J HMI Label plate does not show all switch positions listed in the submittal. Switch label should show all three positions (Auto/Auto, Auto/Man, Man/Man). See attach example. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630758&prj=684&rqi=UPZaFk530uDZ2qKow1AXbQ3Q4a
YT1ELEC-96-004 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | 1MSB_R2 HMI Label plate does not show all switch positions listed in the submittal. Switch label should show all three positions (Auto/Auto, Auto/Man, Man/Man). See attach example. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630754&prj=684&rqi=oRkckoRfKkwDqVpdMGt3tfXxup
GT1ELEC-145-001 | SV18-2 | AMER | Open | P2 Medium CX | ian.tsurumoto@veolia.com | 2026-07-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1PNL_H_HP | DB - Distribution Boards |  |  | 1PNL_H_HP 1CRAH_H_13 (SKID CRAH_H_1) landed at 2,4,6 vice 1,3,5 1CRAH_H_14 (SKID CRAH_H_2) landed at 1,3,5 vice 2,4,6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630624&prj=684&rqi=h8Iucb80KqG3LDp2I83a5csqbi
YT1MECH-40-001 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-07-22 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2B | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_03 | CRAH - Computer room air handler |  |  | (1CRAH_H_03) L2B Source 2 disconnect has been broken off. Replacement needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630461&prj=684&rqi=0CuwLROAua1TMB07DmE57IUxA1
YT1ELEC-88-002 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MDSB_J | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_J) L2BÂ Panel grounding strap not installed in top hat.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630480&prj=684&rqi=3X5PTua8NrsRlErakyG0RupiMz
YT1MECH-66-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_14 | CRAH - Computer room air handler (Skid) |  |  | (CRAH-H-14) L2B Schrader valve core missing from vent point top left of coil | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630391&prj=684&rqi=UnfqqQQQ0RttfH1g51Tr2Ag11X
YT1ELEC-96-003 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-22 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB_R2) L2B Failed comm cable in MSB_R2 that connects to PQM3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630433&prj=684&rqi=fY1umKaQal1UVBKmjUTkxWffp2
YT1ELEC-86-004 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_G) L2B Ground connection to a panel cover was not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630175&prj=684&rqi=7tet4muUZVxsAQSMZ8lZCnMi62
YT1ELEC-86-006 | SV18-2 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | MDSB_G panel ground inside top hat found disconnected during final inspection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630622&prj=684&rqi=umLyiZGiZOScYEpwkJs27egUy4
YT1ELEC-86-005 | SV18-2 | AMER | Closed | P2 Medium CX | ian.tsurumoto@veolia.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | washer found the on incoming bus on MDSB_G | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630621&prj=684&rqi=M8cZTf28zd1uiVTVZTn04tQovB
YT1ELEC-88-001 | SV18-2 | AMER | Open | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MDSB_J | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_J L2B Breaker 1UPS_J_3-RIB (Q07) does not have wires pulled or installed on aux contacts for UPS RIB breaker status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629470&prj=684&rqi=YcU7Imeb8rhiswsVNELvmwxp3H
YT1ELEC-95-002 | SV18-2 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | 1MSB_K Level 2B MSB drawings do not have 240VAC control power called out on drawings or physical terminals in Section 02A in MSB for 1BATT_K_3. (Note: Typical of all MSBs.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629464&prj=684&rqi=dL5TEb7aVptElLdzXKgoB3W9q5
YT1ELEC-96-001 | SV18-2 | AMER | Work Completed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | 1MSB_R2 Level 2B Please see the images below. Need to confirm control wiring (PLC Jumpers) for 1MSB_R2 - Q12 (MBB), Q13 (LBB1), Q14 (IOB1), Q15 (LBB2), Q16 (IOB2). Currently no wiring installation is present in section 10A of MSB. Serial Number: HSUDKEX-6027DV-001 Drawing No: HSU-6027DV-ELC-DWG01 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629458&prj=684&rqi=s4Byp60UXbKqo0dtkwPZvOP9jv
YT1ELEC-93-003 | SV18-2 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | 1MSB_H Level 2B MSB drawings do not have 240VAC control power called out on drawings or physical terminals in Section 02A in MSB for 1BATT_H_3. (Note: Typical of all MSBs.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629462&prj=684&rqi=NN44ne3vCJvHD2ILMdQi2kRCiS
YT1ELEC-86-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_G (L2B) The lug kits for breaker Q03 that feed 1TX_G_R1 are the wrong size and need to be replaced. This work has been completed by Hanley and verified by Veolia. Adding this issue item as a closed case. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629416&prj=684&rqi=8Y7BA9FS5WS0WZnWdOjvN82U6t
YT1ELEC-86-003 | SV18-2 | AMER | Open | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_G L2B Breaker 1UPS_G_3-RIB (Q07) does not have wires pulled or installed on aux contacts for UPS RIB breaker status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629468&prj=684&rqi=JcRy1u2KSRa7aHgJEE7UUqEydV
YT1ELEC-87-002 | SV18-2 | AMER | Open | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MDSB_H | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_H L2B Breaker 1UPS_H_3-RIB (Q07) does not have wires pulled or installed on aux contacts for UPS RIB breaker status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629469&prj=684&rqi=gyR7AGKKQZWtS5PYZZA1PlAoHw
YT1ELEC-89-001 | SV18-2 | AMER | Open | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MDSB_K | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_K L2B Breaker 1UPS_J_3-RIB (Q07) does not have wires pulled or installed on aux contacts for UPS RIB breaker status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629471&prj=684&rqi=kBZ03bjdVzBCu3odwzaTCqJMdx
YT1ELEC-96-002 | SV18-2 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | 1MSB_R2 Level 2B MSB drawings do not have 240VAC control power called out on drawings or physical terminals in Section 02A in MSB for 1BATT_R2_3. (Note: Typical of all MSBs.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629465&prj=684&rqi=UsPD3iy08sQlK1A2kXcTV0y0Ud
YT1ELEC-94-001 | SV18-2 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | 1MSB_J Level 2B MSB drawings do not have 240VAC control power called out on drawings or physical terminals in Section 02A in MSB for 1BATT_J_3. (Note: Typical of all MSBs.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629463&prj=684&rqi=yFTW2WW7dYGhLOn6Occd8GxMyf
YT1ELEC-90-002 | SV18-2 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design | Electrical â€“ LV | equipment | 1MDSB_R2_1 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_R2_1 Level 2B Aux contacts for breaker status on 1UPS_R2_3-RIB (Q07) are not installed. Aux contacts are installed on XQ10 which is a SPARE. Submittals will need to be updated to reflect aux contacts. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629467&prj=684&rqi=IDorpsCiUz2eaU57elfwgRhBpp
YT1ELEC-92-001 | SV18-2 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | 1MSB_G Level 2B MSB drawings do not have 240VAC control power called out on drawings or physical terminals in Section 02A in MSB for 1BATT_G_3. (Note: Typical of all MSBs.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629459&prj=684&rqi=1SBloT5ob25K2an4B5pQSejYJp
YT1MECH-86-003 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-15 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (HP-J-1) L2B Overhead junction box has an unfinished splice that should be a continuous run per Equinix electrical design. Please run a new line from PNL-R2-2-H-2 with no splice. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629433&prj=684&rqi=JOIEhNjuGYUBYRDZV8yRH8ME8K
YT1MECH-88-003 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-15 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (HP-K-1) L2B Overhead junction box has an unfinished splice that should be a continuous run per Equinix electrical design. Please run a new line from PNL-R2-2-H-1 with no splice. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629434&prj=684&rqi=GmDRShLuy8iC632dk9R6hhi3vp
YT1MECH-73-001 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_15 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_K_15) L2B The line side of both Source A and Source B breakers are missing phase separators. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629237&prj=684&rqi=zBexu1CCpmvghsFSuIBvKchZmd
YT1MECH-72-001 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_14 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_K_14) L2B The line side of both Source A and Source B breakers are missing phase separators. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629236&prj=684&rqi=WRGlBluSKp6oviRkAJvtzbTJ3f
YT1ELEC-9-002 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-14 04:00:00.000 +0400 | SCH - Schneider MV | L2B | Installation not complete | Commissioning | Electrical â€“ MV | equipment | 1RMU_R2 | RMU - Ring Main Unit |  |  | (1RMU_R2) L2B Missing nut insert for section 2 dead front panel.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629231&prj=684&rqi=vBsD0P6dxYTUGPKQlzVJ9RtjYW
YT1ELEC-90-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R2_1 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_R2_1 (L2B) Grounding bushing on top of 1MDSB_R2_1 is loose and needs to be tightened. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629235&prj=684&rqi=4Tlm1SIxoFXTECoGgM1iMrSVHB
YT1ELEC-87-001 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MDSB_H | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_H (L2B) Cable entry bushings into MDSB_H are not seated properly and need to be adjusted to sit correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629234&prj=684&rqi=fW3dQsQoM8JghKo02bFmrEpumC
YT1MECH-83-003 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | HP_G_12 L2B No torque marks in WSHP 20 in lb required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629043&prj=684&rqi=EfDYOfJ5USQItGcaSjc47FqGhe
YT1MECH-84-003 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (HP-H-1) L2B Overhead junction box splices 480V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629042&prj=684&rqi=GreTqj82jrxvPE7ykAAg1ssWWn
YT1MECH-77-003 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1EF_G_1 | EF - Exhaust Fan |  |  | (EF-G-1) L2B Overhead junction box splices 120V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629048&prj=684&rqi=hoYJlz5u9h6bBTYcHOT0nejYtV
YT1MECH-79-004 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_J_1 | EF - Exhaust Fan |  |  | 1EF_J_1 L2B Control wires are pulled from UPS_1 and UPS_2, but no control wires are pulled from UPS_3 to Exhaust Fan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629065&prj=684&rqi=NdfCuD1wisNNsoMgfvu01Jvbj9
YT1ELEC-355-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_J3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_J3 (L2B) Green plug adapter for the control power/comm cables inside of the cabinet does not exist and needs to be installed to allow for Rosendin to terminate connections on 1UPS_J3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629089&prj=684&rqi=HpSIQbonpt5aplQy5ISJfTilhh
YT1MECH-88-002 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | 1HP_K_1 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629054&prj=684&rqi=kmeREtYPCFJX9hStXDbv2pbyM3
YT1MECH-91-002 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | 1HP_R2_2 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629057&prj=684&rqi=p1rCFwmGluR9pbfNIagnfO9iWT
YT1ELEC-358-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_K3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_K3 (L2B) Green plug adapter for the control power/comm cables inside of the cabinet does not exist and needs to be installed to allow for Rosendin to terminate connections on 1UPS_K3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629090&prj=684&rqi=yAfZutu9pTpBlQBZRmpDDBEdaN
YT1MECH-78-003 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_H_1 | EF - Exhaust Fan |  |  | 1EF_H_1 L2B Control wires are pulled from UPS_1 and UPS_2, but no control wires are pulled from UPS_3 to Exhaust Fan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629064&prj=684&rqi=L4VmGOiGyZ2lLfbcpyMFsFnL9T
YT1MECH-81-003 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1EF_R2_1 | EF - Exhaust Fan |  |  | (EF-R2-1) L2B Overhead junction box splices 120V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629061&prj=684&rqi=n4N3YEWhPJKxcQqdHStsVnBJlu
GT1ELEC-367-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1GEN_H | GENL - Generator (LV) |  |  | 1GEN_H (L3) KW and PF indications on the GCB and HMI are negative for some values. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629028&prj=684&rqi=Il69xsqCWI0GVgxDoqYQukMTFF
YT1MECH-90-003 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | 1HP_R2_1 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629056&prj=684&rqi=yBezjkroiaU3oQswNFjIYpV5VE
YT1MECH-85-002 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | 1HP_H_2 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629047&prj=684&rqi=laFfhhQFrTeuyhi53MCSEuCBNK
YT1MECH-82-002 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | HP_G_1 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629033&prj=684&rqi=EkTn10GCeTMlVVh7iiBPXvnMDy
YT1MECH-80-004 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_K_1 | EF - Exhaust Fan |  |  | 1EF_K_1 L2B Control wires are pulled from UPS_1 and UPS_2, but no control wires are pulled from UPS_3 to Exhaust Fan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629067&prj=684&rqi=0Up63Xt1zPiZK5vCaezNHhILHH
YT1ELEC-93-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | 1MSB_H (L2B) The breaker rack in device for Q03 (LB Breaker) in 1MSB_H broke during routine testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629086&prj=684&rqi=bqw6gLTfy0RbYMLfRXE1OfpZyG
YT1MECH-79-003 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1EF_J_1 | EF - Exhaust Fan |  |  | (EF-J-1) L2B Overhead junction box splices 120V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629058&prj=684&rqi=X10exu1ZORfEsx74zp67Crz4dv
YT1MECH-89-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (HP-K-2) L2B Overhead junction box splices 480V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629045&prj=684&rqi=QnVCjiy622ANmjCgGoc54IwfG6
YT1ELEC-349-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G3 (L2B) Green plug adapter for the control power/comm cables inside of the cabinet does not exist and needs to be installed to allow for Rosendin to terminate connections on 1UPS_G3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629087&prj=684&rqi=1tGpSv6lNfnecYzMZ2AqJTV7Am
YT1MECH-81-004 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_R2_1 | EF - Exhaust Fan |  |  | 1EF_R2_1 L2B Control wires are pulled from UPS_1 and UPS_2, but no control wires are pulled from UPS_3 to Exhaust Fan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629068&prj=684&rqi=2buHxAOpubvntJ0TtJrCHu5sbz
YT1MECH-80-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1EF_K_1 | EF - Exhaust Fan |  |  | (EF-K-1) L2B Overhead junction box splices 120V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629060&prj=684&rqi=OSfW0Q8PENtmiUe1CkkLYxcHCy
YT1MECH-84-004 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | 1HP_H_1 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629046&prj=684&rqi=HrOwVqhMolJ9AqyPXZC82fqNPy
YT1MECH-82-003 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (HP-G-1) L2B Overhead junction box splices 480V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629044&prj=684&rqi=T8wi6AMHn1a8f2b8ZXlXkKm0I6
YT1MECH-89-003 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | 1HP_K_2 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629055&prj=684&rqi=voHUjjMSxRdkynVraVomDBkD5T
YT1ELEC-361-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_R2_3 (L2B) Green plug adapter for the control power/comm cables inside of the cabinet does not exist and needs to be installed to allow for Rosendin to terminate connections on 1UPS_R2_3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629091&prj=684&rqi=aDIusIh55XK1Bww25Ud6M8VH37
YT1MECH-77-004 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_G_1 | EF - Exhaust Fan |  |  | 1EF_G_1 L2B Control wires are pulled from UPS_1 and UPS_2, but no control wires are pulled from UPS_3 to Exhaust Fan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629062&prj=684&rqi=yXvNrFKCu9qvV8yHk6z0gfHHD4
YT1MECH-87-002 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | 1HP_J_2 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629051&prj=684&rqi=Z5kA8JiHd9N2XGvdb0elt3kqd8
YT1MECH-86-002 | SV18-2 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | 1HP_J_1 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629049&prj=684&rqi=RhaWs1lG92IFwbN19enXm944ow
YT1ELEC-352-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_H3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_H3 (L2B) Green plug adapter for the control power/comm cables inside of the cabinet does not exist and needs to be installed to allow for Rosendin to terminate connections on 1UPS_H3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629088&prj=684&rqi=E8WvGqwcOo6wTXn4YFm46h7A6d
YT1MECH-77-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Controls Contractor | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_G_1 | EF - Exhaust Fan |  |  | (Electrical Skid G) L2B Leak detection communication cable needs to be connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628751&prj=684&rqi=la1ikXw9QFs9MbHiRVayeR7tCr
YT1MECH-79-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Controls Contractor | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_J_1 | EF - Exhaust Fan |  |  | (Electrical Skid J) L2B Leak detection communication cable needs to be connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628753&prj=684&rqi=KChefsxjq3KjJutM6Y8OuJc72P
YT1MECH-78-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_H_1 | EF - Exhaust Fan |  |  | (Electrical Skid H) L2B UPS to Fan interconnection needs to be terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628745&prj=684&rqi=h7qX93Iwz9LqDsY43nfUME4oTv
YT1ELEC-382-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-10 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_G (L2B) Phase C lug for Breaker Q04 is stripped and needs to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628737&prj=684&rqi=6AwXiQ9nzgFl5eaIuWph85FQPG
YT1MECH-80-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Controls Contractor | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_K_1 | EF - Exhaust Fan |  |  | (Electrical Skid K) L2B Leak detection communication cable needs to be connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628754&prj=684&rqi=FrukbZ7wtUANEoFv1fg65SokIs
YT1MECH-79-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_J_1 | EF - Exhaust Fan |  |  | (Electrical Skid J) L2B UPS to Fan interconnection needs to be terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628746&prj=684&rqi=1Aa2qn9tPZPUmKl4a2bixyoZC4
YT1MECH-80-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_K_1 | EF - Exhaust Fan |  |  | (Electrical Skid K) L2B UPS to Fan interconnection needs to be terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628749&prj=684&rqi=oSX3JcSSENEeE55gbwpqkRtWRd
YT1MECH-81-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_R2_1 | EF - Exhaust Fan |  |  | (Electrical Skid R2) L2B UPS to Fan interconnection needs to be terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628750&prj=684&rqi=vl6C8VfTTJhAHGXq2FnnS4uYa9
YT1MECH-81-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Controls Contractor | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_R2_1 | EF - Exhaust Fan |  |  | (Electrical Skid R2) L2B Leak detection communication cable needs to be connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628755&prj=684&rqi=i23UCvVcfjANIqgiMwBozW0LQX
YT1MECH-77-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_G_1 | EF - Exhaust Fan |  |  | (Electrical Skid G) L2B UPS Fan interconnection needs to be terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628744&prj=684&rqi=VruaTgIhtOr6l8o4vfgt2kJLgL
YT1MECH-78-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Controls Contractor | L2B | Incomplete Connections | Commissioning | Mechanical â€“Air | equipment | 1EF_H_1 | EF - Exhaust Fan |  |  | (Electrical Skid H) L2B Leak detection communication cable needs to be connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628752&prj=684&rqi=PRu5wQiI5xxXTrx5frWr8vjnDV
YT1MECH-83-002 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (1HP_G_2) L2B Flex conduit connections are lose. Please connect and tighten. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628623&prj=684&rqi=1ZoQM0lj44zYfU48ZQpQ359Eh5
YT1MECH-84-002 | SV18-2 | AMER | Open | P2 Medium CX | ethan.hang@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (1HP_H_1) L2B Flex conduit connections are lose. Please connect and tighten. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628622&prj=684&rqi=IWpQyci9IkC8taB0FDSbIuwwxb
YT1MECH-90-002 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-09 04:00:00.000 +0400 | Electrical Contractor | L2B | Incomplete Connections | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L2B Flex conduit connections are lose. Please connect and tighten. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628621&prj=684&rqi=nGEgBZXx8f13f4mAZS7qLB6BWn
YT1MECH-87-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | (1HP_J_2) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628448&prj=684&rqi=fxS7F2bGTp0j2dgMbqidAskV8M
YT1MECH-91-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (1HP_R2_2) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628452&prj=684&rqi=h4NlPSr9s7ak5dMN2BlJS5gOBx
YT1MECH-86-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (1HP_J_1) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628447&prj=684&rqi=oZggx0MTe8UphJEQ57BN0d7g2P
YT1MECH-82-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (1HP_G_1) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628443&prj=684&rqi=mSDVa78Ve7jtdljycQUhj0bkp6
YT1MECH-84-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (1HP_H_1) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628445&prj=684&rqi=rwOG3vR7V3ja3VE2JrkkghKnHC
YT1MECH-85-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (1HP_H_2) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628446&prj=684&rqi=lAFUdba2kfW8Acs7acchUTcZV2
YT1MECH-89-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (1HP_K_2) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628450&prj=684&rqi=wplHJINnHsdMHIBr5WKlXLRry3
YT1MECH-90-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628451&prj=684&rqi=E04EyAfEAM14DPBmR3bFGm5RmN
YT1MECH-88-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (1HP_K_1) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628449&prj=684&rqi=PwaRJ9yxyJ9Hxn0Tgj6g7LL08Q
YT1MECH-83-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (1HP_G_2) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628444&prj=684&rqi=AB4frFi1TjaKrdQxiGwG1UG9zp
RT1ELEC-383-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_G3 (L2A) Breaker Q03 is not padlockable because it does not have the locking mechanism installed on the breaker. Per the submittal, drawing # HSU-5736GL-ELC-DWG01 sheet 2, the breaker should be equipped with a locking mechanism that prevents operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628206&prj=684&rqi=LJSlKpCFDGGGwYwxj57ocWImqz
GI-003 | SV18-2 | AMER | Closed | P2 Medium CX | dustin.haugh@veolia.com | 2026-07-07 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1PDU_F1_2 | PDU - Power Distribution Unit |  |  | All PDUâ€™s in data hall are missing one front left floor mounting bolt. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628247&prj=684&rqi=EjeYdmAlOVzi0XV38mAc9FJJoo
YT1ELEC-9-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-07 04:00:00.000 +0400 | Controls Contractor | L2B | DCOS Design Issue | DCOS | Electrical â€“ MV | equipment | 1RMU_R2 | RMU - Ring Main Unit |  |  | (1RMU_R2) L2B 3rd section of RMU does not communicate with BMS.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628259&prj=684&rqi=iNlIN4PGfBXFj3OB5nXhUPooHv
RT1ELEC-386-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_K3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_K3 (L2A) Breaker Q03 is not padlockable because it does not have the locking mechanism installed on the breaker. Per the submittal, drawing # HSU-5736GL-ELC-DWG01 sheet 2, the breaker should be equipped with a locking mechanism that prevents operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628215&prj=684&rqi=2tgqXRZiOHhtjxmdfTuMmvmlmQ
RT1ELEC-384-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_H3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_H3 (L2A) Breaker Q03 is not padlockable because it does not have the locking mechanism installed on the breaker. Per the submittal, drawing # HSU-5736GL-ELC-DWG01 sheet 2, the breaker should be equipped with a locking mechanism that prevents operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628210&prj=684&rqi=mIKHgRiOsN4O3ZBqm5olcxRESL
RT1ELEC-387-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_R2_3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_R2_3 (L2A) Breaker Q03 is not padlockable because it does not have the locking mechanism installed on the breaker. Per the submittal, drawing # HSU-5736GT-ELC-DWG01 sheet 2, the breaker should be equipped with a locking mechanism that prevents operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628217&prj=684&rqi=Sywu52fNxkvlPdvGcUNynCDwFq
RT1ELEC-385-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_J3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_J3 (L2A) Breaker Q03 is not padlockable because it does not have the locking mechanism installed on the breaker. Per the submittal, drawing # HSU-5736GL-ELC-DWG01 sheet 2, the breaker should be equipped with a locking mechanism that prevents operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628213&prj=684&rqi=dPlgfQ6cvelk8xMgHNymsui9oF
RT1ELEC-67-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K2_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_K2_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627726&prj=684&rqi=iPeNZjl95ehT2bcRCrhvjExc8c
RT1ELEC-72-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_1_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_R2_1_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627728&prj=684&rqi=dwqbQvYDKQM1LWskSjlxAzmCsh
RT1ELEC-80-002 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_R2_3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_R2_3) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627730&prj=684&rqi=MGeyHlQ9WGScDyuYQUyQH6juxq
RT1ELEC-63-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K1_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_K1_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627725&prj=684&rqi=enwKoQKbL4V9pjpEPvLJhOS2Sn
RT1ELEC-58-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J2_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_J2_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627723&prj=684&rqi=qSil2Ia56d3MU6atYZ2cYftPPD
RT1ELEC-49-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H2_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_H2_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627720&prj=684&rqi=qUUqDHYCzLs0xXBQqT3V1Ocu9k
YT1MECH-9-003 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-02 04:00:00.000 +0400 | TRN - Trane | L2B | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1ACC_G_16 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_G_16) L2B For tracking purposes, the UPS was cannibalized and needs to be replaced. Per Ryan Vincent, for SV18-1b, the UPS failed at 2-2.5 hours at 100%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627744&prj=684&rqi=tN1aYyADgzRlAjQYObNvJcEEeY
RT1ELEC-45-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H1_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_H1_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627719&prj=684&rqi=4J6N3RxnEDwixE0aesTOAzX3Nu
RT1ELEC-71-002 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_K3) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627727&prj=684&rqi=SZ80z4Sc6ziuWgGExQtQeAhjZI
RT1ELEC-76-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_R2_2_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_R2_2_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627729&prj=684&rqi=HCpiGbHR2bBTPZ7PAatqofnSit
RT1ELEC-54-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J1_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_J1_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627722&prj=684&rqi=QdaVfmA2FYnMh98WKHWNtMxu41
RT1ELEC-62-002 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_J3) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627724&prj=684&rqi=F6stgyTF7XmgDsgk9HsDqeEG82
YT1ELEC-86-001 | SV18-2 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Design Professional | L2B | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_G) L2A: In the SCCS, there is an issue across ALL MDSB where breaker 1TX_X_R1 is missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627717&prj=684&rqi=L1hqU8kqvpVhPR2k9vzMo6VufN
RT1ELEC-53-002 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_H3) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627721&prj=684&rqi=hughwGlePZg6yYuvtflupni4oi
RT1ELEC-8-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-02 04:00:00.000 +0400 | SCH - Schneider MV | L2A | Installation Damage | Commissioning | Electrical â€“ MV | equipment | 1RMU_K | RMU - Ring Main Unit |  |  | (1RMU_K) L2B Breaker operator has been bent during breaker exercising for P2P checks. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627745&prj=684&rqi=DxP5usjiZZxbOJhYIvmxouecet
RT1ELEC-44-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_G3) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627435&prj=684&rqi=7hZZ1e9wTxAoso4DEN4j7ZAuMN
RT1ELEC-384-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-30 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_H3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | (1UMDSB_H3) L2A REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1UPNL_H3_H1 (Q09) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627476&prj=684&rqi=v3Yq8OpegSgDynzQ66NYDKGu6c
RT1ELEC-155-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-30 04:00:00.000 +0400 | Owner | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1PNL_R2_2_H3 | DB - Distribution Boards |  |  | (SKID R2 HP in F) L2A RFI 539: WSHP #2 Power Supply at PH F (Panel R2-2 Dependency) determined that the HP in SKID F has a power supply that is fed from 1PNL_R2_2_H3. The SKID F HP will be installed and ran on temporary power until the end of the SV18-2 project once SKID R2 has completed all Cx activities. Once ready to restore normal power to 1PNL_R2_2_H3, the temp power system and any associated conduit will need to be removed from SKID F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627450&prj=684&rqi=KZk6UVodYYOULhlnWJOwjx02Bf
RT1ELEC-40-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G2_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_G2_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627415&prj=684&rqi=Nd1F9ejveu6ujF7PzUluzbxb5r
RT1ELEC-383-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-30 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | (1UMDSB_G3) L2A REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1UPNL_G3_H1 (Q09) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627475&prj=684&rqi=SRvMtclcqx8WhClLGLibvjX4dI
RT1MECH-86-008 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (Electrical Skid J) L2A At the SW doors, the speaker strobe & pull station devices cannot be installed as the back boxes are too close to the adjacent conduit and security JB respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627242&prj=684&rqi=p4qTUIFVwcROT1Dj5J6p6NLzZD
RT1MECH-88-008 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (Electrical Skid K) L2A At the SW doors, the speaker strobe & pull station devices cannot be installed as the back boxes are too close to the adjacent conduit and security JB respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627243&prj=684&rqi=Q9YaKoArZnz1KbTUZk9TOeIkWP
RT1ELEC-360-002 | SV18-2 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_1 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_1) L2A: Battery cable missing grommet.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627152&prj=684&rqi=80j6foFbXw87HMfBZyNQnvr9Sq
RT1ELEC-97-006 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB R2) L2A: Missing lock tumbler for section 01C.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627151&prj=684&rqi=cZRwfOjg2YEtnxuOxlP3OGCsmb
RT1ELEC-97-005 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (MSB R2) L2A: Gen main breaker has issues with control module. Not sending power to HMI and ERMS.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627150&prj=684&rqi=pLxmhfEo93hBCO0XCQdwhD7MNN
RT1ELEC-361-002 | SV18-2 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_2 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_2) L2A: Multiple battery cables missing grommets.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627153&prj=684&rqi=2R8CsjN8nwuInCcZhHTQDLIkIC
YT1ELEC-95-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2B During P2P checks, it was identified that the CAT6 cable connecting between 1MSB_K Section 02A and the DMark Panel in SKID K does not work. We verified this by connecting an external CAT6 cable between the two connections and the system worked correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626997&prj=684&rqi=knX3OTM0EAuUO2lqC7iKKUz0dl
YT1ELEC-369-001 | SV18-2 | AMER | Ready for Verification | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_G | GENL - Generator (LV) |  |  | (1GEN_G) L2B GEN_G door enclosure to the HMI panel has a bent frame from the temporary rigging that was installed to gain access to the equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626250&prj=684&rqi=KujzrLLjFZrqaxDc8MbL1EDwoR
YT1ELEC-373-001 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-06-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1GEN_R2 | GENL - Generator (LV) |  |  | (1GEN_R2) L2B Piping feeding to the pressure transducer on the SCR is routed incorrectly and not connected to the transducer. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626259&prj=684&rqi=Rje6KlEYOGNYmb3wJodCcPEBcV
RT1ELEC-36-001 | SV18-2 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G1_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_G1_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625852&prj=684&rqi=O8TtUJwNUSLTgmhiAi9TgcoDbX
RT1MECH-62-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_13 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_G_13) L2A Several missing screws on fan access panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625862&prj=684&rqi=jeCkK54WBp7wdWAn0uEjaxWu3Z
YT1ELEC-93-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-18 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Component/ Equipment Failure | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | (1MSB_H) L2B Breaker Q15 (1ACC_H_14) failed to trip during NETA secondary injection testing of the equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625855&prj=684&rqi=iZI6DkxjTjoAMghfDxGi6FnktX
RT1MECH-63-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_14 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_G_14) L2A Missing screws on fan access panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625863&prj=684&rqi=LgNoqYN5XuAovxMFjfPGHhthQo
RT1MECH-74-002 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-06-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_R2_13 | CRAH - Computer room air handler (Skid) |  |  | (CRAH-R2-13) L2A Fan power interconnections not connected correctly. Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625870&prj=684&rqi=fOho4nCkDG2u9N2YwxyBJRUG9K
RT1MECH-68-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_J_13 | CRAH - Computer room air handler (Skid) |  |  | (CRAH-J-13) L2A Torque marks missing from fan section. Bolt pictured is hand-loose. Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625693&prj=684&rqi=xZ0CbTkqORZmiTTE8w12hcjJ1a
RT1ELEC-361-001 | SV18-2 | AMER | Closed | P2 Medium CX | ian.tsurumoto@veolia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_2 | UPS - Uninterrupted Power Supply |  |  | Verify Internal Electrical wiring is completed UPS_R2_1 and UPS_R2_2 Parallel UPS communication cable missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625690&prj=684&rqi=95PFzvKbmB7jhypyjYJvd7yZpd
RT1MECH-67-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_15 | CRAH - Computer room air handler (Skid) |  |  | (CRAH-H-15) L2A Fan power wiring in left fan section need to be zip tied down. Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625692&prj=684&rqi=Con3tKRqAVDamzQiKMmmLySPP8
RT1ELEC-360-001 | SV18-2 | AMER | Closed | P2 Medium CX | ian.tsurumoto@veolia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_1 | UPS - Uninterrupted Power Supply |  |  | Verify Internal Electrical wiring is completed UPS_R2_1 and UPS_R2_2 Parallel UPS communication cable missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625689&prj=684&rqi=z75bv2zdgIb1nR90w0QN52hQbN
RT1MECH-73-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_15 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_K_15) L2A Top left Screw missing on supply air grate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625546&prj=684&rqi=4lWy3bilFHLVaVHUNRaNSm2xqE
RT1MECH-42-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-16 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_05 | CRAH - Computer room air handler |  |  | (1CRAH_H_05) Filter bracket 5 back top and 6 back bottom are missing screws. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625547&prj=684&rqi=t6uVlR6pP7TQ2hyFZeyHemEuDJ
RT1ELEC-370-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-16 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_G | GENL - Generator (LV) |  |  | (1GEN_G) L2A Broken bolt on grounding bar in the back of the GCB enclosure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625483&prj=684&rqi=COuE5mE15NZAQs1VANhTnYXQnl
GI-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-16 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | [6 empty] | (1_LBSB) Inspection During inspection of various equipment, it was identified that the Kirk Key cylinder on the Temp Gen breaker for the LBSB is incorrect. The LBSB Temp Gen breaker has a K1 kirk key barrel that has the serial number of '64161'. This does not match the currently installed/ordered GCB K1 kirk key barrels which have a serial number of '64393'. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625533&prj=684&rqi=TgHfjhc4qrZoQZ1eS4hsgcu8mw
RT1MECH-89-004 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (HP-K-2) Merv 4 filters are currently installed. Must be Merv 8 to match skids G, H, R2. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625379&prj=684&rqi=1sTvcQufTTFMlOS09Gfq5IiHZB
RT1MECH-84-008 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (HP-H-1) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625369&prj=684&rqi=hodgYF2CCr62JVJCOtj2kTpghA
GI-001 | SV18-2 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1GEN_G | GENL - Generator (LV) |  |  | (1GEN_G) L2A Broken bolt on grounding bar in the back of the GCB enclosure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625381&prj=684&rqi=NzyE69bebhqW1nH7Vrs5zMYimV
RT1MECH-86-006 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (HP-J-1) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625371&prj=684&rqi=doekhrmqjJQeZ6gDIqOSbZ50pS
RT1MECH-90-008 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (HP-R2-1) L2A Unit needs to have flex ducting installed between main fan compartment and ducting. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625380&prj=684&rqi=5zoR7tropFjI6MqzCtEGOrugmH
RT1MECH-89-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (HP-K-2) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625374&prj=684&rqi=ahITQKzJygAX09M3q6pjPEqTmW
RT1MECH-85-004 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (HP-H-2) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625370&prj=684&rqi=5usF68lKaR5ZZN16ajIZdTeSZk
RT1MECH-88-007 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (HP-K-1) Merv 4 filters are currently installed. Must be Merv 8 to match skids G, H, R2. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625377&prj=684&rqi=roJOK3haxBPfbBfaZDvQluOrJN
RT1MECH-87-004 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | (HP-J-2) Merv 4 filters are currently installed. Must be Merv 8 to match skids G, H, R2. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625376&prj=684&rqi=98e92Is5srCcXoP6O6LjyAZAiy
RT1MECH-86-007 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (HP-J-1) Merv 4 filters are currently installed. Must be Merv 8 to match skids G, H, R2. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625375&prj=684&rqi=UzpmkdMHyxDRnl9ALu5ZiI3EWu
RT1MECH-87-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | (HP-J-2) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625372&prj=684&rqi=D8YX7NJ6kxDtZJWs6YKGYknztv
RT1MECH-88-006 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (HP-K-1) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625373&prj=684&rqi=hbR3OLdDSxo6k8pUqQjSZnU5zX
RT1MECH-91-011 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-06-14 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (1HP_R2_2) L2A Not enough flex conduit slack to install smoke detectors onto the airflow plenum | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625247&prj=684&rqi=Mfxd090LVoY3VKz06eOKo2PjvR
RT1MECH-90-007 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-06-14 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L2A Not enough flex conduit slack to install smoke detectors onto the airflow plenum. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625246&prj=684&rqi=9050y8IYsX2zxgFlUU0g19LLjJ
RT1MECH-49-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_12 | CRAH - Computer room air handler |  |  | (CRAH-H-12) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625017&prj=684&rqi=pP8GAHID4D50wVUi7aRuW8AFxO
RT1MECH-47-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_10 | CRAH - Computer room air handler |  |  | (CRAH-H-10) L2A Bracket 2 top back bolt loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625015&prj=684&rqi=jGVJqUphZrOSucigalNt3BwbIj
RT1MECH-45-004 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_08 | CRAH - Computer room air handler |  |  | (CRAH-H-8) L2A Debris on coil | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625013&prj=684&rqi=ek9M2mJUxJ5uwfV4BvAc0wv990
RT1MECH-32-002 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (CRAH-G-7) L2A Filter spacer lodged in fan | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625025&prj=684&rqi=WtPP6e45AUCjLUhSFXstiiWZjv
RT1MECH-41-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_04 | CRAH - Computer room air handler |  |  | (CRAH-H-4) L2A Filter bracket 5 bolt is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625008&prj=684&rqi=MP88HuwUgoINbF0Q4h8iyRSDAn
RT1MECH-31-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_06 | CRAH - Computer room air handler |  |  | (CRAH-G-6) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625023&prj=684&rqi=IQxipR8AXMunzGhytkOkEwF8ZF
RT1MECH-30-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_05 | CRAH - Computer room air handler |  |  | (CRAH-G-5) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625022&prj=684&rqi=h5mvsrOfj4r52qZ4d4K6PO2OaA
RT1MECH-43-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_06 | CRAH - Computer room air handler |  |  | (CRAH-H-6) L2A Filter bracket 8 front bottom bolt loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625009&prj=684&rqi=OlJgNx5vG12KtxQIhvExIervgI
RT1MECH-45-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_08 | CRAH - Computer room air handler |  |  | (CRAH-H-8) L2A Filter brackets 1-8 are loose (welds are broken) Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625012&prj=684&rqi=FBGV3MO67LSyUp9xhsbExU3X0C
RT1MECH-28-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_03 | CRAH - Computer room air handler |  |  | (CRAH-G-3) L2A Filter bracket 8 top bolts loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625020&prj=684&rqi=wpPyGGIxtzT5RzEg7oLWRv41xo
RT1MECH-27-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_02 | CRAH - Computer room air handler |  |  | (CRAH-G-2) L2A Mystery screw found in top right filter section | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625019&prj=684&rqi=793uoreCPgddNEDIrMOFY3ldAm
RT1MECH-32-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (CRAH-G-7) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625024&prj=684&rqi=Ko0bumntfmgcP37HVjSZ1OkrKW
RT1MECH-36-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_11 | CRAH - Computer room air handler |  |  | (CRAH-G-11) L2A Filter brackets: #4 both back both top and bottom bolts missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625028&prj=684&rqi=Z3qSs0zUkwxPvg2djx2OcPhanZ
RT1MECH-39-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_02 | CRAH - Computer room air handler |  |  | (CRAH-H-2) L2A 2 bolts missing on filter bracket 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624969&prj=684&rqi=TPDwNlRlYHwzulDNuQmERtamps
RT1MECH-44-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_07 | CRAH - Computer room air handler |  |  | (CRAH-H-7) L2A Filter bracket 7 Top bolt loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625011&prj=684&rqi=XczjqV0Qm2oy4rsDMLXqJhSyPg
RT1MECH-35-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_10 | CRAH - Computer room air handler |  |  | (CRAH-G-10) L2A Filter brackets: #4 top front, #5 top back bolts missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625027&prj=684&rqi=jdIh9ICPxxM7SejyWTtErFYJAR
RT1MECH-33-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_08 | CRAH - Computer room air handler |  |  | (CRAH-G-8) L2A Filter brackets: #4 Top back bolt missing #5 missing integral bolt and completely fallen down | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625026&prj=684&rqi=70KG4aOdvO4msl1ASgzuH9ZmOJ
RT1MECH-48-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_11 | CRAH - Computer room air handler |  |  | (CRAH-H-11) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625016&prj=684&rqi=kIPWiFJpadsGy0PD15lHNctLm0
RT1MECH-37-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_12 | CRAH - Computer room air handler |  |  | (CRAH-G-12) L2A Filter brackets: #4 top back bolt missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625029&prj=684&rqi=1qNyDU5r0PzO3wTUrgVZLTgycc
RT1MECH-29-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_04 | CRAH - Computer room air handler |  |  | (CRAH-G-4) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625021&prj=684&rqi=O5F5JDEJRsnOgzyEiYiHrAHK1U
RT1MECH-26-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_01 | CRAH - Computer room air handler |  |  | (CRAH-G-1) L2A #4 Top back bolt loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625018&prj=684&rqi=EqlZuELKut8VO0MMYBeFgAZ6oy
RT1MECH-46-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_09 | CRAH - Computer room air handler |  |  | (CRAH-H-9) L2A Filter brackets 1-8 are loose (welds are broken) Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625014&prj=684&rqi=BL2Ya45Yr0JNe20AvaLMt4bIyr
RT1MECH-84-007 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (Electrical Skid H) L2A Termination end of leak detection rope is missing it's end of line "Leak Tape | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624182&prj=684&rqi=EMwit37oV67IVK0rM6jdWiWb27
RT1MECH-86-005 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (Electrical Skid J) L2A Termination end of leak detection rope is missing it's end of line "Leak Tape" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624183&prj=684&rqi=JmcuHZBMRXNUqhLJAKv463ujb2
RT1MECH-82-009 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A Termination end of leak detection rope is missing it's end of line "Leak Tape" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624179&prj=684&rqi=eylC97IhsUehZiSLsFMaMTEn5B
RT1MECH-90-006 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A Termination end of leak detection rope is missing it's end of line "Leak Tape" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624186&prj=684&rqi=k31U666VCJ6xFftGQ1Pt4eQwWj
RT1MECH-88-005 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (Electrical Skid K) L2A Termination end of leak detection rope is missing it's end of line "Leak Tape" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624184&prj=684&rqi=YdG6njuSGjkIsyiZZT84y87XB6
RT1MECH-85-003 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (1HP_H_02) L2A Unit missing condensate containment curb. Present in G. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623996&prj=684&rqi=i4oBNcC3zj6SUR13FrwC6Z2TZ9
RT1ELEC-353-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_H3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_H3) L2A The communication interface should have an additional Relay I/O card installed in the SMART slot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623730&prj=684&rqi=4R6egfroCVhfW50MAA6nxjTyAJ
RT1ELEC-93-007 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A 1MSB_G Sections 05A, 06A, 11A, 12A, 13A all have extra hardware installed on the main busway with no cables connected to them. This extra hardware needs to be removed from the busway. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623706&prj=684&rqi=bAEuIW3rKigCz2YwzaOQuToo8Z
RT1ELEC-356-003 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_J3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_J3) L2A The communication interface should have an additional Relay I/O card installed in the SMART slot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623729&prj=684&rqi=Qs9jfbIlR5Qa9M0OdTtavB3RjO
RT1ELEC-91-003 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R2_1 | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_R2_1) L2A The Q10 'SPARE' breaker is not the correct kind of breaker per the submittal. Currently installed is an XT5H 400AF / 400A Plug/Sensor breaker. Per Drawing # HSU-5736GR-ELC_DWG01 of the Hanley submittal, the breaker should be a XT5H 600AF / 600A Plug/Sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623717&prj=684&rqi=o7mkyNTik2c9AKiOV7nMaEpSou
RT1ELEC-350-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_G3) L2A The communication interface should have an additional Relay I/O card installed in the SMART slot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623728&prj=684&rqi=Cv8gYadQgvUOU2zLV2v6WKpmCU
RT1ELEC-91-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R2_1 | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_R2_1) L2A The plastic cover plates beneath the HMI on all six 250A frame breakers (Q01 - Q06) are bent or cracked. This is likely due to the screw on the plastic cover being excessively tightened down. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623716&prj=684&rqi=Jaezeoa5v2j1wB1UIKpfq9cif4
RT1ELEC-359-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_K3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_K3) L2A The communication interface should have an additional Relay I/O card installed in the SMART slot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623731&prj=684&rqi=NQPNurMW49tgsyRctaVMFp6I4V
RT1ELEC-362-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_3) L2A The communication interface should have an additional Relay I/O card installed in the SMART slot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623732&prj=684&rqi=0lj6mvQhAshgu5aKC2VtWdXRzF
RT1ELEC-356-002 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UPS_J3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_J3) L2A The cables fed from MDSB_J into UPS_J3 are not long enough to make proper connections inside of the UPS unit. There is a small amount of slack available on the cables inside of the MDSB but unsure if this is enough to make the connection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623566&prj=684&rqi=NcWi7b9hkzLn9STE73hg8VlD1S
RT1MECH-38-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-01 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_01 | CRAH - Computer room air handler |  |  | (1CRAH _H_01) L2A Upper filter bracket is lose. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623574&prj=684&rqi=hA2avXE7VGuMt4xon8hdLuZnEr
RT1MECH-38-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-01 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Cleaning | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_01 | CRAH - Computer room air handler |  |  | (1CRAH_H_01) L2A Fin section needs to be cleaned out. Miscellaneous debris present. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623575&prj=684&rqi=K23YqLImqmvNIIDh4Rhp3VqiK7
RT1ELEC-93-005 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-01 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A While performing light tug test on cables inside of 1MSB_G Cabinet 02A, cable J400 disconnected from 'Port 13' on the P/PSU1 unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623568&prj=684&rqi=1jFdQe5fwv0rcEY4d41gHKrlaU
RT1MECH-40-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-01 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_03 | CRAH - Computer room air handler |  |  | (1CRAH_H_03) L2A Loose nut/bolts from filter bracket. Fallen onto the fan enclosure. Need to clean out | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623573&prj=684&rqi=IDBfP2KpPQSq6grVQn9up7OGWQ
RT1ELEC-93-006 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-01 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A Protective plastic cover in section 06A of 1MSB_G is not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623570&prj=684&rqi=amjKBc8B6JhwaZOVqBDKnkSbQ1
RT1MECH-83-003 | SV18-2 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (WSHP-G-2) L2A No CAT 6 cables pulled to WSHP (R-4800 & R-4900 on MPS submitall dwg MPS.522). Associated conduit required as well, see Skid H for example of complete install. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622866&prj=684&rqi=esczXHMK5dlNmk71SHyuYsmKjR
RT1MECH-84-002 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (Electrical Skid H) L2A At the 2 # doors on the north side, the pull box back boxes are too close to the adjacent switch for the pull station to be installed/door opened. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622846&prj=684&rqi=APTjezBaLDPfmSuN6eRqvX7PKs
RT1MECH-87-001 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | (WSHP-J-2) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622839&prj=684&rqi=Q7jsI5AObvQKUQcPehXBPw2nwF
RT1MECH-88-002 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (WSHP-K-1) L2A Power wiring to the smoke detectors units is terminated incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622862&prj=684&rqi=zQe6dFEDv9Fzq8zC1dlgRKxcJQ
RT1MECH-89-002 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (WSHP-K-2) L2A Power wiring to the smoke detectors units is terminated incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622863&prj=684&rqi=oMjGb0HlrVGCYPzwOY1imdPKbp
RT1MECH-84-001 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (WSHP-H-1) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622836&prj=684&rqi=BUElGMw3cuWz7EmWp9cQgW6PP3
RT1MECH-82-008 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A At the south end of the PH, the drain valve on the CHW supply line, extends laterally over the UPS. Piping should be modified so it drops down vertically so as to eliminate the possibility of water dripping on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622872&prj=684&rqi=D6ua82AOdX0b75ubYCksvfXWBA
RT1MECH-86-002 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (WSHP-J-1) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622860&prj=684&rqi=ky0EpfQZQVrUgXr5seYVb5J7hb
RT1MECH-82-005 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (WSHP-G-1) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622855&prj=684&rqi=fBJ049lnQDZnlfb2p3ynMmyNfL
RT1MECH-88-004 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (Electrical Skid K) L2A At the south end of the PH, the drain valve on the CHW supply line, extends laterally over the UPS. Piping should be modified so it drops down vertically so as to eliminate the possibility of water dripping on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622875&prj=684&rqi=D4gbn1BWg2goiWPbilRj6npW66
RT1MECH-90-004 | SV18-2 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (WSHP-R2-1) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622864&prj=684&rqi=ZrcYDORtOxJXZoPKrJo5Qq0Em6
RT1MECH-88-003 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (Electrical Skid K) L2A Where insulated CHW lines are supported by unistrut, shields are missing in a couple of locations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622871&prj=684&rqi=8yN6x4Iohn5Qm22EYyWVJ6CJmn
RT1MECH-90-005 | SV18-2 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (WSHP-R2-1) L2A No CAT 6 cables pulled to WSHP (R-4800 & R-4900 on MPS submitall dwg MPS.522). Associated conduit required as well, see Skid H for example of complete install. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622867&prj=684&rqi=OAFBBZHK3mLihfK8rqa6aHcMut
RT1MECH-86-004 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (Electrical Skid J) L2A At the south end of the PH, the drain valve on the CHW supply line, extends laterally over the UPS. Piping should be modified so it drops down vertically so as to eliminate the possibility of water dripping on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622874&prj=684&rqi=m5Zu6KSC0KrNbjZWb1TZBcJsdX
RT1MECH-85-001 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (WSHP-H-2) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622837&prj=684&rqi=IZlQ2A7qSfgPv7QzAtud2a0u5t
RT1MECH-91-010 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (WSHP-R2-2) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622844&prj=684&rqi=LlklrQdEUf5irNSzbmcUQgIpN1
RT1MECH-84-004 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (WSHP-H-1) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622858&prj=684&rqi=8wWqisG5XFv9qeIsDqld8BxnFJ
RT1MECH-90-002 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (WSHP-R2-1) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622842&prj=684&rqi=3NkTJc2jjfPRUkDiShS4TKSS4g
RT1MECH-84-005 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (Electrical Skid H) L2A Where insulated CHW lines are supported by unistrut, shields are missing in a couple of locations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622869&prj=684&rqi=OyDV7vhteqg4fwhjsYyExxLOsK
RT1MECH-83-001 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (WSHP-G-2) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622835&prj=684&rqi=PhDrRL4RWDnndBQGrZyMi5lqfj
RT1MECH-83-002 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (WSHP-G-2) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622856&prj=684&rqi=Q1cZ2qe7lgc9BEp5LC48JUImpI
RT1MECH-88-001 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (WSHP-K-1) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622840&prj=684&rqi=U1cD4VsljmXCddJfHzaxxzhz3L
RT1MECH-90-003 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A At the SW doors, the speaker strobe & pull station devices cannot be installed as the back boxes are too close to the adjacent conduit and security JB respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622848&prj=684&rqi=DUA0EPX8oKhS9g8X9gEF505q3e
RT1MECH-89-001 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (WSHP-K-2) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622841&prj=684&rqi=RLGuL7SQYd9gXC7V7cSeJVFGlX
RT1MECH-82-004 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A Speaker strobe boxes at each of the 4 # doors, require an extension box. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622851&prj=684&rqi=iYQ7EOphTjrWKvvPxt836uzDmg
RT1MECH-87-002 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | (WSHP-J-2) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622861&prj=684&rqi=XU0YQTDZrnyxYbNuNpqoAlW7g5
RT1MECH-82-006 | SV18-2 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (WSHP-G-1) L2A No CAT 6 cables pulled to WSHP (R-4800 & R-4900 on MPS submitall dwg MPS.522). Associated conduit required as well, see Skid H for example of complete install. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622865&prj=684&rqi=71MPaFDKrx9QJQQXFOnM1uqbfn
RT1MECH-85-002 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (WSHP-H-2) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622859&prj=684&rqi=4tHfwSfVlmsawCV7cXjMlISSOv
RT1MECH-82-007 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A Where insulated CHW lines are supported by unistrut, shields are missing in a couple of locations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622868&prj=684&rqi=UGqJOJHTJWDAzUTzOhABH4DbQj
RT1MECH-86-001 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (WSHP-J-1) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622838&prj=684&rqi=A7xxio44sKDmDCuv20As8Hipad
RT1MECH-84-003 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (Electrical Skid H) L2A At the SW doors, the speaker strobe & pull station devices cannot be installed as the back boxes are too close to the adjacent conduit and security JB respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622853&prj=684&rqi=EbkjMr1gEgV02KSAGn8zxzJUM5
RT1MECH-84-006 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (Electrical Skid H) L2A At the south end of the PH, the drain valve on the CHW supply line, extends laterally over the UPS. Piping should be modified so it drops down vertically so as to eliminate the possibility of water dripping on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622873&prj=684&rqi=oyb1fbf1i6yYjyaWyxX8vCo4Sy
RT1MECH-86-003 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (Electrical Skid J) L2A Where insulated CHW lines are supported by unistrut, shields are missing in a couple of locations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622870&prj=684&rqi=YZt7D3rSDVQU9Zgy1vs9n1G9QN
RT1ELEC-97-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB_R2) L2A MSB HMI has 4 key-actuated selector switches, and only 3 are required. Per Hanley submittal drawing #HSU-5478FO-ELC-DWG02, this switch should be removed and blanked off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622702&prj=684&rqi=fY8uN33Bm9xg7ujnc0BQp47ASf
RT1ELEC-95-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | (1MSB_J) L2A MSB HMI has 4 key-actuated selector switches, and only 3 are required. Per Hanley submittal drawing #HSU-5478FO-ELC-DWG02, this switch should be removed and blanked off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622678&prj=684&rqi=3SnYdNNtGl0THVs2vzhHqPBP83
RT1ELEC-353-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_H3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_H3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622742&prj=684&rqi=ndJ1BG1ukb0YUDHamvhfs4zrtZ
RT1ELEC-85-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BTU_R2 | BTU - Battery Tripping unit |  |  | (1BTU_R2) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622750&prj=684&rqi=bMrPUEjE7U1Raw9aDj4czjjcMI
RT1MECH-31-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-21 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_06 | CRAH - Computer room air handler |  |  | (1CRAH_G_06) L2A HMI panel is showing visible bend. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622735&prj=684&rqi=WxqfQHS1mnZ1N4wm8l7dT2Znc3
RT1ELEC-356-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_J3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_J3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622743&prj=684&rqi=Xm91XuKwGZZnlUeN162wq5wyCC
RT1ELEC-83-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BTU_J | BTU - Battery Tripping unit |  |  | (1BTU_J) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622748&prj=684&rqi=N92KAk6thITXBa2ZmJpbwzY6xh
RT1ELEC-97-003 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB_R2) L2A The key-actuated selector switches on the MSB HMI lock the keys when not in the center position. The selector switches should not lock the keys in any position. Sheet 2 of Hanley Submittal Drawing #HSU-5478FO-ELC-DWG02 specifies this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622703&prj=684&rqi=JSunztiOBnZHwddvVCyT7DN58i
RT1ELEC-95-003 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | (1MSB_J) L2A The key-actuated selector switches on the MSB HMI lock the keys when not in the center position. The selector switches should not lock the keys in any position. Sheet 2 of Hanley Submittal Drawing #HSU-5478FO-ELC-DWG02 specifies this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622679&prj=684&rqi=VUfKRD6VGnutxWsB7Pgaz9PxUb
RT1ELEC-80-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_R2_3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_R2_3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622740&prj=684&rqi=r7J2Otedy4ORZr3pqESlFZKbqY
RT1ELEC-97-004 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB_R2) L2A FST identified during FWT that there are missing ground bonding cables connecting the MSB switchboard to the top hats on MSB sections 5A, 6A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622755&prj=684&rqi=H6jdsqPqCltcjxW2sPKsXlHypd
RT1ELEC-362-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_R2_3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622745&prj=684&rqi=88KLXroy31ez4NG2gYplYW2W3g
RT1ELEC-95-004 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | (1MSB_J) L2A FST identified during FWT that there are missing ground bonding cables connecting the MSB switchboard to the top hats on MSB sections 5A, 6A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622753&prj=684&rqi=V11hiwGfvMW5UDTNUZVO8noL9I
RT1ELEC-71-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_K3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_K3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622739&prj=684&rqi=QxqI0cFHZ5bDJvd6WjrxHvGnti
RT1ELEC-94-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | (1MSB_H) L2A MSB HMI has 4 key-actuated selector switches, and only 3 are required. Per Hanley submittal drawing #HSU-5478FO-ELC-DWG02, this switch should be removed and blanked off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622676&prj=684&rqi=GcCuJlPe3uMRj7BNGtVREiYvWp
RT1ELEC-93-003 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A The key-actuated selector switches on the MSB HMI lock the keys when not in the center position. The selector switches should not lock the keys in any position. Sheet 2 of Hanley Submittal Drawing #HSU-5478FO-ELC-DWG02 specifies this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622670&prj=684&rqi=5MDkN4FUaae5yvtmQrCsQuPu6P
RT1ELEC-93-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A MSB HMI has 4 key-actuated selector switches, and only 3 are required. Per Hanley submittal drawing #HSU-5478FO-ELC-DWG02, this switch should be removed and blanked off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622657&prj=684&rqi=bDRSUFXHJDQyMaN65ENwR9W7tV
RT1ELEC-93-004 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A FST identified during FWT that there are missing ground bonding cables connecting the MSB switchboard to the top hats on MSB sections 5A, 6A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622751&prj=684&rqi=F8BznrmeJ25gXHY0UlCidDVvx8
RT1ELEC-84-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BTU_K | BTU - Battery Tripping unit |  |  | (1BTU_K) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622749&prj=684&rqi=CS4fvR6FQYMYnYCMxJQuFGIpfl
RT1ELEC-350-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_G3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622741&prj=684&rqi=AJb97ocx1IA24dFHpjSDOQmT0a
RT1MECH-45-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-21 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_08 | CRAH - Computer room air handler |  |  | (CRAH-H-8) L2A MCP1 fan overload allows user to go straight from "Trip" to "On" without opening the contact first. Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622734&prj=684&rqi=28kYlVLZIPRkoM9I1fKcOJj5mn
RT1ELEC-94-003 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | (1MSB_H) L2A The key-actuated selector switches on the MSB HMI lock the keys when not in the center position. The selector switches should not lock the keys in any position. Sheet 2 of Hanley Submittal Drawing #HSU-5478FO-ELC-DWG02 specifies this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622677&prj=684&rqi=dhnIbfosvw1BKYWiMPJifwV5vk
RT1ELEC-94-004 | SV18-2 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | (1MSB_H) L2A FST identified during FWT that there are missing ground bonding cables connecting the MSB switchboard to the top hats on MSB sections 5A, 6A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622752&prj=684&rqi=sdkUTGKiw77UWEkU4NbLh308M5
RT1ELEC-374-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1GEN_R2 | GENL - Generator (LV) |  |  | (1GEN_R2) L2A Generator Circuit Breaker in GEN_R2 enclosure is missing the kirk key barrel assembly. The required kirk key for this breaker is: K1 (Serial # 64393) The breaker model is: SACE E6.2V-A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622707&prj=684&rqi=4k4PilHMV8KAiM1yIbd0NRGEie
RT1ELEC-96-003 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2A FST identified during FWT that there are missing ground bonding cables connecting the MSB switchboard to the top hats on MSB sections 5A, 6A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622754&prj=684&rqi=dKvWcQHYYBCdfsyYpOUsr8gGGe
RT1MECH-42-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-21 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_05 | CRAH - Computer room air handler |  |  | (1CRAH_H_05) L2A Disconnect shaft for main power source 1 stats in the disconnect handle instead of the disconnect itself. See attached picture. Set screw threads appear to be stripped Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622733&prj=684&rqi=E5y0Mc10IDKB7L3Lx8f6jGHsce
RT1ELEC-359-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UPS_K3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_K3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622744&prj=684&rqi=1BQbJ31mdVgUWD1pDjsu9ZWwjz
RT1ELEC-62-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_J3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_J3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622738&prj=684&rqi=uSXlUhdYwRTIhgbgnsC06o4Yab
RT1MECH-82-003 | SV18-2 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (WSHP-G-1) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622706&prj=684&rqi=acyJJgyiKIxWTfhSSYkxFl2lW4
RT1ELEC-44-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_G3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_G3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622736&prj=684&rqi=hWoP5vBVINRL2oL8R7AQA4dizh
RT1ELEC-81-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BTU_G | BTU - Battery Tripping unit |  |  | (1BTU_G) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622746&prj=684&rqi=XApkihSmgx5y5xkMeMzlCsqtu3
RT1ELEC-96-002 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2A MSB HMI is not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622701&prj=684&rqi=x2iM5JnDvck805IWSRTA6WaAkx
RT1ELEC-82-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BTU_H | BTU - Battery Tripping unit |  |  | (1BTU_H) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622747&prj=684&rqi=WBRx8MEVX6BOHKVnqiy27kh4Tb
RT1ELEC-53-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1BATT_1UPS_H3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_H3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622737&prj=684&rqi=KIgshxlL3aCTFVrJSaUhRziqnS
RT1MECH-55-001 | SV18-2 | AMER | Closed | P1 High CX | ethan.hang@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_06 | CRAH - Computer room air handler |  |  | (1CRAH_K_06) L2A Control board was donated to a CRAH with an earlier start-up date. New control board has been installed, it needs to be programmed during start up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622524&prj=684&rqi=bwlFkMIsOgOkxJK9wjIh4BlHS3
RT1MECH-46-002 | SV18-2 | AMER | Ready for Verification | P2 Medium CX | ethan.hang@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_09 | CRAH - Computer room air handler |  |  | (1CRAH_H_09) L2A Therma has found that the unit has leaks internally on the Vertiv side. A weld and a few spots around the PICV are leaking. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622526&prj=684&rqi=bEj4lhY88Ftvq7tMcQAxHNGRK4
RT1MECH-56-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Cleaning | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_07 | CRAH - Computer room air handler |  |  | (1CRAH_K_07) L2A Right fan section needs cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622576&prj=684&rqi=Zo7cnMLlUQnml3CjF7EIlrFuhK
RT1MECH-55-004 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_06 | CRAH - Computer room air handler |  |  | (CRAH-J-6) L2A Filter brace welds 5, 6, 7, 8 all broken Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622574&prj=684&rqi=Q9HXfGRuUpLUWmYGxOsucOzw1Y
RT1MECH-46-004 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_09 | CRAH - Computer room air handler |  |  | (1CRAH_H_09) L2A PICV actuator was donated to another CRAH with earlier start-up. New PICV actuator needed and installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622525&prj=684&rqi=FGbJ18nYhJ12AyPX76PEAt5Qxr
RT1MECH-55-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Torque required | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_06 | CRAH - Computer room air handler |  |  | (1CRAH_K_06) L2A Loose bolt on fan 4 Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622573&prj=684&rqi=s9SmUbGELwIDxEWo8jOvcHKXyV
RT1MECH-56-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_07 | CRAH - Computer room air handler |  |  | (1CRAH_K_07) L2A Filter brace 2 is missing bolts. Bolts not found! | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622575&prj=684&rqi=qSmhmNoFoGWNCe0Pyd3ktvlTzU
RT1MECH-53-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_04 | CRAH - Computer room air handler |  |  | (1CRAH_K_4) L2A Filter brace #8 is missing a bolt | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622317&prj=684&rqi=s9prIVrOs8EHNtIOX9okT2Wqdc
RT1ELEC-5-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | SCH - Schneider MV | L2A | Installation not correct | Commissioning | Electrical â€“ MV | equipment | 1RMU_G | RMU - Ring Main Unit |  |  | (1RMU_G) L2A RMU cover plates were inadvertently swapped following L2A testing. The left most switch panel cover is currently installed over the center switch. Please refer to attached images for additional information. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622339&prj=684&rqi=yf74rTOLL9f3bzDRHgGYNmoUos
RT1ELEC-371-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1GEN_H | GENL - Generator (LV) |  |  | (1GEN_H) L2A Generator Circuit Breaker in GEN_H enclosure is missing the kirk key barrel assembly. The required kirk key for this breaker is: K1 (Serial # 64393) The breaker model is: SACE E6.2V-A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622355&prj=684&rqi=CAzZt9W4yjTHE5SOdik9cJoqAS
RT1ELEC-373-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1GEN_K | GENL - Generator (LV) |  |  | (1GEN_K) L2A Generator Circuit Breaker in GEN_K enclosure is missing the kirk key barrel assembly. The required kirk key for this breaker is: K1 (Serial # 64393) The breaker model is: SACE E6.2V-A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622357&prj=684&rqi=41sTCxnLIDvFBmA1BMsszkQkb3
RT1MECH-54-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_05 | CRAH - Computer room air handler |  |  | (1CRAH_K_5) L2A Very minor damage to fan 1 due to fallen filter brackets. Small scratches, adding for tracking purposes to keep an eye on it. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622319&prj=684&rqi=6B7cXMsbb2xRabPmGoFAPdp4Ww
RT1MECH-60-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_11 | CRAH - Computer room air handler |  |  | (1CRAH_K_11) L2A Missing bolt on #6 filter bracing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622347&prj=684&rqi=0cvyFTmJvfBkCEXszHoofK5CAn
RT1MECH-53-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_04 | CRAH - Computer room air handler |  |  | (1CRAH_K_4) L2A Lower right panel door upright is missing a rivet. Inspect Equipment for missing hardware | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622318&prj=684&rqi=1zeCBAozhlr26QJGw57gK4gRuW
RT1MECH-54-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_05 | CRAH - Computer room air handler |  |  | (CRAH-J-5) L2A Weld 5 broken Inspect all sections for dents, scratches, fit, corrosion, etc. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622321&prj=684&rqi=SCLxiMQvU66W9o7sFKSIEkBgZu
RT1MECH-57-003 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_08 | CRAH - Computer room air handler |  |  | (1CRAH_K_8) L2A Filter bracket 3 bolt fallen off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622352&prj=684&rqi=6b8Ah0jZV0yrNqVyIkKAv9DqeO
RT1MECH-61-001 | SV18-2 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Cleaning | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_12 | CRAH - Computer room air handler |  |  | (1CRAH_K_12) L2A Air filter brackets have fallen into fan 8. CANNOT STARTUP UNTIL REMOVED | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622345&prj=684&rqi=A5Bmr1ToWV8LiH0KAW6yjCY9A9
RT1ELEC-370-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1GEN_G | GENL - Generator (LV) |  |  | (1GEN_G) L2A Generator Circuit Breaker in GEN_G enclosure is missing the kirk key barrel assembly. The required kirk key for this breaker is: K1 (Serial # 64393) The breaker model is: SACE E6.2V-A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622353&prj=684&rqi=j3czFINjo04hxlGyMzTPNosNwy
RT1MECH-54-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_05 | CRAH - Computer room air handler |  |  | (1CRAH_K_5) L2A Bad fitment of left upper fan door Confirm that CRAH access doors open/close freely and have adequate seals | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622320&prj=684&rqi=VfZsQP9P2OpzN0IgFD2KKugm3k
RT1ELEC-386-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_K3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | (1UMDSB_K3) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1UTX_K3_L1 (Q06) 1UPNL_K3_H1 (Q09) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622337&prj=684&rqi=VGtFEJj59rawX02zwoWfxJYKLk
RT1MECH-59-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_10 | CRAH - Computer room air handler |  |  | (1CRAH_K_10) L2A Filter brace 3 missing bolt | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622348&prj=684&rqi=K177uN9oCVJ5l4vmLCIgpmKrra
RT1ELEC-372-001 | SV18-2 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1GEN_J | GENL - Generator (LV) |  |  | (1GEN_J) L2A Generator Circuit Breaker in GEN_J enclosure is missing the kirk key barrel assembly. The required kirk key for this breaker is: K1 (Serial # 64393) The breaker model is: SACE E6.2V-A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622356&prj=684&rqi=4nAH3o9z9JwCfQL8tuJuv1tFp3
RT1MECH-58-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Cleaning | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_09 | CRAH - Computer room air handler |  |  | (1CRAH_K_9) L2A Bolt missing from filter brace 7. Found as fodder above fan see photos. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622349&prj=684&rqi=3TRQpPN1OaZELRS7lBfuH3JxdL
RT1MECH-52-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_03 | CRAH - Computer room air handler |  |  | (CRAH-J-3) L2A Filter brace weld #7 is broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622316&prj=684&rqi=lSzOzcc33FzXFPPMre9jXEdbRS
RT1MECH-58-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_09 | CRAH - Computer room air handler |  |  | (CRAH-J-9) L2A Broken filter brace welds #1 and 4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622350&prj=684&rqi=FZq2Fa9RofccWgm6PpvY3EMTZG
RT1MECH-57-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_08 | CRAH - Computer room air handler |  |  | (CRAH-J-8) L2A Filter brace weld 8 broken Inspect all sections for dents, scratches, fit, corrosion, etc. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622351&prj=684&rqi=Om7DGg6QsvSCTllg8neSk31MbR
RT1ELEC-387-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UMDSB_R2_3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | (1UMDSB_R2_3) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1UPNL_R2_3_H1 (Q07) 1UPNL_R2_3_H2 (Q08) 1UPNL_R2_3_H3 (Q09) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622338&prj=684&rqi=oSHYScJt8Vk3RDRNBmeabK3LMq
RT1MECH-61-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_12 | CRAH - Computer room air handler |  |  | (CRAH-J-12) L2A Filter brace weld 4 is broken. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622346&prj=684&rqi=3hy2awLaSjvhXFvMGjufXbEvvu
RT1MECH-51-002 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (1CRAH_K_2) L2A dP sensor loose in left upper fan section. Inspect Equipment for missing hardware | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622315&prj=684&rqi=nckh7wRFFx3yEYOjb94ShQqpgP
RT1MECH-50-001 | SV18-2 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_01 | CRAH - Computer room air handler |  |  | (1CRAH_K_1) L2A Filter brace missing 2 bolts. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622312&prj=684&rqi=UHBQKxbEaq7Qn6oOC0m4ecP64Y
RT1MECH-3-004 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-13 04:00:00.000 +0400 | Controls Contractor | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1ACC_R2_05 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers (ACC)) For tracking purposes Heat trace failures create a hardwired fault status to the BMS, creating a latching BMS fault for the chiller skid. Approved solution is to have ETech run an additional wire from the heat trace relay to use as an additional hardwire point to use for ignoring this hardwire fault status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621739&prj=684&rqi=53QKxIVfPFfHXePzkcdzM7T8px
RT1MECH-26-002 | SV18-2 | AMER | Closed | P1 High CX | ethan.hang@veolia.com | 2026-05-13 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_01 | CRAH - Computer room air handler |  |  | (All Data Hall CRAHs) For Tracking Purposes Interconnection between smoke detector and control panel to be completed by Vertiv. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621740&prj=684&rqi=bIovAwC6JJFb2tDv9xhCRD0jaO
RT1MECH-51-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-13 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (1CRAH_K_02) L2A Cable coming off of CAT6 is missing a connection header. Correct photo attached. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621723&prj=684&rqi=I2xix05wSPuAeAAIyciI63cEbO
RT1MECH-3-003 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-13 04:00:00.000 +0400 | TRN - Trane | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1ACC_R2_05 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers (ACC)) For Tracking Purposes Please confirm that all freeze protection valves are modulating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621738&prj=684&rqi=AOcynpAFUs9lhs4epg79GnjWSD
RT1MECH-56-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-13 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_07 | CRAH - Computer room air handler |  |  | (1CRAH_K_07) L2A 3A fuse cover on F5 in the power panel is broken. Replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621735&prj=684&rqi=t8C1OGKkodHlNweHVhaPvmnujU
RT1ELEC-96-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2A MSB breaker labels from the Hanley submittal do not match the electrical one line diagram. Specifically, breaker Q02 does not exist on the electrical one line diagram which causes all other breaker labels to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621157&prj=684&rqi=0NMkPCoI8pSbOJLgYbHSPg2Eh9
RT1ELEC-88-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MDSB_H | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_H) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_H_HP (Q06) 1UPS_H3 (Q07) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621161&prj=684&rqi=Xsj0MsW3iqzNz7Sen8eVJSspOh
RT1ELEC-93-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A MSB breaker labels from the Hanley submittal do not match the electrical one line diagram. Specifically, breaker Q02 does not exist on the electrical one line diagram which causes all other breaker labels to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621152&prj=684&rqi=zjRUt6I0Kspc3eU4PuIUlUbRe7
RT1ELEC-87-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_G) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_G_HP (Q06) 1UPS_G3 (Q07) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621159&prj=684&rqi=E06N8rKNsk7W3w348QD0ymgpIW
RT1ELEC-90-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MDSB_K | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_K) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_K_HP (Q06) 1UPS_K3 (Q07) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621164&prj=684&rqi=p619MusfqhSWu86gylXUq2lq9B
RT1ELEC-89-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MDSB_J | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_J) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_J_HP (Q06) 1UPS_J3 (Q07) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621162&prj=684&rqi=cIrHrEohY9YjxdOsgcLIJy4BvL
RT1ELEC-95-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | (1MSB_J) L2A MSB breaker labels from the Hanley submittal do not match the electrical one line diagram. Specifically, breaker Q02 does not exist on the electrical one line diagram which causes all other breaker labels to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621155&prj=684&rqi=99FA6jQHYmueHs89kADXUrqy4A
RT1ELEC-94-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | (1MSB_H) L2A MSB breaker labels from the Hanley submittal do not match the electrical one line diagram. Specifically, breaker Q02 does not exist on the electrical one line diagram which causes all other breaker labels to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621154&prj=684&rqi=aXjx6QfwZ6ecPfdoOjMldrLXUW
RT1MECH-82-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A At the 2 # doors on the north side, the pull box back boxes are too close to the adjacent switch for the pull station to be installed/door opened. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620461&prj=684&rqi=PFBBKF2yVGTdQoofrplZ3VgG55
RT1MECH-74-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_R2_13 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_R2_3) L2A Pipework has been damaged/cut and isn't holding pressure - needs to be repaired to allow Therma to progress. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620452&prj=684&rqi=xicCfhOmqjPBQ3PUARqrdpGk5f
RT1MECH-91-005 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (1HP_R2_2) L2A Conduit clamps for the disconnect are impeding removal of the filter and will damage the filter on removal and maintenance. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620454&prj=684&rqi=VK1fDfGK2qieCNkjh8meAAisve
RT1MECH-91-006 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Design correction needed | Design | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (R2, and G HPs) Access to the strainer, balancing valve, isolation valves, is very difficult, due to arrangement of fire alarm and various electrical JBâ€˜s in front of them. Issue is not present on J, H, K skids. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620456&prj=684&rqi=20i1UrviByQnBOcdISgvwMY98R
RT1MECH-91-008 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A Speaker strobe boxes at each of the 4 # doors, require an extension box. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620459&prj=684&rqi=5AcVJGYBmZww9vFVVeGBUFBFk4
RT1MECH-26-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | General Design Issue | Design | Mechanical â€“ Water | equipment | 1CRAH_G_01 | CRAH - Computer room air handler |  |  | (All Data Hall CRAHs) L2A Discrepancy between 18-1 and 18-2 leak detection set up. At 18-1, leak detection was installed by MC and placed on the unit INTERIOR, to identify leaks in the coil. Photo attached with yellow rope leak detector. At 18-2 It's a point leak detector on a cable which has a plug on the bottom left of the unit EXTERIOR. Please confirm if this was the intended part shipped out and if so, when it will be installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620430&prj=684&rqi=7rJOaTr30XkLNSsNthB2eAjA3M
RT1MECH-91-007 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (WSHP-R2-2) L2A Power wire at the smoke detectors at the Trane WSHPs has not been pulled. Currently they have only pulled the control wiring that shuts the units down. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620457&prj=684&rqi=0agXM7RNw78iJUaiE1MwOKLQe4
RT1MECH-91-009 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A At the SW doors, the speaker strobe & pull station devices cannot be installed as the back boxes are too close to the adjacent conduit and security JB respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620460&prj=684&rqi=HypS0KVD7mhF2GQPhF7XzeJ1s4
RT1MECH-3-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1ACC_R2_05 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers (ACC)) Putty inconsistently applied to conduit bushings between the harmonic filter and the ACC power cabinet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620317&prj=684&rqi=PQUSL2RUEe3CXCf88O2Ks2zbTs
RT1MECH-91-004 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A Intake hoods need to be installed on the exterior of the skid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620299&prj=684&rqi=AsnwcJavaHK6mHOWTLFcGNku1W
RT1MECH-57-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_K_08 | CRAH - Computer room air handler |  |  | (1CRAH_K_08) L2A Left side coil has no pressure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620286&prj=684&rqi=WbFhoVBcZIc4MCBV9ZYV1Ehob5
RT1MECH-45-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_08 | CRAH - Computer room air handler |  |  | (1CRAH_H_08) L2A Left side coil holds no pressure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620283&prj=684&rqi=vezkIFnxm6zfP4429R4r3G2K39
RT1MECH-6-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | TRN - Trane | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1ACC_H_13 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_H_13) L2A N5 jumper in control panel is missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620292&prj=684&rqi=qZOE6eREhfuEp4Mqy6HDLzbtL3
RT1MECH-82-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A Intake hoods need to be installed on the exterior of the skid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620300&prj=684&rqi=0McX65Tys3cbh7XjH1fPlEtPsr
RT1MECH-91-001 | SV18-2 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A At the south end of the PH, the drain valve on the CHW supply line, extends laterally over the UPS. Piping should be modified so it drops down vertically so as to eliminate the possibility of water dripping on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620294&prj=684&rqi=TgMkibLWU0ZzTF8U1ws1O4vdx3
RT1MECH-46-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_H_09 | CRAH - Computer room air handler |  |  | (1CRAH_H_09) L2A Right side coil has no pressure. Needs circuit setter housing gasket and flange weld repair on the return side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620285&prj=684&rqi=Slo2NmqNxmOVAeyFyT8P5rg2U1
RT1MECH-90-001 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L2A A number of joints on the ductwork have not been sealed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620297&prj=684&rqi=QpGUlQV2O8QkCEHdFoZS3wlBqB
RT1MECH-91-002 | SV18-2 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A Where insulated CHW lines are supported by unistrut, shields are missing in a couple of locations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620295&prj=684&rqi=cWpPIjfl0vvERfQwNlzlCFRyHC
RT1MECH-91-003 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (WSHP-R2-2) L2A No CAT 6 cables pulled to WSHP (R-4800 & R-4900 on MPS submitall dwg MPS.522). Associated conduit required as well, see Skid H for example of complete install. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620296&prj=684&rqi=pDynH7X5GIA2Z2m6hmXrAYOz8G
RT1MECH-35-001 | SV18-2 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CRAH_G_10 | CRAH - Computer room air handler |  |  | (1CRAH_G_10) L2A Left side coil holds no pressure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620298&prj=684&rqi=D7vCsmGiWRteSeagakmDFjn4Yy
RT1ELEC-81-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-04-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1BTU_G | BTU - Battery Tripping unit |  |  | (1BTU_G) L2A '1BTU_G ground plate 4' connection is not made up correctly. Please refer to attached photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619367&prj=684&rqi=lltGWQMWkNpdp8ywcPCvmV2Qlo
RT1ELEC-97-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-04-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB_R2) L2A MSB breaker labels from the Hanley submittal do not match the electrical one line diagram. Specifically, breaker Q02 does not exist on the electrical one line diagram which causes all other breaker labels to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618581&prj=684&rqi=6lHHQ6sxq7ER7h5sc1WgM6qOw5
RT1ELEC-92-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-04-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R2_2 | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_R2_2) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_R2_2_H1 (Q02) 1PNL_R2_2_H2 (Q03) 1PNL_R2_2_H3 (Q04) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618585&prj=684&rqi=fm5mdCSrwic8y0kZLf8jkvgJJz
RT1ELEC-91-001 | SV18-2 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-04-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Incomplete Connections | Commissioning | Electrical â€“ LV | equipment | 1MDSB_R2_1 | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_R2_1) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_GEN_R2 (Q02) 1PNL_R2_HP (Q05) 1UPS_R2_3 (Q07) 1UMDSB_R2_3 (Q08) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618583&prj=684&rqi=PR4HM70Mz3XwTqNMHf5WSmn7DV
L2L3 Sun-27-002 | SY05-4 | APAC | Open | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-09-14 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | Communications | equipment | SY5-FCMS-9A | FCMS Outstation |  |  | TMD-M-SY5-4 (Ethernet cables and junction box loose inside of FCMS Panel) The DCOS junction box and ethernet cables are untidy inside the FCMS 9A Panel. See image attached. Can these be installed neatly inside the panel. Please provide evidence of work completed before moving to Ready for verification. If not ready, please leave a date on when the works can be completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637856&prj=644&rqi=wKsuFu1pW28J8eUsyr3U83q1by
L2L3 Sun-27-001 | SY05-4 | APAC | Open | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-09-14 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | Communications | equipment | SY5-FCMS-9A | FCMS Outstation |  |  | TMD-M-SY5-4 (Missing gland in FCMS Panel) A hole in the bottom of the FCMS Panel where the temporary power cable is coming through is missing a gland. See image attached. Please upload evidence of gland installed before moving to Ready for Verification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637855&prj=644&rqi=PaydDcP2ioZ9CF2HAuxSC9rcFQ
L2L3 Sun-33-001 | SY05-4 | APAC | Open | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-09-08 04:00:00.000 +0400 | General Contractor - BMS |  | Documentation not issued/ Required | Commissioning | Communications | equipment | SY5-FCMS-10A | FCMS Outstation |  |  | TMD-M-SY5-4 (Crossmuller to supply completed panel drawings) Crossmuller have developed red line drawings due field device changes terminated in the panel. Crossmuller to convert red line drawings to complete drawings and supply physical copies in the panels SY5-FCMS-10A & 10B. Same issue applies for panels SY5-FCMS-9A & 9B as they have the same changes made. Please provide evidence of completion of works before pushing to ready for verification. Alternatively leave a comment on when works will be completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637137&prj=644&rqi=AtzDqVMcsIaVlYbPVLtx35AXmb
GI-131 | SY05-4 | APAC | Closed | P3 Low CX | steven.hoang@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | General Contractor |  | DCOS Design Issue | DCOS | [6 empty] | SH-E-SY5-4 (DCOS Graphic Queries) Graphics for STS does not specify where they are receiving supply from EG CB number. It also does not specify which STS is supplying which UDB. Can the template be modified to show text labelling on graphics or is this an approved and agreed graphic design? This issue is raised for the purpose of understanding, tracking and improvements of graphics. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636625&prj=644&rqi=8MbST90JNxpG34ALTIvAqjvag8
GI-125 | SY05-4 | APAC | Open | P3 Low CX | steven.hoang@bureauveritas.com | 2026-08-24 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | SH-E-SY5-4 (A9 UDB FAT Missing) FAT Documents Missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634982&prj=644&rqi=IDykWVC43MfQjEpQzVL6JZa3kn
GI-124 | SY05-4 | APAC | Open | P3 Low CX | steven.hoang@bureauveritas.com | 2026-08-24 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | SH-E-SY5-4 (A13 UDB FAT Missing) FAT documents missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634981&prj=644&rqi=xA1gUh7gdCZyfKIltNL9od8bKr
GI-120 | SY05-4 | APAC | Open | P3 Low DCOS | steven.hoang@bureauveritas.com | 2026-08-17 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | SH-E-SY5-4 (No Analogue values on GSB08) - DCOS Mapping Incorrect for GSB breaker up stream of A9 MVTB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634009&prj=644&rqi=07pqDVmh968OmX8ocjDqGHAtgZ
GI-116 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-14 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | ##SY5-4-E-AOB (COLO13-DAZZA PDU LABELLING) Issue to be raised as assets are being energised for tracking, this is part of the L2 scripts. Understanding they have been ordered. Labels (on order ##Push Issue) PDU-7A PDU-32A PDU-48B PDU-47B PDU-46B PDU-46A PDU-47A PDU-48A TEMP label shave been placed to coverer the energisation process. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633732&prj=644&rqi=6eeSdKoVhCkFIIuPQKNb7wwY3l
GI-118 | SY05-4 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-14 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [6 empty] | SY5-4-E-AOB -Earth Grid / Bar Field Test (CxL2A, CxL2B) Raising this for tracking as no clear asset for this on FG, open to add an earthing asset if this works. FIC003 â€“ Earth Grid / Earth Bar Field Testing is currently planned to be completed as a single activity at the end of the project (longest distance testing point) rather than progressively for each room/area prior to energisation. From a commissioning perspective, progressive completion and recording of earth grid/earth bar testing for each room as it is handed over and energised would provide improved traceability and verification throughout the staged energisation process. This comment is recorded to ensure the item remains visible and is not overlooked during the course of the project, particularly given the staged nature of energisations and potential personnel changes prior to project handover including the CxA team. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633734&prj=644&rqi=vLMMx5zzwELjoTo5NM7OXs4dLz
GI-115 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-14 04:00:00.000 +0400 | General Contractor |  | Incomplete Connections | Commissioning | [6 empty] | SY5-4-E-AOB COLO13 DAZZA (UDB/PDU Common Issues) Raising for tracking, before EE. PDU-26A - loose CT terminal block HDPM6000 PDU-28A - has a loose cable crimp above the fuse F1 HDPM6000 PDU-29A - paper above the HDPM6000 to be removed & cable crimp on top of power terminals PDU-31A - CT terminal block HDPM6000 disconnected & cable crimp above meter which needs to be removed PDU-32A - isobar cover above the PM and loose CT terminal block HDPM6000 PDU-32A - loose CT terminal block HDPM6000 PDU - 39A - loose CT terminal block HDPM6000 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633731&prj=644&rqi=wEKNk7yHW3C4deZutvuezXNfNQ
GI-117 | SY05-4 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-14 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [6 empty] | SY5-4-E-AOB (PDU-COLO13-DAZZA Cable Routing Across Unprotected Metal Edge) The cable entering the assembly is routed across a metal cut-out without any grommet, edge trim, or mechanical protection. The cable sheath is in direct proximity to the sharp edge at the cable entry point. The installation presents a risk of cable sheath abrasion and insulation damage due to contact with the metal edge. This condition is not considered good installation practice for cable protection and may impact the long-term integrity of the cable If this arrangement is intentional and forms part of the Schneider Electric design, please provide confirmation that the cable routing has been assessed and that the risk of cable wear against the metal edge over the operational life of the equipment is accepted by the design authority. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633733&prj=644&rqi=lw0kam1W58gcHKv5uEzZHCoaZg
GI-113 | SY05-4 | APAC | Closed | P3 Low CX | steven.hoang@bureauveritas.com | 2026-08-12 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [6 empty] | SH-E-SY5-4 (R2-OSB-09A & R2-OSB-09B) - R2-OSB-09B STS-05B graphics showing Open close position but does not show trip position - R2-OSB-09A STS-05A graphics showing trip position and unable to be cleared to show open & close positions. - R2-OSB-09A & R2-OSB-09B Missing Comms cable connection from ACB to Comms Outlet. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633382&prj=644&rqi=w3ygYisYS9CwplhJRztVOVu4KG
GI-114 | SY05-4 | APAC | Closed | P3 Low CX | steven.hoang@bureauveritas.com | 2026-08-12 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | SH-E-SY5-4 (A9-STS-01A - 08A & A9-STS-01B - 08B) - Permanent labels indicating Sources 1 & 2 supply not present. Issue raised for tracking purposes | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633386&prj=644&rqi=48WxTwM0dKdWVvd8XfYm3mHcNj
GI-112 | SY05-4 | APAC | Open | P3 Low CX | steven.hoang@bureauveritas.com | 2026-08-06 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | SH-E-SY5-4 (CALIBRATION CERTIFICATES FOR FAT EQUIPMENT) L1 FAT Documents reference 3 types of testing instruments. The uploaded equipment certificates do not match what was used during FAT. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632686&prj=644&rqi=4waUPaF98M03Xm63C5z8ZuTVKd
GI-111 | SY05-4 | APAC | Closed | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-08-05 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | TMD-M-SY5-4 (Fed from labels needed for A9 & A10 MCPs) Power source fed from labels are needed for the MCPs in A9 & A10. Temporary Labels ahave been applied. Issue raised for tarcking. Please provide evidence of completion of wo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632395&prj=644&rqi=1BCdAwYC1XKvp9Ja6q0fG6k2Q3
GI-102 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-01 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | AOB-E-SY5-5 (Delivery Documentation Outstanding) Delivery documentation is outstanding. Acceptance dockets and supporting delivery photographs have not been provided/uploaded for review. These records are required to verify equipment receipt, delivery condition, and completion of project documentation requirements. A09-BAT-01-18 A09-MSB/OSB-01 A09-EDB-01 M5-02-BAT-01-03 M5-02-UPS-01 A10-BAT-01-18 A10-MVTB-01 A10-BTU-01 A10-TRX-01 A10-EDB-01 SY5-R2-OSB-10A SY5-R2-OSB-10B A10-MSB/OSB-01 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631970&prj=644&rqi=30u0i4jf9i2VGyOzrETXWK4Ath
GI-105 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-01 04:00:00.000 +0400 | General Contractor |  | Incomplete Connections | Commissioning | [6 empty] | SY5-4-AOB-E-R2 09A & 09B OSB Busduct Elbow Connections Issue raised to facilitate YT The final elbow connections for the R2 09A & 09B OSB busducts remain outstanding. Once the busduct is connected, the asset will have a direct connection to the R2 lineup redundancy block on live facility, creating the potential for energisation. The OSB's require to be Yellow Tagged prior to the final elbows being installed. This issue has been raised to track the outstanding works and ensure the appropriate controls are in place before connection to the live facility. Issue can be close upon final connection and test result upload. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631975&prj=644&rqi=oT20O57sEII2ftPBj05bv8vV7J
GI-098 | SY05-4 | APAC | Closed | P3 Low CX | steven.hoang@bureauveritas.com | 2026-07-27 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | AOB-E-SY5-4 (A09-BTU-01) ##LV FIC001 cable dead test and fed from label AC Cable not connected Raising this for tracking only as EDB is not ready. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630992&prj=644&rqi=ZmzoYBfCpWj75q928Ro02ZcIVV
GI-097 | SY05-4 | APAC | Ready for Verification | P3 Low CX | steven.hoang@bureauveritas.com | 2026-07-27 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [6 empty] | AOB-E-SY5-4 (A02 & A09-BTU-01) TAPE Residual on Front Door No Visible Torque Marks on Battery Terminals No Cable Label No Panel Label No Battery Manufacturing Date DC cables not Connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630991&prj=644&rqi=ltLxRb2C1JsL7O29nPF0CzvNVW
GI-091 | SY05-4 | APAC | Closed | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-07-05 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [6 empty] | TMD-M-SY5-4 (Variation of DCOS terminations to A9 MCPs) Termination blocks had to be added to the MCPs to facilitate Crossmuller terminations. Crossmuller to add this to their ITPs to show these works have been completed in the A9 MCP & FCMS Panel Upload ITP with comments of work variation to MCP or FCMS Panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627969&prj=644&rqi=sGiTvBS3fWq2Ep3cPfmcRvg5fP
GI-078 | SY05-4 | APAC | Closed | P3 Low CX | raluca.bastucescu@bureauveritas.com | 2026-07-01 04:00:00.000 +0400 | General Contractor |  | Cleaning | Commissioning | [6 empty] | A2 Switchroom to be cleaned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627660&prj=644&rqi=0CeeFx9qJ4lUd5xmjSjlhw9kqZ
GI-074 | SY05-4 | APAC | Open | P3 Low CX | raluca.bastucescu@bureauveritas.com | 2026-06-30 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [6 empty] | TRACKING PURPOSES ONLY - VERTIV PURPOSLY REMOVED AP22-X1 cable in UPS Prior to L3 Cx Calibration Activities. Vertiv will put it back once calibration activities are done. Will be closed once Vertiv have completed the tasks. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627482&prj=644&rqi=tNaXAkX1DoYbEVe3KQHCYSinh0
GI-067 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-06-25 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [6 empty] | No visibility of the Earth bonding as this is in underfloor containment. BVPI cannot validate the underfloor containment bonding, test results of bonding and earthing to be reviewed for site / area / sub area. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627029&prj=644&rqi=8Vrzf3KpeyruZwUBY8yFVPe5qK
GI-059 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-06-17 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [6 empty] | AOB-E-SY5-4 (A2-MVTB TEMP POWER APPROVAL) Loop & Good Testing Outstanding. Hi @Satheesh Kumar Natarajan, To allow Cx activities to proceed and keep the program moving are you happy to authorise the temporary supply works on A2-MVTB for testing tomorrow morning? This was the first room where we walked earlier today. o Remaining L2 testing (except Loop), see attached, have been completed & witnessed today by BVMC (awaiting documentation upload to FG) ï‚§ Loop Feeder Testing (##Push issue to be raised to track this 29.06) Team, Moving forward, the first priority and aim is to have tags signed off and in place first, as this is what firstly enables permanent / temp energisation, if this not achievable and as per the MVTB scenario can you please ensure the Cx team are aware and present in the room to ensure the correct chain of approval is being followed to allow an issue to be raised for tracking and to ensure this is pre-approved. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625770&prj=644&rqi=4EDKl7fLTO9m9NMmbhLIpVDdLp
GI-058 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-06-16 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | AOB-E-SY5-4 (A09 & A10 TRX NAME / SERIAL / RATING PLATE) Physical rating plate visibility/access may be limited, or details have not been captured during installation/inspection. Transformer nameplate information (TRX ID, serial number, rating plate details) not installed on the newly delivered assets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625557&prj=644&rqi=37UXpbfEvPEThYAWOX6rI86C2q
GI-056 | SY05-4 | APAC | Closed | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-06-14 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [6 empty] | TMD-M-SY5-4 (Ceiling Tiles not modified for CRAH Units) Modification of ceiling tiles above the new 14 CRAH units (7 in COLO1 & 7 in COLO 2) have yet to be completed. L2 Tagging has been pushed back due to incompletion of construction works. Please provide evidence of completion of works. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625255&prj=644&rqi=o4ndlt3OqJDK710i4hpH5VCQvG
GI-055 | SY05-4 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | **QC**AOB-E-SY5-4 (M5 & M6-02A ROOMS EXTERNAL LABELING) External Room labeling currently shows storeroom, this needs to be labeled prior to energisation of any power within this room., this clearly identifies the room in the event of a fault or safety issue. Supporting photo to be uploaded. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623853&prj=644&rqi=xoLNBNbdTb927k7sPEGXlxpRJU
GI-054 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | General Design Issue | Design | [6 empty] | AOB-E-SY5-4 STS Panel Openings â€“ Foreign Object & Live Risk This design has been used around the site in all previous phases, Vertiv to comment and acknowledge the risk The Static Transfer Switch (STS) panel has open penetrations on the top of the enclosure (roof). These openings present a risk of foreign objects (e.g., nuts, bolts, tools, debris) falling directly onto internal live electrical components. Operation in bypass mode, where the system is configured to allow maintenance. In this condition, the top (isolated) section of the panel is de-energised, however the bottom section remains live with no physical separation or internal barriers. This creates a risk where tools, fixings, or debris can fall through the top openings and come into contact with energised components below during maintenance activities. During maintenance temp separation will be required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623850&prj=644&rqi=nzQYsloVNCwYs6pOTfs63Jl87c
GI-052 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-05-25 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | AOB-E-SY5-4 (A2 STS L1/L2 Documents) â€¢ Equinix â€“ SY05 Phase 4 â€“ STS â€“ GA Drawing â€¢ Equinix â€“ SY05 Phase 4 â€“ STS â€“ Product Description â€¢ Equinix â€“ SY05 Phase 4 â€“ STS â€“ Cross Cabinet â€“ User Manual Screenshot below showing how to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623066&prj=644&rqi=mfkx0Lz8qBjRxobyhS610dpoEZ
GI-053 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-05-25 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | AOB-E-SY5-4 (A2 STS Calibration Certs) Cal certs required for the below FAT & L2 QA/QC ITP testing. 02A 02B 08A 08B Screenshots below | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623067&prj=644&rqi=EwgGAxKKyenV24HBEFTlHJYOVr
GI-051 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-05-25 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | AOB-E-SY5-4 (A2-STS IDENTIFICATION LABEL's) - Main Label - Fed From (S1&S2) 02A 02B 08A 08B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623063&prj=644&rqi=eIHuSnoh3c5F0jeHWwRcL1RD5T
GI-050 | SY05-4 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-04-29 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | **QC**-AOB-E-SY5-4 COLO13 PDU FED From labeling to be addressed and made site location applicable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619986&prj=644&rqi=XtCBap69BU7mWjrAnYEJuQk6Qm
GI-049 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-04-21 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [6 empty] | AOB-E-SY5-4 (A11 to A12 MVTB VLF CONSTRAINTS) The EC has flagged the risk that the â€œloopâ€ line from A11 to A12 MVTB cannot be re-VLF tested at 80% due to the . Since the cable has been cut and terminated loop in/out of MVTB-A12. Missing the VLF testing provides the risk to verify that the cable will withstand normal operating voltage, will the splice hold up. As of 21.04.2026 BVPI had been informed megger testing can still be performed with the removal of VTs/CTs within A11-MVTB which will prevent the risk of trips. Please provide Comments of next steps to move forward. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618935&prj=644&rqi=5xKfdShxjHUAnC0FrA94iiaz41
GI-046 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-04-20 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS | [6 empty] | AOB-E-SY5-4 (UPS DCOS POINT ERROR BCB) Screenshots and photos to be provided to close out this issue Testing Battery Breaker Open, graphic shows Output Breaker Open getting Output breaker Open and should be Battery breaker Open check Alarm - need to be checked again when testing load we need Output breaker Open alarm active to compare Modbus register This point is reversed on the Modbus register Testing Output Breaker Open , graphic shows Battery Breaker Open, getting Output breaker Open and should be Battery breaker Open check Alarm - need to be checked again when testing load we need Output breaker Open alarm active to compare Modbus register | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618796&prj=644&rqi=PZxzErUw3r27kmNxKedQMjNHet
GI-047 | SY05-4 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-04-20 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | **QC**-AOB-E-SY5-4 (A1 & A2 UDB LABELING) Updated Labeling to be printed and applied against the below assets. A1-UDB-02A A1-UDB-02B A2-UDB-02A A2-UDB-02B A2-UDB-08A A2-UDB-08B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618805&prj=644&rqi=qjH23RrgmrY5jVQ6YJt1mpY8wC
GI-038 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-04-07 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | AOB-E-SY5-4 (A12-TRX - Documentation Outstanding) Factory Reports - Hitachi to provide Delivary dockets - Hitachi to provide As-Builts (attach as a bulk item to all TRX assets) - Hitachi to provide A12 Equipment layout - WIP - I need to investigate to confirm the status of these submissions. Documents attached to MVTB FIC002 Control Cabling - Uploaded 7/4 FIC012 HV Comms cabling - Uploaded 7/4 FIC-003-Earth Grid-HV- Uploaded 7/4 FIC016 HV Cable Test Cx Reports - Uploaded 7/4 FIC037 : Attached to documents but not visible on the asset (if these can be attached to the asset please) - I need some assistance with linking the documents FIC016 : Attached to documents but not visible on the asset (if these can be attached to the asset please) - I need some assistance with linking the documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617466&prj=644&rqi=00D0IoYS8ja4EO0cH9luIw0pgR
GI-032 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-25 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | ##SY5-HSB & GSB No Asset Identification Labels on new incomer / outgoing GSB and HSB for the new assets installed across the site issue applicable to SY5 site wide | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616469&prj=644&rqi=90dcevNgaldhpIa23Eqf06im8D
GI-030 | SY05-4 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-25 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [6 empty] | **QC**-AOB-E-SY5-4 (SCADA / GSB / HSB / ELEC ROOMS SLD) Single Line Diagrams (SLDs) for SCADA, GSB, HSB, and ELEC rooms are outdated and do not reflect recently installed equipment on the SLD. Updated to cover site wide once IFC drawings are approved, Red lines to be completed in the interim . Current diagrams lack new assets, updated electrical connections, circuit configurations. This impacts maintenance procedures, emergency response accuracy, compliance records, and personnel safety. Updated SLDs are required to align with current installations and ensure accurate reference. All HSB / GSB / SCADA ROOMS AND ELEC Rooms to be updated as required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616448&prj=644&rqi=Of4flFTEJpFAbBBQU2iDkqMSDS
GI-031 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-25 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [6 empty] | AOB-E-SY5-4 (A12 -MVTB LOOP CONNECTION) connection & testing outstanding Raising push issue to allow Red & Yellow Tags to be installed This issue will track the full Cx process and testing of the outstanding MVTB works, pending CR date of 20th April | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616468&prj=644&rqi=ZZrYiwV5ynQuBPkz7csy59LgGo
GI-028 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | SY5-4 PDU AS-BUILT Drawings CB reflect 32A EQX & Grog the costumer has upgraded the brakers to 63A for customer requirements | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615950&prj=644&rqi=BztutoJ7PRCugLHoAftDq65pas
GI-027 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning | Commissioning | [6 empty] | SY5-4 GEN17 & 18 Load Testing @ 1.0 PF SY5-4 - Cummins Generator Power Factor Requirements Hi YK Aaron has just been asking me last week about the power factor requirements for the GENs at SY5-4, I know the site based load bank which is unity has been agreed upon but I can't find the correspondence, Are you able to share please? We're now hyper aware of ensuring we have a track of all agreed deviations from the playbook Thanks very much Matthew KERRIGAN Program Manager Wed 18-Mar-26 11:44 AM Hi Matt, We have a FoK 4hrs load test in Sydney factory due to new enclosure manufacturer.. it will be 0.8pf load bank test.. As onsite, we only have 1pf load bank and many onsite units have been done with 0.8pf, thus, we will proceed with using onsite 1pf load bank for site testing.. Cheers Y.K Choong Senior Commissioning Manager More secure, more connected, more sustainable. Learn more about Equinix Australia. EQUINIX PROFESSIONAL SERVICES, DATA CENTER ¦ 578 Lorimer Street, Port Melbourne, VIC 3207, Australia E ychoong@ap.equinix.com ¦ M +61418 614 393 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615925&prj=644&rqi=iCtbsLD27w52Ic2y2mdTnEOztU
GI-024 | SY05-4 | APAC | Closed | P3 Low CX | jade.pries@bureauveritas.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Cleaning | Commissioning | [6 empty] | All CRAH units to be properly cleaned on dust and debris prior to energising units. Dust, insulation and footprints present in unit internal chambers and trays. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615761&prj=644&rqi=ZCN4ds4HFiDxhLBOHhJnvjxgrF
GI-026 | SY05-4 | APAC | Closed | P3 Low CX | jade.pries@bureauveritas.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [6 empty] | Tiles require cutting so that return air path is clear and free of restriction. All CRAHs to be checked. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615770&prj=644&rqi=I6FOMu2X7XXqcZ1gAU2G4nMkLu
GI-023 | SY05-4 | APAC | Closed | P3 Low CX | jade.pries@bureauveritas.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Installation Damage | Commissioning | [6 empty] | Damage found on CRAH unit locks and scratches found to front covers. CRAH units 29 and 30 - Have damaged locks CRAH unit 34 - Scratch to front panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615756&prj=644&rqi=2igrAz7Py3XWBSyCcWddEGiWzh
GI-025 | SY05-4 | APAC | Closed | P3 Low CX | jade.pries@bureauveritas.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Torque required | Commissioning | [6 empty] | Earth terminals to be torqued and marked in all CRAH units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615766&prj=644&rqi=lMrJzmCu8T2mkKp4FSwEwK9drG
GI-022 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-15 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [6 empty] | ## #STW-MOP-020 - MDB to EMDB Cutover (COLO14 M5-EMDB) Raising push issue to track the energisation of M5-EMDB-01 with SUB circuits outstanding which fall under MOP-020 M6 EMDB Central Feeds Terminated & Energised > Board will then be de-energised and made safe to install CRAH circuits in COLO14. Panel chart/schedule for CBs to be updated once all sub-circuits are installed This push issue will allow L2A & L2B Tags for initial energisation to test submains before MOP works. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615686&prj=644&rqi=9NPFCKpTrGdaberOcIotdzPBxP
GI-015 | SY05-4 | APAC | Open | P3 Low DCOS | aaron.obrien@bureauveritas.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | **QC**AOB-E-SY5-4 (A12-PDU LABELING) No Asset Identification Labels on PDU's - Issue applicable to all Colo 14 PDU's. PDUs have no fed from or permanent assets tags leaving it unclear to the user if an urgent isolation is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615151&prj=644&rqi=Iv4ExqspRRzrJiBjRNVr3ZpE98
GI-016 | SY05-4 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | **QC**-AOB-E-SY5-4 (A12-UDB LABELING) No Asset Identification Labels on PDU's - Issue applicable to all Colo 14 PDU's. PDUs have no fed from or permanent assets tags leaving it unclear to the user if an urgent isolation is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615153&prj=644&rqi=Swem0Tmz3Yn5hqSOievIAqyKrf
GI-013 | SY05-4 | APAC | Closed | P3 Low CX | luke.kerin@bureauveritas.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | GSB-12 Panel 03 & 04 Permanent feeder labels not affixed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483493&prj=644&rqi=zX7cTIsUUT6yr0CJHj1W2VZlF3
GI-002 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-01-06 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [6 empty] | SLD (Panel Drawings) RED MARK terminal numbering to be updated on all pages to reflect relay terminal numbering on A11 MVTB Schneider team working on this internally | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196409&prj=644&rqi=FMAkuz0FJvENZOspECCox0uob3
GI-001 | SY05-4 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-01-06 04:00:00.000 +0400 | General Contractor |  | Component/Equipment Failure | Commissioning | [6 empty] | A11 MVTB Relay K06 (Contact Sticking) Latching Cubicle 103 Schneider HV have replaced this K06 contactor and re-tested the new relay. Tracking purpose as a component has been changed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196407&prj=644&rqi=QkqJdQgf47W9LqlBZco1nYT3E4
GI-043 | SY09x-2 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-18 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | Error | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615923&prj=528&rqi=A1e3wGIncmbUDmrK9014DvOpRM
FPT-269-001 | SY09x-2 | APAC | Closed | P1 High CX | matthew.kerrigan@bureauveritas.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L4 | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | This issue is being raised due to directed works from Equinix to Hanley not yet being performed. Earlier in the project there was a clarification required from Equinix regarding the control wiring of the PQAs in all MSBs across site. This is related to the alarms through the PM8000s where the power meter is used as a gateway to the DCOS Equinix provided clarification and direction to modify wiring. Due to this and the relative simplicity to resolve an issue was not raised however now BVPI has no choice as they are not completed and will delay project progression to L5 Issue is related to L4 activities. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198822&prj=528&rqi=sF0WLzXSTeyTVnjEqwFkLOCcCY
GI-025 | SY09x-2 | APAC | Closed | P3 Low DCOS | sulaiman.khan@bureauveritas.com | 2026-01-28 04:00:00.000 +0400 | Equinix Design Engineer |  | Commissioning Issue | Commissioning | [6 empty] | CHWP-M4 - FT04 has no value mapped to it in DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197697&prj=528&rqi=Tdq5Bcvwx4CFv1kKPyGrgxn7yP
GI-239 | SY09x-2 132kV Substation | APAC | Open | P2 Medium CX | CiaranConlon@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | General Contractor |  | Component/Equipment Failure | Commissioning | [6 empty] | UPS inside comms panel 2-HMTX-2-CP is alarming and needs to be investigated and possibly replaced by Ausconnex. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636231&prj=562&rqi=S44hpAg7lXNzJsHvkuWF4E20ca
GI-233 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - 7UT85 Relays - Slight discrepancy seen in settings installed against IFC Grading Study. Settings to be confirmed. See screenshot for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625568&prj=562&rqi=ipwjEZrQskJQqvuUBs6CKljGbf
GI-236 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - HMTX TMR/AVR - PT100 Device displays ER2 (Sensor interrupt) error message across all transformers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625574&prj=562&rqi=GqMMWLxjcYQMiUrve9JSZZK2O7
GI-232 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2B - 132kV Cabling - Plus ES Calibration Certs to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625244&prj=562&rqi=ieqQEWyytXCnKJqgK3wCHi8XHp
GI-229 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 Switchroom & Controlroom - Filters to be installed within vents at access doorways to Switchrooms and Controlrooms. See photo for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623736&prj=562&rqi=QRhoor1epQz5AYe1jti3qqbPXs
GI-230 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10 Switchroom & Controlroom - Filters to be installed within vents at access doorways to Switchrooms and Controlrooms. See photo for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623737&prj=562&rqi=dzVzzoakMjAJcV16HHroXZRRx8
GI-226 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - SY10 Switchrooms - FCU Labelling incorrect / cable supplies installed in incorrect orientation. When isolating specific FCU in switchroom the alternate FCU is isolated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622758&prj=562&rqi=oTusikrsYMIICH0rYMpXzG3zsc
GI-225 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - SY9 Switchrooms - FCU Labelling incorrect / cable supplies installed in incorrect orientation. When isolating specific FCU in switchroom the alternate FCU is isolated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622757&prj=562&rqi=4aPnuOqHgbqIoXWnWSHzdTXtGe
GI-224 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL3 - 2-HMTX-1-PP & 2-HMTX-2-PP - Transformer Protection Relay No.2 has intermittent comms losses to DCOS. Causing repeated comms alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621543&prj=562&rqi=kgAwsRNV3uXzQ7TcF9gK5v3PBT
GI-223 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL3 - 1-HMTX-1-PP & 1-HMTX-2-PP - Transformer Protection Relay No.2 has intermittent comms losses to DCOS. Causing repeated comms alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621542&prj=562&rqi=tvapZE8u0atavl19NKV32Ksyn5
GI-222 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ LV | equipment | 1-MDSB-1 | MDSB - Mech Distribution Switchboard |  |  | CxL2A - 1-MDSB-1 - Exhaust Fan Label shows incorrect On/Off position. Label shows EF On when it is Off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621532&prj=562&rqi=hlAARdkAgJjGX3UXDnmkmbSVzr
GI-219 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 - Sealing of the floor tiles at door entry of the control / switchrooms yet to be completed (GHD Issue) See photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620887&prj=562&rqi=qteGpOSLsDpXeT3vCwgAkDsCP5
GI-207 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 132kV Cabling Link Box - Links removed for purposes of testing to be reconnected, torqued and marked on completion of CxL2B testing. Some dust found in link box. Link box to be cleaned. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620859&prj=562&rqi=v6oXC4ZvNH5WmHe2fCVb6A9Q5i
GI-211 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 Cable Pits - Cable Pits to be sealed against rainwater accumulation (GHD Issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620878&prj=562&rqi=ZecKs1JWLeHoyaG8I4cs7k7cY6
GI-214 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10 - Arc flash labels to be installed as mentioned in SYSS1-1-RPT-EL-691.3S Arc Flash Study Report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620881&prj=562&rqi=5BkRw41hraAcyeGbG9yUCxkB1A
GI-215 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 - Excess lengths of earth connection bolts in control room yet to be cut off (GHD Issue) See photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620883&prj=562&rqi=sc2T7wbuV6TXTdwp9dZE1SlI8t
GI-210 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10 132kV Cable screens - Cabling currently secured to supporting structure using plastic cable ties. Correct means of securing cables to be confirmed and updated if required. Potential requirement for cleats or stainless steel. See photos for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620863&prj=562&rqi=NjcdeY4VFHTdpv4WRgsakBHMnY
GI-218 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10 - General cleaning required in transformer bund area. Dirt & Debris to be cleared, Rope in cable ducts o be cut back. Stains on the floors of transformer bunds yet to be removed (GHD Issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620886&prj=562&rqi=Foa1xHSHSqu0dikxejqtvXoqkc
GI-206 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ MV | equipment | 2-HMTX-1-K2 | HVCABLE - Aerial Flexible Conductor |  |  | CxL2B - 2-HMTX-1-K2 - Ductor Test results missing for C Phase PG Clamp. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620851&prj=562&rqi=n2NwIC1upbmPxm9gxjvwyDTYUX
GI-221 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9B - Earth connection cable within the SY9B transformer bund to be securely clamped to the bund wall (GHD Issue) See photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620889&prj=562&rqi=8Adkr4Z3kgkRJM1bNdqyBxIjEb
GI-209 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 132kV Cable screens - Cabling currently secured to supporting structure using plastic cable ties. Correct means of securing cables to be confirmed and updated if required. Potential requirement for cleats or stainless steel. See photos for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620862&prj=562&rqi=A23bbIAmksGRUd88TOq0ay2Rc9
GI-212 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10 Cable Pits - Cable Pits to be sealed against rainwater accumulation (GHD Issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620879&prj=562&rqi=yPkUzHzmjqudBBrcyQpnCubNfN
GI-213 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 - Arc flash labels to be installed as mentioned in SYSS1-1-RPT-EL-691.3S Arc Flash Study Report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620880&prj=562&rqi=HHEhB3qCq64wE0YlCv0KpNPGww
GI-208 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10 132kV Cabling Link Box - Links removed for purposes of testing to be reconnected, torqued and marked on completion of CxL2B testing. Some dust found in link box. Link box to be cleaned. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620860&prj=562&rqi=aqedy0WjP8Qln33feiz7QtgPEs
GI-217 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 - General cleaning required in transformer bund area. Dirt & Debris to be cleared, Rope in cable ducts o be cut back. Stains on the floors of transformer bunds yet to be removed (GHD Issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620885&prj=562&rqi=rrKrKzprZqH7KhXrBS1l1ho34F
GI-220 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10 - Sealing of the floor tiles at door entry of the control / switchrooms yet to be completed (GHD Issue) See photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620888&prj=562&rqi=IL8k4UBhZ1HbQsgHEDjWzC86Fd
GI-216 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10 - Excess lengths of earth connection bolts in control room yet to be cut off (GHD Issue) See photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620884&prj=562&rqi=fD2Wy1JRFhrQOY5n03aM7dunBD
GI-204 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-MLTX-1 & 1-MLTX-2 - Various terminations require torque marking. Surge arrestor termination to chassis, Bonding within CT wiring enclosure (at earth bar and to chassis) and bonding within LV compartment. See photos for further reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620475&prj=562&rqi=dVGaJy4LtfVDydg5kWyTf7YQR9
GI-201 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A & CxL2B - 2-MLTX-1 - Report to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620465&prj=562&rqi=rt32Mf7zajjKIjXHyIU01vjXtY
GI-205 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-MLTX-1 & 2-MLTX-2 - Various terminations require torque marking. Surge arrestor termination to chassis, Bonding within CT wiring enclosure (at earth bar and to chassis) and bonding within LV compartment. See photos for further reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620477&prj=562&rqi=N5JRBmmxR9OY4zDTW9J3Fps4Et
GI-203 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2B - 1-MLTX-1 & 1-MLTX-2 - Tap to be adjusted to tap 5. Power Transformer output voltage set to 10.5kV. Auxiliary transformers tap settings to be updated to allow for lower supply voltage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620470&prj=562&rqi=6tvzGUsJJhX07nnBYlFMfaWZIt
GI-200 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 Earthing - Earthing to be torqued and marked at all earth bars and cable connections (Switchrooms and Transformer pit) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618953&prj=562&rqi=pPEFF3udvU3H0qom7gHQnJZdCf
GI-187 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ LV | equipment | 2-BTU-1 | DCDB - DC Distribution Board |  |  | CxL2B - 2-BTU-1 - Report missing cable test reports. Report to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618470&prj=562&rqi=1naSVYhGpLl9V9KcvYKep9kzhQ
GI-196 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ LV | equipment | 2-DB-1 | ACDB - AC Distribution Board |  |  | CxL2A - 2-DB-1 - Middle cover to be installed and door bonding terminated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618484&prj=562&rqi=5PH7Lwu1HggLOOJ2633AzfcjIl
GI-182 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - 1-SUSP-1 & 1-SUSP-2 - MIMIC Labelling to be updated. Panel 1 Incomer currently shows incoming cable as a feeder. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618465&prj=562&rqi=6xZXFplKILfKlf8pBGJKBTtu0n
GI-180 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10B Permanent Labelling to be updated for all equipment and cabling. Includes Equipment, HV Cabling, Submains, Subcircuits and Earthing. Note: In addition to the above SUSP, SEP to be updated. Phase indication for Disco. HV Cabling, Earth Cabling and Subcircuits missing labels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618463&prj=562&rqi=kVeAY4Wlz3e4bhu8xLUi2fhcBE
GI-197 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-HMTX-1 & 1-HMTX-2 - Cable end box works to be completed. Silicone sealing between gland plates to be installed. Bonding between gland plates to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618485&prj=562&rqi=QE6RWMMB6eS6Dap2gUUxAblnBS
GI-181 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-SUSP-1 & 2-SUSP-2 - Thermostats to be set up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618464&prj=562&rqi=2pL7MHQ8ooL5hcP0TRxxUfAkdc
GI-183 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-SUSP-1 & 2-SUSP-2 - MIMIC Labelling to be updated. Panel 1 Incomer currently shows incoming cable as a feeder. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618466&prj=562&rqi=Zlu4XwORugsASmDF857MpsMyuf
GI-192 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Fire Detection | equipment | 2-FIP-2 | FP - Fire Panel |  |  | CxL2A - 2-FIP-1 & 2-FIP-2 - Cleaning required within panel. Dust and debris present to be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618475&prj=562&rqi=uo7TqK4Y0Jz1WaUAEOBYX4ckdm
GI-179 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY10A Permanent Labelling to be updated for all equipment and cabling. Includes Equipment, HV Cabling, Submains, Subcircuits and Earthing. Note: In addition to the above SUSP, SEP to be updated. Phase indication for Disco. HV Cabling, Earth Cabling and Subcircuits missing labels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618462&prj=562&rqi=CVI7mimXUXeOF4BEnKzNGJ17xW
GI-186 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ LV | equipment | 2-DB-1 | ACDB - AC Distribution Board |  |  | CxL2B - 2-DB-1 - Report missing cable test reports. Report to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618469&prj=562&rqi=zlJYhXgBDoFeSE9rJd9Tis11Mp
GI-193 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Fire Detection | equipment | 2-FIP-2 | FP - Fire Panel |  |  | CxL2A - 2-FIP-1 & 2-FIP-2 - Earthing requires torque marks | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618476&prj=562&rqi=pdkYRYS0oDWyVqnMIKusRHxOuW
GI-198 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-HMTX-1 & 2-HMTX-2 - Cable end box works to be completed. Silicone sealing between gland plates to be installed. Bonding between gland plates to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618486&prj=562&rqi=6YZPJ3Nhr4trTFi0cbmlSBjG6U
GI-191 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Fire Detection | equipment | 2-FIP-1 | FP - Fire Panel |  |  | CxL2A - 2-FIP-1 - Unable to access panel. Key sheared off inside lock. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618474&prj=562&rqi=TQguUsp81NJacFJFat6ROtXnLa
GI-177 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - 1-HMTX-1 & 1-HMTX-2 - TMR/AVR Various Equipment Rating settings incorrect. Time Not set correctly. Time Sync non functioning correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617464&prj=562&rqi=A2BvjTSkeDhPTQcJSi7z7opsRt
GI-178 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - 1-DB-3 & 1-DB-4 - Metering not reading current only voltage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617474&prj=562&rqi=Y1bS4WA2fdPMIw65l9oMdEPeBH
GI-173 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-20 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9 Substations - WIFI Router to be affixed to agreed location | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616053&prj=562&rqi=8Sh40XNOxWCJEhH6GUKY8cvL6G
GI-172 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-20 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Communications | equipment | 2-HMTX-2-NP | HMI - HMI Panel (Network Panel) |  |  | CxL2B - 2-HMTX-2-NP - Missing Network cabling test results in report. Updated report to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616051&prj=562&rqi=OViy1srERUJooimRu45U6k2XUq
GI-175 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - 1-HMTX-1 & 1-HMTX-2 - TMR/AVR Cx Reports incomplete, missing various info and attachments. To be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616055&prj=562&rqi=8I4M9sadmU48GXIygCw4QAQJqB
RT1ELEC-1-001 | SY09x-2 132kV Substation | APAC | Closed | P1 High CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Incomplete Connections | Commissioning | Electrical â€“ MV | equipment | 1-HMTX-1-SA3 | HVCABLE - Surge Arrestors |  |  | CxL2A - 2-HMTX-1 & 2-HMTX-2 - Earthing for surge arrestors to be installed. No bonding between arrestors and earth nest. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615916&prj=562&rqi=Zigrrt6neKu4SGZ4R1SYkRwnse
GI-158 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-HMTX-1-NP & 2-HMTX-2-NP - UPS Cabling install incomplete | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615911&prj=562&rqi=3yth1FLOvFMQCVfTZvq0ACom8k
GI-167 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-DB-1 & 2-DB-2 - Heat Shrink to be installed on bare copper at Load side of MTS to DB Section of Switchboard. Top and bottom sections. See picture for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615920&prj=562&rqi=bitgccJID2RnzJqxkX84AD5jn8
GI-165 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - SY10 Earthing - Earthing to be torqued and marked at all earth bars and cable connections (Switchrooms and Transformer pit) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615918&prj=562&rqi=XhYo0PhPuIY60LDFPY8ChaFxxC
GI-160 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - 1-HMTX-1 & 1-HMTX-2 - TMR/AVR DCOS Points not mapped correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615913&prj=562&rqi=2cBzzNZi0XLiePHyGfG6bDpque
GI-169 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2B - 2-HMTX-1 & 2-HMTX-2 - Thermostats to be set up within switchgear. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615922&prj=562&rqi=J9cR59191KERa16kcc3HuAlYKb
GI-170 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-HMTX-1 & 2-HMTX-2 - Dust & Debris present within LCP. Cleaning required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615927&prj=562&rqi=xwAK53YwwNXr1PuzCh5mYEhkue
GI-171 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-MLTX-1 & 2-MLTX-2 - Neutral earth cable needs to be clearly identified as earth/neutral | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615929&prj=562&rqi=nDUtwEVk7b0xl8mtWdDC2Jaue1
GI-162 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-BTU-1 & 2-BTU-2 - Holes in escutcheon on DB to be sealed. 2 x large holes within escutcheon of DB cut out to allow for door to be closed, devices will prevent this presently. Some form of recessed cover to be installed in empty spots to seal up holes. Pole fillers also to be in place where missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615915&prj=562&rqi=vqEu2wr3CXMoY0aG4avYXThSof
GI-164 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-MLTX-1 & 2-MLTX-2 - Extra External Protection needed for 11kV Cables (UV/Water/Mechanical). Cover to be installed over cables to provide extra protection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615917&prj=562&rqi=4OrAe94iFK807APMQFe9G0Gnbn
GI-168 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-HMTX-1 & 2-HMTX-2 - Neutral Earthing to be completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615921&prj=562&rqi=f2O2rN6clpnIF8xQf1K3pObVUq
GI-159 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - 1-HMTX-1 & 1-HMTX-2 - TMR/AVR LED Mapping not programmed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615912&prj=562&rqi=0PX3sHc1zQpzdDChgDiubEB48L
GI-166 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-SUMP-1 & 2-SUMP-2 - Enclosure door screws not fixed. Panel door to be secured. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615919&prj=562&rqi=D9UD7jk4jNEiKyQKANpxPViMjt
GI-161 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-DB-3 & 2-DB-4 - Labelling to be updated. Labelling associated with DB still shows previous naming convention. All small wiring labelling internal to DB and GPO / Light Switches associated with DB to be updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615914&prj=562&rqi=Q95Smc6PeR5R1EjAF2wMcDaIte
GI-151 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ LV | equipment | 2-DB-2 | ACDB - AC Distribution Board |  |  | CxL2A - 2-DB-2 - Comms Cabling not terminated. Potentially not required. If not required, it is to be removed and gland blanked off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615776&prj=562&rqi=NFhkpu29gbsTzWyClDK8S3x8FG
GI-152 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ LV | equipment | 2-DB-2 | ACDB - AC Distribution Board |  |  | CxL2A - 2-DB-2 - Pole Fillers missing. To be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615777&prj=562&rqi=PR9Rer0SVNBbbSWSf2dYOMKFr7
GI-154 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY910B Permanent Labelling to be updated for all equipment and cabling. Includes Equipment, HV Cabling, Submains, Subcircuits and Earthing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615780&prj=562&rqi=n3EWWdXWy2FOMWs9395tX5YwGh
GI-153 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-DB-1 & 1-DB-2 - Heat Shrink to be installed on bare copper at Load side of MTS to DB Section of Switchboard. Top and bottom sections. See picture for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615778&prj=562&rqi=cXDmm2MZnSH1VKDsaXAxbDMTaI
GI-150 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ LV | equipment | 2-DB-2 | ACDB - AC Distribution Board |  |  | CxL2A - 2-DB-2 - Trunking cover misssing interal to Switchboard (Left side) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615775&prj=562&rqi=jgZ7aVeojHDqTRjQZCApcBasCz
GI-149 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-SUMP-1 & 1-SUMP-2 - Enclosure door screws not fixed. Panel door to be secured. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615168&prj=562&rqi=kiZ1IDc5xXcBjkHrN8DXTzBl99
GI-148 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - 1-SUMP-1 & 1-SUMP-2 - Level alarm indication on Pump controller not operating as expected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615166&prj=562&rqi=Apd1gyyGnM7jFEdlexda6IUiG8
GI-147 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A & CxL2B - SY9 Overhead Conductor - Test reports to be submitted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199810&prj=562&rqi=3BnT3Q8amph6axAe4pB4yzKeuF
GI-146 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2B - 1-MLTX-1 & 1-MLTX-2 - Oil Sample / Oil Tests of transformer not completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198975&prj=562&rqi=xtxmm0ggFdcqtHmrnG8r1zqylz
GI-143 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-MLTX-1 & 1-MLTX-2 - Extra External Protection needed for 11kV Cables (UV/Water/Mechanical). Cover to be installed over cables to provide extra protection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198823&prj=562&rqi=oYjHiS4h1ZKmk7HvsHFbH9zg3q
GI-145 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - SY9 Earthing - Earthing to be torqued and marked at all earth bars and cable connections (Switchrooms and Transformer pit) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198832&prj=562&rqi=EZ0OCd4V4vTY4hdkC2zoLaIAUv
GI-144 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 132kV Power Transformers - LCP Supplied by vendor allows for two power sources from alternate supplies (9A & 9B). Allowance made for this with both AC & DC Supplies. Currently only 1 Source has been provided to the LCP. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198829&prj=562&rqi=aRBaZCDMU44ThJQywEfD2JfvB1
GI-135 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | Fire Protection System - SOO to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198742&prj=562&rqi=tGtbEdzrxvTqXqPPCyOmzmdSnn
GI-136 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | Fire Services Installer - Calibration Certificates to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198745&prj=562&rqi=7zNUI6LWt3zMUYvYE4tg64Vu0Y
GI-141 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 2-HMTX-1 & 2-HMTX-2 - Neutral CT to be installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198751&prj=562&rqi=an9pO5gEv5Pxw7YUhZUxZHvv2V
GI-138 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-FIP-1 & 1-FIP-2 - Bonding to be torque marked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198747&prj=562&rqi=YiHvXC4SadCIfEHIoxe3nSDaM3
GI-137 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-FIP-1 & 1-FIP-2 - Dust and Debris present within panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198746&prj=562&rqi=oXBn8TYHfKDkXSBkCzgXFKDyGX
GI-139 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Fire Detection | equipment | 1-FIP-1 | FP - Fire Panel |  |  | CxL2A - 1-FIP-1 - Unused gland on top of panel to be removed and blanked off if not required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198748&prj=562&rqi=Twm9741UjXVO0K4ohude3BBFZB
GI-142 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-HMTX-1 & 1-HMTX-2 - Dust & Debris present within LCP. Cleaning required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198752&prj=562&rqi=K3D0nLTRXKSb3sYqQiYC9laaJk
GI-133 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9A Switchroom - Light not securely fitted. Held up with cable ties on one side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198663&prj=562&rqi=wdbfBHJ4uSJ6aCsiztBVRFCfxz
GI-134 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9A Switchroom - Cabling not secured. Phase tape used to secure earthing in cable tray. Cable to be secured with cable ties. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198664&prj=562&rqi=nqAEJsbWc1DXfxR9x0lcHJfSp0
RT1ELEC-1-002 | SY09x-2 132kV Substation | APAC | Closed | P1 High CX | AmmarKhawaja@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2A | Incomplete Connections | Commissioning | Electrical â€“ MV | equipment | 1-HMTX-1-SA3 | HVCABLE - Surge Arrestors |  |  | CxL2A - 1-HMTX-1 & 1-HMTX-2 - Earthing for surge arrestors to be installed. No bonding between arrestors and earth nest. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198570&prj=562&rqi=E2tCK5PnUp57alcvNiFbOjodxR
GI-129 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 132kV Disconnectors and Overheads - Some concern present of tension being on Disconnectors and Surge Arrestors/Bushings. Tension seems to be caused by overhead length and rotating disconnector terminal plates. Potential for damage to equipment when operating disconnectors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198181&prj=562&rqi=0PzJ55IXJJgOmLTQPUkkRNAAEe
GI-127 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - MLTX All - Amalgamating tape to be applied at Aux Tx 11kV Cabling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197844&prj=562&rqi=0CGPmXfr0nqP7FO4iKBjKMT648
GI-123 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ LV | equipment | 1-MDSB-1 | MDSB - Mech Distribution Switchboard |  |  | CxL3 - 1-EF-1 - Exhaust Fan in fault | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197827&prj=562&rqi=qX7e559AF3eUd7uqGQzqwRbGyF
GI-126 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - ACDB All - Lack of clearance between Main Neutral cabling and MTS secondary outgoing contacts. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197842&prj=562&rqi=rjj9VasKIZGgRd1TYPEYbYLtFs
GI-125 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - Sump Pump All - Unable to see change of state for various DCOS Points. Potential wiring issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197840&prj=562&rqi=c15XlITYNpfFkNj7b0KYnXZikw
GI-121 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - 110VDC Battery Chargers - Unable to see DCOS status for various points | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197825&prj=562&rqi=eWRxKvFW0zLfxFKCSpDjHEAqHm
GI-122 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - FCU All - Unable to see status of all FCU on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197826&prj=562&rqi=2YR1hzmD9zE04sOuwpKK3Uox9x
GI-120 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2B - 132kV Power Transformers - Siemens Calibration Certificates to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197632&prj=562&rqi=HQX5YhSrnbhIki1kcOvqxOGVMq
GI-115 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ MV | equipment | 1-ERTH-1 | ERTH - Earthing |  |  | CxL2A - Earthing - SY9A & SY9B Control Room Door bonding loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196908&prj=562&rqi=SNVx1hU9S1zzH3PvkrpfHQxiqD
GI-116 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - Earthing - Bonding required on various trays within SYA&B. Oil Water Separator, Linkbox & Auxiliary Transformer MV Cable support structure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196933&prj=562&rqi=rhad8Va05mkOx6FibZbZaikXlL
GI-114 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | Electrical â€“ MV | equipment | 1-ERTH-1 | ERTH - Earthing |  |  | CxL2A - Earthing - 1-BTU-1 Earthing loose at earth bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196907&prj=562&rqi=KTqknnJJIhmKdprWPI7Owe8hFM
GI-117 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 132kV Transformers - Interface cabling required to be installed between TMR and SUSP for voltage monitoring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196934&prj=562&rqi=OJyHJjni6D8AsfeyumjChs1mLW
GI-119 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - SY9 Auxiliary Transformers - 11kV Cabling earth screens to be sealed with amalgamating tape | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196939&prj=562&rqi=CFTlEKax0dQ3Rm2jmSc7vYXbzm
GI-110 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL3 - FCU All - No visibility of FCU's on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196833&prj=562&rqi=omFhpd3ahrBBu3MmgIgub1GK8b
GI-108 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - SY9A Permanent Labelling to be updated for all equipment and cabling. Includes Equipment, HV Cabling, Submains, Subcircuits and Earthing Note: In addition to the above SUSP, SEP to be updated. Phase indication for Disco. HV Cabling, Earth Cabling and Subcircuits missing labels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196832&prj=562&rqi=zFrI0KMoL4ebmM0VEhgQTUJsrW
GI-107 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | AmmarKhawaja@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - SY9 Auxiliary transformers - Not bolted down/fixed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196829&prj=562&rqi=0DvDHM2BUmkET56OG2hrfzUeXj
GI-112 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | AmmarKhawaja@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-MLTX-1 & 1-MLTX-2 - Neutral earth cable needs to be clearly identified as earth/neutral | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196834&prj=562&rqi=9GzcmuS2YifbHlj41gAdYELSSB
GI-111 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-DB-1 & 1-DB-2 - Neutral cabling resting on live outgoing terminals. Separation to be created between cabling and terminals. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196835&prj=562&rqi=6LxPOVFtalLXSM8woij43z40HB
GI-109 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | AmmarKhawaja@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - SY9 Auxiliary Transformers - Bonding required for MV Cable support structure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196830&prj=562&rqi=vHV7ndPvOthsgYPE8DxmkK5HOF
GI-106 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 132kV Power Transformers - No presence of earth cabling between LCP Earth Bars and transformer chassis. No continuity seen between various Earth Bars within LCP to Transformer chassis. Potential requirement for adding more bonding. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196541&prj=562&rqi=S0sZqaaiSbqkJFs5lU7gwuVk9R
GI-105 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - 1-SUSP-2 - A04 CB Cover damaged. To be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196405&prj=562&rqi=26Ky6yuP1LtleYadWM0nfrkkMq
GI-104 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | equipment type |  |  |  |  | CxL2A - 1-HMTX-1-K1 & 1-HMTX-2-K1 - Supports / cable cleats required to be installed for cabling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196365&prj=562&rqi=4RgwjgIQPPcrgpUKmHvyq0fx4f
GI-103 | SY09x-2 132kV Substation | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-05 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [6 empty] | CxL2A - LPS - Lightning Mast Pending installation. Works to be completed & Test report to be submitted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196298&prj=562&rqi=vUXmgTSRZwAtnUc0ejPf26Bk6n
GI-612 | TR06-2 | AMER | Closed | P3 Low CX | Ocean.Kwan@veolia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Manufacturing | Commissioning | [6 empty] | The posted procedures at the new MSBs is not correct. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623562&prj=358&rqi=rBjkYjqc4XzATLCty2mbTHRX8K
GI-613 | TR06-2 | AMER | Closed | P3 Low CX | Ocean.Kwan@veolia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor |  | Installation | Commissioning | [6 empty] | Main Service gear 1PUSP_1 & 2 sections are missing equipment identifiers/labels, e.g., Interrupter, Protective Relay, Power Quality Meter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623563&prj=358&rqi=W40DGzTTpkBPQSKVsfrUumi2c7
GI-614 | TR06-2 | AMER | Closed | P3 Low CX | Ocean.Kwan@veolia.com | 2026-06-01 04:00:00.000 +0400 | Vendor- Manufacturer |  | Manufacturing | Commissioning | [6 empty] | TR6-2 (Electrical Block A & R SKID): A few MSB_A breakers were mislabeled (incorrect spelling, incorrect label background color, font size), e.g., UPS_RIB_2, 1UPS-A-2-LBB, 1-CH-A-2, 1LBB_A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623564&prj=358&rqi=6gtkZHLYzFAT4N8UIir8uIjw7t
GI-116 | TR06-3 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-09-15 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | FWT | Factory Witness Test |  | equipment type |  |  |  |  | AMG NETA Report - Following a preliminary review of the breaker test reports provided for TR6-3, it was noted that the primary injection test of the INS protection for the MSB circuit breakers was not included. AMG to verify with your testing team whether additional reports covering this test are available? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638208&prj=657&rqi=K5SewSb9acj8I437Kw7i2L3Ucb
GI-117 | TR06-3 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-09-15 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | FWT | Factory Witness Test |  | equipment type |  |  |  |  | AMG MSBs- While reviewing the FAT documents, it was noticed no torque reports available for the bus. Report is missing this information. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638210&prj=657&rqi=RurenAowV2oUkGxOlAZArhBPiz
GI-115 | TR06-3 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-09-15 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | FWT | Factory Witness Test |  | equipment type |  |  |  |  | AMG Breaker Test Reports - Upon reviewing the reports, it was identified that certain records include Ground Fault Protection test results for 400A breaker equipment fitted with the MicroLogic 5.3 trip unit. However, the MicroLogic 5.3 unit provides LSI protection only and does not include ground fault protection. AMG is to review and clarify this discrepancy. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638196&prj=657&rqi=guqYCxtN80uQrFXiUD4vmn42lE
RT1MECH-32-001 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-09-11 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CH_A_2 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-A-2: The fitting connecting the pump skid to the chiller evaporator is a different model number comapred to fitting seen on the remaining 6 chillers. Please refer to the attached pictures. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637815&prj=657&rqi=8BHeUpPzmxgX6kZl6pjUPC5Vkt
GI-114 | TR06-3 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-09-10 04:00:00.000 +0400 | SCH - Schneider Mech |  | Component/ Equipment Failure | Commissioning | [6 empty] | 0.75 in gap in chilled water piping connection between top and bottom mega crah | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637701&prj=657&rqi=yXRkTqkv1CyJphUCT8Bsy34Ust
RT1MECH-87-009 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-09-04 04:00:00.000 +0400 | Consultant | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Applicable to all Skid CRAHs - Secondary source fed from R Block: The max input current mentioned on the CRAH name plate is 13A, the upstream breaker for primary source of the CRAHs installed by MPS are 20 A. However referring to drawing # E715, the upstream breakers for second source on the panel schedule mentions 35 A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636925&prj=657&rqi=xJjJtD1sJj1vLBmRXAQljr37ae
RT1MECH-116-001 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-09-03 04:00:00.000 +0400 | Consultant | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1HP_R_05 | HP - Heat Pump |  |  | Common for all MPS skid Trane WSHPs: On the water source heat pump submittal, the "Max Overload protection (A) is given as 15A. On the panel schedule for WHSP fed from R block, The upstream breakers on the panel schedule are 20 A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636780&prj=657&rqi=AyYUHhThukhbDrhwiDSFEI1C9J
GI-112 | TR06-3 | AMER | Open | P1 High CX | steve.knezevic@veolia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_D | MSB - Main Input Switchboard |  | no | Water ingress through conduit penetrations behind MSB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636750&prj=657&rqi=9hF3uPaKSwLQg8DuodmzbmyIK5
GI-113 | TR06-3 | AMER | Open | P1 High CX | steve.knezevic@veolia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | Water ingress through conduit penetrations behind MSB and at middle shipping split of skid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636751&prj=657&rqi=yqt3Hhl9vQPCYLK4n4Xyl2wqrh
GI-103 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDP_D_1 | UDP - UPS Output Switchboard |  |  | UDP_D_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636548&prj=657&rqi=LoEaBOocC7Gh3zLmQpoBUf9S7E
GI-106 | TR06-3 | AMER | Open | P3 Low CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_D | MSB - Main Input Switchboard |  | no | UPS_D_1_LBB & UPS_D_2_LBB status contacts were not wired to a terminal block to be monitored by the UPS. Three spare EF contacts exist at each breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636556&prj=657&rqi=sBRKnLSreV7zsY12vvWf81htVU
GI-105 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  | no | UPS_C_1_LBB & UPS_C_2_LBB status contacts were not wired to a terminal block to be monitored by the UPS. Three spare EF contacts exist at each breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636555&prj=657&rqi=PfrviCTgySiJn6Hkg2GOOxeR6G
GI-109 | TR06-3 | AMER | Open | P3 Low CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UDPR_C_1 | UDP - UPS Output Switchboard |  |  | UDPR_C_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636559&prj=657&rqi=u40qioa7J4iq1MhaXOWulL7MBN
GI-102 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDPR_D_1 | UDP - UPS Output Switchboard |  |  | UDPR_D_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636547&prj=657&rqi=y8qywIWpLhTaZoyWIJvq29aSON
GI-110 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UDP_C_2 | UDP - UPS Output Switchboard |  |  | UDP_C_2 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636560&prj=657&rqi=qXjsDole0Ik1POAlvsG6pxy6f0
GI-111 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UDPR_C_2 | UDP - UPS Output Switchboard |  |  | UDPR_C_2 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636561&prj=657&rqi=TUl7t1rthdGKyafr1g7WnW1GmI
GI-108 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1UDP_C_1 | UDP - UPS Output Switchboard |  |  | UDP_C_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636558&prj=657&rqi=5qMLpw64gKVyWk6NtXZ54tMkZZ
RT1MECH-112-001 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1HP_B_04 | HP - Heat Pump |  |  | Common for all MPS skid Trane WSHPs: On the water source heat pump submittal, the "Max Overload protection (A) is given as 15A. The upstream breakers on the panel schedule are 20 A for the skid WSHPs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636525&prj=657&rqi=WzgkflLu3exHjk9SQ6r7R94HOe
GI-107 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | UPS_E_1_LBB & UPS_E_2_LBB status contacts were not wired to a terminal block to be monitored by the UPS. Three spare EF contacts exist at each breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636557&prj=657&rqi=KPv2JsFFXwfI3e4I0VHQvTcCMJ
GI-104 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDP_D_2 | UDP - UPS Output Switchboard |  |  | UDP_D_2 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636554&prj=657&rqi=BsuFJ1mggrVZpjRUdq3gqipAPy
RT1MECH-87-006 | TR06-3 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | As per review of drawing M405 and on site configuration it was noted that the CRAH labeled 1CRAH_ER_11 is mislabeled as 1CRAH_ER_10. This impacts the following: -BAPI10 - incoming and outcoming EMT labels -wire labels for CB1 and CB2 and main ground. -CRAH Label itself | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636166&prj=657&rqi=aNGNFqlo96suhTmQ0cXirnFWeS
RT1MECH-87-005 | TR06-3 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | As per review of the submittal package RMC070, the specification cut sheet individual components are not attached. review Table 2.6 Spare Parts item 12,15,16 -EC Fan -MC-22b -MC-9b -Auxiliar contactor -Step down Transformer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636163&prj=657&rqi=04Sg1oEgg1ASpdE9fLCfuFlSSm
RT1MECH-87-002 | TR06-3 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Ferrule connectors are exposed for terminal 1.1, 1.2, 2.1, 2.2 on component QUINT CAP 4KJ. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636159&prj=657&rqi=got2czOUkVed9e5AqIazi8Gf5N
GI-101 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | system | meWall E |  |  |  | Skid E: Rope Leak Detector: Extra Slack on the rope leak detector is not secured neatly in the skid. (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636206&prj=657&rqi=qX2ENfPMKmaYNMSioQlzhyfoX3 | https://equinix.facilitygrid.co.uk/x/project/657/system/13317
RT1MECH-87-008 | TR06-3 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Cleaning | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Construction dust and FOD found inside high-voltage electrical section and on top of the unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636168&prj=657&rqi=v5LGQUuIU3HiIalGH4j1ZoKqCb
RT1MECH-87-001 | TR06-3 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Installation Damage | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Damage cooling coil observed upon inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636158&prj=657&rqi=LWsuuX6ItBOfkobn7ZGgpN5Nny
RT1MECH-87-003 | TR06-3 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | CB1 and CB2 are loosely mounted, there is significant play in the breakers upon inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636161&prj=657&rqi=3KNMCF9ZcYbqbCpGXvJ2jeqUFK
RT1MECH-88-003 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | Applicable to all MPS Skid CRAHs: Missing cut sheet of the T sensors on the submittal. (Attaching pictures to indicate the sensors we are referring to) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636089&prj=657&rqi=QWF1vnmtzQr0LfRgbnYc6N5yLB
RT1MECH-87-004 | TR06-3 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Terminal block labels deviate from the shop drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636162&prj=657&rqi=ohoeso8PdeF2PoHr3d2ZlUMQH3
RT1MECH-88-001 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | Applicable to all MPS skids Delta CRAHs: The controls wiring drawing provided in the submittal is not readable, cannot be used for verification of the wiring or the controls components. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636079&prj=657&rqi=cDeOkMshNaDq2FmbEA1V14VAME
RT1MECH-88-006 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | Common for all three CRAH units in Skid E: The panel schedule needs to be revised as per the CRAH asset names inside Skid. It was found that the CRAH names do not match as per drawing M405 (Attached) Also refer to Issue # 152, 155 and 156 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636211&prj=657&rqi=osNMQPayqntOCwbsmVTCpQ8bqY
RT1MECH-86-001 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_12 | CRAH - Computer room air handler |  |  | For 1CRAH_ER_12: As per review of drawing M405 and on site configuration it was noted that the CRAH labeled 1CRAH_ER_12 is mislabeled as 1CRAH_ER_11. This impacts the following: -BAPI10 - incoming and outcoming EMT labels -wire labels for CB1 and CB2 and main ground. -CRAH Label itself | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636193&prj=657&rqi=f6mECkJ467Q4qioyHgbXaS22RW
RT1MECH-88-005 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | Common for all MPS Skid CRAHs: The safety labels on the CRAH electrical panels need to be in English and French for Skid ESA inspections to pass. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636208&prj=657&rqi=nbaiaUAr6IGPSPwD2travPSAL3
RT1MECH-87-007 | TR06-3 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Installation not correct | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Upon review of submittal OFCI-12 Section 2.1.2.2 Single Line Diagram -it was noted the following fuses have FA Fuses, which deviate from the shop drawing. F3 4Amp fuses found instead of the specified 10Amps F5 10A fuse found instead of a 3Amp fuse. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636167&prj=657&rqi=WT1zGA0P6m0o0YztvTcPSUMwfD
RT1MECH-88-004 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | For 1CRAH-ER-13: As per review of drawing M405 and on site configuration it was noted that the CRAH labeled 1CRAH_ER_13 is mislabeled as 1CRAH_ER_12. This impacts the following: -BAPI10 - incoming and outcoming EMT labels -wire labels for CB1 and CB2 and main ground. -CRAH Label itself | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636190&prj=657&rqi=9piZLnxeMl9IQaSw9Jk65SIvtk
RT1MECH-88-002 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | Applicable for all MPS Skid Delta CRAHs: The T Sensors in the submittal, if the intend of these is to sense the chilled water return and chilled water supply temperature, then these sensor were found not to be thermowells but to touch the copper pipes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636083&prj=657&rqi=YDTzqKG2sXktSRV3GmCrTAHWz7
RT1MECH-37-008 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-08-21 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: Housekeeping PAD has one corner broken. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634620&prj=657&rqi=9TjFbJpYccFNqZW8W66z9vYdVr
GI-095 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDPR_B_1 | UDP - UPS Output Switchboard |  |  | UDPR_B_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634545&prj=657&rqi=ZtaUcDc4XBFYxXyL2VaHtjZZDo
GI-098 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  | no | UPS_B_1_LBB & UPS_B_2_LBB status contacts were not wired to a terminal block to be monitored by the UPS. Three spare EF contacts exist at each breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634548&prj=657&rqi=Cxs4W9tJCqL1AxTDq7M8Jokx0T
GI-097 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  | no | SPD bus in section 01C missing cover. Hazard to operators is currently present with exposed busbars | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634547&prj=657&rqi=nXuczx8w9Rre4SKjs5LSylwEYt
GI-094 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDP_B_2 | UDP - UPS Output Switchboard |  |  | UDP_B_2 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634544&prj=657&rqi=V5K66IU9ADi2bLDOxiEGosUWNw
GI-099 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1BATT_B_1_1 | LIBATT - UPS Battery |  |  | TB3 1-3 from the BIBR to battery cabinets (MCCB Status) has not been completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634549&prj=657&rqi=9S9uV7FpMtizLESE4v9BFMNyPY
GI-093 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDP_B_1 | UDP - UPS Output Switchboard |  |  | UDP_B_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634543&prj=657&rqi=utQWuj05AzGKzjOqMSseyhP9jf
GI-096 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDPR_B_2 | UDP - UPS Output Switchboard |  |  | UDPR_B_2 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634546&prj=657&rqi=x4yvi5zcKn4URvUTaKSvffzDVW
GI-100 | TR06-3 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [6 empty] | At UPS_B_1 & UPS_B_2 (XVLDC 21-24) the UPS Charge Limit wiring has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634551&prj=657&rqi=BjcC92JrDquFKCoyE8zvHVcqsA
GI-092 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-08-07 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | FWT | Factory Witness Test | [6 empty] | Skid D: 1UDP_B_1 and 1UDP_C_1 on the TR6-3 project. The current configuration does not provide sufficient space in the front lug holes to achieve the required wire bend radius, causing the lug to press against the insulator. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632770&prj=657&rqi=KupcCj3gZZqyRtkepSLCLfGI7I
GI-090 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-28 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Applicable to three Chillers as of now: The Air Vent on the Air Separator was found to be able to rotate by a push. The connection need to be inspected. See on below chillers. (video available on request) 1CH-A-2 1CH-B-2 1CH-B-1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631076&prj=657&rqi=PDIplpTDbYp4TQLOzfswFcmAYo
GI-091 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-28 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Common to all chillers: Model # of the Onicon Flow meter does not match the cut sheet on the submittal. The one received on site Model # is FT-3400-200-1C31 Vs the Submittal which mentions F-3500 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631082&prj=657&rqi=AIu6wACCgRQBzabhQo9HG0rmi7
RT1MECH-38-019 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation Damage | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CU-E-1: The fins are bent on the condenser on the roof. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630930&prj=657&rqi=g8RudaujiM5EUDRbs4d6JMj6ur
RT1MECH-38-020 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to TR6-3 chiller submittal: For the MG2 module on the chiller condenser, the drawing shows the termination at P1- and P1 + terminals. The actual terminations on site are on P2- and P2 + terminals. These two terminals are not shown on the drawing. The drawings needs to be updated to match the site installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630932&prj=657&rqi=HIOyi961lRxTJJhDsCp9dhPnEJ
RT1MECH-38-014 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-E-1, pump skid electrical panel: As per the drawings FU-5 is 8 A fuses but we found 5A fuses installed downstream of 5L1 and 5L2. (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630889&prj=657&rqi=YqySasCzRBv8TUvdYOrXEqWTbk
RT1MECH-38-016 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-E-1: The FU2 fuse holder label needs to be rectified on the submittal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630898&prj=657&rqi=tlBBfl6pL5e2AxaRSOXwt7xsea
RT1MECH-38-015 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | Applicable to TR6-3 Chiller Submittal: On the panel drawing for the pump, the transformer in the panel layout is shown as 460 to 120 V, in the electrical single line drawings it is shown 460 to 24 V and the wiring on site is also as per 460 to 24V. The panel layout drawing needs to be corrected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630895&prj=657&rqi=TuwRVs5WYNypiBsO30cUoVlgQl
RT1MECH-38-021 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment type |  | ACC - Chiller â€“ Air Cooled |  |  | Common for all chillers: CBTB1 - fusible terminal blocks FU-SIA1 through FU-SIA8 do not denote fuse size. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630934&prj=657&rqi=SNYPGH8GEl11MAQpUrsprCMeiB
RT1MECH-38-018 | TR06-3 | AMER | Closed | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-E-1: Missing outdoor air sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630926&prj=657&rqi=inRuFE4kLqSsj0Cqy9Nr0PuKh8
RT1MECH-38-017 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to TR6-3 Chiller Submittal: Missing Cutsheets for the following components: 1.) Evaporator Liquid Level Sensor 2.) Smardt Lift VFD Module 3.) Expansion Valve 4.) Freeze Protection Bypass Valve (BRAY) 5.) Temperature transducers 6.) Pressure transducers 7.)Evaporator Barrel cutsheet provided is a general cutsheet does not provide a model number specific to TR6-3 project. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630899&prj=657&rqi=6Qdo3NUW42y00M8sCGJISOdrAr
RT1MECH-38-013 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-24 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | Applicable to 1CH-E-1 and 1CH-D-1: The model number of the two isolation control valves at the bottom side does not match the cutsheet. Refer to the attached pictures. The Model Number mentioned on the cutsheet is PKRBUP-MFT-T and these two valves the model number is PKXUP-3-T | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630756&prj=657&rqi=03IfpQ2jhiNHNaMCmEciSRIhuR
RT1MECH-37-006 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-24 04:00:00.000 +0400 | SMT - SMARDT | L2A | Component/ Equipment Failure | Commissioning | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: ABB breaker SACE Tmax XT4H 250 in L2 enclosure is not resetting, and stuck in the tripped position, preventing door from closing and requires inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630777&prj=657&rqi=v2kjLcBnsxkjsJ11VSKCmaQIyf
RT1MECH-37-007 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-24 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: The conduit connection in the splitter panel entering panel L3 enclosure side is loose and not properly torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630779&prj=657&rqi=wrxTHlyqMKA045btKdu5HbOCQb
RT1MECH-38-011 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-24 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | Applicable to new chillers 1CH-E-1 and 1CH-D-1: The model number of the freeze protection bypass value does not match the model number of the freeze protection bypass valve installed in the TR6-2 phase. As compared to TR6-2 bypass valve (800 In Lbs.) the torque value is less on the TR6-3 chiller bypass valve (600 In Lbs.) The SMRARDT submittal for TR6-3 phase does not include the cutsheet of the BRAY valve. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630718&prj=657&rqi=wrNtN3TRerOMdWTW2wVgVqHhSF
RT1MECH-38-012 | TR06-3 | AMER | Closed | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-24 04:00:00.000 +0400 | SMT - SMARDT | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to 1CH-D-1 & 1CH-E-1: Missing the onicon flow meter on the pump skid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630741&prj=657&rqi=KAW8CiKS9ILgA0lrQF7soSgGLt
RT1MECH-38-010 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-E-1: Seals / Ports missing on the below location on the chiller. - Pump skid and Chiller connection. - Evaporator two ports - Air Separator bottom drain port. Concerns of FOD /Rust . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630602&prj=657&rqi=wON5XDl7WJjCJWKK9m451wT89r
RT1MECH-38-009 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to 1CH-E-1 & 1-CH-D-1: (As of now these two chillers are on site) The model number of the main disconnect of the chiller does not match the model number mentioned on the submittal. On the submittal the selection is highlighted on Model # OT600U03 and the model # noted on the onsite chiller main disconnect is OT800U03. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630586&prj=657&rqi=Y2kQhFRNKBL64OUKZkVvnyK51z
RT1MECH-38-008 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to the 1CH-E-1 & 1-CH-D-1: (At this point inspection is done only on the chillers received on site) As per the EOR comments on the Pump Skid submittal the fittings on the pump skid connecting to the building chilled water header is supposed to be Victaulic. The fitting seen on the these two chillers is not Victaulic. (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630579&prj=657&rqi=M5HmjDWGJ2sHNuSJUfzhf2XAGc
GI-089 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Applicable to 1CH-E-1 and 1CH-D-1: The location of the flow switch was changed in last phase from its original location (close to the evaporator) to a location on the pump skid. But the new chillers on site still has the flow switch installed close to the evaporator. (Reference picture attached) (Also Refer Issue # 1109 on TR6-2 Facility Grid) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630661&prj=657&rqi=JbOMw7ne6MJCYaDVC8WrVEWvXs
RT1MECH-37-003 | TR06-3 | AMER | Ready for Verification | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | SMT - SMARDT | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: Power Entry Label is incorrect. Shows 480 V but this is a 120V panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630595&prj=657&rqi=WnPrTW7Qwd85rugK6kNgy7RrE5
RT1MECH-37-004 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: Seals / Ports missing on the below location on the chiller. - Pump skid and Chiller connection. - Evaporator two ports - Air Separator bottom drain port. Concerns of FOD /Rust . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630604&prj=657&rqi=Nab85aZsGoS34WYXsCm99xYEi8
RT1MECH-37-005 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CHWP-D-1: The chilled water pump electrical panel door is jammed and does not open all the way. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630606&prj=657&rqi=kyGFkn5iwS4Us3ssRKB0CsdlwB
GI-088 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-22 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  | no | Insulation boards are missing at Sections 6 and 10, a recurring issue previously observed on Skid C. An email has been sent to AMG requesting immediate action before MPS closes the back panels; we are awaiting their response. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630459&prj=657&rqi=B9zEiWI0Bvb1AwCB7QD1vF0gxV
GI-087 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-22 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  | no | Insulation boards are missing at Sections 6 and 10, a recurring issue previously observed on Skid C. An email has been sent to AMG requesting immediate action before MPS closes the back panels; we are awaiting their response. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630458&prj=657&rqi=aHVz5IrASNZAqvuNPwd37wxKtm
RT1MECH-37-001 | TR06-3 | AMER | Ready for Verification | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH_D_1: The pump skid CHWR piping are not aligned, and needs adjustment so that the pump skid can be connected to the chiller. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630177&prj=657&rqi=kDO8js4o2f5AUY4zLNEuLcYAmw
GI-086 | TR06-3 | AMER | Ready for Verification | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Applicable to all Chillers: Issue is for tracking purpose. Smardt to confirm the chiller proof of flow logic and confirm if its as per Equinix standards. (Also tracked on the on going email chain. screenshot attached) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630332&prj=657&rqi=nFLCdndsEmqWJBrrISF7udmQIQ
RT1MECH-38-002 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - BMS | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to all chillers part of TR6-3 phase: The Equinix PLC Control panel is missing on the chiller. On the TR6-2 phase chillers this control panel came from SMARDT Factory with the chiller LCP installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630181&prj=657&rqi=8cciHq2abVUoPs3FeSzscZHTmR
RT1MECH-38-003 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | Applicable to 1CH-E-1 & 1CH-D-1: Power Entry # 3 Panel: As per the Submittal Pg # (13 of 48), the circuit diagram shows one LED or light but the panel on site does not have any LED or Light. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630194&prj=657&rqi=jzhoKjldvqMgstHbtdxzozvLX7
RT1MECH-38-001 | TR06-3 | AMER | Ready for Verification | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not complete | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH_E_1: The pump skid CHWR piping are not aligned, and needs adjustment so that the pump skid can be connected to the chiller. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630178&prj=657&rqi=9XphoJO9aRAZShSN1AH7czWkZF
RT1MECH-38-006 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-E-1: The Equipment label does not match the label on the submittal. The submittal mentions two part numbers one on the main header page and one has a detailed name plate. The header matches the name plate model number on the chiller (Refer to the attached picture) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630201&prj=657&rqi=LTHeurgPQWgVm02s7jrNcpYAJb
RT1MECH-38-004 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | Applicable to 1CH-E-1 & 1CH-D-1: Power Entry # 3 drawing on the submittal does not match the panel on site. (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630195&prj=657&rqi=1bVf6mQC3mdq0e0msIVhKqYq76
RT1MECH-37-002 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Labelling | Commissioning | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: The Equipment label does not match the label on the submittal. The submittal mentions two part numbers one on the main header page and one has a detailed name plate. (Refer to the attached picture) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630208&prj=657&rqi=VJtaOXXIv5aMlOuKFa4kv4JeJY
RT1MECH-38-007 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - BMS | L2A | Missing Components | Commissioning | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to all Chillers : We noticed that the phase monitoring relay is not present in the Compressor panel # 2 as seen on the TR6-2 phase chillers. Upon review of the new submittal for TR6-3 we noted that the phase loss relay is not shown on the single line diagram of the compressor # 2 panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630212&prj=657&rqi=hbGzCwBfXeswVTE1JhX1faex9N
RT1MECH-38-005 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to all chillers part of TR6-3 Phase: In order to resolve the ongoing chiller compressor fault on low ambient temperature (Refer to Issue # 1113 from TR6-2 phase) the three discharge isolation valves were to be wired such that they can be controlled individually to open / close from the Kiltech controller. Referring to the new submittal for TR6-3 phase it looks like this correction has not been made. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630198&prj=657&rqi=effTbjG3wzWmYL5VOpc1DSbzEs
GI-079 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1UDP_C_2 | UDP - UPS Output Switchboard |  |  | For 1UDP-C2: The sub feed breaker # 5, micrologic module is missing is the protective plastic cover which is seen on the dials. (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629743&prj=657&rqi=VDCubeL9qjo3PwhQjkixuRJKKZ
GI-082 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | "For D Skid: Applicable to the control power section of UDP - D1 and UDP -D2: The section should have a protective plastic cover and caution label since a 460 V input is landed in this section. " | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629749&prj=657&rqi=fWsEWkWrA8RbldmAKk7YW4cqco
GI-083 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | For B Skid: Applicable to the control power section of UDP - B1 and UDP -B2: The section should have a protective plastic cover and caution label since a 460 V input is landed in this section. " | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629750&prj=657&rqi=qYDfo7J2AnIsNHXxmOkfaqzzy1
GI-084 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1UDPR_E_2 | UDP - UPS Output Switchboard |  |  | "Applicable to 1UDPR-E2: The location of the sub feed breaker 5 does not match the location shown on the submittal. (refer to the attached pictures)" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629758&prj=657&rqi=LIWHbXoX0EHUf5b5Wwfq3iuhiP
GI-085 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | Applicable to the all the MPS Skid Equipment: Below lamcoids are needed: - MSB labels for the breaker as mentioned in the MSB submittal. - Fed from labels for all equipment - CRAH - WSHP - UPS - UDPR (subfeed breaker # as well) - Battery cabinets - STS (Some pictures attached for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629766&prj=657&rqi=gqMbpqZrihakHzJVW0KfpP5Vdu
GI-081 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | equipment type |  |  |  |  | "For C Skid: Applicable to the control power section of UDP - C1 and UDP -C2: The section should have a protective plastic cover and caution label since a 460 V input is landed in this section. " | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629748&prj=657&rqi=XsjtD9TcOkzga3djzt2iXqo1Jz
GI-080 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  | no | For MPS Skid C - Section 06C: Edge guarding for controls cables is missing on the edges as seen on other skids (Highlighted in the attached picture) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629745&prj=657&rqi=WhA8BEYV26NNV7DUzgSsYHWiUW
GI-069 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1BTU_RMU_E | BTU - Battery Tripping unit |  |  | For MPS Skid E: The BTU rough in work inside the MPS Skid is not completed. As per discussion during the Factory visit on 15th July, it was decided that will be done by MPS before shipping the skid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629477&prj=657&rqi=lVLfHZnt1EnueEylyuLpSlS04p
GI-071 | TR06-3 | AMER | Ready for Verification | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1BTU_RMU_C | BTU - Battery Tripping unit |  |  | For MPS Skid C: The BTU rough in work is not completed. As per discussion during the Factory visit on 15th July, it was decided that will be done by MPS before shipping the skid. (Reference pictures attached from E skid) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629479&prj=657&rqi=BYMieVhWwuc2smNoGB35Ht6SMv
GI-077 | TR06-3 | AMER | Closed | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDP_D_1 | UDP - UPS Output Switchboard |  |  | Applicable to 1UDP-D-1: As per the submittal the breaker should be LSI, but the sub feed breakers 1,2,3 and 4 installed in this UDP are with micrologic 6.0A (with ground fault) trip units. (Picture attached for one sub feed breaker for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629488&prj=657&rqi=GwaHGvwoe3rxz9mVBWFLCxrhvW
GI-078 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Documentation not issued/ Required | Commissioning | Electrical â€“ LV | equipment | 1UDPR_C_2 | UDP - UPS Output Switchboard |  |  | Applicable to 1UDPR-C2: The location of the sub feed breaker 5 does not match the location shown on the submittal. (refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629490&prj=657&rqi=3TWWjWHN4iYIbWboUtRLWk6sgn
GI-072 | TR06-3 | AMER | Ready for Verification | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1BTU_RMU_B | BTU - Battery Tripping unit |  |  | For MPS Skid B: The BTU rough in work is not completed. As per discussion during the Factory visit on 15th July, it was decided that will be done by MPS before shipping the skid. (Reference pictures attached from E skid) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629480&prj=657&rqi=NoD7pLc5whajVjHySPbJ5jn8wm
GI-076 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | For MPS Skid B: The CSA / UL Label is currently not present on the Skid Label. (Per discussion on site this will be once the Skid is at TR6 site) (Issue is added for tracking purpose) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629484&prj=657&rqi=PoV0OcVfue6Kf1cxXPy1BNg7SQ
GI-075 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | For MPS Skid C: The CSA / UL Label is currently not present on the Skid Label. (Per discussion on site this will be once the Skid is at TR6 site) (Issue is added for tracking purpose) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629483&prj=657&rqi=It0U3xUpEI9yaf7kLqYaHS89F6
GI-074 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | For MPS Skid D: The CSA / UL Label is currently not present on the Skid Label. (Per discussion on site this will be once the Skid is at TR6 site) (Issue is added for tracking purpose) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629482&prj=657&rqi=nFif2MAJKpUMF5V2Ko44xlp52t
GI-073 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | For MPS Skid E: The CSA / UL Label is currently not present on the Skid Label. (Per discussion on site this will be once the Skid is at TR6 site) (Issue is added for tracking purpose) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629481&prj=657&rqi=tU1L1IdzLBSuIW0yEYwv4Dg6hT
GI-070 | TR06-3 | AMER | Ready for Verification | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1BTU_RMU_D | BTU - Battery Tripping unit |  |  | For MPS Skid D: The BTU rough in work is not completed. As per discussion during the Factory visit on 15th July, it was decided that will be done by MPS before shipping the skid. (Reference pictures attached from E skid) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629478&prj=657&rqi=8hbLIg8ap47J69dmZzBwG0crAR
GI-057 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | Metallic debris falling into the breaker and busbar compartments. This hazard must be mitigated while drilling and installing the conduit assembly at Section 03A and other Sections. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629272&prj=657&rqi=uQQQ784GwQhJr4MYDhNBayHeKM
GI-064 | TR06-3 | AMER | Ready for Verification | P3 Low CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | MSB LV panel: Missing circuit directories | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629282&prj=657&rqi=gSbmRq7VLtSYhOhNYfVyb7o1T8
GI-059 | TR06-3 | AMER | Open | P3 Low CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Labelling | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | -Sections 07 & 10 UPS Instructions SOO need to update with correct equipment ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629275&prj=657&rqi=58ckNHLkLlrGJcwkuaZj00sedG
GI-062 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  | no | For MSB C: Noted during Spilt Inspection at MPS Factory: The Mimic representation is missing on the areas highlighted in the attached pictures. This is where a plate is installed by AMG for the ERMS switch . (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629274&prj=657&rqi=u7Meu8QofMXTpw6DqZcKV4QM21
GI-068 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | For E Skid: Applicable to the control power section of UDP - E1 and UDP -E2: The section should have a protective plastic cover and caution label since a 460 V input is landed in this section. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629327&prj=657&rqi=1Q3RdhkPjU3jheO5lacdK1x5sf
GI-056 | TR06-3 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | All Skids : K-Kirk devices are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629219&prj=657&rqi=LBPcXe2RaE22vOtT32CrGSTQCi
GI-067 | TR06-3 | AMER | Ready for Verification | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [6 empty] | For MPS Skid E: The CRAH labelling in the skid does not match the labelling provided on the mechanical schedule. On the mechanical skid its 1CRAH-ER-11, 1CRAH-ER-12 and 1CRAH-ER-13. Inside the skid the CRAH labelling is 1CRAH-ER-10, 1CRAH-11 and 1CRAH-12 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629325&prj=657&rqi=X27APUj5H7iJvowZuhC31ndRXN
GI-060 | TR06-3 | AMER | Open | P3 Low CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | Section 08C - Missing mimic lines | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629276&prj=657&rqi=7Mqeknrk2w4espKY2EbgRv2s6l
GI-061 | TR06-3 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | Breaker 12B - 1600A LSI breaker is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629278&prj=657&rqi=23m22vd1mlMGUJ89rUF46gesy9
GI-065 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | Electrical â€“ LV | equipment | 1UDPR_E_1 | UDP - UPS Output Switchboard |  |  | UDPR-E-1 &2 : Incorrect LSIG tripping units have been used for 800A LSI breakers in both UDPR-E 1 & 2. Need correction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629283&prj=657&rqi=6ml0KcG4Nkr4PSWHkvbDBrZbi9
GI-058 | TR06-3 | AMER | Closed | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  | no | For Skid C: Missing Kirk Keys on the MSB C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629273&prj=657&rqi=K5vsuNbP5mGDK7YkINcGbC1x05
GI-066 | TR06-3 | AMER | Ready for Verification | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | Mechanical â€“Air | equipment | 1EF_E_3 | EF - Exhaust Fan |  |  | For MPS Skid E, applicable to the Exhaust fan control panel; The auto / Run selector switch is not labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629315&prj=657&rqi=e6zJCGCZWqZeXzH0o1fD9dGHvz
GI-063 | TR06-3 | AMER | Ready for Verification | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | MSB back cover bolts were not tightened. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629280&prj=657&rqi=t9X94eK83jYgmB90LKAnVBe6XE
GI-055 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-12 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | Applicable to 7 Harmonic Filters: During the receiving inspection, it was noted that the harmonic filters on site do not match the Motor Size (HP/kW) parameter mentioned on the submittal | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628779&prj=657&rqi=I400TzdlQ0ohMJ63b5MjBYwBJn
GI-051 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | [6 empty] | MSB (General) - Section 6 & Section 11 have the voltage present lights for the IOB breakers tapped on the "Critical Bus" output side of the IOB breaker. The voltage present lights by Equinix design should be tapped on the "UPS Output" (cable side) of the IOB breaker. Anord should move the voltage present taps to the same side of the IOB breaker as the PQM voltage sensing leads. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627694&prj=657&rqi=BRnQujRlnuaIK0rq7tm7g5JCvO
RT1ELEC-405-001 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group | L2A | Installation Damage | Commissioning | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | MSB-E - Main PQM 5000A Phase C CT has a cut on the wire. Wire should be repaired. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627695&prj=657&rqi=iK4RIKtIUAFLeEnsdQ8UrxfSDo
RT1ELEC-404-001 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group | L2A | Missing Components | Commissioning | Electrical â€“ LV | equipment | 1MSB_D | MSB - Main Input Switchboard |  | no | MSB-D - Section 11 is missing the barrier that is installed in the same Section 11 on MSB-D on the critical bus section. Anord to install barrier in MSB-D assuming it is needed and to make consistent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627691&prj=657&rqi=7mAMQg0M1SfUwSUo7D4GBPY9I4
GI-054 | TR06-3 | AMER | Ready for Verification | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [6 empty] | TR6-3 submittal: It looks like the HMI terminals were not shown correctly on the MSB side. I updated the names in the yellow cells. Some of the MSB terminals were not shown correctly for breaker, on gen and on static bypass signals. The corrections are in the yellow highlights. The LBB breaker statuses I could not find in the Anord submittal. Did MPS find this or make an assumption? The items highlighted in blue may have to be added by Anord. The maintenance bypass breaker status is not something that MPS wires. These are installed by Anord internal to the gear. Therefore those cells in red should be removed. Assuming these are the standard Vertiv battery cabinets, these should have the 480V control power to the receptacles and SO cords above the battery cabinets. If this has not yet been discussed with Equinix, please discuss to add in MPS scope. This will also need to corrected in the orange cells. Missing some of the battery controls, which I did not add to the spreadsheet. MPS will wire the major/minor alarm (TB1158) from the BIBR to the top hat terminal block in Cabinet 1 [already shown in spreadsheets but missing detail of point to point shown below]. TB1158 #1 (Critical Alarm COM) = Maj Alarm COM TB1158 #2 (Critical Alarm NC) = Maj Alarm NO [Note Samsung and Vertiv NO and NC terminology are inverted] TB1158 #3 (Critical Alarm NO) = Maj Alarm NC [Note Samsung and Vertiv NO and NC terminology are inverted] TB1158 #4 (Maint Alarm COM) = Min Alarm COM TB1158 #5 (Maint Alarm NC) = Min Alarm NO [Note Samsung and Vertiv NO and NC terminology are inverted) TB1158 #6 (Maint Alarm NO) = Min Alarm NC [Note Samsung and Vertiv NO and NC terminology are inverted) MPS will wire the trip (TB4) field wires from the BIBR to the top hat terminal block in Cabinet 1 [not shown in spreadsheets]. TB4-1 - Ground TB4-3 - Input MPS will wire the Vertiv dry contact wire harness from the battery cabinet module to the top hat in Cabinet 1. MPS will wire the MCCB (breaker status) field wires from the BIBR TB3 to cabinet #1 (2 wires) and cabinet #7 (1 wire). Leave the wires coiled up in front of the battery breaker. MPS will leave the MCCB (breaker status) Vertiv wire harness coiled up in front of the battery breaker. Vertiv will make the connections between the MCCB wire harnesses between cabinets and the TB3 field wires. This is at least what we agreed with the DC21 Vertiv team. Will need to confirm with the TR6 Vertiv team. Perhaps Veolia can assist. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627698&prj=657&rqi=dnOu440wzImh1I4y8BnAOWB95R
GI-050 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Design correction needed | Design | [6 empty] | MSB (General) - There is nothing in the submittal that indicates where barriers are to be installed. Is there a drawing that can be provided? In light of the issue above and issues at other sites, we request Anord verify all barriers needed are installed. In particular, we noticed that in Section 6 & Section 11, we don't have barriers on any MSB above the UPS output (IOB). This is the only cable termination section that doesn't have a barrier below. Is this intentional by design? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627693&prj=657&rqi=j4Wu71niCTAVfzXL8nrp79PfEj
GI-053 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | [6 empty] | UDP/UPR (note that only saw the "E" block) - 800A Breaker lugs appear to only be capable for cables up to 500MCM. Per the site design and the breaker schedule attached, the lugs should be able to accomodate up to 600MCM. Anord to confirm and replace lugs as required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627697&prj=657&rqi=hF7JUvw5Ew12KJBWRpQo8QY1nR
GI-052 | TR06-3 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | [6 empty] | UDP & UPDR were shipped with a random combination of 800A Micrologic 5.0A (without ground fault) and Micrologic 6.0A (with ground fault) trip units. Per Equinix standard, the submittals and the breaker schedule attached, all breakers should be 5.0A (without ground fault). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627696&prj=657&rqi=Z88WNVBDZKVdUkP90uK4zj1giC
GI-048 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-06-24 04:00:00.000 +0400 | SMT - SMARDT |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Common for all chiller condensers: Discrepancy in the condenser model number Vs model number noted on the condenser nameplate received on site. On the submittal the model number is "CA150.A020RA.010" On the nameplate of Condensers received on site the model number is "CA150.A020RA.F10" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626708&prj=657&rqi=MZBN1eY3HttRxqnDaLZxUPYnEc
GI-049 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-06-24 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1CH_E_1 PQF | HF - Harmonic Filter |  |  | For 1-CU-E-1: One condenser fan is clipped was found to be not connected to the fan guard. (Fan 1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626797&prj=657&rqi=GWLwELyndulHMFuP7xfZcwx7ov
GI-026 | TR06-3 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | condenser units: 2 units missing product tag/serial number | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625806&prj=657&rqi=OshpRPNCgfgoZMKdUDsFWqBHXs
GI-028 | TR06-3 | AMER | Open | P3 Low CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | condenser unit 4432, 4030, no tag missing book and spair gasket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625817&prj=657&rqi=zDIDuIZVGvL9hfSluEruUyZwG1
GI-027 | TR06-3 | AMER | Open | P3 Low CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Component/ Equipment Failure | Commissioning |  | equipment type |  |  |  |  | Missing plug for fill in port in condenser | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625808&prj=657&rqi=RVyODyFX4mV7fVBjbrn5duEzJQ
GI-025 | TR06-3 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not correct | Commissioning |  | equipment type |  |  |  |  | Condenser skid unit: For all 7 units skid Refrigerant line holder too low, do not support refrigerant piping weight.(Pictures attached) After inspecting this for existing chiller condensers it was noted that this issue is also applicable to 1CU-A-1, 1CU-903B-1, 1CU-904-1, 1CU-R-1 and 1CU-R-2. (Pictures Attached) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625799&prj=657&rqi=MDKsQeOtQWUOKcjscjCuDoEEPk
GI-031 | TR06-3 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not correct | Commissioning | [6 empty] | unit 4430, 4433: exposed copper wire in disconnect | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625825&prj=657&rqi=YVk2Rx4LYacNoOogsWqp4lVf4C
GI-029 | TR06-3 | AMER | Closed | P3 Low CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning |  | equipment type |  |  |  |  | for all condenser unit submittal drawing and unit don't match contactor showed 20 in drawing, only 10 in unit. Two fans connected to one contactor, vendor to notify if wiring valid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625820&prj=657&rqi=aCUJLIeH5e4wTovhHBzY19Hxt6
GI-030 | TR06-3 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Component/ Equipment Failure | Commissioning |  | equipment type |  |  |  |  | condenser unit 4032, no tag: com wire out | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625821&prj=657&rqi=kh3gkNqCn9kmHCCKBnrb1jZrLO
GI-024 | TR06-3 | AMER | Closed | P2 Medium CX | vijay.singh@veolia.com | 2026-06-11 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | FWT | Factory Witness Test | [6 empty] | MSB-E: CTs 4 and 6 may be wired or labelled incorrectly. Phase A has wiring for CT6 and phase C has wiring for CT4. This is reversed from the submittals orientation: | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625010&prj=657&rqi=Pww8FApV2aTIVlAtFFyjKuH34Q
GI-022 | TR06-3 | AMER | Closed | P3 Low CX | qubert.quintal@veolia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | Electrical Block A & R SKID: A few MSB_A breakers were mislabeled (incorrect spelling, incorrect label background color, font size), e.g., UPS_RIB_2, 1UPS-A-2-LBB, 1-CH-A-2, 1LBB_A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623969&prj=657&rqi=avfsB5wNYRDtdFTENgL4fFVULS
GI-021 | TR06-3 | AMER | Open | P3 Low CX | qubert.quintal@veolia.com | 2026-06-04 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Labelling | Commissioning | [6 empty] | The posted SOO procedures at the new MSBs is not correct. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623968&prj=657&rqi=XcBwTLXNFAhv3VzDyOI1TKrF3P
GI-023 | TR06-3 | AMER | Closed | P3 Low CX | qubert.quintal@veolia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [6 empty] | Main Service entrance switchgear 1PUSP_1 & 2 sections are missing equipment identifiers/labels, e.g., Interrupter, Protective Relay, Power Quality Meter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623971&prj=657&rqi=z1Hh1TOP6smjzJO8zuZXccGuqb
GI-020 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Applicable to all the Chillers for TR6-3: It came up part of the GOE inspection that the chillers should include the lamacoid which also matches the name on the BMS along with the lamacoid as per schedule. The chiller panel are missing the labels mentioned on the BMS faceplate associated to the chiller. (refer to the attached picture)(We have used the TR6-2 chillers to demonstrate an example) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623796&prj=657&rqi=DVxwu1TQZbOA4oMRcEsSJq14DW
GI-019 | TR06-3 | AMER | Open | P3 Low CX | jerome.deschenes@veolia.com | 2026-05-25 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning | [6 empty] | chillers submittal need to be provided with new updated drawing 57-0161, as new chillers differ in design from the existing one on Equinix Tr6 from project 2. Valves need to have individual tag and number. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623127&prj=657&rqi=yjhjo6L2zPGJm9BVGxAfOPjgGM
GI-018 | TR06-3 | AMER | Closed | P2 Medium CX | jerome.deschenes@veolia.com | 2026-05-25 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not complete | Commissioning | [6 empty] | Chillers not completed for factory visit Piping cleaned up and joints Missing parts and tie ins for controls and compressors completed. Valves missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623052&prj=657&rqi=zNYt4FVphDuSnL9g9OPE3ovUiK
GI-017 | TR06-3 | AMER | Closed | P3 Low CX | jerome.deschenes@veolia.com | 2026-05-22 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning | [6 empty] | Torque report is required for all high voltage, with calibrated tools, date, value. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622831&prj=657&rqi=DYcq2avAWNz5BFOeRFzXyMqttz
RT1ELEC-128-001 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-04-23 04:00:00.000 +0400 | AMG - Anord Mardix Group | L2A | Installation not complete | Commissioning | Electrical â€“ LV | equipment | 1MSB_Z | MSB - Main Input Switchboard |  | no | Factory assembly is in progress. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619266&prj=657&rqi=xyS2djU3ganGmXrw9GeevKV4y2
GI-016 | TR06-3 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-04-23 04:00:00.000 +0400 | Consultant |  | General Design Issue | Design |  | equipment type |  |  |  |  | For MPS Skid CRAHs in TR6-2 Phase, issue was raised for missing strainers. Based on the discussion with Equinix Design / GOE team this was going to be captured in future designs. Creating issue to track this item or capture feedback on the requirement of strainer on skid crahs. (Refer to attached email chain in the document section of this issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619260&prj=657&rqi=yF9XhaEoCKKs4HjGqCLba3AQ04
GI-015 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-03-02 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design | [6 empty] | Upon failure of the preferred source, the STS will transfer to the alternate source fed by System R. In the event of multiple UPS failures, the first primary block UPS load will transfer to System R via the STS. However, there is a risk of overloading System R if control signals are not sent to the other primary block STSs to engage a transfer inhibit function. This function is necessary to prevent those STSs from also transferring to the redundant block. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483425&prj=657&rqi=IbmH5Ff86vjVbzCjCg4SjUc6Vx
GI-012 | TR06-3 | AMER | Closed | P3 Low CX | Ocean.Kwan@veolia.com | 2026-02-24 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design | [6 empty] | Electrical Single Line for Block B, C, D & E - E605 to E608 Logic detail of K-Key interlock betewwn equipment's to be provided. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199962&prj=657&rqi=xDtr55hG7icd0yuzjAfb3ntMkp
GI-011 | TR06-3 | AMER | Closed | P3 Low CX | Ocean.Kwan@veolia.com | 2026-02-24 04:00:00.000 +0400 | Consultant |  | General Design Issue | Design | [6 empty] | Electrical drawing E601 - The key interlock details for K32 and K31 to prevent parallel of two MV sources is not provided. The number of keys be avaliable and captured in the corresponding cylinder to be specified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199960&prj=657&rqi=MM24dOxzOjHPCwUIofEn2tmLks
CCD-L0-3-001 | TR06-3 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-02-24 04:00:00.000 +0400 | Consultant | DELIVERABLES | Design correction needed | Design | [6 empty] | Electrical drawing E602 MV Single Line diagram has missed RMU shunt trip signal line to RMU protection relay from downstream transformers: - 1RMU_Z -1RMU_901/2 -1RMU_903R -1RMU_903A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199957&prj=657&rqi=f1vpQY3Te5cPuMt9i8KmERpplE
GI-013 | TR06-3 | AMER | Closed | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-24 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design |  | equipment type |  |  |  |  | The Room # mentioned in the mechanical schedule (dwg # M702) for "B Block Mech UPS & Batt.Room 1613" does not match with room # mentioned for this room on the dwg # M131.F and dwg# A120.F, which is Room 1612.Â Same for D Block, in the mechanical schedule for "D Block Mech UPS & Batt.Room 1613", where as in rest of the drawings its 1614. (Refer to the attached pictures)Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204067&prj=657&rqi=j97KvA6DCuvusoBMzp2tGWXLrS
GI-007 | TR06-3 | AMER | Ready for Verification | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Design correction needed | Design |  | equipment type |  |  |  |  | Referring to the Mechanical Schedule Dwg # M702 (Issue G1) (Issued on 5th Feb 2026) For the Electrical Skid CRAH's, the chilled water entering temperature specified is 70 deg F, whereas the Chiller Plant leaving water temperature for the building is 65 deg F. (Screenshot attached) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199719&prj=657&rqi=38jW0z0kRZkMRlI9hC55Oc5Q3J
GI-008 | TR06-3 | AMER | Closed | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-22 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design | Mechanical â€“Air | equipment | 1HP_B_03 | HP - Heat Pump |  |  | 1HP_A_01: The asset name has already used by the WSHP in Block R Electrical Skid. (Attaching screenshot from Mechanical Schedule dwg # M701) (Attaching screenshot from TR6-2 phase BMS screen for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199720&prj=657&rqi=gP8kggtYftH29OAKbXtYYJjMWp
GI-009 | TR06-3 | AMER | Closed | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-22 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design | Mechanical â€“Air | equipment | 1HP_R_03 | HP - Heat Pump |  |  | 1HP_R_01: The asset name has already used by the WSHP in Block R Electrical Skid. (Attaching screenshot from Mechanical Schedule dwg # M701) (Attaching screenshot from TR6-2 phase BMS screen for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199722&prj=657&rqi=s0RegduyRpIkRSRLZNUsWbHgpO
GI-006 | TR06-3 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-22 04:00:00.000 +0400 | SCH - Schneider Mech |  | Design correction needed | Design |  | equipment type |  |  |  |  | Referring to the Mechanical Schedule Dwg # M702 (Issue G1) (Issued on 5th Feb 2026) The DH 906 and DH 907, the leaving air temperature is shown 76 deg F. Comparing with the TR6-2, phase DH908 CRAH's, the leaving air temperature in schedule was 71 deg F. (Screenshot attached) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199718&prj=657&rqi=8rswJTzO8cRB2OuIsco2fM27U1
GI-010 | TR06-3 | AMER | Closed | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-22 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design | Mechanical â€“Air | equipment | 1HP_R_05 | HP - Heat Pump |  |  | 1HP_R_02: The asset name has already used by the WSHP in Block A Electrical Skid. (Attaching screenshot from Mechanical Schedule dwg # M701) (Attaching screenshot from TR6-2 phase BMS screen for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199723&prj=657&rqi=fYnYGhBZqkqykNtikyj8W8cHXL
GI-005 | TR06-3 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-02-21 04:00:00.000 +0400 | Consultant |  | Design not as specified | Design | Electrical â€“ LV | equipment | 1CH_B_1 PQF | HF - Harmonic Filter |  |  | ACCH have recuring issues regarding cold start-up when OAT not available to enable free-cooling. This generate fails to start alarm each time, requiring a service call and unavailability of a redundant chiller during fail period. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199715&prj=657&rqi=k9s7a1goCaAQqfWKkhwFO3cyak
GI-004 | TR06-3 | AMER | Closed | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-20 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design | Mechanical â€“ Water | equipment | 1TST_A_2 | TST - Thermal Storage Tank |  |  | For 1-CH-A-2, the associated thermal storage tank asset name is "1TST A-2". In the TR6-2, phase the asset name "1TST A-2" has been used by the Thermal storage tank associated with chiller 1-CH-903B-1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199703&prj=657&rqi=L3pikTKPiKRuD3hOuni5onzwUG
GI-003 | TR06-3 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-02-18 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design | [6 empty] | Chilled water filtration missing from system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199463&prj=657&rqi=Ub3vmTnpW6xvPijLAeD4RvmG5c
CCD-L0-2-001 | TR06-3 | AMER | Open | P3 Low CX | jerome.deschenes@veolia.com | 2026-02-18 04:00:00.000 +0400 | General Contractor - BMS | DELIVERABLES | Design correction needed | Design | [6 empty] | SOO is missing from specification package. A building standard operating sequence will provide clarity of how the system is designed to operate at day1, avoiding cost and changes during cx | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199471&prj=657&rqi=88xWEWH2JMc1RKjRyvHGggiqP5
GI-002 | TR06-3 | AMER | Closed | P2 Medium CX | jerome.deschenes@veolia.com | 2026-02-17 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design |  | equipment type |  |  |  |  | Outside air temperature for chillers are set at 102.4 F (39.1 C) Last year highest temperature was 36 C, on ground. Chiller capacity shall be selected at a 20 yrs extreme outside temperature, to allow for optimum capacity of remote condenser at peak summer month. Also , chiller remote condensers are now juxtaposed one to one in TR6-3 projects, creating a increased air temperature at condenser intake, plus roof air temperature. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199382&prj=657&rqi=1i0QcmZQ5ui6SqRv21QRtMN8zD
GI-006 | TY11-P3 | APAC | Closed | P3 Low CX | gerrydevera@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | UPS No. 6 IST On the BMS screen â€œPDU-U46-A1,B1,â€ the assignment for the common spare circuit breaker display for PDU-U46-B1-5C1 was incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626026&prj=649&rqi=hdeZIeEhoOc8eAr6deemAuv1nl
GI-005 | TY11-P3 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Commissioning Authority |  | Component/Equipment Failure | Commissioning | [6 empty] | During an in-house PDU switching test, the thyristor fuse (200A) blew. The cause was identified as the transformer's inrush current. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619208&prj=649&rqi=oX3XagH0bDVI9kQWZWKR4OuYVh
GI-004 | TY11-P3 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT-Elec-Lv2-The breaker labels are not attached to PDU distribution panels for Units 7 and 8. The breakers for PDU No. 1 to 6 also require verification. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618313&prj=649&rqi=0dleJHUQM0A8Nom6Ab45KQVyB7
GI-003 | TY11-P3 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT-Elec-Lv2-Load names (FED FROM) are not affixed to PDU power distribution panels Units 1 to 8. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618183&prj=649&rqi=2twNiYbgiUQdsGU70Tju2sysSb
GI-002 | TY11-P3 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Installation not complete | Commissioning | [6 empty] | CxLv3-ELEC-UPS No.6-BMS communication test pending due to incomplete wiring from the relay terminal panel to BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199437&prj=649&rqi=wyUNKi6UzzGQxw4TTN8mgJqYrq
GI-001 | TY11-P3 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-02-16 04:00:00.000 +0400 | Commissioning Authority |  | Installation Damage | Commissioning | [6 empty] | SAT-ELEC-Lv2-UPS No.6-The side part of output breaker 52P603 was found damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199327&prj=649&rqi=HZLsgb6YAZRWlS7VK2MvLwI4ow
GI-018 | TY15-1 | APAC | Closed | P3 Low CX | JezkielDomingo@sygna-apac.com | 2026-04-06 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT: Mechanical L3 During the operation check of the CHW motor valve, condensation occurred on the CHW pipe near 2-1-SWIT-12-4 including the bypass pipeline. The room temperature at the time of the test was 26Â°C, the humidity was 71%, and the CHW supply temperature was 20Â°C. contact Takasago for the cause and solution. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=88453&prj=352&rqi=ZHEI1axSiVacmOBJATgbbb2UeE
GI-078 | TY15-2 | APAC | Open | P3 Low CX | MasafumiOkuno@commtechasia.com | 2026-08-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | B-IST No.1 After switching to GEN power, a communication error was reported for the following FCU. On-site, it was confirmed that the equipment continued to operate, and the alarm on the BMS automatically reset approximately 5 minutes later. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635015&prj=548&rqi=IW662rJDYRymId4PDefY0YR3zg
GI-080 | TY15-2 | APAC | Closed | P3 Low CX | MasafumiOkuno@commtechasia.com | 2026-08-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | B-IST No.1 (Power outage test) After the switch to GEN power, the four exhaust fans in generator rooms No. 6 and No. 7 (1-1-EF-12 18a, 1-1-EF-12 18b, 1-1-EF-12 19a, 1-1-EF-12 19b) were supposed to shut down, but they continued to operate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635030&prj=548&rqi=W9W2w1kbHa5PgBBaxZycaPwlMW
GI-079 | TY15-2 | APAC | Open | P3 Low CX | MasafumiOkuno@commtechasia.com | 2026-08-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | B-IST No.2 (Generator Failure/Restoration Test) Because the procedures for restoring the generator and DPF system are complex, detailed instructions and sequences should be included in the user manual. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635023&prj=548&rqi=3x2t0lMKbgKXZeRDKmmXEwz6fz
GI-081 | TY15-2 | APAC | Closed | P3 Low CX | MasafumiOkuno@commtechasia.com | 2026-08-25 04:00:00.000 +0400 | Commissioning Authority |  | improper settings | DCOS | [6 empty] | B-IST No.5 The relationship between the UHV-B power output of 0 kW and the TRB secondary-side power of 107 kW; the reason for measuring power at the TR secondary side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635036&prj=548&rqi=iAV7nsmkAyd7pNQ80kuvM3Il9c
GI-082 | TY15-2 | APAC | Open | P3 Low CX | MasafumiOkuno@commtechasia.com | 2026-08-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | B-IST No.1 Regarding the timer setting for the black smoke removal system: although it is currently set to 20 seconds (with a maximum of 24 seconds), black smoke was observed being emitted for several minutes. Discussions are required to reconfigure the timer setting. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635037&prj=548&rqi=yUTyIYShGfksQVZKABkWSgg4rF
GI-074 | TY15-2 | APAC | Closed | P3 Low CX | SabinBasnet@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | During MIST operation check on chiller (8-1-CH-12-1), it was confirmed that the solenoid valve on drain pipe on Mist panel-1 was broken which caused the flow of water into the drain as soon as the Mist system was started. Although the MIST Control check is done on all the mist systems from BMS side, the MIST system operation confirmation is yet to be checked on (8-1-CH-12-3) as the main breaker for MIST system had to be replaced and yet not replaced. so confirmation on valves and operation of (8-1-CH-12-3) mist is yet to be confirmed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623175&prj=548&rqi=bZtsECgt3cQVvqzY9EIh5D7uSG
GI-073 | TY15-2 | APAC | Closed | P3 Low CX | SabinBasnet@commtechasia.com | 2026-05-26 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | During MIST operation check on chiller (8-1-CH-12-4) even when the run command was issued on auto mode from BMS side the Mist pump on controller-1 didnot start up causing up a congestionor breakge alarm on BMS side and the MIST-2 started instead. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623092&prj=548&rqi=vZ8r9BYropK0gkHW4I0qKqP39X
GI-072 | TY15-2 | APAC | Closed | P2 Medium CX | SabinBasnet@commtechasia.com | 2026-05-25 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  | equipment type |  |  |  |  | SAT : - Mechanical - (Mist System on Chiller) [NTTF/Carrel - 8-1-CH-1, 8-1-CH-2, 8-1-CH-3 &8-1-CH-4) - Cx3] During Mist operation check on chillers(8-1-CH-1, 8-1-CH-2, 8-1-CH-3 &8-1-CH-4) alarm signal was being received on BMS side for an instant only whenever mist operation was started. Due to which the mist pump was stopping soon afterwards. therefore the mist control operation couldnot be confirmed on time. (refer to issue GI-066) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623022&prj=548&rqi=HnEyCxsuuAqyP6Sn9TlNjQD31C
GI-071 | TY15-2 | APAC | Closed | P3 Low CX | SabinBasnet@commtechasia.com | 2026-05-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | During Mist operation check on chillers, the nozzle head on the sprinklers pipe of mist system of 8-1-CH-12-12 got blown away while the mist system was on operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623017&prj=548&rqi=w5hiAIJy2XBwyhYzdlnLyS4lkG
GI-069 | TY15-2 | APAC | Closed | P3 Low CX | SabinBasnet@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | During UPS No.5 IST (Test9: Fire system test) while deactivating the central fire system control the BMS side control was also disabled mistakely so the fire alarm did not show up on BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622607&prj=548&rqi=PkYLJWALQaUK3ZmjBaISKGYt72
GI-068 | TY15-2 | APAC | Closed | P3 Low DCOS | SabinBasnet@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | During UPS No.5 IST Test6, during the STS automatic switching test, on the BMS side both the primary and redundant side sources were shown as supplying the output for 7-1-STS-12-U5-2-1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622605&prj=548&rqi=sEPF2Tkmdaf8Rr5P0KNbvdfoi1
GI-066 | TY15-2 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | SAT-Chiller system-regarding the mist system (æ•£æ°´) , NTT-F plans to interchange the Solenoid Valves and Low Switches location on all chillers due to recurring alarms. However, parts must be ordered from Italy (unavailable in Japan), causing procurement delays. They admit this may push completion beyond the end-March deadline, despite their efforts. Requested action: They must submit a report detailing their exact plan and schedule immediately. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615793&prj=548&rqi=T7Kb39GpFzdTKuYRr6w6DrCI4l
GI-064 | TY15-2 | APAC | Closed | P3 Low DCOS | SabinBasnet@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | During STS load test, Analog values did not match during communication between the STS and BMS. During testing, when switching communication mapping between the old and new addresses, the old address was considered even when the new address was correct. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614686&prj=548&rqi=lhZJ7adGWN7YedVoIX5pjGwoQI
GI-063 | TY15-2 | APAC | Closed | P3 Low DCOS | SabinBasnet@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | During the alarm verification on STS, the General Alarm on the BMS screen for the STS ((5-1-STS-12-U5-2-2) was not showing up even though the alarm was produced on the equipment side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483414&prj=548&rqi=Z8HQanJzMqsLkEYtJIIvTrf3aY
GI-062 | TY15-2 | APAC | Closed | P3 Low DCOS | SabinBasnet@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | BMS Graphics Errors: 1.On the Generator (No. 3, 4) BMS screen, the [Synchronizing] setting for DEG No. 4 was not set. The point during synchronization verification was selected incorrectly, so the [Synchronization] indicator did not light up. 2. On the Generator (No. 5, 6) Gen No. 5 screen, [Manual] was displayed even though the mode was automatic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204136&prj=548&rqi=ctVcdps4w1WrhqSiUdbVFyt8Ud
GI-060 | TY15-2 | APAC | Closed | P3 Low CX | SabinBasnet@commtechasia.com | 2026-02-02 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [6 empty] | On the display panel of generator circuit breaker board (1-1GSB-GCBP-4) & (1-1GSB-GCBP-5) of DEG no. 4 &5, the output voltage and current to theã€€DEG control panel (1-1-GSB-CP-4&5) through transformer was displayed as zero although the output on the control panel display was okay. The same problem might be there on other DEG system as well so it is necessary to check the previously commissioned DEG No. 1, 2&3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198089&prj=548&rqi=X67hBJ2UqkOGNTsSYoYvX7eEzX
GI-124 | ZH04-6 | N-EMEA | Open | P3 Low CX | agryszko@global-cxm.com | 2026-09-04 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Permament label with ID name missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636841&prj=555&rqi=EQ28JhCxpxhtBVpeMHZsFG6kEG
GI-125 | ZH04-6 | N-EMEA | Open | P3 Low CX | agryszko@global-cxm.com | 2026-09-04 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | equipment type |  |  |  |  | Permament label with ID name missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636842&prj=555&rqi=DapJw8vwVvA5tVGBqpPZCOMvRM
FPT-98-001 | ZH04-6 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Multi-Discipline | system | Migration A |  |  |  | potential issue during switching A5. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636759&prj=555&rqi=9jNHNc9MfF2fHNpWYtlVOhd3eF | https://equinix.facilitygrid.co.uk/x/project/555/system/14760
GI-122 | ZH04-6 | N-EMEA | Open | P3 Low CX | gmcdonough@global-cxm.com | 2026-09-03 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | equipment type |  |  |  |  | All test conducted on CRAH-03-13 and only the fan failure test failed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636680&prj=555&rqi=MvPCC4DT9tUJZlIosmiUXrc2px
FPT-98-002 | ZH04-6 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning | Multi-Discipline | system | Migration A |  |  |  | fuse blown on A2 during switch to put IT load on batteries | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636761&prj=555&rqi=vBVMmMSzqSYI1RLuSc9qh6PP1i | https://equinix.facilitygrid.co.uk/x/project/555/system/14760
GI-123 | ZH04-6 | N-EMEA | Open | P3 Low CX | gmcdonough@global-cxm.com | 2026-09-03 04:00:00.000 +0400 | General Contractor |  | DCOS Comms Issue/Fault | DCOS |  | equipment type |  |  |  |  | During the power failure test, when the alternative power supply was open the alarm info on Vertiv control side stats fire alarm in steady alternative power supply open. Seems like an addressing issue, potentially related to the software upgrade? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636683&prj=555&rqi=hinExAsP3QA88ii3L0RscKkLsz
GI-121 | ZH04-6 | N-EMEA | Open | P1 High CX | agryszko@global-cxm.com | 2026-08-27 04:00:00.000 +0400 | Equinix Project Manager |  | Component/Equipment Failure | Commissioning | [6 empty] | During RMU testing GEN tripped on overcurrent without any load on it, during investigation, burned spots on Step-up transformer were identified. Equipment on that connection is being investigated by Siemens/Schneider/Avesco, The asset will be updated as soon the root cause of the issue is identified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635579&prj=555&rqi=JXuWhZ2ds86TyQ6tOENVCYGwhE
GI-120 | ZH04-6 | N-EMEA | Open | P2 Medium CX | gmcdonough@global-cxm.com | 2026-08-25 04:00:00.000 +0400 | General Contractor |  | Incomplete Connections | Commissioning |  | equipment type |  |  |  |  | Shielding cable on the CRAH DB not completely sleeved from cable to earth bar. This is an issue on EVERY ground floor CRAH, not on one or 2 but on all. Hardly any ferrules attached to the sleeving either to the earth bar, again need to be rectified before powered on. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635034&prj=555&rqi=4PnYU9SekbBKVLVKdoExx77ovl
GI-108 | ZH04-6 | N-EMEA | Closed | P2 Medium CX | agryszko@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Not Correct | Commissioning |  | equipment type |  |  |  |  | Trip Lockout not working properly for intertrip. Breaker opens properly, but operator is able to close it immediately, without clearing the lockout. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618823&prj=555&rqi=ysgF3UIQ5nqGlwp5OiyLPmB2L0
GI-104 | ZH04-6 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-03-04 04:00:00.000 +0400 | General Contractor |  | Installation Not Correct | Commissioning | [6 empty] | Cable connections into the 3rd floor CRAH's Glands are lose as the cable is smaller than the gland size | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614684&prj=555&rqi=j6oqwBjlpqxcyd9gqvEc8tqRRi
GI-106 | ZH04-6 | N-EMEA | Open | P2 Medium DCOS | Matt.Harker@eu.equinix.com | 2026-02-24 04:00:00.000 +0400 | Equinix Project Manager |  | Commissioning Issue | Commissioning | [6 empty] | Major incident occurred when Siemens attempted to upload additional pieces of Equipment to the live system: Extract of RCA issued by Siemens below: In calendar week 8, the PLC CPU (S7-400) had to be set to "Stop" mode for loading new components as part of project ZH4.6 (project ZH4.6 relevant). After the software download and the restart of the CPU, a MODBUS RTU communication string to several CRAHs could not be put back into operation (existing BMS relevant). This communication strand belongs to the investment part "legacy system" and comes from earlier projects. Siemens started the investigation in coordination with Mr. Milovan Kovacevic (email of 19.02.2026, 15:31). The aim was on the one hand to restart the aforementioned MODBUS RTU string and on the other hand to identify the cause of the fault (existing BMS relevant). In the course of the recommissioning of this mentioned string and the troubleshooting, a firmware update was prepared for the affected legacy part of the BMS. This update was planned for 02/24/2026 and related exclusively to the legacy part of the BMS. The installation of the FW update was carried out exclusively on the PLC level via Profibus (ZH4.6 no longer has Profibus but exclusively Profinet). Further details can be found in the document "Technical Root Cause Analysis Modbus RTU.pdf". Resolution to be added once finalised. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616273&prj=555&rqi=hhnVa0uzQfLvUmJsLQzyHKGTsX
GI-100 | ZH04-6 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-02-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Design not as Specified | Design | Fuel | system | Fuel System |  |  |  | In the Fuel system SOO, the day tanks have 5 different Fuel level sensor and values. However, on site only 3 sensors are in the tanks. Clarification needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199659&prj=555&rqi=uSHjR0eyeGc7AlyCqfobEb79Mw | https://equinix.facilitygrid.co.uk/x/project/555/system/13439