## Issues_FG_2026202609210932_Manu
issue_code | fg_issue_uuid | project_name | fg_project_id | region | issue_status | priority | reported_by | reported_on | responsibility_name | cx_level | issue_type | issue_category | issue_manufacturer | discipline | asset_type | asset_name | equipment_type_name | manufacturer | model_number | description | issue_url | system_url
GI-017 | 3e1b5414-1396-4970-8aa9-7d453f52b6a3 | AM04-P3 | 620 | N-EMEA | Ready for Verification | P2 Medium CX | bjorn.ketelaar@eu.equinix.com | 2026-07-02 04:00:00.000 +0400 | Vendor- Manufacturer |  | Installation Damage | Commissioning | [7 empty] | GSCP has sustained transport damage not clear if internal components are operational, Cummins to verify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627803&prj=620&rqi=IvNvH2WM3dfljj7pO0wZoe62kP
GI-011 | 6530269a-8870-40b8-9a7d-be86f0845c97 | AM04-P3 | 620 | N-EMEA | Closed | Outstanding Paperwork/Documentation | Willem.Zwaagstra@eu.equinix.com | 2026-06-03 04:00:00.000 +0400 | Vendor- Manufacturer |  | General Design Issue | Design | [7 empty] | Following site observations, Equinix would like to clarify the specification and compliance, particularly for the flange connections used in the cooling water piping. It appears that some of the flanges may have been fabricated, rather than standard manufactured flanges. As this system is part of a pressurized installation, we need to confirm that all installed components comply with the relevant pressure equipment standards. Additionally, based on observations in a previous project phase (AM4.P2), similar flange connections in comparable positions also appeared relatively light compared to the mating equipment flanges. However, in the current AM4.P3 installation, this difference appears more pronounced, with visibly thinner flanges being applied. Could you please confirm: - Which standards these flanges are designed and manufactured to (e.g. EN / ASME, pressure class / PN rating, DN designation); - That the flanges are suitable for the operating pressure and conditions of the system; - Whether the required markings (including DN, pressure class, and material/specification) are applied or otherwise traceable. This information is required to ensure compliance and to verify that the installation is suitable for safe and reliable long-term operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623916&prj=620&rqi=6G4jIKjO0xTDbhoAOomp8RvyG0
GI-007 | f07d63fb-7db2-1127-50d5-a8e2c48438c7 | AM04-P3 | 620 | N-EMEA | Work Completed | P2 Medium CX | christiaan.Gillot@se.com | 2026-04-30 04:00:00.000 +0400 | Vendor- Manufacturer |  | Commissioning Issue | Commissioning | [7 empty] | extra terminals for supply loop XM144 XM145 k205 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620034&prj=620&rqi=m4d9GErcKoUtuRQzC40IO75eiQ
GI-019 | bd93564f-8601-7375-ced9-6a2e75bd3f2a | AT10x-1 | 601 | AMER | Open | P3 Low CX | christopher_boyle@fsttechnical.com | 2026-06-30 04:00:00.000 +0400 | VER - Vertiv |  | Installation not complete | Commissioning | [7 empty] | Containment bonding missing throughout Ehouses sparaticly. Please see attached examples of missing bonding throughout multiple Ehouses. Once all bonding is complete please coordinate a walk with Vertiv and FST to verify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627617&prj=601&rqi=24jol6Ithj5qbjw6h9t04v1sU7
GI-007 | 7b68b519-86b5-4b5c-9801-2aa0dc3be87b | AT10x-1 | 601 | AMER | Closed | P3 Low CX | christopher_boyle@fsttechnical.com | 2026-06-29 04:00:00.000 +0400 | Electrical Contractor |  | Documentation not issued/ Required | Commissioning | [7 empty] | 1GEN Torque report document issues please see attached red lined report. Affected reports -1GEN_R3 -1GEN_P -1GEN_Q -1GEN_S -1GEN_U -1GEN_V -1GEN_R4 -1GEN_W -1GEN_AA -1GEN_BB -1GEN_CC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627257&prj=601&rqi=6irqVkghNP6KgEe3fN5uTmrEBb
SOR-57-001 | ca16661a-2376-4828-821a-6a1eb764745e | AT10x-1 | 601 | AMER | Open | P3 Low CX | eric_reinhard@fsttechnical.com | 2026-06-11 04:00:00.000 +0400 | Fire Contractor |  | Installation not correct | Commissioning | [7 empty] | Fire Pump Fuel Tank. Fuel line is called out in drawing #FP401-FPH, Detail 10 to have a "1/2 CL BLK nipple and electronically supervised ball valve or potter rbvs tamper switch". Inspection of the tank found that there is not a tamper switch installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635681&prj=601&rqi=Plf6GU3MoIg3JGFk0Zt8jtoW2V
GI-016 | ada8a82a-bde2-5833-2885-bda1aa1aeddd | AT10x-1 | 601 | AMER | Closed | P3 Low CX | christopher_boyle@fsttechnical.com | 2026-06-10 04:00:00.000 +0400 | VER - Vertiv |  | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MPZ_R2_1 | PP - Power Panel |  |  | ground cables not labeled inside asset or at earth bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624795&prj=601&rqi=EVC40qfxRepHTrSXZeKnMTQawR
GI-012 | 6c6951ab-00fe-af17-9f42-0b4dfff0f88d | AT10x-1 | 601 | AMER | Closed | P3 Low CX | christopher_boyle@fsttechnical.com | 2026-06-10 04:00:00.000 +0400 | VER - Vertiv |  | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MPZ_L_2 | PP - Power Panel |  |  | Ground cables not labeled inside asset and not labeled at earth bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624782&prj=601&rqi=cAOOp5DZYjsP71NSXoNwrI70vp
GI-011 | 19e1b152-04d1-9f3e-f8da-85284020a393 | AT10x-1 | 601 | AMER | Closed | P2 Medium CX | christopher_boyle@fsttechnical.com | 2026-06-10 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MPZ_L_2 | PP - Power Panel |  |  | loose strands and broken strand in terminal on main circuit breaker to transformer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624781&prj=601&rqi=9ObCXCP2IKkd5yvknv8FE5chyA
RT1ELEC-2341-002 | d46e06b1-0fd9-5b31-3667-8f27c29b8b9a | AT10x-1 | 601 | AMER | Closed | P3 Low CX | joseph_donnelly@fsttechnical.com | 2026-06-09 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1MPZ_L_2 | PP - Power Panel |  |  | latch on door damaged/loose. Will not hold open. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624594&prj=601&rqi=x3ZYdOxRIa9jHAoJqH8MTjRfBV
RT1ELEC-2341-003 | 86557366-e92b-66da-da3e-5047a15a8258 | AT10x-1 | 601 | AMER | Closed | P2 Medium CX | joseph_donnelly@fsttechnical.com | 2026-06-09 04:00:00.000 +0400 | Electrical Contractor | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1MPZ_L_2 | PP - Power Panel |  |  | Extension toe for neutral connection to terminal block loose. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624614&prj=601&rqi=MGAxkUnCNXFBOHXCQc3cUBJK7d
RT1ELEC-2341-001 | 68849c77-acd3-7aa4-ee74-2a5aaf06cfc8 | AT10x-1 | 601 | AMER | Closed | P2 Medium CX | joseph_donnelly@fsttechnical.com | 2026-06-09 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MPZ_L_2 | PP - Power Panel |  |  | cable strands damaged/exposed on main breaker tx side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624593&prj=601&rqi=fqRVnetjM98MmXiDv0PJ3Mpd8q
GI-005 | c8a58c9a-cd9f-4370-b12a-73adbf71a4ef | AT10x-1 | 601 | AMER | Closed | P2 Medium CX | eric_reinhard@fsttechnical.com | 2026-06-02 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | [7 empty] | The underground electrical duct terminations with pulled cable should be provided with temporary closure per spec 26 0543.3.5.I. "Sealing: Provide temporary closure at terminations of duct with pulled cables. Seal spare duct at terminations. Use sealing compound and plugs to withstand at least 15-psig hydrostatic pressure" This should be corrected site wide. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623708&prj=601&rqi=DjNfEBrFM0tAFDNycZDk8jTsxC
GI-004 | ffa44ce2-0d51-40e6-b985-6e9d74b1d5ab | AT10x-1 | 601 | AMER | Closed | P2 Medium CX | eric_reinhard@fsttechnical.com | 2026-05-26 04:00:00.000 +0400 | VER - Vertiv Electrical |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | Per Equinix, opening issue for tracking purposes given the following concerns brought up in E-house permitting & Fire Protection meeting on 5/26/26: â€¢ Vertiv to share the Industrial Building Permit documents, and confirm the status of approvals and inspections. o Stamped EoR drawings showing final installation to be confirmed o Once shared, Northstar will coordinate this with the fire marshall | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623166&prj=601&rqi=2UoDsuH7ElxUGvcJmeqH7ZHHSC
RT1ELEC-2374-001 | dbef15ae-8577-2972-21b8-175c63f7f3e7 | AT10x-1 | 601 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-22 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1MPZ_AA_2 | PP - Power Panel |  |  | One of the leads heading to the transformer (480v) is not landed correctly, one half of the wire strains were in the breaker and it pulled right out. The other two leads are done very poorly.. The leaving leads (120v) coming from the transformer also have a lot of stray strains. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622810&prj=601&rqi=UWdDfvPMBAhBMw7iRiIPHju2Su
GI-002 | d575decd-c72b-498d-b4c8-fdfaca0d4866 | AT10x-1 | 601 | AMER | Closed | P3 Low CX | eric_reinhard@fsttechnical.com | 2026-05-20 04:00:00.000 +0400 | Commissioning Authority |  | CxA Miss | Commissioning | [7 empty] | Facility Grid Training Session - Test Issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622424&prj=601&rqi=l4qItUA35rU26wANDfxOn6AZs0
RT1ELEC-2380-001 | 0d83143a-af01-0e65-2f63-021307f3fde6 | AT10x-1 | 601 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-20 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MPZ_CC_2 | PP - Power Panel |  |  | This panel is missing 2 covers, the main dead front to protect the breaker area and the other smaller dead front that protects the 90amp breaker feeding the transformer above. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622478&prj=601&rqi=ciimCfavDuWp8LGy1pvCNn6VdX
GI-001 | 0bfd8256-cf63-f4ab-c2d7-74a08f12b2ef | AT10x-1 | 601 | AMER | Closed | P2 Medium CX | eric_reinhard@fsttechnical.com | 2026-05-14 04:00:00.000 +0400 | General Contractor |  | CxA Miss | Commissioning | [7 empty] | marvair units sitting on pad are not wrapped and are exposed to dust. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621915&prj=601&rqi=OGLFOlOP9o8ynQ5yexBSVCnilB
RT1ELEC-2365-001 | e0952897-f700-203b-5d42-9a5154248b8d | AT10x-1 | 601 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-12 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MPZ_W_2 | PP - Power Panel |  |  | The transformer wires coming down into the breaker and frayed and wire strands are not secured in the block | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621431&prj=601&rqi=cY2iMdQr69uKgiIIuNR9EykybO
RT1ELEC-2365-002 | 0ae1cd7b-9ed9-affc-905a-30518532c025 | AT10x-1 | 601 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-12 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1MPZ_W_2 | PP - Power Panel |  |  | Missing project required double torque marks on the neutral wire landed on the neutral bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621432&prj=601&rqi=wDe89FDv2ljAq9jVje3HDeEa3M
RT1ELEC-2350-001 | 7b133d1b-108e-5738-8845-8751e1196e32 | AT10x-1 | 601 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1MPZ_Q_2 | PP - Power Panel |  |  | Missing double torque marks on on the neutral line coming from the transformer landed on the neutral bus, see attached picture. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620590&prj=601&rqi=LEb0Z5f7AHg1vsPgWv7eI7UIpb
RT1ELEC-2359-002 | a3c3e0b3-1ba7-2449-7fa8-502fdb065d2d | AT10x-1 | 601 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1MPZ_U_2 | PP - Power Panel |  |  | The small bare ground is not landed on the ground bus | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620596&prj=601&rqi=5CCuLxd9HpBy5lkC6HW7iqN7lb
RT1ELEC-2359-001 | db81d235-ae12-f628-fe49-dbe993d37d7a | AT10x-1 | 601 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MPZ_U_2 | PP - Power Panel |  |  | This unit is missing the dead front in the panel section of the unit. It is not anywhere in the room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620595&prj=601&rqi=Ylxg0nhOR11n8Q3LTChJlYNfkQ
RT1ELEC-2353-001 | 8347a30e-2309-f528-47ce-20c2e6584b73 | AT10x-1 | 601 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1MPZ_S_2 | PP - Power Panel |  |  | Missing the the double torque marks on the 3 transfer leads coming down to the breaker and on the 1 Neutral line heading to the neutral bus bar. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620592&prj=601&rqi=3gIAMPscEmp9GCfLnZV65mirUN
RT1ELEC-2383-001 | c00f9aae-6965-98dd-7acd-8533ae053cb2 | AT10x-1 | 601 | AMER | Closed | P1 High CX | Joe_Richardi@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1MPZ_R3_1 | PP - Power Panel |  |  | Missing double torque marks on the transformer line coming down into the lower panel. See attached picture | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620571&prj=601&rqi=li2SyTNDq4zoNVm0KbmRP7BBmX
BKT1ELEC-9-006 | 65bf1979-3773-40fd-a539-055d98cacab2 | AT10x-1 | 601 | AMER | Closed | P3 Low CX | Rangsiya_Faihin@fsttechnical.com | 2026-04-16 04:00:00.000 +0400 | VER - Vertiv Electrical | L1 | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | MSB_AMCOP Panel has not been received. In the delivery inspection that was submitted by Cleveland repetitive identify that a panel has been missing, and Vertiv is aware that all units is missing a panel, they stated that it will be installed at a later date. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618412&prj=601&rqi=wyJUdiplIffFsSdmJyCls8rX4n
SOR-14-001 | 0fad4f47-84b8-4d5b-b06a-ad485ac20765 | AT10x-1 | 601 | AMER | Closed | P3 Low CX | eric_reinhard@fsttechnical.com | 2026-03-30 04:00:00.000 +0400 | Fire Suppression Contractor |  | Installation not correct | Commissioning | [7 empty] | FST inspected one of the Dry Pipe Sprinkler Valve assemblies in Area C and found that the downstream isolation valve w/ tamper switch was not installed. The double-interlock Dry Pipe Valve is identified in detail #2 and #5, located on drawing [FP500-AT10x]. See attached images of details. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616879&prj=601&rqi=5NJyU7OTMRNSgd3MkqFOZPQz3H
YT1ELEC-512-001 | f4cc0148-5488-4632-bd36-3da1ba06de26 | CH05-2 | 638 | AMER | Open | P2 Medium CX | christian.rivera@veolia.com | 2026-09-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_H_3 | LIBATT - UPS Battery |  |  | 1BATT_H_1 Level 2B Missing CAN bus cables | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638754&prj=638&rqi=BrL2KGHDL5CbC4Qeiz2YMiFbLe
YT1ELEC-510-001 | bd7628f5-4862-425c-a875-6f53cb80ed5a | CH05-2 | 638 | AMER | Open | P2 Medium CX | christian.rivera@veolia.com | 2026-09-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_H_1 | LIBATT - UPS Battery |  |  | 1BATT_H_1 Level 2B Missing CAN bus cables | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638751&prj=638&rqi=uisoQ796cCYaIGr0EmkayblUh6
YT1ELEC-511-001 | b8d6765e-dfc9-46a9-b43f-e1c2c542ba96 | CH05-2 | 638 | AMER | Open | P2 Medium CX | christian.rivera@veolia.com | 2026-09-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_H_2 | LIBATT - UPS Battery |  |  | 1BATT_H_2 Level 2B Missing CAN bus cables | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638752&prj=638&rqi=ka71jjvfVahRtth6uzGcPPnnFq
YT1MECH-150-002 | fb3e4512-2554-41e1-a7f8-fc3e5956f2f2 | CH05-2 | 638 | AMER | Closed | P2 Medium CX | benjamin.mei@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Design not as specified | Design |  | HVAC | equipment | 1WSHP_D_1 | HP - Heat Pump |  |  | Common to all WSHPs, breaker size off panel are 20A breakers which is correct per equipment submittal and panel schedule. Nameplate on units call for 15A breakers. Submittal for Phase 2 also lists for carrier as manufacturer not trane. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629145&prj=638&rqi=FoCaBRy0fRl6UskWIspeYKxpYQ
GT1MECH-123-001 | cf8def97-8483-4a4c-963e-19ee3a8231bc | CH05-2 | 638 | AMER | Closed | P2 Medium CX | marcello.scalise@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Missing Components | Commissioning |  | HVAC | equipment | 1WSHP_E_2 | HP - Heat Pump |  |  | (1WSHP_E2) On/off switch is missing lockout bracket that is present on D skid WSHPs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628595&prj=638&rqi=CwmAmzkFWRmWnl5Tk8r3hPKzzB
GT1MECH-122-001 | 2ef23805-e102-470d-86d3-fc1661f46d01 | CH05-2 | 638 | AMER | Closed | P2 Medium CX | marcello.scalise@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Missing Components | Commissioning |  | HVAC | equipment | 1WSHP_E_1 | HP - Heat Pump |  |  | (1WSHP_E1) On/off switch is missing lockout bracket that is present on D skid WSHPs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628594&prj=638&rqi=UIkUiVQfXnDyuG6BJGLaEgbNT4
GT1MECH-124-001 | 018d3842-96d8-43db-9007-4d3cf73dc13c | CH05-2 | 638 | AMER | Closed | P2 Medium CX | marcello.scalise@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Missing Components | Commissioning |  | HVAC | equipment | 1WSHP_F_1 | HP - Heat Pump |  |  | (1WSHP_F1) On/off switch is missing lockout bracket that is present on D skid WSHPs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628596&prj=638&rqi=YMFWnvrt3TPlwtyuWDy2W5ATL2
GT1MECH-125-001 | fe6e990e-7904-4afd-9eaa-c8ed55aa2ad5 | CH05-2 | 638 | AMER | Closed | P2 Medium CX | marcello.scalise@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Missing Components | Commissioning |  | HVAC | equipment | 1WSHP_F_2 | HP - Heat Pump |  |  | (1WSHP_F2) On/off switch is missing lockout bracket that is present on D skid WSHPs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628597&prj=638&rqi=h99dgbyx0lrbp2Hx2IzqZThJbU
YT1MECH-150-001 | 305a7ead-0cbe-4859-80c9-107044596815 | CH05-2 | 638 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | HVAC | equipment | 1WSHP_D_1 | HP - Heat Pump |  |  | (1WSHP_D_1) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624758&prj=638&rqi=PkarsNaE1KpZ7cA6xxU7AM3w6p
YT1MECH-154-001 | 99f9e4ee-66b9-4620-a40a-83d37796d340 | CH05-2 | 638 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | HVAC | equipment | 1WSHP_F_1 | HP - Heat Pump |  |  | (1WSHP_F_1) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624765&prj=638&rqi=LWNfpzLHtXwfOWQKWSuRmm2BaK
YT1MECH-152-001 | 6c4efcc9-fcd1-4c97-b7a4-83a0ded74086 | CH05-2 | 638 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | HVAC | equipment | 1WSHP_E_1 | HP - Heat Pump |  |  | (1WSHP_E_1) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624761&prj=638&rqi=zQQxCsguvZV4GY5x7kH5tEivfb
YT1MECH-151-001 | ea2e2fc6-a1c7-4cd8-88d6-e9c1a8f49915 | CH05-2 | 638 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | HVAC | equipment | 1WSHP_D_2 | HP - Heat Pump |  |  | (1WSHP_D_2) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624760&prj=638&rqi=CLJ4qadZLGoLDapUcpe71vgNmh
YT1MECH-153-001 | 53db4645-6508-4379-a0ed-eebc27661af5 | CH05-2 | 638 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | HVAC | equipment | 1WSHP_E_2 | HP - Heat Pump |  |  | (1WSHP_E_2) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624763&prj=638&rqi=LzZvzUUYBWJbh60IkGjTAYC8Xi
YT1MECH-155-002 | 53ed817c-2235-46bb-b9d3-339215c5a085 | CH05-2 | 638 | AMER | Open | P2 Medium CX | marcello.scalise@veolia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | HVAC | equipment | 1WSHP_F_2 | HP - Heat Pump |  |  | (1WSHP_F_2) 24V power input on alarm sensor is not connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624767&prj=638&rqi=fL9Kz2Iov7t2QgSX8iAIm8dNxx
YT1MECH-155-001 | 02b8191f-d9df-4b1d-902b-4c26b0b555a3 | CH05-2 | 638 | AMER | Closed | P2 Medium CX | benjamin.mei@veolia.com | 2026-06-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Torque Required | Commissioning |  | HVAC | equipment | 1WSHP_F_2 | HP - Heat Pump |  |  | Common to all WSHPs, there are no factory torque marks on any connections. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623962&prj=638&rqi=xuPr0ATXSVNIjqylq8bPGVNIcM
RT1MECH-148-001 | ccb23dbb-889d-4643-b9bb-6ee625e55a94 | CH05-2 | 638 | AMER | Open | P3 Low CX | benjamin.mei@veolia.com | 2026-06-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/Required | Commissioning |  | Mechanical â€“Air | equipment | 1EF_D_1 | EF - Exhaust Fan |  |  | Common to all SKID EFs - Factory Quality Control document has not been received. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623977&prj=638&rqi=qj98oJpKgsvSeZS82m4yJ9cEY8
CCD-L2B-2-001 | c1c9d0a8-e77d-4f39-8685-dfb71b048b7e | CH05-2 | 638 | AMER | Closed | P2 Medium CX | ian.tsurumoto@veolia.com | 2026-04-29 04:00:00.000 +0400 | Design Professional | DELIVERABLES | Documentation not issued/Required | Commissioning |  |  | equipment type |  |  |  |  | STANTEC has not issued a final (SCCS) short circuit coordination study | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619954&prj=638&rqi=X7fvkelC0GQjwu9NRfAQIt2AbZ
RT1ELEC-500-001 | e7278701-2eae-441e-b6cd-6a5d1d634706 | CH05-2 | 638 | AMER | Closed | P3 Low CX | karina.leonard@veolia.com | 2026-04-16 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_D_2 | LIBATT - UPS Battery |  |  | (1BATT_D2_2) 1BATT_D2_2 door handle is not secured. The bolt that attaches the locking mechanism to the handle is missing. Door doesnâ€™t stay shut.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618386&prj=638&rqi=1qXWxJWC2AyE0ABaKGYpW341u3
GI-016 | f2d8eb27-b3aa-4c03-a05d-bd8726caf214 | CH05-2 | 638 | AMER | Closed | P3 Low CX | zachary.riddle@veolia.com | 2026-03-18 04:00:00.000 +0400 | Owner |  | General Design Issue | Design | [7 empty] | PDU Similar for all equipment. Provided hardware for PDU input cable connections is insufficient to complete proper connections. Higher grade hardware was used with approval from Equinix. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616004&prj=638&rqi=Fsagy23dEgD47cpZB1rlT6YA8A
GI-013 | 02246de3-dd22-4fb6-bc1d-2eb0da472915 | CH05-2 | 638 | AMER | Closed | P3 Low CX | mcoday@etechgroup.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | There are not CAT6 cables between the Delta BATT3 and the E Skid DMARK in each skid â€“ (3) total. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199785&prj=638&rqi=PsRea14tGwXa6GJZaYtJgsBf6m
GI-012 | 2bf52899-4741-4439-8608-28ce4d716ead | CH05-2 | 638 | AMER | Closed | P3 Low CX | mcoday@etechgroup.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | Each Delta CRAH remote temperature sensor is not mounted, and cable not ran to the associated UPS in each skid â€“ (6) total. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199783&prj=638&rqi=mnYUKOCXe2w9N5U3UpKAO90NUx
RT1MECH-153-001 | 7fdbcb3b-3cf2-4c81-aa2e-56bb39f3b971 | CH05-2 | 638 | AMER | Closed | P3 Low CX | mcoday@etechgroup.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | HVAC | equipment | 1WSHP_E_1 | HP - Heat Pump |  |  | There are not CAT6 cables between the Trane WSHPâ€™s and the E Skid DMARK in each skid â€“ (6) total. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199786&prj=638&rqi=oW7aALBIUlY4EIrLE9Hd6aXAnH
GI-016 | ec8f51fe-cd83-420e-a041-720b144cc4e3 | CH08x-1 | 677 | AMER | Ready for Verification | P3 Low CX | dayele@equinix.com | 2026-08-06 04:00:00.000 +0400 | Electrical Contractor |  | FWT Issue | Commissioning | [7 empty] | The outside air intake openings on the Marvair ACUs are fully exposed to the environment and do not include protective hoods or weather protection. This configuration may allow rainwater ingress into the units during adverse weather conditions, potentially impacting equipment reliability and operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632647&prj=677&rqi=1PNPGe02wTCcpW49o7epGo8aSd
GI-018 | 803e00b7-290b-4ea1-8cce-cd2e8d1a4417 | CH08x-1 | 677 | AMER | Closed | P3 Low CX | dayele@equinix.com | 2026-08-06 04:00:00.000 +0400 | Electrical Contractor |  | FWT Issue | Commissioning | [7 empty] | The Marvair ACUs are currently configured to control cooling based on their individual return air temperature sensors rather than the E-House temperature sensors as specified in the design. This configuration does not align with the intended control strategy and may result in non-uniform cooling operation within the E-House. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632652&prj=677&rqi=QF2NtZJUxqfGKvh4qYLtsCPfsI
GI-017 | f9133b99-773f-4eb1-b3e7-3e57a6010e99 | CH08x-1 | 677 | AMER | Closed | P3 Low CX | dayele@equinix.com | 2026-08-06 04:00:00.000 +0400 | Electrical Contractor |  | FWT Issue | Commissioning | [7 empty] | The local temperature control setpoints configured on the Marvair ACUs do not match the individual unit control setpoints specified by Equinix. This discrepancy may result in unintended or non-standard cooling unit operation during communications loss conditions, as the units may not stage and operate in accordance with the intended control sequence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632648&prj=677&rqi=Du8jcESt28AdQy54fQOxyq6Dbm
GI-014 | 70710f7a-9e3c-49e2-bd53-7522896d3886 | CH08x-1 | 677 | AMER | Ready for Verification | P1 High CX | dayele@equinix.com | 2026-08-06 04:00:00.000 +0400 | Electrical Contractor |  | FWT Issue | Commissioning | [7 empty] | During functional testing, activation of the fire alarm signal resulted in a UPS battery alarm being generated at the UPS system. Investigation indicates that the VESDA fire alarm signal and the UPS battery alarm signal are both terminated on the same input terminal of the MPC10 PLC. As a result, activation of the fire alarm signal backfeeds the UPS battery alarm circuit, causing an unintended battery alarm condition at the UPSs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632632&prj=677&rqi=uevewzIc3bBkZTWuVnxUgrDjuC
GI-015 | 071f2de8-532a-4b17-b4a9-6303be7cf790 | CH08x-1 | 677 | AMER | Ready for Verification | P1 High CX | dayele@equinix.com | 2026-08-06 04:00:00.000 +0400 | Electrical Contractor |  | FWT Issue | Commissioning | [7 empty] | The E-House contains three UPS systems and their associated battery cabinets. During testing, activation of a battery alarm from any battery cabinet caused all three UPSs to generate battery alarms. The expected operation is for a battery alarm to be reported only by the UPS associated with the battery cabinet experiencing the alarm condition. CECCo's investigation determined that the battery cabinet alarm input signal to the UPS and the outgoing alarm signal to the Marvair PLC are connected at the same point, allowing the alarm signal to propagate across all UPS systems and generate unintended battery alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632640&prj=677&rqi=u3pu9Hsgk9BAUXSEEgyRIZUuJs
GI-006 | 6b1948c9-242d-44cc-8579-877b62384d67 | CH08x-1 | 677 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-29 04:00:00.000 +0400 | DEL - Delta Elec |  | FWT Issue | Commissioning |  |  | equipment type |  |  |  |  | FWT an out of phase alarm triggered | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619906&prj=677&rqi=PqRXXNCPItvxJgTokwqrBd7bjk
GI-007 | 6c8d2432-8aa5-4191-90aa-ba38e8f082fb | CH08x-1 | 677 | AMER | Closed | P1 High CX | rtyler@equinix.com | 2026-04-29 04:00:00.000 +0400 | Equinix Design Engineer |  | FWT Issue | Commissioning |  |  | equipment type |  |  |  |  | Logic Controller was not initiating source seek, upon S2 (GEN) supply failure whilst Load was supported by S2 (GEN) and S1 (UTILITY) was already available. Issue found during FWT for logic controller. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619907&prj=677&rqi=o10RlHjq79YST97euln8iZDLdn
GI-005 | 18847b6b-4480-44a6-95b9-a7dbeb01234f | CH08x-1 | 677 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | FWT Issue | Commissioning |  |  | equipment type |  |  |  |  | Controller was opening UMB or GMB if trip was issued by either breaker as the Service Disconnect state was intended to isolate both S1 and S2. Issue found during FWT Logic Controller testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619624&prj=677&rqi=ZFz5pWOZHGYTyvELVzYeTxCQjv
GI-003 | 877e79d9-00ed-4851-ad86-3aec9c163eda | CH08x-1 | 677 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | FWT Issue | Commissioning | [7 empty] | Upon normal S2 > S1 re-transfer (UTILITY RESTORE), as that is manually initiated by the operator, existing delays were insufficient for operator to step away from being in front of the panel. Issue found during FWT Logic Controller Testing. Equinix added a 10s walkaway timer. Delay mitigates risk of arc flash event affecting the operator. The requirement for the operator to step away at a safe distance from the panel board needs to be covered in the SOP. It should be noted that this delay is not present if fail to open/close or trip alarm are being acknowledged. SOP for those activities should require for the operator to disable the ATC first (ATC MODE = DISABLED or MAN) prior acknowledging any latched-on alarms inhibiting transfer/re-transfer sequences. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619597&prj=677&rqi=dbgJgX7rQfBKrMrNU5yGzw8Fkf
GI-002 | 94d10d4b-b9a6-4752-8b15-d40c15799c04 | CH08x-1 | 677 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | FWT Issue | Commissioning |  |  | equipment type |  |  |  |  | Internal buss needs to have more phase stickers applied to more easily identify buss to prevent confusion when working on the buss. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619594&prj=677&rqi=x4lNfY0CpoOi1rftoCh5NKJ8uY
GI-001 | e205339e-64ea-48f7-851b-ee8a07135665 | CH08x-1 | 677 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | FWT Issue | Commissioning |  |  | equipment type |  |  |  |  | Equinix advised Hanley to separate the RELT and source lamp on/off circuits. In addition, the naming convention for the DC# breakers need to be updated per new circuits. Hanley to verify sources are correct throughout the shop drawings especially for the source for the door mounts. (See attached marked drawings) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619571&prj=677&rqi=Pk9hyd8NYlEC161ZOx0Vl0vAjx
GI-004 | 34dbbc40-cce3-4e2a-b257-6867aa26cc62 | CH08x-1 | 677 | AMER | Closed | P3 Low CX | rtyler@equinix.com | 2026-04-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | FWT Issue | Commissioning |  |  | equipment type |  |  |  |  | Upon normal S2 > S1 re-transfer (UTILITY RESTORE), as that is manually initiated by the operator, existing delays were insufficient for operator to step away from being in front of the panel. Issue found during FWT Logic Controller Testing. Equinix added a 10s walkaway timer. Delay mitigates risk of arc flash event affecting the operator. The requirement for the operator to step away at a safe distance from the panel board needs to be covered in the SOP. It should be noted that this delay is not present if fail to open/close or trip alarm are being acknowledged. SOP for those activities should require for the operator to disable the ATC first (ATC MODE = DISABLED or MAN) prior acknowledging any latched-on alarms inhibiting transfer/re-transfer sequences. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619623&prj=677&rqi=NE7cP7HfqBkBSqZ3drOsnOkAuL
GI-080 | 7f6d6e2c-2cd8-4c20-bd82-80f45e4e90b2 | CN01-2 | 664 | APAC | Open | P2 Medium CX | sivakumar@abluae.com | 2026-09-18 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | All the earthing junction box permanent tag need add In G and J block | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638775&prj=664&rqi=dw7aR1d8s6PMjlaRAKiPhdzpz1
GI-078 | 21864490-0143-433a-a845-9bb88e78d807 | CN01-2 | 664 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [7 empty] | Arc flash covers interrupt the Communication cable need to be prepare dressing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622627&prj=664&rqi=z0bMGO2NGLng9xpcWqgMftmomt
GI-062 | ff83e30e-ea95-48fa-9d26-6cdc70d3c0b1 | CN01-2 | 664 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [7 empty] | BMU Filter to be provided at Back door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622120&prj=664&rqi=Eqe7QN4wRNFu2wpCopsMQLIIB8
GI-050 | 11b55111-ebdb-4720-9f74-44f78a312566 | CN01-2 | 664 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [7 empty] | In module V welded bottom sheet overlaps to foundation holes need to be corrected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622105&prj=664&rqi=8vajX7vHvEzrvGDY7PdIOwC9AF
GI-042 | bfe6eaad-2dc5-44aa-930a-e8904fd3d2b0 | CN01-2 | 664 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [7 empty] | Ronis key not available in the RMU during the FWT, So not able to check Ronis keys interlock ABB has to do perform demonstrate at the site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621945&prj=664&rqi=GFa9DHZboypXnL0hyXASE5B7t3
GI-043 | 1f24e8b3-55b7-4e68-b163-88cf97b02c63 | CN01-2 | 664 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [7 empty] | Ronis key not available in the RMU during the FWT, So not able to check Ronis keys interlock ABB has to do perform demonstrate at the site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621946&prj=664&rqi=IUwH5ozcGbJ6SOVbPpURzaY2id
GI-048 | 9963a58a-8a3a-475b-bdcf-95950efb97f0 | CN01-2 | 664 | APAC | Closed | P3 Low CX | sivakumar@abluae.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning | [7 empty] | Aluminium gland plate dimensions to be added in the GA drawing. The gland plate thickness is specified as 3 mm in the drawings; however, the actual observed thickness is 2.5 mm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621954&prj=664&rqi=VUsZnp5Wk7ZmxzeCeL8Q3GTnFa
GI-041 | d2ff8318-a36c-48c6-8815-2635f6686ac4 | CN01-2 | 664 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [7 empty] | Ronis key not available in the RMU during the FWT, So not able to check Ronis keys interlock ABB has to do perform demonstrate at the site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621944&prj=664&rqi=r91BECtw9qgXKhPbMMZztti9Zg
GI-047 | 2e5e4fc4-83c3-400b-b16e-2ec938b74713 | CN01-2 | 664 | APAC | Closed | P2 Medium CX | sivakumar@abluae.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [7 empty] | The bolts provided at the cable clamp are too long. The bolt size should be reduced, as the clearance between the bolt and the earthing connection is very less | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621951&prj=664&rqi=EzF6kJAksPge5BSKZ996b3hjJx
GI-200 | c94be4b9-46d3-450d-a2de-d8009a8a52de | DA11-4 | 614 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-08-28 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [7 empty] | Door to Electrical Room N is not latching shut. Pulls open freely. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635929&prj=614&rqi=KLhsvwUA2Da1t40XcunLdjVyTb
GI-196 | 6a2c8a84-d530-4b29-a414-bc9e739a6c78 | DA11-4 | 614 | AMER | Closed | P3 Low DCOS | jonathan.wright@alphafacilities.com | 2026-08-26 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | [7 empty] | Ground bus EGB-T-4 contains Zinc and Stainless Steel fasteners. Dissimilar metals would likely cause electrolysis and have dissimilar torque values. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635310&prj=614&rqi=arioxs7xSWVEXO0EoMXglWfHl5
GI-199 | c117a6f4-c581-4ed8-b042-ed25d2f25a86 | DA11-4 | 614 | AMER | Open | P3 Low CX | bramsay@critical2u.com | 2026-08-26 04:00:00.000 +0400 | Electrical Contractor |  | Cleaning | Commissioning | [7 empty] | T-Block room needs to be cleaned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635416&prj=614&rqi=4cvEgqY0066OdoQaTtkgcKTh6Q
GI-195 | 50b102f0-35ba-4142-a102-ecec2619df0f | DA11-4 | 614 | AMER | Ready for Verification | P3 Low CX | jonathan.wright@alphafacilities.com | 2026-08-25 04:00:00.000 +0400 | Mechanical Contractor |  | Cleaning | Commissioning | [7 empty] | Listed ACUs contain Material (I.e. brackets, screws) & FOD (I.e. dust, debris, trash) and need to be cleaned: ACU-2-16 ACU-2-17 ACU-2-18 ACU-2-19 ACU-2-20 ACU-2-21 ACU-2-22 ACU-2-23 ACU-2-24 ACU-2-25 ACU-2-30 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635097&prj=614&rqi=mYjxgFxSASlTiLWNoeMH9I24aI
FPT-430-002 | e49910e4-7017-4fc1-85fc-836c27fe4b78 | DA11-4 | 614 | AMER | Closed | P2 Medium CX | pnavarro@critical2u.com | 2026-07-30 04:00:00.000 +0400 | Controls Contractor | L4 | DCIM BCM Issue | DCIM |  | Electrical â€“ MV | equipment | Existing GEN-4A | Existing Generators |  |  | Gen 4A is not communicating with BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631450&prj=614&rqi=6e8x2gnGyFXlf5fWAUBVULXJo0
FPT-430-001 | b5fcc1e8-6326-422e-8d97-6b7f39c3ce2d | DA11-4 | 614 | AMER | Ready for Verification | P2 Medium CX | pnavarro@critical2u.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Component/Equipment Failure | Commissioning |  | Electrical â€“ MV | equipment | Existing GEN-4A | Existing Generators |  |  | Frequency recovery time do not meet the iso 8528 standards. See attached screenshots of readings and standard. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631330&prj=614&rqi=1DIKFoxbpBLfphJwTNMTRUBM22
GI-172 | 93f1cae1-9bb2-4425-b69d-72689f7c7990 | DA11-4 | 614 | AMER | Ready for Verification | P3 Low CX | shuyck@morleymoss.com | 2026-07-14 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | DP-GEN-3 | DP-Distribution Panel |  |  | DP-GEN-3 is to have (2) Kirk keyed main breakers that are 800AF/600AT per W-Block SLD sheet E-601.20W but the panel currently has 600AF/600AT main breakers installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629262&prj=614&rqi=UwG9ybh1YuG6nzF07TTkN4H2Ap
GI-142 | 585b0c98-061d-4a25-9214-481dbb8df2db | DA11-4 | 614 | AMER | Closed | P3 Low CX | cdavis@clunegc.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning | [7 empty] | In CH-14, the 12" condenser water connection to the heat exchanger has 1" difference. Please advise a solution. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623672&prj=614&rqi=j34o9BXhzhIKga79UTX5uugIC5
GI-120 | 8d0c4330-6bca-4b1a-92fb-df5e13a663dc | DA11-4 | 614 | AMER | Open | P2 Medium CX | sadkins@critical2u.com | 2026-04-30 04:00:00.000 +0400 | Owner |  | General Design Issue | Design | [7 empty] | USP-A-1, B-1 and C-1 Settings need to be updated. : DA11-2 moved the building to the substation, SCCS was not done correctly to coordinate the move. With DA11-4 being the first to tie directly into the substation, after we got the settings from Oncor it was found that we were not coordinated. Then we worked with Oncor to establish the correct settings, which is what has been implemented into DA11-4. Oncor has since go back and adjusted their side of POD 1, the only remaining item is to have Schneider update our side of the POD 1 to match the functions and settings that were established for DA11-4. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620086&prj=614&rqi=0covCxR9C6t968O1o7sIzdVbrn
GI-073 | 9773efb0-6000-4277-84fc-04879a196b28 | DA11-4 | 614 | AMER | Closed | P3 Low CX | mwarwick@morleymoss.com | 2026-03-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | CRAH-1-47 | CRAH - Computer room air handler |  |  | Pre-installed VA cable is on the wrong terminal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618545&prj=614&rqi=kTrz7TWEfWIArTM4z8PI7pperf
GI-048 | ebae2bf5-abf7-4b9b-85f8-b5931fd7a9c7 | DA11-4 | 614 | AMER | Closed | P3 Low CX | mwarwick@morleymoss.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  |  | equipment | MV Coms Panel Primary |  |  |  | Unit arrived with shipping damage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617268&prj=614&rqi=iA14zovDVQazBHmzan3ga3EFGH
GI-049 | b5195cd3-69f0-4068-85ce-6629de717279 | DA11-4 | 614 | AMER | Closed | P3 Low CX | mwarwick@morleymoss.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  |  | equipment | MV Coms Panel Secondary |  |  |  | Cabinet arrived with shipping damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617269&prj=614&rqi=unVJd7PBgnnM6LRW4h6N8A1M4P
L2L3 Sun-151-001 | 3eda7ce6-fe71-4295-bd05-224205b9857b | DA12-1 | 695 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-07-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_BR1_2 | CRAH - Computer room air handler |  |  | Fan section - Upper door furthest RH side is misaligned and colliding against frame | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631081&prj=695&rqi=5sqnRLNseUcVXLbmdg3c7BNtGr
L2L3 Sun-184-001 | f721e77d-d492-4ce9-adce-08ad64edda7d | DA12-1 | 695 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-07-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_AR1_3 | CRAH - Computer room air handler |  |  | Fan section - Upper door furthest RH side is misaligned and colliding against frame | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631077&prj=695&rqi=qObqJwqODCP1Mkao0CT3qQi0l1
L2L3 Sun-185-001 | ad6d9f6e-9ff4-4374-9f49-dd58762dad1a | DA12-1 | 695 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-07-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_AR1_4 | CRAH - Computer room air handler |  |  | Electrical Vestibule - Bottom most door latch cannot fully rotate to locked position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631079&prj=695&rqi=dG8h1M0bEYNTlKrAOHnDdhwsKQ
L2L3 Sun-155-001 | 312e11c1-717c-47af-8fac-b5df8419f5a4 | DA12-1 | 695 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-07-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_BR1_4 | CRAH - Computer room air handler |  |  | ICDM Section - Top latch not aligned and cannot rotate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631083&prj=695&rqi=HVn47XMWOCwjLTD9t02sZic0jT
L2L3 Sun-20-001 | 1af213fa-dec4-4a1c-9e29-5db08c59d9a7 | DA12-1 | 695 | AMER | Open | P3 Low CX | sballard@critical2u.com | 2026-07-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1MVCB_Z | MVCB - Medium Voltage Circuit Breaker |  |  | Labels on both doors do not match wording from the submittal (page 73) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629267&prj=695&rqi=SlH9FZhxOO8wuQxurKqryTT245
GI-030 | 5ca27db0-9c94-49de-ab9d-67cf89fedb75 | DC17-1 | 658 | AMER | Open | P2 Medium CX | EMAHLER@ramboll.com | 2026-09-02 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [7 empty] | Communications EMT (Division 27) does not have insulating bushings (Per Division 26) to protect the conductors at terminations with EMT connectors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636535&prj=658&rqi=iWdiTQ6d1NOyBkmndcSyUlOixv
GI-027 | e19ae140-76fc-4634-98b8-37d4155f13ed | DC17-1 | 658 | AMER | Open | P3 Low CX | SOGOTI@ramboll.com | 2026-08-28 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1RSSB_1 | RSSB - Reserve Spine Switchboard |  |  | Unit has damage to the metallic plate located on top of the unit, please refer to the attached photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635877&prj=658&rqi=wnzI3jtZMC7QlPCKKSB4DOlgSz
GI-028 | d1f99ee8-0b69-41f7-9f9c-77fe5c4b2c41 | DC17-1 | 658 | AMER | Open | P3 Low CX | SOGOTI@ramboll.com | 2026-08-28 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1RSSB_2 | RSSB - Reserve Spine Switchboard |  |  | Arc flash label on the front panel of the unit is missing, please refer to the photo attached for referece | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635878&prj=658&rqi=QeTbM1d8gW0s5sZwMg3I9vIYYj
GI-029 | 33017aed-0ac4-44fd-8bc8-58e29c94c1a0 | DC17-1 | 658 | AMER | Open | P2 Medium CX | Jshaffer@ramboll.com | 2026-08-28 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1RSSB_1 | RSSB - Reserve Spine Switchboard |  |  | K55 and K52 key are both broken off inside the cylinders | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635985&prj=658&rqi=4BLoHqqt2CyWXYYYGEzpXq5kVE
GI-024 | a85c7285-b1a4-476b-a288-562ab05557fe | DC17-1 | 658 | AMER | Open | P3 Low CX | jbeall@rosendin.com | 2026-07-31 04:00:00.000 +0400 | SYC â€“ Systecon |  | Component/ Equipment Failure | Commissioning | [7 empty] | SSB-Q Chiller Breaker failed NETA testing - Would not trip on long time | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631868&prj=658&rqi=sEKwNDC7q3zvQSPQLbnyI7sUVs
GI-023 | 9193fa5c-279c-4156-a8a4-5db572a49a58 | DC17-1 | 658 | AMER | Open | P3 Low CX | jbeall@rosendin.com | 2026-07-31 04:00:00.000 +0400 | SYC â€“ Systecon |  | Component/ Equipment Failure | Commissioning | [7 empty] | SSB-R1 Chiller Breaker failed NETA testing - Long time would not trip | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631863&prj=658&rqi=66Iz8KzxkOM6FUqB1wsjKlklNd
GI-020 | 5a16e05f-5153-4a7c-8fb4-e7047dfe541a | DC17-1 | 658 | AMER | Open | P2 Medium CX | gkuczler@rosendin.com | 2026-06-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | UMDSB Termination Points for UPS-3 RBB. Hanley confirmed UPS-3 RBB Points will be 5 & 7 at UMDSB for DC17. Terminal Block in UMDSB only has (5) poles. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627247&prj=658&rqi=atVBTJQt97xil0tpHLOPE5O9K6
GI-016 | 13db2c17-d9e5-4ed9-bc9b-0a545b15f3c1 | DC17-1 | 658 | AMER | Closed | P2 Medium CX | gkuczler@rosendin.com | 2026-05-20 04:00:00.000 +0400 | Owner |  | General Design Issue | Design |  |  | equipment type |  |  |  |  | Hanley PDU Transformer Testing Polarization Index testing of PDU's requested by EQX requires isolation of transformer in PDU. Isolation requires removal of factory connection from XO to GND. Hanley has advised factory connections cannot be removed without warranty impact. Need direction on if test is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622633&prj=658&rqi=HUQ8ix0TiL8GH3lfO3iE5UBPI6
GI-013 | 3a8732b2-742c-4b48-b9b7-4364a18a8e08 | DC17-1 | 658 | AMER | Closed | P3 Low CX | emilyma@dpr.com | 2026-05-11 04:00:00.000 +0400 | SGB-SMIT |  | Design correction needed | Design | [7 empty] | SGB MLTXs relay cut out incorrect size. SGB did not align the SE relay cutout per the dimensions in the submittal. Current dimensions are 8.07x5.12. Required dimensions based off SE relay is 8.07x7.09. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621176&prj=658&rqi=iVfDPc5clSGpcRD60vkDualQ1i
GI-012 | cabc272d-e681-4022-9081-77508639ac9d | DC17-1 | 658 | AMER | Closed | P2 Medium CX | emilyma@dpr.com | 2026-04-29 04:00:00.000 +0400 | JCI - Johnson Control |  | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | Chiller W has a good amount of visible rust inside piping from factory. Other chillers may have the same problem. - Field inspection of Chiller W shows heavy, visible rust scale and oxidation on the internal surfaces of factory-installed piping and nozzle connections. Photographs confirm uniform orange/brown corrosion inside multiple pipe sections, including flanged connections and inlet/outlet barrels. The condition appears pre-installation and is consistent with improper factory preservation, moisture ingress, or lack of nitrogen purge/desiccant protection. Based on identical construction, other chillers are at high risk of the same internal condition. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619949&prj=658&rqi=8DCFREWe1afttQuwarDlTiEEj7
GI-009 | 101f2ae3-c793-483f-9077-5b3bf99b4fa5 | DC17-1 | 658 | AMER | Work Completed | P2 Medium CX | gkuczler@rosendin.com | 2026-04-21 04:00:00.000 +0400 | DEL - Delta Elec |  | Component/ Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | (3) STS Molded Case Switches were damaged by 3rd tier subcontractor in warehouse. Replacements are needed, DPR has been notified. Need update on replacement order. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619043&prj=658&rqi=FEHXLxll2Sj5MUzlbzGSrOYiHg
GI-008 | dbeafcc6-bf41-41d3-97bd-062a51a3ce5a | DC17-1 | 658 | AMER | Work Completed | P2 Medium CX | gkuczler@rosendin.com | 2026-04-21 04:00:00.000 +0400 | DEL - Delta Elec |  | Component/ Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | (2) STS Molded Case Switches arrived with bent pins. Replacements were ordered and expected with March delivery of STS units. No switches were received. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619026&prj=658&rqi=b9yjqIvLzjAuffBFIxjUnPSDa9
GI-007 | 1ddfdb29-91b2-4896-9fd7-76d51352511c | DC17-1 | 658 | AMER | Closed | P2 Medium CX | emilyma@dpr.com | 2026-04-13 04:00:00.000 +0400 | VER - Vertiv |  | Installation Damage | Commissioning | [7 empty] | Damaged battery cabinet for L3. Vertiv to come out and inspect unit. model PHR3462-001A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617974&prj=658&rqi=AoUVIJUh6zPpJZY3N8DNEIRTrz
GI-001 | d14209a8-9441-46c6-b80a-06550619bee5 | DC17-1 | 658 | AMER | Closed | P2 Medium CX | emilyma@dpr.com | 2026-02-09 04:00:00.000 +0400 | VER - Vertiv |  | Installation Damage | Commissioning | [7 empty] | DC17-2 asset - Vertiv Damaged 1200kva UPS at A&A. 1/20/26. SN D25M006518. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198806&prj=658&rqi=bnvmK9tHb0QEEwt3VCPmXRB4xU
GI-108 | a56677b4-a40f-4175-be35-73c74393b7e4 | DC21-P2 | 678 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-09-17 04:00:00.000 +0400 | General Contractor |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | ALL G and H Electrical Skid CRAH's: Side doors on unit were left off and the screws are missing to put the doors back in place. We need replacement screws and the doors back on the unit for L4 Testing. Delta HVAC issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638474&prj=678&rqi=jjfI0NNOC8WyLlkNJ7uTXdX1RO
GI-110 | 06a8b2ba-6c27-4e01-9859-d915bc01bc20 | DC21-P2 | 678 | AMER | Open | P2 Medium CX | francis.callan@veolia.com | 2026-09-17 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | [7 empty] | Common to all Harmonic Filters; The hardware installed for the control circuit inside the harmonic filter is incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638601&prj=678&rqi=G4GFjXmkdWMqhZQ4BLIiW1pIOO
GI-107 | f5446782-e9cc-471b-a757-0b6dbaf7a829 | DC21-P2 | 678 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-09-14 04:00:00.000 +0400 | General Contractor |  | Component/ Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | All Electrical Skid CRAH's: Fan feedback (rpm) values are reading 0, even when fans are running. Awaiting PLC upgrade from Delta HVAC for 9/15/26 in the morning. Delta HVAC issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638006&prj=678&rqi=VoD3hP25sUXCtw4suaEkd55xS6
GI-105 | a429f74d-7dc2-45bf-bd19-adf328fef498 | DC21-P2 | 678 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-09-14 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/ Fault | DCOS |  |  | equipment type |  |  |  |  | All Electrical Skid CRAH's: BMS displays the supply air temperature setpoint at 0 and the differential setpoint as 0. Points do not match between HMI and BMS. The differential temperature setpoint automatically reverts back to displaying 0 after changing this setpoint on the unit HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638002&prj=678&rqi=zwDQMDAqeJBPHoYBxYFVFxGCbM
GI-106 | af3575f2-0fa6-4cc6-acd4-0bd77a7e9875 | DC21-P2 | 678 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-09-14 04:00:00.000 +0400 | General Contractor |  | Component/ Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | All Electrical Skid CRAH's: G and H. Valve feedback stays at 0 or in "Error" while the valve is commanded open Delta HVAC issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638003&prj=678&rqi=E45FrOPUEuegmhzVrHR21cv9S8
GI-103 | 357e6ff1-2fc7-420f-8c8a-9d23f703aaae | DC21-P2 | 678 | AMER | Open | P3 Low CX | william.park@veolia.com | 2026-09-09 04:00:00.000 +0400 | Electrical Contractor |  | Missing Components | Commissioning | [7 empty] | Exhaust Fan: Electrical Room H - Ground wire is missing from the exhaust fan controller box. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637530&prj=678&rqi=oZEe2J4Z1elmvbeo08s9cPuENH
GI-104 | 25b2e812-7e30-4e27-b530-7ed14593b97d | DC21-P2 | 678 | AMER | Open | P3 Low CX | william.park@veolia.com | 2026-09-09 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [7 empty] | Exhaust Fans: Electrical Rooms H and G - Both exhaust fans have UPS wires not terminated and hanging within the exhaust fan controller box. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637534&prj=678&rqi=JhPDEedkarHPzzl9rujVI16wNr
GI-100 | 0b9720f9-74f3-4fed-95a2-0b806c09ec7c | DC21-P2 | 678 | AMER | Open | P3 Low CX | Aaron.Cross@veolia.com | 2026-09-04 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning | [7 empty] | Water on floor of GEN-H source unknownÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636880&prj=678&rqi=Dz840tZC00CY5kJxcSZTMucJQg
GI-090 | 2f7a5f18-49e8-4eab-8c71-805edd1445ef | DC21-P2 | 678 | AMER | Open | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-08-20 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | [7 empty] | Some washers appear to be installed on the incorrect side of the ground terminations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634475&prj=678&rqi=WztmA5gTknQioY7WdpmSzc6REz
GI-092 | 9900234f-164d-a2fd-dbe6-8c182a7bcb11 | DC21-P2 | 678 | AMER | Open | P3 Low CX | samuel.bruce@veolia.com | 2026-08-20 04:00:00.000 +0400 | Electrical Contractor |  | Incomplete Connections | Commissioning | [7 empty] | HVL-G knockout must be removed to route interconnect wires between sections 1 and 2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634512&prj=678&rqi=39xFFoV8KIBHlKuHHBQdLM4w7i
GI-091 | 90d9cb33-9629-423d-995f-59611647fbdc | DC21-P2 | 678 | AMER | Ready for Verification | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | 1-UPS-G-2: Too much copper is showing between the wire insulation and the crimp at the battery termination. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634482&prj=678&rqi=84ZFwxNxgszgxkdSuDbXNk12Nf
GI-074 | f9b77135-1384-4e8a-b04b-bb0a3ecd5750 | DC21-P2 | 678 | AMER | Ready for Verification | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/ Equipment Failure | Commissioning | [7 empty] | Skid D: Â Exhaust Fan Not Operational Â The exhaust fan on Skid D is not operational. Initial inspection indicates that the fan motor appears to be faulty, preventing the exhaust fan from running. The fan and motor should be inspected, tested, and replaced if confirmed defective | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630366&prj=678&rqi=g4Uk65CAmQdlnq48fqBOEoO396
GI-075 | 29cea7c4-c073-481e-8e95-c88d6647a620 | DC21-P2 | 678 | AMER | Ready for Verification | P1 High CX | ayorinde.akinrinlola@veolia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [7 empty] | Skid D - Battery Exhaust Fan Control Box: Â Openings and Cable Protection The fan control box has two unused openings that are not sealed and should be fitted with appropriate hole plugs/covers. Additionally, the conduit entry currently in use is missing a protective collar, leaving the wire exposed where it passes through the conduit opening. Install the appropriate collar to protect the wiring and ensure proper installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630387&prj=678&rqi=lOs7TYUeJENIV7ByXFst4Si8Wb
GI-078 | fe00ca16-ee68-4c60-a2b6-a51e5f71a7e7 | DC21-P2 | 678 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning | [7 empty] | Water appears to be present on the floor outside and around the boardÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630465&prj=678&rqi=m99GeH7uaSMRCU4wqrxBoLq8cE
GI-073 | cf72209e-beab-476f-aeaf-2626fc6fc619 | DC21-P2 | 678 | AMER | Closed | P2 Medium CX | taquonya.washington@veolia.com | 2026-07-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Design correction needed | Design | [7 empty] | ECB-R-G needs the K2 Kirk key cylinder replaced with the KLB cylinder that matches the site (KLB SN 63374) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630038&prj=678&rqi=99umQlCOg1r7duUK8j3JCwuZuG
GI-072 | 498779e5-238f-4ea9-b414-753ac723488c | DC21-P2 | 678 | AMER | Closed | P1 High CX | william.park@veolia.com | 2026-07-15 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | New Data Hall CRAH's: Main power conduit to the CRAH's was left in place on top of the dampers within the top damper section of the unit. Conduit was found to fall in between the dampers, and dampers will force closed on this conduit resulting in electrical failure and CRAH failure. The conduit must be propped on the side wall or top wall of the inside of the CRAH's with clamps to avoid this conduit from being near the dampers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629456&prj=678&rqi=WckehDLKzQqotKDbm6sdTKVyNc
GI-043 | f585bf3f-0e6a-4c23-8a71-9eae076bbf09 | DC21-P2 | 678 | AMER | Ready for Verification | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [7 empty] | Skid G -The fire protection main line is missing the required connection point and has not been properly secured. The fire protection main line is not connected in accordance with the project requirements and must be properly connected and supported. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627464&prj=678&rqi=3ADZyQYBGpgaY6wzi9858Nt9wd
GI-038 | 7ceef32f-7b7c-4302-8d0a-e335f82143b9 | DC21-P2 | 678 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [7 empty] | SKID G & H- Ground bars not complete: Ground bars are not jumped together inside of skids- 4 Ground Plates do not have jumpers between them. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627383&prj=678&rqi=J0WqqcwmfUN7NT6Q4GwFiN4PpF
GI-044 | b912d59d-b011-437e-9173-268c1145f2a3 | DC21-P2 | 678 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [7 empty] | Skid D&H- Card Reader are higher. The Card Reader is at 56'' to Center. Need to be at 46''. MPS started to rectify these before it shipped out. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627467&prj=678&rqi=EVMeRPJoR2MkwzPigE41oSYc5T
GI-045 | 2603aed2-167a-4482-8d88-8f85c264a030 | DC21-P2 | 678 | AMER | Ready for Verification | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [7 empty] | SKID G- Two sprinklers heads are missing in Skid G as shown in design drawings. Two Sprinkler heads were missing and not installed as shown in drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627468&prj=678&rqi=RZLTCu6r95Lph91pKU7IPVVIDh
GI-039 | 91192139-c989-4eae-a302-6360c49cdaf3 | DC21-P2 | 678 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [7 empty] | SKID G & H- F/A Box need to be changes: Top F/A box will be removed and changed to an 11B box to provide proper clearance | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627391&prj=678&rqi=7Zmha81ZblWasqBhB60g2syVu2
GI-030 | 20f52bfc-4ec1-4259-8d1f-aa6f10bedcbe | DC21-P2 | 678 | AMER | Open | P2 Medium CX | michael.acciaioli@veolia.com | 2026-06-29 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Chilled Water Pump Wiring - The Chilled water pump wiring connection was removed from Chillers D-17 & D-18. The chillers at this site have their chilled water pump getting power from the chiller main circuit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627238&prj=678&rqi=dEnwirkTNVRwg4lfaaXo51pYTV
GI-029 | 33d4e76a-39c6-43e2-bf56-eb6c67704be4 | DC21-P2 | 678 | AMER | Open | P3 Low CX | taquonya.washington@veolia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [7 empty] | Label and placard outside of skid D needs to be updated now that the skid will no longer be tethered. One is made by REI, the other is made by MPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625529&prj=678&rqi=0ErBXutWA2wvNSx45hpt0z7iZ2
GI-028 | 78b8e317-8d89-4555-8f9c-40c194b62d31 | DC21-P2 | 678 | AMER | Closed | P3 Low CX | ron.brackin@veolia.com | 2026-05-26 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | [7 empty] | Flat washer installed is not in accordance with PDU submittal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623158&prj=678&rqi=LQLRYa1iBdgL3kxn1yAnSLzqDA
GI-027 | 01b6c51d-3675-4c34-8562-ae92229f93c6 | DC21-P2 | 678 | AMER | Closed | P3 Low CX | ron.brackin@veolia.com | 2026-05-26 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Labelling | Commissioning | [7 empty] | Phase labeling on incoming feeders are labeled incorrectly. In field -CBA, should be changed to ABC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623157&prj=678&rqi=iPvPsHIjyQ3NE6w4B0LyEfg07E
GI-026 | c88c5a92-d6bd-4aa4-9546-1a0939105b87 | DC21-P2 | 678 | AMER | Open | P3 Low CX | ron.brackin@veolia.com | 2026-05-26 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | Change bus labeling on all G and H RPP's incoming feeders (currently says CBA, change to ABC). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623155&prj=678&rqi=sQBiAgXlJiKotcwZguVsiFQxaP
GI-025 | 72111290-ea16-4642-ab76-2006a943f304 | DC21-P2 | 678 | AMER | Open | P3 Low CX | ron.brackin@veolia.com | 2026-05-20 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning | [7 empty] | Exhaust fan receptacle fed from ups-backed source, shoud be non-ups. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622536&prj=678&rqi=c3ShXlGAnrHadthzTO3P4ZGuNg
GI-023 | b8715c33-3f9b-4608-86c6-54a079045805 | DC21-P2 | 678 | AMER | Open | P2 Medium DCOS | michael.acciaioli@veolia.com | 2026-05-14 04:00:00.000 +0400 | Owner's Representative |  | DCOS Design Issue | DCOS | [7 empty] | BMS Standard - The DC21 site was originally commissioned in 2020 and used the EBCS3 version 2.6 standard. At the time of DC21-P2&P3 the version for EBCS3 has changed to 4.8. During the Software Factory Acceptance test it was noted that the controls for the new equipment will match the existing standard and not the latest EBCS3 version. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621878&prj=678&rqi=iJCM3B6H4R6GLd5jsMBPKlZcb5
GI-024 | e7cddf3c-a44b-4ce5-8f05-e85a51af3bf9 | DC21-P2 | 678 | AMER | Open | P3 Low CX | ron.brackin@veolia.com | 2026-05-14 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | [7 empty] | MV Switch D currently has primary and alternate designation swapped in terms of labeling.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621907&prj=678&rqi=UVHoGB8UgLfJoAuqx4FYMV5nPI
GI-022 | a364794a-1a0a-4561-bdae-fce5d2cd99a2 | DC21-P2 | 678 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning | [7 empty] | SKID-D Existing chilled water piping and new chilled water piping in new half skid appear to be at different elevations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617092&prj=678&rqi=kJzXbFvAlZMYXMeERS3PSHv41T
GI-546 | cc955d3d-0b74-4b5e-9007-d9e5479c1bcf | DC22-1 | 475 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | Commissioning Authority |  | DCOS Installation not complete | DCOS | [7 empty] | . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623745&prj=475&rqi=JyXuL1Ih1yLu8eq420ptYsvCgQ
GI-545 | 5a35a076-9527-4351-bd3b-610ea8bcf8e9 | DC22-1 | 475 | AMER | Open | P2 Medium DCOS | manuel.gomez@eu.equinix.com | 2026-05-29 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [7 empty] | Post RFS --- The Vertiv CRAHs have been wrongly integrated, duplicating 3 Modbus registers : -Return Air Temperature Setpoint -Supply Fan Command -Supply Fan Speed Command | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623469&prj=475&rqi=ahSXvrQugcHMUco3JnT3nYC113
GI-542 | 11c6a551-d9c7-45c2-826b-72bda5a035dc | DC22-1 | 475 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-04-16 04:00:00.000 +0400 | SCH - Schneider Electric |  | Installation not complete | Commissioning | [7 empty] | E-house 2 wiring for the one BARD is not complete - this is wiring that should be done by the skid manufacturer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618443&prj=475&rqi=0MvGhycRd6ZAC09u9mtbs0GkHk
GI-538 | 4e0cc155-3d87-43fd-8a6e-0c569bf1cc3e | DC22-1 | 475 | AMER | Work Completed | P3 Low CX | jonas.wudkwych@veolia.com | 2026-03-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design correction needed | Design | [7 empty] | Design Change --- No external control power to the ECBâ€™s (If the R-spine is down there is no control power and no communications through the BMS) - Qty: 3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615465&prj=475&rqi=ti0tth49UjSvKZ43DYWoJ0AXAn
GI-539 | 9a8454df-dc0d-42c3-b437-11252f6531c6 | DC22-1 | 475 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-03-12 04:00:00.000 +0400 | Equinix Ops |  | Installation not correct | Commissioning | [7 empty] | RPP BCM â€“ Unlcear of setup of Janitiza for RPP BCM. 1/27 â€“ Trevor is currently reconfiguring RPP setup for 415V and single row consecutive at DC22-1. 2/9 â€“ Approximately 10 RPPâ€™s were locked out and not yet complete. Once placed back in service, will complete at DC22-1. 2/23 â€“ Veolia will follow up with DPR/REI on status of RPPâ€™s at DC22-1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615476&prj=475&rqi=7B1ziP0Unk4GibQ924JcYgNICk
GI-537 | 9d8d7ad2-8e1c-420f-8d6c-162048b00295 | DC22-1 | 475 | AMER | Open | P3 Low CX | jonas.wudkwych@veolia.com | 2026-03-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | General Design issue | Design | [7 empty] | Kirk Key system for DC22 MV Ring design appears incorrect. ECB_R1_Q1 Final Solution â€“ Replace the K2/K55 cylinder with new K2 cylinder. K2 cylinder is at IAD but need to confirm that you can reuse the housing of the existing cylinder. ECB_R1_Q2 Final Solution â€“ Will swap door with another onsite Will take door from 4th floor (ECB_R1_RS_Q1) and take to 3rd floor (ECB_R1_Q2) once new door arrives. ECB_R1_RS_Q1 Final Solution (not till Tower 2 during DC22-3) â€“ Replace kirk key cylinder and transfer blocks as per design to be determined during DC22-3. New door with transfer blocks shipped from Ireland. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615464&prj=475&rqi=IJfqSEajLP9Lz7WMoSjBR91T7f
GI-509 | 091ae395-8547-4155-8d52-5b9ee89bf388 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | At the time of commissioning, we were unable to click on the individual compressors on the Chiller Faceplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198504&prj=475&rqi=znc86Sv27W1zDJIffcjaIQYy2f
GI-508 | ccf6461b-efba-431e-98e0-1134d64eeef3 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | At the time of commissioning, the chilled water pump data was not showing on the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198503&prj=475&rqi=aYPDv1srhcXwUd9xSHQTLpiSdK
GI-507 | 65b47742-9cad-4abd-8c6f-c68490dc2878 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | General Aveva Graphics Issue: At the time of commissioning, there was a hidden box at the name of equipment or type that didn't allow you to navigate to the correct window. It appears to be hidden for every name and if clicked it didn't do anything. These needed to be removed or hidden. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198502&prj=475&rqi=vMCDfD48owVz80W6vte6DnrTOP
GI-494 | 03eec441-6f3d-4e55-a554-bb031a468a56 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | Riser designation text did not match actual destination. i.e. "first floor" corresponded to the riser serving the 3rd and 4th floors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198487&prj=475&rqi=8rp0lMHNha7eft63AK2NzkKNuS
GI-529 | f86f20a7-ee2d-4e49-94c8-8147a6b16e97 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | CRAH Program: During commissioning, CRAH's did not pick a new lead unit when the lead unit was not communicating | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198534&prj=475&rqi=FWAMuCcvLpK0vTXfCgpc7b0hBc
GI-525 | 5ec98cd9-f41e-4560-b172-18ac7f8bf224 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | CRAH Alarm Program: During commissioning, the return air sensor probe failure did not appear on the BMS. It only appeared on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198523&prj=475&rqi=Ooi9QlyUL16mQoWVK7KWuI2iNf
GI-489 | 1791d062-764f-4133-b7ff-57332ed3c23e | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment type |  |  |  |  | Chilled Water Manager - BMS During commissioning, chilled water bypass valve control wasn't functioning as intended. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198477&prj=475&rqi=Y3xeYOh51NjJKT6bTibyoJnsmy
GI-515 | fc863dc8-a61e-454c-a43c-2421d6136a05 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [7 empty] | BMS Chilled Water Layout: The Weather Station Temperature was not reading accurately. When the ambient air temperature was below 40 degrees, the weather station was reporting 57 degrees on all three sensors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198512&prj=475&rqi=MJB8E4HLBFdJ4jHWKDPaYxpuHF
GI-487 | feca65b9-356b-4a7a-993b-5213887624bc | DC22-1 | 475 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | FOH/BOH --- At time of testing, BMS was not showing DX equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198475&prj=475&rqi=dFvsSC9Rwg15M7s2AF42MokfLY
GI-486 | 84a52b4c-f181-4de9-925d-cfcc6c22d209 | DC22-1 | 475 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | At time of testing, BMS was not showing FCU's | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198473&prj=475&rqi=TlM0e6iZ3SPavUshNTUM0WYOlW
GI-521 | 68a9a2b2-af72-4dd5-ac33-1d15b7a696f0 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | During commissioning, the System Bypass Valves were hunting and going to 100%, making the pump speed increase to 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198519&prj=475&rqi=fhiqIkohgEarHwgdHvUcxtZe3i
GI-506 | 30a0ee70-d47d-4204-a129-e01c5689c2cc | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | At the time of commissioning, multiple chillers had active faults when a fault at the chiller is not present. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198501&prj=475&rqi=3mBpRKtfRYt2LvYctKST79cUOT
GI-503 | d9e289a2-ffbf-4953-bb22-66c6a31880f9 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | At the time of commissioning, none of the first-floor mechanical was visible on the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198498&prj=475&rqi=b0VIpGY3DKSRpbk8x4Eho3XDjH
GI-501 | e8f75310-b175-41ea-a6ab-da383f638fe6 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | All Electrical Rooms: At the time of commissioning, Remote temp sensors for ER CRAH's needed their scaling updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198496&prj=475&rqi=Mq1rBLUHMsOrX8c3TIIGkjNzxz
GI-497 | 5850a721-dce9-44a0-ac6c-1aefe41b20e0 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment type |  |  |  |  | Chilled water flow deviation was not responding to range changes C5 and C6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198492&prj=475&rqi=MuBEmp5Unrb5JsrOPtjGhqsT15
GI-496 | fbca51b6-c5e0-4f7e-9193-feed9d729065 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | At the time of commissioning, chiller data was not being displayed on the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198491&prj=475&rqi=i8FyVGteTQZS7d0tjDO6mSJUVX
GI-495 | 0e40fe1d-187a-4da7-8c49-9c090a9353c9 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | Chilled Water System BMS graphics: The DP being used on the manager page (to control pump speed) did not match the DP on the system page of the graphics. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198488&prj=475&rqi=m1lDKHBsaVmcCxpREe0M5Sqbs5
GI-505 | 94ee0cbc-b324-49dd-8337-be4b005103ae | DC22-1 | 475 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [7 empty] | A generator yard plan should be provided Equipment in the Generator Yard, such as FCU's and Generator Fuel are not visible on a floor plan. Unable to see on the BMS. Suggest providing a generator yard plan with all devices being communicated to, or a way for end user to see all required control devices. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198500&prj=475&rqi=e3YPk0ukjgenq1SppmO8dDnYy2
GI-523 | 7352d746-0636-481e-852b-21c105cf745f | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | CRAH Program: At the time of commissioning, The Supply Air Setpoint could not be changed manually on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198521&prj=475&rqi=y8TvUG28StWWeWrN28uGw7E6K3
GI-516 | 823132cd-676c-454c-91be-b9d5e4ddf2d5 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | During commissioning, the Isolation Damper Command Mismatch Alarm triggered within 22 seconds of the unit being commanded OFF by the BMS. The alarm cleared after 105 seconds. The Isolation Damper fail time is supposed to be 90 seconds. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198513&prj=475&rqi=hsTvek6xW6dbUvpl1d3flulRZr
GI-514 | 74dccd9e-8aec-4a2d-8d7e-72ed891f1738 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | During commissioning, a CRAH Summary alarm on the BMS was not triggered when there was an alarm on the CRAH. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198511&prj=475&rqi=MRXijI7CkpuqeDAdYc6Al4jmEV
GI-517 | a09d7025-0d3a-439e-bfe8-e64a8c4809b1 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | At the time of commissioning, an acceptable range of values for the supply air temperature (60-80F) needed to be set. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198514&prj=475&rqi=Fu6pfbUGpqzmzQxPjGf1UUGcaA
GI-513 | b94698ba-a64b-4d4f-ba71-370ebd28a5e4 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | During commissioning, we were able to write a negative Supply Air Temperature Setpoint on the HMI. We needed to set the range to not allow a value less than 0. Allowable range: 0-100F | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198510&prj=475&rqi=PKMOeMEkUjLGMKojIkJjnfas2V
GI-512 | efcce090-1692-4848-9810-8e8b76119142 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | During commissioning, the supply and return CFM differed at the unit. Also, the BMS was registering the return CFM and not the Supply CFM on the Faceplate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198508&prj=475&rqi=fz24UhwQWFdI7nIdijoknk5sHM
GI-524 | aedaa359-e2a9-4385-8431-2096ad8cd2a9 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | CRAH Alarm Faceplate: During commissioning, in the event of a remote sensor fault, it showed a purple box on the CRAH alarm faceplate when it should have been a blue box around the alarm for a remote sensor fault. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198522&prj=475&rqi=sooqMfkuKWySsCqXzAWxfKty16
GI-511 | 72db5ee9-f59a-428b-b9af-8f63795f807d | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | During commissioning, whenever a CRAH unit lost power, the dirty filter alarm was generated on the BMS. The normally closed contact was changed to normally open | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198506&prj=475&rqi=jVs3v9xfaSjNkv28EcSzY906XM
GI-510 | 3d17d95f-14a6-4b57-8997-b2939896ef51 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | At the time of commissioning, the supply fan percentage did not match the unit HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198505&prj=475&rqi=E6AsIT8o4YEsQs4ReNKJzqxJKJ
GI-485 | 1f770bba-0556-47de-a011-a1e0f7370f5f | DC22-1 | 475 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | At time of testing, BMS was missing all VAV's | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198469&prj=475&rqi=RL1Wciwu62RuTuOBSYmIfSA2Vy
GI-527 | 21152902-0111-48db-99b2-e8bc4ca3c084 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | CRAH Alarm Program: During commissioning, a timer needed to be added to supply fan mismatch. When shutting down, as fans ramp down and command is 0, we shouldn't be in fan mismatch, add 30+ second supply fan mismatch timer. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198531&prj=475&rqi=yrx8ySJxoli4k46WkChaHEEsgs
GI-518 | d196fe5f-796a-4030-a519-9a38c76a1eaa | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | During commissioning, when we tried to set the minimum fan speed in the setup menu (445), the minimum fan speed changes but did not reflect it on the faceplate Fan Speed Command. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198515&prj=475&rqi=gendX3x7xIBubj1eEBam78Br2e
GI-484 | 194f677e-3ec2-472c-8a67-6114747b1519 | DC22-1 | 475 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | At time of testing, Exhaust Fans were not shown on the BMS graphics. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198468&prj=475&rqi=sDoMQnq7vJ8n1NALSSok2DjFuC
GI-534 | babbc36d-6a57-4f29-b030-6f247e9b37b4 | DC22-1 | 475 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | Battery Room WSHP's: At the time of testing, heat pumps had no values that were shown on the faceplate that correspond to the actual units themselves. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198544&prj=475&rqi=sKzCuMz1IeybYQGxEuOJ2FEFJw
GI-532 | 9f7317e9-071a-4f8d-8101-73c53c78d52f | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [7 empty] | Chiller String: During commissioning, Multiple Valves end switches did noy make while valves are fully open. We've seen this issue with Bray Valves due to temperature changes. E-tech verified if valves were configured correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198541&prj=475&rqi=lDMTHWrcBsW4MGv8GIqdeDcy5d
GI-533 | 2080a2a2-6058-48d0-8ca9-ffa0274636da | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | CRAH Alarm Faceplate: During commissioning, the chilled water valve mismatch created a mismatch alarm without an alarm rectangle as well as a unit alarm with an alarm rectangle. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198542&prj=475&rqi=5pwg9VSwkf44S9l3AGIkzbF3sX
GI-491 | d0357aa6-298b-437a-b135-8c2bf2bc4c69 | DC22-1 | 475 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment type |  |  |  |  | MAU valves need to be controlled via temperatures sent by the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198481&prj=475&rqi=BVsd96XvszTjWmjO8OAP8ULG2d
GI-519 | 20a9ffa4-d510-4d0a-844a-e6d8623762fd | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | CRAH Faceplate - During commissioning, we needed to add the min and max speed command (%) in the setup menu for unitary mode. Minimum fan speed should be 30% per the Equinix Standard | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198517&prj=475&rqi=yHvCrfscTyMhdnUeZ522eFPWjv
GI-531 | c4d9d396-668d-4f39-862e-328d36e3605e | DC22-1 | 475 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | Alarm Banner: PLC_IO_Network Alarms were not counted in the full site alarm banner during commissioning. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198536&prj=475&rqi=NDMoXa1Njts2aUlFeNilksbbEN
GI-504 | 227a1f13-c51f-4b90-ae70-e83ccca73359 | DC22-1 | 475 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | Fuel Fill Station is not shown on the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198499&prj=475&rqi=azLSFWq9D8pIhXLNigTHp3e3uv
GI-500 | 3e235728-ee1e-490b-9900-6beb2b874adc | DC22-1 | 475 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | Boilers and Make Up Water are not shown on graphics on both the FOH and MOF | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198495&prj=475&rqi=mf7mT2fAWa9rG4NIf1SlYr0xI6
GI-530 | 6de34f1e-63ef-438c-84ec-9d6daba37f72 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | CRAH HMI Program: During commissioning, CRAH's did not break out of grouping mode when not enough sensors are present. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198535&prj=475&rqi=iA4Gq5R56yzegTQPV9Vt4XOqh3
GI-520 | 44da00a9-0fbd-4bc1-b94d-dfbc6f3b4897 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | CRAH Program: During commissioning, the PID ramped up/down too fast when changing remote or supply temperature. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198518&prj=475&rqi=T5iuFyaQIHKZLQkZMtcKnrG4SK
GI-490 | 451feca5-ef48-46a2-b60d-66313c0d1a0e | DC22-1 | 475 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [7 empty] | Multiple Flow Meters and temp sensors are not reading correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198479&prj=475&rqi=WxmhZv3YGmwuRTNN6sWSNQDuLg
GI-528 | 7ea2fc16-55d6-4b6f-9e42-b2e662bfd980 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | Chiller Cooling Strings: During commissioning, a Wrench was displayed by the chilled water pump on cooling string chiller pages. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198532&prj=475&rqi=KflwMdgTC9e8enapNqhtppZohc
GI-535 | 40539be1-abff-4fbf-84ee-473b89695e73 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [7 empty] | RTU's: At the time of commissioning, we were losing comms on and off for RTU's. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198545&prj=475&rqi=nVo2B7w0qo8hmjjvrui32W2MZ9
GI-522 | 889a7820-0f15-40c4-8a28-37d8ea901451 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | CRAH Program: At the time of commissioning, a power loss event on the CRAH unit didn't trigger a loss of Power alarm. A "Loss of Power" or separate power loss alarm is needed for this event. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198520&prj=475&rqi=dzyboEWqbN9RdfbZgDx7WPRoLO
GI-526 | e8e973c3-ccab-4d3c-9cfe-e884458f8bbc | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | CRAH Alarm Program: During commissioning, a "High Air Flow" alarm did not appear on the BMS. Alarm only appeared on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198524&prj=475&rqi=PWe9M347dFQMcRBqLUg6dJ1Fbx
GI-488 | 19e50b0c-3552-4657-a4ab-3722dd934aa6 | DC22-1 | 475 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-02-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | During commissioning, BMS did not have a roof plan showing - All required devices | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198476&prj=475&rqi=sZCgwmPmBcwP9B2cfwfJfIh7gR
GI-105 | 2819df0e-0beb-45b5-bdcc-810a9430db3c | DC22-2 | 673 | AMER | Open | P2 Medium CX | francis.callan@veolia.com | 2026-09-17 04:00:00.000 +0400 | TRN - Trane |  | Missing Components | Commissioning | [7 empty] | 1-ACC-G-01: Pump VFD housing is missing hardware. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638472&prj=673&rqi=SbGNsjVmJ58NQhiPvlkKdgzNRp
GI-104 | e6429f1f-4a3b-4b6e-a24e-0aa955183e81 | DC22-2 | 673 | AMER | Ready for Verification | P3 Low CX | jonas.wudkwych@veolia.com | 2026-09-14 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS the faceplate for the MLTX does not open when the MLTX is clicked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638012&prj=673&rqi=kpkhgaDWcsnGpTXRirkG0BSjFw
GI-102 | 72fd2ff7-5fe9-4712-8ffe-949bc862d914 | DC22-2 | 673 | AMER | Ready for Verification | P3 Low CX | jonas.wudkwych@veolia.com | 2026-09-14 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS Both buttons 1UPS_H_1 and 1UPS_H_2 are linked back to the C block onelines not H block | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637987&prj=673&rqi=r9lkCWThv8JDrEOOeicpkaLIEv
GI-103 | 1d842165-ea18-4e11-a333-08fcd530faaf | DC22-2 | 673 | AMER | Ready for Verification | P3 Low CX | jonas.wudkwych@veolia.com | 2026-09-14 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS the TO DH 3001 button on the H block onelines page is not linked. Please fix | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638009&prj=673&rqi=QfVLQPKlRBwzWsmumRMTG2AIlO
GI-099 | 8e8ebd49-957a-4533-ab85-87283326e4f8 | DC22-2 | 673 | AMER | Ready for Verification | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-09-09 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [7 empty] | Onelines are displayed differently for phase 2 compared to phase 1. Please clarify if we are using a different standard throughout the same building. Specifically there is now a second page that the UDPs STSs and PDUs are being shown. See screen shots. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637514&prj=673&rqi=KdKlWN3VdsFQEFPbCiNuk9cDgv
GI-098 | e359d6e1-1974-47fc-af51-f2a2ceca4c5a | DC22-2 | 673 | AMER | Ready for Verification | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-09-09 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | MSB-ALL When one of the LBB breakers is closed the line animation between both the LBBs does not show power going through. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637502&prj=673&rqi=2bjfuuljcPzRyXDMqfD7RU2Qya
GI-096 | 64223020-4c92-4494-b97e-1d2100da96ea | DC22-2 | 673 | AMER | Open | P3 Low CX | michael.acciaioli@veolia.com | 2026-09-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS |  |  | equipment type |  |  |  |  | DH CRAHs - Active number of CRAHs in Group on Unit HMI does not update. When removing units from the group or powering off units the number of units in the group does not change. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636872&prj=673&rqi=114I2zIZgILohZTU4eNxU0fBSQ
GI-097 | a2b9d592-e00f-424b-8fc5-620f5bdfe172 | DC22-2 | 673 | AMER | Open | P3 Low CX | michael.acciaioli@veolia.com | 2026-09-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS |  |  | equipment type |  |  |  |  | EF's - Exhaust Fans that have been started and energized are not shown on the BMS. i.e. EF-C | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636877&prj=673&rqi=qrUngIAbAihLe8fwhACW276vPN
GI-095 | 74c15845-d2ef-4e5b-8f31-79f3f959e031 | DC22-2 | 673 | AMER | Open | P3 Low CX | michael.acciaioli@veolia.com | 2026-09-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | DH CRAHs- CRAH graphics indicate CRAHs are in alarm for "not in Group" when units are in group mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636870&prj=673&rqi=kA7G6pYA6oRQM4tscbx75xcrv2
GI-094 | 9f1c1f35-2052-4efe-8b7f-ad40f28a27c2 | DC22-2 | 673 | AMER | Ready for Verification | P3 Low CX | william.park@veolia.com | 2026-09-01 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS |  |  | equipment type |  |  |  |  | Chiller Bypass Valve logic: [Common to all ACC's on previous phase] After stage up to a new chiller, the enabled chiller goes through its normal start-up and starts increasing from 0 GPM to a flow similar to all running chillers. However, the bypass valve immediately reads this start-up as a failing to meet minimum flow state and starts to open. The bypass valve does not need to open during every stage up of a chiller, and should let the new chiller go through its normal ramp-up before being called to open. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636302&prj=673&rqi=PVgEkeWx7kXbj478vVvYP5gIYv
GI-093 | 5e4caad2-2a0f-448d-8737-b29ee57625ea | DC22-2 | 673 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-08-26 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | [7 empty] | Battery Cabinets - ALL the control power for the battery cabinets has not been labeled showing where power comes from. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635311&prj=673&rqi=L3rby6AP2RNVKAfwjwamTRBdQL
GI-092 | ac7d4f96-1a51-46b8-a61f-805c7597ad5c | DC22-2 | 673 | AMER | Open | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-08-25 04:00:00.000 +0400 | DEL - Delta Elec |  | Missing Components | Commissioning | [7 empty] | On STSs there is hardware missing from multiple locations on multiple units. See photos. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635100&prj=673&rqi=nX3LEPd8iGSk3ivF6AbFtMolbo
GI-085 | f029190f-0d0e-45bb-a503-d1435ff8202b | DC22-2 | 673 | AMER | Open | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-08-12 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | [7 empty] | On UPS_A_1, A_2, B_1, B_2, C_1, C_2, D_1, D_2, H_1 and H_2 There is a typo on the control wires labeled 1UPS_A_1-AP30_TB1-1 / 1UPS_A_1-AP30_TB1-2. These labels should read 1UPS_A_1_TB1-1 / 1UPS_A_1_TB1-2. This typo is across the 1 and 2 UPSs in all rooms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633234&prj=673&rqi=7SxPrFOY3dcBgh16xIDTJFKfQ0
GI-072 | df660ba3-6a2d-46c0-a205-80ea4531f2f1 | DC22-2 | 673 | AMER | Closed | P2 Medium CX | francis.callan@veolia.com | 2026-08-11 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [7 empty] | [Common to all ACC's/ Harmonic Filters]: Fuses continue to fail when opening and closing disconnect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633083&prj=673&rqi=2SxvHmxMDoPx1MxKivYQwphmYf
GI-074 | bb76638f-1f4a-4e06-b094-ae2a74e69a0b | DC22-2 | 673 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [7 empty] | 1GSB_1 IO/Control Cabinet - During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633101&prj=673&rqi=AKD33nopBO7EWCa1SXwN7SX9IU
GI-075 | c55fa17e-1390-4a9e-9593-144ef55f3cd2 | DC22-2 | 673 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [7 empty] | 1GSB_3 IO/Control Cabinet - During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633103&prj=673&rqi=WtGJFoSA3uQNCIF6lpUcVct9ID
GI-073 | f0246081-cdbe-4153-8c0b-abc727eaf988 | DC22-2 | 673 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [7 empty] | 1GSB_2 IO/Control Cabinet - During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633094&prj=673&rqi=fUb8KRF1rEWk3BzW3KrqljGubv
GI-079 | 8ceb77d3-6b5e-407b-92d3-ee8112f3669b | DC22-2 | 673 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [7 empty] | 1GSB_7 IO/Control Cabinet - SE DP discovered a common issue to all GSBs during phase 2 testing and inspection. During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633109&prj=673&rqi=M1s9zIGKoPMXvHBBjZdYEeLk5c
GI-076 | abbdf909-d30b-470c-9fa3-35552eeeede4 | DC22-2 | 673 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [7 empty] | 1GSB_4 IO/Control Cabinet - During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633105&prj=673&rqi=CTkWYdNcrVuH8WNmgdiRxSByFc
GI-078 | 9f821db3-7cc4-4304-8cc2-cb37d0c83ad6 | DC22-2 | 673 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [7 empty] | 1GSB_6 IO/Control Cabinet - SE DP discovered a common issue to all GSBs during phase 2 testing and inspection. During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633108&prj=673&rqi=ZhERV9azvGhsanOEiykF4gxvqw
GI-077 | 5b7d3716-cdb5-432c-b044-81a60fbeb875 | DC22-2 | 673 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [7 empty] | 1GSB_5 IO/Control Cabinet - SE DP discovered a common issue to all GSBs during phase 2 testing and inspection. During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633107&prj=673&rqi=82OTDC4T1u2HcnqNfumRFgIuOV
GI-080 | 18b9f518-d48f-4627-a038-84ebfe72c3e0 | DC22-2 | 673 | AMER | Ready for Verification | P2 Medium CX | mike.davenport@veolia.com | 2026-08-11 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [7 empty] | 1GSB_8 IO/Control Cabinet - SE DP discovered a common issue to all GSBs during phase 2 testing and inspection. During phase 1 when temporary 120V Â control power was removed from the GSB Control cabinet, the permanent control power was not installed properly. Proper wire labels are missing that indicate circuit source. Additionally, the 120V power source has never been energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633110&prj=673&rqi=k49ZCZhcLidtA6gvxpNpfUbsKR
GI-071 | 9858f982-d115-440d-871c-c3c5bc77f9f4 | DC22-2 | 673 | AMER | Open | P1 High CX | francis.callan@veolia.com | 2026-08-06 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | [Common to All CRAH's] No torque marks present on all victaulic clamps. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632600&prj=673&rqi=RdIJrMm94ZqgfZqkkAAobwPQXb
GI-070 | d79295c8-7295-4d75-afc4-8b21dc6934c6 | DC22-2 | 673 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-07-29 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/ Fault | DCOS | [7 empty] | MSB-ALL The PQMs on the MSBs cause comms loss when added onto the switch in the controls section of the MSB. Hanley troubleshooting is ongoing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631211&prj=673&rqi=dXMHMFQpsF46tKMSc5ZXAsd0EZ
GI-068 | 719c1569-2eb3-432b-b813-26ab183f4185 | DC22-2 | 673 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-07-28 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | MSB-All The breaker racked out status displays when the breaker is racked out to the test position but the status returns to racked in when racked all the way out. This appears to be an issue with the point being brought in through Modbus. The test position status works correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631103&prj=673&rqi=NZNu7dgntVFt76kY9FaIQyniJI
GI-069 | 1db59168-0a6d-4279-bd7f-532ec4626ba3 | DC22-2 | 673 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-07-28 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/ Fault | DCOS |  |  | equipment type |  |  |  |  | MSB-All The Communication Alarm Status is not properly displaying on the faceplate for the breakers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631104&prj=673&rqi=vn1dxojKz83QEeU5hTMpklMdLM
GI-067 | 5542a72a-8e39-404d-a9b1-b157bd0eed17 | DC22-2 | 673 | AMER | Closed | P2 Medium CX | william.park@veolia.com | 2026-07-28 04:00:00.000 +0400 | Electrical Contractor |  | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | ALL NEW DH CRAHS: Metal Shavings have been found all around and on top of the ATS within each electrical section of the Data Hall Mega CRAHS after drilling into the metal frame. Metal shavings need to be vacuumed and wiped away from each ATS and within each electrical box of the new 40 Data Hall CRAHS. Energization cannot occur until this action is completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631069&prj=673&rqi=VLaGc4rctA7FQJlORYPZBIUuwM
GI-062 | e84ecdfc-bf23-abe0-194f-d0f8d6269707 | DC22-2 | 673 | AMER | Closed | P3 Low CX | eric.gremp@veolia.com | 2026-07-10 04:00:00.000 +0400 | Electrical Contractor |  | Torque required | Commissioning |  |  | equipment type |  |  |  |  | STSs in electrical room H have all had 2 ground lugs torques broken. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628727&prj=673&rqi=8NOriPveOCMeKiOdgtmOyWmV2U
GI-056 | b82de68b-7fcd-49dd-86a8-bd4d44123979 | DC22-2 | 673 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-07-08 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning | [7 empty] | Hanley Gear- MSBs and UDPs ALL are missing the top hat grounding wires | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628386&prj=673&rqi=Sj2WbZIJOOgekcKicaqwnJSVZJ
GI-053 | 42cafb9f-9685-4939-8fdc-0b702b7ea3cf | DC22-2 | 673 | AMER | Closed | P3 Low CX | eric.gremp@veolia.com | 2026-06-30 04:00:00.000 +0400 | VER - Vertiv |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | UPSs: All of H-block UPSs are missing kickplates. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627447&prj=673&rqi=nT49uXDQl2DgnFO5UvInpcyguL
GI-052 | d8d5c995-baac-4b44-8108-5a599119a349 | DC22-2 | 673 | AMER | Work Completed | P3 Low CX | eric.gremp@veolia.com | 2026-06-25 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | PDUs: This general issue is to track all of the damaged nut inserts in the back of the PDUs so far for this issue damaged inserts have been discovered in 1PDU_C2R1_3, and 1PDUC2R1_2. As mor damaged inserts are found they will be added to this issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627076&prj=673&rqi=AV5PLmOtWMhKpfTAHrvYw8gODJ
GI-050 | 96b6955e-67cc-4604-80c8-6d9c3cea79ce | DC22-2 | 673 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-06-16 04:00:00.000 +0400 | SGB-SMIT |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | MLTX-All We are missing the fiberglass supports for the MV cables on the high side of the transformers. I believe SGB will be shipping these to site to be assembled by Rosendin. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625543&prj=673&rqi=BSpXdrjtnR9heKa83mly7P4hcy
GI-049 | 80266aa0-b61b-4658-afd6-7fe7da15f99c | DC22-2 | 673 | AMER | Closed | P3 Low CX | jonas.wudkwych@veolia.com | 2026-06-08 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning | [7 empty] | Electrical room CRAH stands came tack welded and are different from the first phase please see photos. Are these stands acceptable and can we get updated submittals showing these stands? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624340&prj=673&rqi=uWrvpgOJeXmahED026eN2nYcKR
GI-048 | d9f46550-de3f-4d34-86b8-240edd387322 | DC22-2 | 673 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-06-08 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Damage | Commissioning | [7 empty] | One of the stands for the Vertiv electrical room CRAHs is damaged and will need repaired/replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624339&prj=673&rqi=t6MsABnQOGZQPlr1ZeatOAOcCL
GI-047 | 5e4ea92f-12f3-4fbd-abc7-78d1e4c3fb8b | DC22-2 | 673 | AMER | Open | P3 Low CX | eric.gremp@veolia.com | 2026-06-04 04:00:00.000 +0400 | DEL - Delta Elec |  | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | STSs(H-Block): 1STS_H1R1_1, 1STS_H1R1_2, 1STS_H1R1_3, 1STS_H2R1_1, 1STS_H2R1_2, and 1STS_H2R1_3 all have been scratched and damaged while pulling MC cabling . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623984&prj=673&rqi=KTsW87wwgr0YOlfQ5m5KfdI2ph
GI-045 | e167e50d-579c-4c84-8025-059f8b74e392 | DC22-2 | 673 | AMER | Open | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-05-18 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | UMDSB-ALL The Spare Breakers in Q08 have a 250A breaker plug but the submittal shows a 150A plug set @ 70A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622211&prj=673&rqi=Zs7nv4UUUgrJ3iKIA4tI5RA8jh
GI-044 | caf67106-abf6-434c-b95f-869c2e7f5ddf | DC22-2 | 673 | AMER | Closed | P3 Low CX | eric.gremp@veolia.com | 2026-05-14 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | MSB (ALL): The Hanley Submittal RS-485 communications wiring does not match field installation including location of EOL resistors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621883&prj=673&rqi=MwNsLKSktV8Vpl3VOImuRmjedp
GI-043 | 9d4541d0-3c89-49cb-a663-2883544bea9a | DC22-2 | 673 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-05-05 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design correction needed | Design |  |  | equipment type |  |  |  |  | MSB-ALL the top hat access in the top back of section 09A for chiller power faces the wall and will need to be modified or changed out to face forward to allow the conduit and cables to be installed. On the last phase the top hat was modified. (See photos of both attached) The front top hat is for the MC going to the MDSB (breaker Q10) and the back top hat is for the power to the chillers (breaker Q11). Â Because of the top hats that were included for the MC cables on this phase there still might be issues with access on the install and it might be better to install the chiller cables before the MC on section 09A Talking with Hanley there are 2 options, either the modification of the existing top hats or ordering new ones. Both will need approval from Hanley and ordering new will have a lead time that could push schedules. Â This will need to be done on 1 top hat on all 5 MSB lineups and has potential to cause delays with install and startup. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620450&prj=673&rqi=te2nZdWyzRr1e8KL47AZUsb4UJ
GI-042 | f53cbda1-1c33-40f4-ac96-4593e582de39 | DC22-2 | 673 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-05-05 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | MSB-H B & C a plate on each phase on each shipping split was missed when the bolts were torqued. Everyone on site is aware, old hardware is being removed, new hardware is on the way and the re-torqueing will start tomorrow. Â This issue has been added for tracking purposes.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620449&prj=673&rqi=vJFIpI43iERDssgZ7DlcQFkEvJ
GI-041 | 3a881195-9fcb-44e7-9529-67da60c6b762 | DC22-2 | 673 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-05-05 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | UMDSB-ALL 2 breakers on each board Q06 and Q07 have the incorrect lug sizes that can only accept 3/0-350 kcmil. The electrical 1 lines call for #1 or 2/0 AWG depending on the length of the run.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620387&prj=673&rqi=CLntu0NgSgVyhwOGELoXzmBM6g
GI-038 | b4645f4d-a062-4a2c-a8e6-8277f4689282 | DC22-2 | 673 | AMER | Closed | P3 Low CX | jonas.wudkwych@veolia.com | 2026-05-04 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | MDSB-ALL Make sure that the equipment meets the minimum clearance of 4 inches from the wall. It appears that MDSB-H as well as other units are less than the required 4 inches. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620248&prj=673&rqi=Yw0iybmZPaUfBRX2MvxW0s3GCF
GI-036 | 33b0544e-0529-4301-91e3-b3724f64bef6 | DC22-2 | 673 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-05-01 04:00:00.000 +0400 | SGB-SMIT |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | MLTX-ALL Missing components to land cables run going from the MVTBs to the MLTXs, on the last phase the connections were made on bus bar inside a separate part of the enclosure (see picture) and there were factory cable connections to the actual transformer. I do not see these connections or cabling and support. Will we be connecting the MLTXs the same way as the last phase, if so are we missing parts from SGB? If the cables are being terminated differently can we make sure we have proper documentation and instructions on making the terminations from SGB? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620133&prj=673&rqi=R69TcDsGd5RSpaSiUUM9e4fAP6
GI-035 | 79651f18-f8b7-496a-a6dc-f75d00099071 | DC22-2 | 673 | AMER | Open | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-05-01 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | MLTX-ALL The control wiring is landed in the control box terminations and not on the transformers. REI has schematics to land the wires in the control box but not on the transformer. Please confirm that this is a task for REI and not SGB as well as obtaining proper documentation to install these wires on the transformer from SGB if this is an REI task. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620132&prj=673&rqi=rmnzv9xE6Tz4ddPb6Ar1LD0pwb
GI-033 | 51b7a81f-aa33-479b-99f1-01eed9dd3e40 | DC22-2 | 673 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-04-28 04:00:00.000 +0400 | Electrical Contractor |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | MLTX-ALL The bus bar inside the enclosure on MLTX A, B, C, D, and H has been improperly installed and will need corrected. There is a missing insulator that should connect the bus bar to a support bracket. Please see pictures and attached document. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619767&prj=673&rqi=1bVLE64TQvPSuwVrxNZ192muV9
GI-032 | e28f0b77-0e8f-4e18-9eb5-fdc3aff0d8e3 | DC22-2 | 673 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-04-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | MSB-ALL The ground bus bar on the back of all MSB sections that was converted to MC bus connections is missing a 1/4" spacer. This was missed during the rework done at the warehouse. This is an issue already known by Hanley and is being added for tracking purposes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619371&prj=673&rqi=ZqratVPXQjbvmVBH6OooPubL9V
GI-031 | fc323909-82ef-450f-8f36-9c7f09a622b2 | DC22-2 | 673 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-04-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | MSB-ALL. During the torqueing of the shipping splits between sections 3 and 4 it was found that some of the factory torque connections will need to be broken and associated hardware replaced because of the MC bus bar conversions. This was missed during the warehouse work completed by Hanley and will now need to be done on site. This will This will affect all MSBs This issue was entered for tracking purposes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619370&prj=673&rqi=ZFxTtBZgQmLp3k69tKW1Bv8tSH
GI-027 | a8cefef4-a494-4533-bfdd-ff408539e452 | DC22-2 | 673 | AMER | Closed | P2 Medium CX | jonas.wudkwych@veolia.com | 2026-04-22 04:00:00.000 +0400 | DEL - Delta Elec |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | STSs (common to all) - fuse kits for MSB control power were not installed on the units. The photo with the fuse kit is from an STS on the previous phase.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619092&prj=673&rqi=3KyCU9k5sMIE5uzVF1fGZmb5rE
GI-028 | 0fa8e728-515f-4ead-a017-56d623db42bf | DC22-2 | 673 | AMER | Open | P3 Low CX | jonas.wudkwych@veolia.com | 2026-04-22 04:00:00.000 +0400 | DEL - Delta Elec |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | STSs (common to all) - SOO placards to be replaced with accurate placards showing correct key #s. The SOO placard installed shows references to K1 K2 and K3 keys but the actual keys are A1 B1 and A3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619100&prj=673&rqi=hJ1oTxJIyXFX3tQBDwbqNQhPGG
GI-029 | 74b4e746-1c68-4f4c-877a-0c8a39fab111 | DC22-2 | 673 | AMER | Open | P3 Low CX | jonas.wudkwych@veolia.com | 2026-04-22 04:00:00.000 +0400 | DEL - Delta Elec |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | STSs (common to all) - Neutral kit placards are missing. Please confirm that the neutral kits were installed on the units and provide/ install missing placards. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619101&prj=673&rqi=4FgcaZqLxBJbP9JTs0cCl4nZlV
GI-026 | d0abc242-eb98-49a1-9598-5877df0af66c | DC22-2 | 673 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-04-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | MSB-ALL The ground bus bar between sections 3 and 4 appear to be improperly installed. Leonard from Hanley is already checking with the engineer on proper installation and sourcing the correct hardware. This is an issue across all the MSBs on site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618925&prj=673&rqi=KVVVqJofE5vIcCY57lt1I8hpnr
GI-018 | d06dc97a-b747-4e04-aa09-0f81c885668a | DC22-2 | 673 | AMER | Closed | P3 Low CX | jonas.wudkwych@veolia.com | 2026-03-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | General Design Issue | Design |  |  | equipment type |  |  |  |  | MSB - ALL on page 2 of the MSB as-built the Q03 Breaker is shown as having accessory 7 (the 120V Shunt open) but that should be shown on the Q10 Breaker. Also Accessory 8 is not included in the accessories legend. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616568&prj=673&rqi=LB3zAl2Ui0fv5qSdvDBk57DlMI
GI-006 | 333cc480-6400-4c15-95b2-9722e477fe42 | DC22-2 | 673 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-03-20 04:00:00.000 +0400 | SCH - Schneider MV |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | MVTB: Multiple bolts on the bus bars located in the bottom sections are not long enough to go all the way through the nuts to properly secure the bus bar. These will need to be replaced with longer bolts so at least 2 threads are showing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616148&prj=673&rqi=K8qcxvqYrYpNcpwL5OrRdRe5C6
GI-005 | cecdbab3-5162-481b-b9c1-6266523b642c | DC22-2 | 673 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-03-20 04:00:00.000 +0400 | SGB-SMIT |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | MLTX: Upside down washers on a bunch of the connections | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616147&prj=673&rqi=PQVCTOoJyN9NnRZeQOLddAzSN0
GI-002 | a9e24400-1b6a-495e-b7e1-91992490cb8f | DC22-2 | 673 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-03-20 04:00:00.000 +0400 | SGB-SMIT |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | MLTX: Washers on non-electrical connections are not uniform in size across multiple transformers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616143&prj=673&rqi=vkbMpnQhbySzRg4tuTg7DvH3s8
GI-009 | a839a689-1265-453b-97e3-f37953d9c86b | DC22-2 | 673 | AMER | Open | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-03-20 04:00:00.000 +0400 | Electrical Contractor |  | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | MVTB: The bottom front covers when taken off the unit are easily knocked over in a way that damages the front handles. One of these was accidentally knocked over when inspecting the unit and was damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616151&prj=673&rqi=6g3JSxJ1yPo6njaZtZispcNap7
GI-007 | 8d6feeb7-0a1e-4b0d-b380-9c64abd23286 | DC22-2 | 673 | AMER | Closed | P3 Low CX | ayorinde.akinrinlola@veolia.com | 2026-03-20 04:00:00.000 +0400 | SCH - Schneider MV |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | MVTB: Edge guard throughout the unit is held in place with painters tape in some places and is not properly fitted/installed to protect wiring from rubbing against metal edges. This issue is in multiple sections of the unit and will need to be addressed and wiring thoroughly checked to make sure the outer insulation on this and other units was not damaged during transport | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616149&prj=673&rqi=xPT8TRKsT0giAR2pCJPhXYV5J4
GI-392 | 784e4daa-fd45-4c32-a12e-2bea70fae972 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-07-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Access Control System (ACS) â€“ Battery monitoring is not available. The system does not provide battery status, battery fault, or low battery indications for monitoring and alarm purposes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629340&prj=603&rqi=gM3rUSOw6FDnYMXVyuUlDpk9Yx
GI-391 | cd37f091-bd54-47a3-88cc-00f26455bc9a | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-07-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Access Control System (ACS) â€“ The "Door Not Used/Opened" event shall be configured and programmed in the ACS. During testing, when a valid card was presented and the door was not opened within the configured time period, no corresponding event or notification was generated or recorded in the event log | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629339&prj=603&rqi=p7R4uLIYpGsw81FqRV6b5qk70n
GI-388 | 57fb87ec-0ce9-67e3-ad1e-6da47a85bc8d | DX03-2 | 603 | S-EMEA | Closed | P2 Medium CX | v.baddegama@core-group.me | 2026-07-13 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/ Equipment failure | Commissioning |  |  | system | Fuel System |  |  |  | Fuel PLC-1 was not communicating with DCOS. Fuel system vendor confirmed PLC-1 is operating correctly on site. DCOS team was not able to ping the PLC from Equinix local server however, it was possible to ping the PLC from the global EQX server. DCOS team advised it could be a network IT issue. UPDATED: DCOS team have confirmed the PLC is communicating to the PLC when connecting directly with the DCOS laptop. Several workshops have been held between the DCOS team, Vendor and Equinix Gen2/Server teams to work through why the PLC is not able to communicate across the network. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628805&prj=603&rqi=p3nmo8IdPN5CogDAQa6xITqjL6 | https://equinix.facilitygrid.co.uk/x/project/603/system/12118
GI-389 | cb08548c-83bc-751d-f76e-f932e101b15d | DX03-2 | 603 | S-EMEA | Closed | P2 Medium CX | v.baddegama@core-group.me | 2026-07-13 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/ Equipment failure | Commissioning |  |  | system | Fuel System |  |  |  | For Fuel storage tanks (FST) No. 3 and No. 4 located in DX3.1 (part of DX3.2 phase), an interstitial leak alarm was active on DCOS system. The fuel system vendor (Green Adaptech / GATSS) stated that the tank leak sensor is connected to the numeracator panel installed in the fuel pump room and the signal originates from numeracator panel and goes to the fuel PLC. GATSS stated the manufacturer of the numeracator panel and leak sensor (in the US) will need to be contacted to troubleshoot and resolve this issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628806&prj=603&rqi=P8MfUCW6KNMgVjVM09UJtSrkSD | https://equinix.facilitygrid.co.uk/x/project/603/system/12118
GI-387 | 5d59d1f3-f21e-4600-9ce1-e29d55405513 | DX03-2 | 603 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-07-02 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Component/ Equipment failure | Commissioning |  | Electrical â€“ LV | equipment | 1-RPP-F-4 | RPP - Remote Power Panel |  |  | During Thermal scanning of the RPP's it was observed that the temperature with 54kW load connected . During investigation it was found that connection at the incoming MCCB (Factory assembled) was loose. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627711&prj=603&rqi=r14KO2Z2vwutPMZ4IcXXyeYlRD
FPT-277-001 | e96a8bad-4d0a-494f-0db9-c1d06af724bc | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-06-29 04:00:00.000 +0400 | ABEC - DCOS | L4 | Component/ Equipment failure | Commissioning |  |  | equipment | CHWS L4 FPT & Mech IST |  |  |  | During CHWS level 4 it was observed that one of the redundant RAS-13 sensors was not reading correctly. One of 3 flowmeters on one supply flow header going to data hall (RAS-13) was removed to send for calibration. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627287&prj=603&rqi=9XQzwqElFjIEOLpw3P2wEOvxSs
GI-386 | 17981bf3-69c5-4bf4-99e3-0e469db2e5ea | DX03-2 | 603 | S-EMEA | Closed | P2 Medium CX | v.baddegama@core-group.me | 2026-06-27 04:00:00.000 +0400 | VER - Vertiv |  | Component/ Equipment failure | Commissioning |  |  | equipment type |  |  |  |  | APPLICABLE FOR ALL CRAH's: Vertiv/MDS stated that the CRAH HMI is a new product and that all HMIs need to be replaced. The following issues were observed during various times of testing: 1). When fan speed reaches 100% the HMI goes blank/white and HMI makes a sound. To reset the HMI, the cable connected to the HMI will need to unplugged and plugged in again. MDS engineer was observed to carry out this action multiple times on random CRAHs during various tests (chiller load testing and GF Data Hall load testing). 2). On random data hallCRAH's the HMI freezes preventing any touch input on the display by the user. This was particularly observed in the data hall CRAHs. 3). On random data hall CRAHs it was observed the response to user touch inputs was very slow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627170&prj=603&rqi=vxgYWQJANO2YUFBjkEHTW4aCNC
GI-385 | 02ba72f8-92e6-9056-dabb-e63cb624b04b | DX03-2 | 603 | S-EMEA | Closed | P2 Medium DCOS | v.baddegama@core-group.me | 2026-06-26 04:00:00.000 +0400 | ABEC - DCOS |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | It was observed on 26th June 2026, the DCOS auto/Manual switch for number of devices in cooling manager manager was not working. Could not be changed from Auto to Manual. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627163&prj=603&rqi=r5M8js4vxdzNpT6T9F3HdyMDeD
GI-383 | eb54acf4-107b-4dd9-9063-f6c0a3a21510 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-19 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | DCIM BCM Issue | DCIM |  |  | equipment type |  |  |  |  | During RPP checks with operations for DCIM communications it was recorded there were communication issues. ABEC traced the communication issue with the Schneider Gateway. The polarity of the internal connection to the SCU100 was found to be reversed. ABEC connected a separate cable directly from the SCU100 controller to the Schneider Gateway and confirmed that communication with the gateway is working properly. The panel wiring needs to be reverified to ensure proper communication. The cable is currently marked as A(-) and B(+), which appears to be incorrect. It should be A(+) and B(-). The termination should also be checked and verified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626225&prj=603&rqi=smYdh7u2OrbhrfdI0KJvSB0RTx
GI-111 | 6837a223-89fa-4dc2-8b02-62620897cb44 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-06-17 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/ Equipment failure | Commissioning | [7 empty] | Luminaires CMP2-GF-L7-15, CMP2-GF-L7-17, CMP2-GF-L7-19, CMP1-GF-L2-02, and CMP1-GF-L2-04 failed the Battery Autonomy Test (Ground Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625637&prj=603&rqi=QX88YeyBxandHw3OmrBWr5hDeN
GI-110 | 3ade75dc-4235-4ac4-840e-42c3847a123f | DX03-2 | 603 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-06-16 04:00:00.000 +0400 | VER - Vertiv |  | Component/ Equipment failure | Commissioning |  |  | equipment type |  |  |  |  | During STS-F-2 Testing the following was Observed in the ground floor Data Hall CRAH: - low Humidity Summary Alarms present in several CRAH. - Above alarms not resetting on HMI - â several HMI unresponsive - Several HMI were observed to have their â time & date reset to defat (year 2000) - â GC had to switch the CRAH off and on to reset alarms - â Fans not ramping up with return temp reaching 36deg (advised the CRAH were set to 36Deg return air). These were not reamping up individually or as a group. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625525&prj=603&rqi=LiLKsVClveneq9A0gI8HyeMIIx
GI-106 | 21b5ed63-ff18-4700-8915-e9e73be5549b | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-11 04:00:00.000 +0400 | TRN - Trane |  | Commissioning Issue | Commissioning | [7 empty] | Trane site technician placed the HMI into STOP mode without notifying anyone. This caused the Chiller to not operate correctly (Compressors failed to start when required). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624896&prj=603&rqi=yfzSl2QIl92B4HrAwBhA04dVGd
FPT-366-001 | 3e99c6e0-b13a-f7cf-c2ac-de2680d48edc | DX03-2 | 603 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-06-09 04:00:00.000 +0400 | ABEC - DCOS | L4 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1-STS-E-1 | STS - Static Transfer Switch |  |  | Observed the Kw reading not matching actual output kW on 1-STS-E-1 graphic. output side of STS and STSSB not energised (white) line. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624634&prj=603&rqi=DBwBS8DKqYopS5g0rIJi8tGN8G
GI-105 | 86eafb43-95bc-7944-1d06-430d06b41f34 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-06 04:00:00.000 +0400 | VER - Vertiv |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | UPS labels to be corrected. 415V not 400V | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624283&prj=603&rqi=jmCiwYkuq3RVm8XQzHOviCFMmY
GI-103 | 4de6be58-073a-4593-b879-81ae13c05b53 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-05 04:00:00.000 +0400 | CMM - Cummins |  | Component/ Equipment failure | Commissioning |  |  | equipment type |  |  |  |  | During UPS level 4 testing, while on Generator source it was observed at both the Generator controller and DCOS the Power factor and the KVAR were reporting 'out of range' at the DCOS. The Power factor was showing a negative power factor. The readings at the Generator ACB on the MSB were found to be reading correctly. it is noted that the load bank from DX3.1 is a resistive LB and there is also live loads on the MSB Output board (CRT SMDB). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624126&prj=603&rqi=y208zpSXZJwHBVZ7RsYETrTVJU
GI-098 | 9adde382-9f22-4ce9-864c-bd6d1fcd33a6 | DX03-2 | 603 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | ABEC - DCOS |  | DCOS Template Issue | DCOS |  |  | equipment type |  |  |  |  | DCOS LCP Templates are BLANK. This is applicable to ALL DCOS LCP panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623891&prj=603&rqi=B13vsG3KAP2R9rnfnEN8RxE1BF
GI-101 | 3de197f3-34a7-4bbe-9425-e65587d8ff35 | DX03-2 | 603 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | ABEC - DCOS |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | DCOS footer/banner missing Values from DX3.1 weather station including the OAT, OAH, OAWB, DX3.2 PUE value and Fire alarm status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623894&prj=603&rqi=FKMSqQLat6gufceAj9JQGBGmJZ
GI-100 | 79c18a42-05dc-4fdc-a55c-9f4ffa0fe9e1 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Graphics Issue | DCOS | [7 empty] | UPS High Alarm limit incorrectly calculated on the DCOS Template (80%). Value inputted on the template is 2250, this should be 1780. These were corrected for UPS-D & UPS-E level 4 testing, however it has been observed these have reset to the incorrect values. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623893&prj=603&rqi=TniA4ZN91xBkG0uIUweTvybzQ2
GI-097 | 1d91e932-4450-4de5-8885-02848586287b | DX03-2 | 603 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | ABEC - DCOS |  | DCOS Comms Issue/ Fault | DCOS |  |  | equipment type |  |  |  |  | CHWS no/low flow observed across the system during UPS Level 4 testing (DCOS Cx is ongoing for valves and sensors) after the Data Hall CRAH were started up. In the off positions the CRAH PICV should be held in 100% open position. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623883&prj=603&rqi=TrvRlqZIiTbjOJdtL2dI39NWg5
GI-102 | b855912c-91b8-4e09-97f0-cd9ac646f5b5 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | Battery cabinets (D, E & F) Cores 1 & 2 Labels to be corrected after cable orientation swap. ALL UPS battery cable labels to be corrected also. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623896&prj=603&rqi=3MtwS1fskECO0NXeWFgvs8ykx5
GI-096 | 633a6ffc-d3bc-477e-9d30-8d6fec8ca5ce | DX03-2 | 603 | S-EMEA | Closed | P2 Medium DCOS | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Design Issue | DCOS |  |  | equipment type |  |  |  |  | Chiller Valve (located at the return to the chiller) was closing when the Chiller compressors switched off. This was causing the chiller to shutdown on Evaporator no flow alarm'. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623878&prj=603&rqi=jYKO5Qwjk1wAzMYWzR9SiWdQvS
GI-099 | 9dc382d0-a964-496d-b037-47c66bb5f11e | DX03-2 | 603 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-06-04 04:00:00.000 +0400 | ABEC - DCOS |  | DCOS Template Issue | DCOS |  |  | equipment type |  |  |  |  | DCOS Generator Template 'Deviation from set point' Was shown as Voltage instead as Percentage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623892&prj=603&rqi=VyIuzA2NDl3cecQhfNBdkhiFlW
GI-092 | d03b1453-fbfd-4897-a58e-3e132669a6b5 | DX03-2 | 603 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-05-22 04:00:00.000 +0400 | Consultant |  | General Design Issue | Design |  |  | equipment type |  |  |  |  | CHWP supply MCCB at the MSB is furnished with an ELR with trip function. Is this necessary? During the UPS-D level 4 testing we observed that CHWP-D tripped on earth leakage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622809&prj=603&rqi=2QujyaoEdgWm1u0jSnFVISwGi2
GI-090 | c2da986a-cdc8-4787-8171-5ef34b833d4c | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/ Equipment failure | Commissioning |  |  | equipment type |  |  |  |  | During the inspection of Generator D, it was observed that when a low fuel alarm is triggered, fuel is pumped not only to Generator D but also to Generator E&F. This is not compliant with the intended operation, as each unit should function independently. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622466&prj=603&rqi=eIIEXmVabLcOrlKg6qkiVezVL9
GI-089 | 9bf19e28-6c54-4a64-afe3-71527f181a35 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/ Equipment failure | Commissioning |  |  | equipment type |  |  |  |  | When switching the fuel system from Auto to manual the system operates fine. When switching from Manual to Auto Vendor is advising us that the PLC requires a re-boot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622465&prj=603&rqi=CRbpWI0BDUx1knsyD4A7gR4g5k
GI-088 | 5c7768ab-4030-4f26-8fa3-efe741aecc30 | DX03-2 | 603 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-05-18 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | During the level 3 and pre-level 4 verifications, the discrimination study has been updated since L2B. The MSB Breaker settings to be secondary tested based on the latest revision LV Coordination study. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622195&prj=603&rqi=9p8KTnLknff8sAJxOnq25VTJfC
GI-087 | c844422c-34ac-4e61-acbb-3035a3ef8dff | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | RMU castell key operation sequence description on the panels for the castell key operation to be corrected (this was observed during L2 testing and has been recorded on the Cx meeting from 5th February). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621769&prj=603&rqi=CSDCHxgoB4XSfIxhWtht8yoaXV
GI-086 | 1cf274f8-c325-49c3-a17e-8e944149a3dd | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-05-12 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | LVBR Specification section #23 'Aux Power supplies'. The sequence upon losing PS1 & PS2 then rebooting to PS3 upon receipt of Generator is not working correctly as the HMI moves to Maintenance Manual mode and locks out (requires manual resetting and no aut transfer can occur). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621252&prj=603&rqi=sacvV0zDml8VtM3a4Vah3Bh9OY
GI-084 | c9e1ac9c-e2bf-47f6-aa75-69176264e09b | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-05-09 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Component/ Equipment failure | Commissioning |  |  | equipment type |  |  |  |  | It has been confirmed the LV Switchgear MSB-LVBR PSU has an inverted signal providing a constant DC (P1) alarm at HMI and to DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621038&prj=603&rqi=tzLNxRTg6A9hYrvOgcpv5ONE4o
GI-081 | c304c9f6-2325-e9d9-d560-8ee495c632d0 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-05-05 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning | [7 empty] | FUTURE LIQUID COOLING CHW LINE IN 1st floor Data Hall (1 No.) near CRAH-48: A minor clash was observed between 1 isolation valve handle and the DRV handle. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620388&prj=603&rqi=vX4mXtaC17w31IqzFX7rJKWNPZ
GI-074 | 7c5ba39a-3773-4b8f-81eb-dd2f41dc3776 | DX03-2 | 603 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Battery cables from UPS to Battery found to have been terminated in the incorrect battery cubical which do not correspond with the correct UPS_Cores. although this does not impact the operation of the UPS, this does not align with the design arrangement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619061&prj=603&rqi=hyJS50dSV4p2qh0ITLBwG970Fg
GI-073 | e4dc512b-bbe4-4b52-9069-69b8a95eacbf | DX03-2 | 603 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-04-21 04:00:00.000 +0400 | VER - Vertiv |  | Component/ Equipment failure | Commissioning |  |  | equipment type |  |  |  |  | Advised by the GC & Vertiv during UPS L3 commissioning the UPS PCB requires replacement (applies all 3 UPS).. Vertiv to provide a report and advise what the cause of the issue was. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618820&prj=603&rqi=M9dyntYoz5URVEmUxrLSdhe5gn
GI-072 | 7c0ae3df-6bf7-8104-3d8c-c5668e30bead | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-04-14 04:00:00.000 +0400 | General Contractor - Commissioning |  | Incomplete Connections | Commissioning |  |  | equipment type |  |  |  |  | All CRAH isolators Incoming earth cable is not connected to the outgoing side of the isolator. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618106&prj=603&rqi=5MURJjqbu0HLTuVi9CtxtXVN57
GI-067 | 65d8cd43-5825-4567-af9b-75cd83eec065 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-03-26 04:00:00.000 +0400 | CMM - Cummins |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | Generator enclosure DB labelling in the field for circuits are incorrect and do not provide the circuit reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616551&prj=603&rqi=a3BuTZNgAEZHditGyAYGS3Kz9o
GI-066 | 1ebd95ff-0dfe-4cd6-9eb5-d3ea2c21a452 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-03-26 04:00:00.000 +0400 | Equinix Design Engineer |  | General Design Issue | Design |  |  | equipment type |  |  |  |  | During Level 3 STS Start up, during total maintenance bypass (Bypass is energised but the STS including the HMI is shut down) there is no indication on the STS breakers/isolators (other than S2 MCCB LED) that there is LIVE power passing through the busbar, or any interlocks (doors, panel covers etc..The busbar is exposed within the panel as there is no isolation between panel sections of the STS. This is seen as potential safety risk hazard during maintenance activities. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616535&prj=603&rqi=dmCOEQcTkR9b4OnbWcBDlTpYfy
RT1ELEC-586-001 | ce50618e-86c5-b1b5-5a90-30e3af30a4ce | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-26 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1-GSM-RACK-02 | CAB - ICT Cabinets |  |  | GSM Rack-02: At the top of the GSM rack where the fiber optic cables enter into the rack, there is no brush type cover. There is a risk of dust and debris falling into the rack through this cable penetration hole. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616506&prj=603&rqi=Eldw5SvWJl9gR7QSUqc6cAoDPa
GI-060 | 401d3613-b0b1-4046-8ac0-4ca18f43c389 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning |  |  | system | CHW System |  |  |  | It was observed that there was no chilled water flowing through the CRAHs in 1st floor electrical rooms (switchrooms and STS Rooms string D & E). Contractor needs to investigate the issue on site and provide a reason for no chilled water flow based on their observations at site. Please see attached some photos from the CRAH HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616268&prj=603&rqi=UilVXf8s5XF28Nsgou2Nz05bHi | https://equinix.facilitygrid.co.uk/x/project/603/system/12115
YT1SEC-1-001 | 5318d5f2-99c1-a9d6-eb98-c5e86f5a0656 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-03-18 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not complete | Commissioning |  | Electronic Safety and Security | equipment | ACP-01-NER-C | ACU - Access Control |  |  | During ACP-01-NER-C inspections, it is noted the doors on Buffer Vessel Room (1331-B, 1331-C, 1331-D, 1331-E) and Future ETS Room (1351-B) are not aligned, preventing the completion of ACS device installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615932&prj=603&rqi=JlpLF8mGGTy6qoAxqQ3Q0XgdT3
YT1ELEC-143-001 | 41b9dc07-ce98-bfd0-2ada-d4ad51ae4268 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-03-16 04:00:00.000 +0400 | Low Voltage Electrical Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1-RPP-F-8 | RPP - Remote Power Panel |  |  | 1-RPP-F-8 Drawing pocket missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615708&prj=603&rqi=qGlkKqcxiWZMrDyKpGFrgBrmwY
YT1ELEC-557-001 | 0495e609-b1ae-c39d-7d5e-1d0f6c82344c | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | B2-ODF 4 | CAB - ICT Cabinets |  |  | The cable tagging inside B2-ODF-04 rack in DX3.2 FER-C is incorrect. Refer to attached photo for details. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615714&prj=603&rqi=d2CP1P3K43EpyHKOFt99qTrRfn
YT1SEC-3-003 | 0d7222b0-9d87-fc60-4a69-3a9257816a36 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-03-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not complete | Commissioning |  | Electronic Safety and Security | equipment | ACP-01-NER-E | ACU - Access Control |  |  | Access control panel ACP-01-NER-E: The door between 3.1 and 3.2 has not been installed, resulting in the installation of acs device remain pending. This issue is raised to record this and allow a conditional yellow tag to be applied. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615408&prj=603&rqi=aoj7wuk4eIbT9Km8oODW64JM4l
GI-057 | 07b5e023-2308-4bcc-871f-0f9ae1f1a390 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-03-10 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | ALL MSB PQMs used for monitoring the Transformer points have not been configured at the factory. this has impacted the Transformer L3 testing, | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615252&prj=603&rqi=WRTe9DQzIL4RbPU3Hfc4JLGbgq
GI-055 | 5b9aac99-7c11-4dfd-a319-50ba8cfa00a0 | DX03-2 | 603 | S-EMEA | Closed | P3 Low DCOS | n.forde@core-emirates.com | 2026-03-10 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | DCOS Installation not complete | DCOS |  |  | equipment type |  |  |  |  | During DCOS P2G testing it was observed that when the ACB on the MSB were racked to the test position then retuned to Service, these remained in the 'test' status showing on the DCOS Graphics. SAS Site team confirm that Modules for the ACB are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615250&prj=603&rqi=uHOIS390ZyHmTX9xWSaGE4N3me
YT1SEC-3-001 | 8ebee70b-a219-70b7-6db7-b5a7f905423d | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning |  | Electronic Safety and Security | equipment | ACP-01-NER-E | ACU - Access Control |  |  | Access control panel ACP-01-NER-E L2B inspection: No continuity observed on cable from ACP-01 NER-E panel to STS Room E motorized lock (EM). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615246&prj=603&rqi=YBy41gUn3LN2qiLtLx2iiURB9W
YT1SEC-4-001 | d6736277-a180-36fe-fb8a-eeafeb74a0a8 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Documentation not issued/ Required | Commissioning |  | Electronic Safety and Security | equipment | ACP-01-NER-F | ACU - Access Control |  |  | FOR ALL Access Control Panels: The related shop drawings (Schematic, Layouts and panel wiring diagrams) need to be updated as per site condition then uploaded officially to ProCore for approval. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615200&prj=603&rqi=iFiwyvHDYx9g3jVK3uHiXKumEh
YT1SEC-3-002 | 521588be-c8ba-3a6b-804e-0a37ff7b0cce | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning |  | Electronic Safety and Security | equipment | ACP-01-NER-E | ACU - Access Control |  |  | ACP-01 NER-E: FF ELECT ROOM has no label on door Motorised lock. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615247&prj=603&rqi=OVfYWUPgNy4wfjhorBoslGMQNb
YT1SEC-2-003 | 78bddb3d-e482-cc65-e7b8-ee90f688b3a2 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning |  | Electronic Safety and Security | equipment | ACP-01-NER-D | ACU - Access Control |  |  | ACP-01-NER-D L2B inspection: No cable continuity observed for door contact of GF Data Hall door B (1500 B). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615118&prj=603&rqi=LeUYLI7zTgZA3aK6XVgAnln0en
YT1SEC-2-002 | 15400576-590f-1408-3e6b-e4c1a77db852 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not complete | Commissioning |  | Electronic Safety and Security | equipment | ACP-01-NER-D | ACU - Access Control |  |  | Access control panel ACP-01-NER-D: The junction box cover is missing for the door to STS Room G (1100A). Also ensure junction box cover has the correct tag label. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615117&prj=603&rqi=YqYcB4WJm0M4knhFaDcd4yRbsW
YT1SEC-2-004 | 9bcfb673-06d7-fb96-4c4c-64633a6e4b59 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning |  | Electronic Safety and Security | equipment | ACP-01-NER-D | ACU - Access Control |  |  | Access control panel ACP-01-NER-D L2B inspection: One of the door contact devices for the door of MMR-D (1081A) is damaged and needs to be replaced. Cable continuity test to be carried out after new door contact. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615119&prj=603&rqi=2dHY5xo4kEfIwQvMxdvoDX4IlR
GI-049 | f1ecfd57-540c-ee81-76d5-464c691e6c43 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-03-04 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning |  | Electronic Safety and Security | equipment | ACP-01-NER-F | ACU - Access Control |  |  | ACP-01 NER-F: Labelling on junction box above FF Data Hall Door C is pending. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614689&prj=603&rqi=39gk40m7js3y348IeORJnqpQF9
GI-048 | b9cf8140-6145-4b57-b923-13416fce14f8 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-03-03 04:00:00.000 +0400 | Equinix Design Engineer |  | General Design Issue | Design |  |  | equipment type |  |  |  |  | AHU - Air Handling Unit: It is observed there is no Humidity control via a Heater battery or any other physical device within the AFU/MAU's. There us a concern with the high humidity in the region the unit will not provide dehumidification efficiently. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614606&prj=603&rqi=RoOFQEbWBLunwBTOqb2R7geJOW
GI-047 | 99c2b869-0ae5-90e2-8f98-ad285a4d59b6 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-02-26 04:00:00.000 +0400 | TRN - Trane |  | Incomplete Connections | Commissioning |  |  | equipment type |  |  |  |  | Chillers: Although torque marked, manufacturers earth bar connections was found to be loose (checked with hand) and requires tightening. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352229&prj=603&rqi=b0QgpbVwsWv8olmtcBBbCmGBEw
YT1SEC-2-001 | 9b42759e-2f2e-461b-b9d9-2c4e15fdb37b | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-02-25 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning |  | Electronic Safety and Security | equipment | ACP-01-NER-D | ACU - Access Control |  |  | Access control panel ACP-01-NER-D: During L2B Cable Point to Point inspection on 25th Feb 2026, it was observed that the cable connecting to the door contact in Battery Room F was damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212851&prj=603&rqi=qzEaTmZp2rU6h9nMR63Godco7z
YT1ELEC-540-001 | 2e5bf178-0c8d-45df-ab88-6dfe37a3e845 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | m.louie@core-group.me | 2026-02-20 04:00:00.000 +0400 | Low Voltage Electrical Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1-PFC-E | PFC - Power Factor Correction |  |  | 1-PFC_E isolator rotary handle is missing. PFC cannot be safely energised with this missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199672&prj=603&rqi=1Y9wopCQC1oH2c7Xa7VUO2RMoY
GI-042 | eafb558b-934c-42e4-8324-e526a7c6c894 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-02-19 04:00:00.000 +0400 | Consultant |  | General Design Issue | Design |  |  | equipment type |  |  |  |  | Exhaust fans (EF) are not interfaced with the fire alarm system and therefore do not shut down in fire. This has been confirmed by the desing team and general contractor. Concern that ducts and fans are not fire rated and the risk of transerring smoke through adjacent fire zones and cause fires in adjacent areas. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199546&prj=603&rqi=pADS2GRsODW5lpPCtprfxHAhXz
GI-041 | cda6db37-6cf6-1748-f1df-e351c61642c1 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-02-18 04:00:00.000 +0400 | SOC - Socomec |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | LOTO provisions missing from all STS source 1 isolator. The padlock accessory for the isolator has not been provided or fitted. This does not allow the STS to be fully locked off under the approved GC LOTO procedures. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199456&prj=603&rqi=5CuszzXjEAI5geiainK2vNSMZh
GI-040 | f879e96f-d941-4dfc-a73a-7fa60b6e8e7f | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | v.baddegama@core-group.me | 2026-02-17 04:00:00.000 +0400 | General Contractor - Commissioning |  | Cleaning | Commissioning |  |  | equipment type |  |  |  |  | Red rust was observed inside the CRAH on the CHW pipe supports. In addition, white rust was observed on the internal side walls of the CRAH. Refer to attached photos for reference from CRAH-F-E-59 in Switchroom F. This has been discussed with Equinix and Vertiv . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199350&prj=603&rqi=igjMZhpHIeSjbMTDRr2FSuXktD
GI-035 | 69b91c2b-f770-410f-b8b0-244a93ad6d09 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-02-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Incomplete Connections | Commissioning |  |  | equipment type |  |  |  |  | All RMU incoming VT's were left in the open position which was picked uop during DEWA energisation. As per Se email dated 10thy februray RMU are safe to energise with the VT in the out of service position. PMU currently not measuring Voltage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199221&prj=603&rqi=RH2Mj412f8w5tkQTuVDsCS9acO
YT1ELEC-559-001 | 9ea3d97e-bc2a-405b-b77b-30a69f582733 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-02-13 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | B2-GF-SEC-RACK-02 | CAB - ICT Cabinets |  |  | B2-GF-SEC-RACK-02 door lock is damaged and unable to close. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199206&prj=603&rqi=yCrUGWthjkoly2QbTHtAx4Tfoq
YT1ELEC-560-001 | f9bcc3c3-2aed-e8f3-3b52-a7569c1a42cb | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | c.castro@core-group.me | 2026-02-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | B2-FF-SEC-RACK-01 | CAB - ICT Cabinets |  |  | During white glove inspection for B2-FF-SEC-RACK-01, it is observed the body of the Rack has been sprayed with gray paint to cover scratches/defect. The finish is poor and to be addressed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199146&prj=603&rqi=USrG1V59RrMAGcXE3pKdbunHT7
GI-031 | b8fa2af5-0fd5-48d4-b43a-a6b06304fd53 | DX03-2 | 603 | S-EMEA | Closed | P2 Medium CX | v.baddegama@core-group.me | 2026-02-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1-RPP-F-4 | RPP - Remote Power Panel |  |  | The earth bar inside all RPP's are missing provision (holes) for terminating earth cables. Refer to attached photo as a reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198852&prj=603&rqi=06pCxU3XEqXbtvcbKfahOvYdnA
YT1ELEC-532-001 | 56374864-5f3a-c7e2-cc6d-91603080b50a | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-02-06 04:00:00.000 +0400 | SOC - Socomec | L2B | Component/ Equipment failure | Commissioning |  | Electrical â€“ LV | equipment | 1-STS-F-2 | STS - Static Transfer Switch |  |  | STS-F-2 top cover showing deflection/damage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198684&prj=603&rqi=ZAU4hjEMLbE8KvvEea4zv7D5hg
GI-029 | 73422119-64d5-7823-c140-1d9b7cef0c7f | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-01-30 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Component/ Equipment failure | Commissioning |  | Electrical â€“ LV | equipment | 1-PFC-F | PFC - Power Factor Correction |  |  | PFC-F Blue phase LED cover damaged/missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198054&prj=603&rqi=0SFb5tVUkiO5cu980h7QmilHpw
YT1ELEC-530-001 | 4d5c8bba-80e0-a841-e717-e47ded00ef89 | DX03-2 | 603 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-01-20 04:00:00.000 +0400 | SOC - Socomec | L2B | Component/ Equipment failure | Commissioning |  | Electrical â€“ LV | equipment | 1-STS-E-1 | STS - Static Transfer Switch |  |  | STS door lock is faulty (not locking) and requires repair/replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197135&prj=603&rqi=wjBPlTacilx3WlnYotoVoQyOxd
GI-018 | 2421b0a3-4c8c-464d-b366-b3e9ba39f008 | DX03-2 | 603 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-01-06 04:00:00.000 +0400 | SCH - Schneider MV |  | General Design Issue | Design |  |  | equipment type |  |  |  |  | RMU Cannot be fully isolated (for LOTO pruposes). A cover has been provided on the mechanical ''On'' button only and not for the 1 - Earth switch (separate issue) 2 - CB on/off, Disconnector on/off by local pushbuttons or 3 - The remote pendant. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196386&prj=603&rqi=b9WjuNY0C2YARRI8YgKkwzOxwM
GI-017 | 8eb86323-48e7-4f99-9fed-5c550d7a1e5d | DX03-2 | 603 | S-EMEA | Closed | P2 Medium CX | n.forde@core-emirates.com | 2026-01-06 04:00:00.000 +0400 | SCH - Schneider MV |  | General Design Issue | Design |  |  | equipment type |  |  |  |  | All RMU's Earth switch are not furnished with Locking devices. This deviates from Equinix design standards for MV Switchgear/RMU. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196385&prj=603&rqi=Ov2GCLmWGJc7WXBSFFsZcDJEED
GI-005 | 71279fe0-eb5e-4fb7-9f83-900701c2357a | DX03-P1 | 699 | S-EMEA | Open | P2 Medium CX | n.forde@core-emirates.com | 2026-09-17 04:00:00.000 +0400 | TRN - Trane |  | Cleaning | Commissioning |  |  | equipment type |  |  |  |  | During the red Tag inspection it was observed the pipework within both Trane chillers will require flushing (more than back flushing) due to the rust observed. (The same was observed from the Trane chillers for DX031). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638476&prj=699&rqi=xlVaEKux6Yrsle1VUDU1YaG95R
GI-004 | c3682e49-f053-4d9e-ac19-fb8cf61744c8 | DX03-P1 | 699 | S-EMEA | Open | P3 Low CX | n.forde@core-emirates.com | 2026-09-15 04:00:00.000 +0400 | SOC - Socomec |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | STS are missing LOTO provisions on Q41 isolator (Source 1 Primary supply). This issue applies to ALL 4No STS supplied to DX3.P1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638274&prj=699&rqi=REnuVuL0Xjc5fwuncLBMapMOe6
RT1ELEC-54-001 | 67cb7d27-0df9-9c81-56c5-e75ccd9b6167 | DX03-P1 | 699 | S-EMEA | Open | P3 Low CX | c.castro@core-group.me | 2026-09-11 04:00:00.000 +0400 | Low Voltage Electrical Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1-MSB-G | MSB - Main Input Switchboard |  |  | 1-MSB-G EKIP power supply modules are missing for 11Q1 and 12Q1 breakers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637733&prj=699&rqi=52j8nuPfrBV2l8RgLbhrE0FIoP
RT1ELEC-76-001 | 45470fd6-ee3f-5f47-68a1-683aa97ea168 | DX03-P1 | 699 | S-EMEA | Open | P3 Low CX | c.castro@core-group.me | 2026-09-09 04:00:00.000 +0400 | Low Voltage Electrical Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1-RPP-H-1 | RPP - Remote Power Panel |  |  | 1-RPP-H-1 controller SCU100 is missing / not installed within the RPP. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637474&prj=699&rqi=4iDtImKDhhmoxKU7bTIKGrTBbA
RT1ELEC-35-001 | cb4642e4-e9ef-1a3b-d1a8-65d3138ed7df | DX03-P1 | 699 | S-EMEA | Open | P3 Low CX | c.castro@core-group.me | 2026-09-09 04:00:00.000 +0400 | SCH - Schneider MV | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1-BTU-RMU-H | BTU - Battery Tripping unit |  |  | 1-BTU-RMU-H panel Door limit switch found damage (switch is bent). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637473&prj=699&rqi=22E0F9pHYmZ31ZYsssLLitOnU1
RT1ELEC-55-002 | 63133ab8-5f9d-7e05-9605-4e1851f0bcb1 | DX03-P1 | 699 | S-EMEA | Open | P3 Low CX | c.castro@core-group.me | 2026-08-24 04:00:00.000 +0400 | Low Voltage Electrical Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1-MSB-H | MSB - Main Input Switchboard |  |  | 1-MSB-H: The door of 6.3 Q1 in cubicle 6 is not properly fitted to the breaker. A gap is visible between the door and the breaker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634881&prj=699&rqi=Ub3nzNJetFskaIVmjXnPSQU4k6
GI-003 | e5c4093d-7d63-4baf-aa15-a6230cab26be | DX03-P1 | 699 | S-EMEA | Open | P3 Low CX | l.drake@core-group.me | 2026-08-13 04:00:00.000 +0400 | VER - Vertiv |  | Cleaning | Commissioning |  |  | equipment type |  |  |  |  | White rust was observed on the internal side walls of the CRAH. Refer to attached photos for reference taken from CRAH's 1-CRAH-G-F-55 1-CRAH-G-F-56 1-CRAH-G-F-57 1-CRAH-G-F-58 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633590&prj=699&rqi=ztogc94Lh4fhvDma13eaJTrog3
GI-002 | c800fc2d-a052-4b1d-8efb-1949cf79f035 | DX03-P1 | 699 | S-EMEA | Closed | P3 Low CX | n.forde@core-emirates.com | 2026-08-12 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1-MSB-H | MSB - Main Input Switchboard |  |  | MSB-H ACB serving STSSB-H-2 is missing its' ABB EKIP Module (Complete module including Comms and power modules). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633404&prj=699&rqi=UUt3PDE36GKpXJw1CVq8oXF2FF
GI-001 | 8eff1b7f-245e-452e-b12c-169a71f215be | DX03-P1 | 699 | S-EMEA | Ready for Verification | P3 Low CX | n.forde@core-emirates.com | 2026-08-12 04:00:00.000 +0400 | Low Voltage Electrical Contractor |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1-MSB-H | MSB - Main Input Switchboard |  |  | MSB-H section 6.3Q MCCB (including handle) is missing. It appears the panel has been delivered to site with this component missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633403&prj=699&rqi=xXAnoU17s4zydtjVBdmXcBMBMw
RT1ELEC-55-001 | 43ddc72f-c0a9-88aa-50d5-9f4fa34ad991 | DX03-P1 | 699 | S-EMEA | Open | P3 Low CX | g.madulid@core-group.me | 2026-08-05 04:00:00.000 +0400 | Low Voltage Electrical Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1-MSB-H | MSB - Main Input Switchboard |  |  | MSB-H Cubicle 9 and and 10 plinth damage/deformed. The damage is preventing remove of the panel cover als0. . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632271&prj=699&rqi=pYDMWEnZUzrPktAoxK38AWV2DB
GT1ELEC-147-001 | 6c5216a9-3ae3-483c-8a61-973e323c8692 | FR08-3 | 630 | N-EMEA | Closed | P1 High CX | jyusufi@global-cxm.com | 2026-08-31 04:00:00.000 +0400 | SOC - Socomec | L3 | Installation Not Correct | Commissioning |  | Electrical â€“ LV | equipment | 1_STS_N_2 | STS - Static Transfer Switch |  |  | During Energisation the bolt losed and had a direct contact with the busbar which caused an ARC Flash incident. The Unit needs to be replaced or all the Parts within mentioned Area needs to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636058&prj=630&rqi=Gu3VMlJMiyKYGDRSx1vuwmNrCW
GI-091 | 8b87fa17-5fa7-44a1-90e7-75af80b2fe08 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-08-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1_STS_N_1 | STS - Static Transfer Switch |  |  | on STS N1 the Lock on the Door handle is defective Broken. needs to be replaced. The Door is bended | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634877&prj=630&rqi=uDTclBDIBYomw27LmJNhbrrvXQ
GI-092 | 465265d3-c7a3-4d0f-8882-efa5ffb42a31 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-08-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1_STS_N_2 | STS - Static Transfer Switch |  |  | plates on Top of STS N2 has been bended / Damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634878&prj=630&rqi=MYeCMkly6D3Uox1Zwbbvnz1Kre
GI-090 | 87c9b222-ba9e-4579-abf7-ce865407f017 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-08-07 04:00:00.000 +0400 | VER - Vertiv |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1_UPS_K | UPS - Uninterrupted Power Supply |  |  | Batteries UPS K showing constant charge mode. Core 1 Right | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632694&prj=630&rqi=uEVc5uSBYBEBEsapSGXBptRe9r
GI-089 | bab9d0c2-66a0-4abe-8aae-83774a3bec5e | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-08-07 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1_STS_J_1 | STS - Static Transfer Switch |  |  | power factor incorrect on STS J | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632693&prj=630&rqi=SY4krxNPHCKggW3wXu3q2ZFXQA
GI-087 | ad9429dc-a307-4eb5-b054-e226f2d5e24a | FR08-3 | 630 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-07-30 04:00:00.000 +0400 | Design Professional |  | Design Correction Needed | Design | [7 empty] | When utilitly failure and generator supply takes over, it takes 20 seconds for generator supply to take over. This generates AFD unhandled fault, comm loss AFD, AFD bump complete alarms on the chiller and shuts it down and they have to be manually reset. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631420&prj=630&rqi=9OrFhA7lshQjwIUJZajus4ed8W
GI-084 | 995e9ed8-0bb5-43d2-9621-76fa4ab48cbe | FR08-3 | 630 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-07-27 04:00:00.000 +0400 | VER - Vertiv |  | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1_BATT_M3_01 | LIBATT - UPS Battery |  |  | UPS M3 Battery cabinet 1 needs to be replaced. During snag remediation works on battery cabinet 7 of the UPS M3, a short circuit occurred, which resulted in the need to replace the cabinet, the MCCB, the AC power supply module, internal communication cables and a cable for the fan exhaust | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630839&prj=630&rqi=tXX2H2JuhMVhWafVmowGxK2y0m
GI-086 | dc8569c1-5ab8-48bc-b6ff-2cdffdc3ca12 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-07-27 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1_CWST_10_CWP_J_2 | CWP - Chilled water pump |  |  | Leak on motor shaft going into the impeller on the primary pump in PPR10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630888&prj=630&rqi=LgNlnfepOoa8snr36iRUlCf5PP
GI-085 | c824302b-66ad-4018-b115-3395a66cb69b | FR08-3 | 630 | N-EMEA | Closed | P2 Medium CX | drobertshaw@global-cxm.com | 2026-07-27 04:00:00.000 +0400 | VER - Vertiv |  | Installation Damage | Commissioning | [7 empty] | UPS K Battery K - 10 MCCB needs to be replaced. During a site walk, Mercury and Global Cx brought to my attention that there were black soot marks visible on the MCCB breaker in battery cabinet 10 of UPS K. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630880&prj=630&rqi=6QNGEqPdOwI8MfyQJ3ITT6eJ2Q
RT1ELEC-148-001 | fad1b25d-ca46-4181-9162-2716830fe448 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-07-07 04:00:00.000 +0400 | SOC - Socomec | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1_STS_N_1 | STS - Static Transfer Switch |  |  | Damage to door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628147&prj=630&rqi=hgQzWV1d9ysPzN2LjiUS3EK6l2
GI-081 | 4302cb6e-2b31-4370-8e63-8d9109a8fceb | FR08-3 | 630 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-07-03 04:00:00.000 +0400 | VER - Vertiv |  | Component/Equipment Failure | Commissioning | [7 empty] | UPS M3 - The issue with M3 occurred during the transient tests on the generator. No hardware faults were detected on the UPS. This behaviour is likely related to the interaction between the UPS and the generator, as the transient tests on the mains supply and all other tests were completed without any abnormalities. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627799&prj=630&rqi=81XQMKOAJxaowoIrMBMfR8r2uj
GI-080 | 669ee4d8-af1b-4ae5-a9f2-9501f90895cf | FR08-3 | 630 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-07-03 04:00:00.000 +0400 | VER - Vertiv |  | Component/Equipment Failure | Commissioning | [7 empty] | UPS H core 2 does not allow to go on battery autonomy. when you isloate the other cores on the UPS to perfom battery autonomy on that one core as soon as load is applied to the core while on battery the core goes offline. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627798&prj=630&rqi=wE2H4CsZXaEB9c5GFL8w1FV3hV
GI-079 | b226f151-d644-4ed5-b620-aead1005481a | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-06-19 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design | [7 empty] | MSB Y x 1 250A breaker with neutral protection to be investigated. Breaker Q13 in panel MSB Y is a 3-pole MCCB and does not include neutral functionality. According to the engineering design by Anord Mardix and approved by RHK and Equinix, Q13 is configured accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626208&prj=630&rqi=svlp5t8PqOY2TLCyJpu0SLCjUD
GI-077 | 908389a0-4467-488e-8381-7b8176e92011 | FR08-3 | 630 | N-EMEA | Closed | P2 Medium CX | drobertshaw@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [7 empty] | Transformer for the chiller control panel has failed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624778&prj=630&rqi=A6iiwNh7VUKkBd4IVeQyR92x9y
GI-072 | d781b8f7-5e93-432d-88de-a92f8d095be1 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1_STSSB_L_1 | STSSB - Static Transfer Switchboard |  |  | Covers / Plates are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624724&prj=630&rqi=EFBNJNt2AXgESugNnibjQKdcoL
GI-076 | 47149a11-e39c-4dc0-bed3-5cfe1b9ca002 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1_STSSB_L_1 | STSSB - Static Transfer Switchboard |  |  | Covers / Plate is missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624755&prj=630&rqi=xgj7T2xBekEt8L73ymwGuV9PWr
GI-073 | 7dc526bb-6fbe-4458-bb6e-0a07fa878188 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1_STSSB_L_2 | STSSB - Static Transfer Switchboard |  |  | Covers / Plates are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624726&prj=630&rqi=ZjaQBDa7X7tA8QNfKd0BhZc2YC
GI-070 | 659c8aa4-d59d-433b-9559-14ea07d661fb | FR08-3 | 630 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | VER - Vertiv |  | Component/Equipment Failure | Commissioning | [7 empty] | UPS K core 2 Rectifier / Inverter module PH.V failed when load is applied. This needs to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624672&prj=630&rqi=0wjFBPPfYKq2CU3KjL2OcjcKgn
GI-074 | 6c12ee4f-55a7-4259-a062-fc3e66671642 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1_STSSB_L_3 | STSSB - Static Transfer Switchboard |  |  | Covers / Plates are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624727&prj=630&rqi=XfHfGGSNt2QQzamvwCOwnJLwNZ
GI-071 | c260a7b8-adce-4a2b-8784-39cd977ad2c7 | FR08-3 | 630 | N-EMEA | Closed | P1 High CX | drobertshaw@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | SOC - Socomec |  | Component/Equipment Failure | Commissioning | [7 empty] | STS in PPR 12. Went into fault due to back feed alarm causeing the output to open. STS was on S1 bypass, S1 has been seen as an unhealthy source STS has then tried to switch to S2 while S1 bypass is still engaged. Socomec to investigate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624685&prj=630&rqi=qOitge6CSXPnNlFnYnkfmKWv8E
GI-075 | 6222ecc0-2147-44f2-ac7c-17b840b8898b | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1_STSSB_L_4 | STSSB - Static Transfer Switchboard |  |  | Covers / Plates are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624728&prj=630&rqi=g20Ckp2v2Qz94F0HChKHnEm14j
GI-069 | e9c399e2-285e-4f80-91aa-73018dfa687e | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-09 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  | Mechanical â€“Air | equipment | 1_CWST_12_DC_K_1 | HDAC - Hybrid Dry Air Cooler |  | HTK 3.24/10.9-2S-P4-CU-SLNF | Water distribution over the coils on the HDAC. On PPR 12 if stood facing the HDAC the right side of the unit is performing far better than the opposing side. need confirmation from Jaeggi if balancing has been done and if not, does the water distribution affect the WET mode of the HDAC which also affects performance in WET mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624480&prj=630&rqi=fG7qEyf39BuW9luDFRORBItoDj
GI-068 | 335312ae-a1fe-4931-bad6-5b63ad73bcf0 | FR08-3 | 630 | N-EMEA | Closed | P2 Medium CX | drobertshaw@global-cxm.com | 2026-06-09 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Component/Equipment Failure | Commissioning | [7 empty] | MSB R3 Q2 breaker chasis needs to be replaced. The winding mechanism has been turned to far and put stress on the internal gears causing the failure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624449&prj=630&rqi=6ECHS6vX4QtYpLa3awzANyKZy8
GI-052 | c271bd27-7a88-47cf-88a3-42d851acc418 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [7 empty] | PPR 09 TT10 - shows incorrect value when chiller is running. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623809&prj=630&rqi=jy0302a7EODqyvbGJ7oagetFnN
GI-067 | 87805dd6-0637-4198-bd1a-a610a13caa4e | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [7 empty] | Leak on drain off valve below the bypass near the heat exchanger in PPR 09 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623828&prj=630&rqi=c6PaldTCBCX1IzVVGCTR081kql
GI-055 | 54f6f4da-16a5-474b-a0b2-d78399f695c3 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [7 empty] | PPR 08 Leak on PICV 01 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623814&prj=630&rqi=dMvBMWpmlxownlFlf1eN15pCzu
GI-051 | b9f9a732-8c84-4052-b880-711c2a669124 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | [7 empty] | Glycol sensor on HDAC 10 needs to be replaced. Vortmann advised it will be done next week | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623807&prj=630&rqi=LiRClpohw2coSNnNzl8W0vrgGH
GI-059 | 34d07f09-288e-47b5-a420-7170b487274e | FR08-3 | 630 | N-EMEA | Closed | P2 Medium CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1_CWST_15_CWP_H_1 | CWP - Condensator Water Pump |  |  | Leak on condenser pump in PPR15 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623819&prj=630&rqi=7x7aonMkiJ7QeEM99nJuaq4gYh
GI-053 | 937b65f2-4f8b-4a3d-9164-ace2e0073f8d | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [7 empty] | Leak on TT09 in PPR10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623812&prj=630&rqi=EJY17ugpz8UPD2Uarvqyd0AG6r
GI-062 | ac364606-a941-4a5f-b20f-f3a02457b8df | FR08-3 | 630 | N-EMEA | Closed | P2 Medium CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [7 empty] | Leak on PPR 08 condenser pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623823&prj=630&rqi=zFrmHpT8gzFgZmtyCzMJKUziYc
GI-054 | c6ef40d2-504e-4fe5-873c-5dcb40b6cd8a | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [7 empty] | PPR 09 Leak on Overpressure valve (near to TT05) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623813&prj=630&rqi=RzszV1qG5GFhimIuJrQNDRGKEM
GI-056 | 893efe2e-6ea1-424d-8a64-09a13c0b873d | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [7 empty] | PPR 12 leak on PICV 01 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623816&prj=630&rqi=BdEkIqig9YGWDH5ppbuxgEP4hP
GI-063 | 8d675d0b-f80d-4f76-a3cd-2368099634f8 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [7 empty] | Leak on TT05 in PPR 15 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623824&prj=630&rqi=J48JXcsoWJOHCRqns1i3C65Jsa
GI-060 | 64b00534-e4d8-468c-90f5-ef6280c74b48 | FR08-3 | 630 | N-EMEA | Closed | P2 Medium CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1_CWST_10_CWP_J_1 | CWP - Condensator Water Pump |  |  | Leak on Condenser pumps in PPR10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623820&prj=630&rqi=IVEWssURjhJwhD9GK2CkygeGiy
GI-061 | 1901ce63-9a54-4718-b883-b372e90c6159 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1_CWST_10_CWP_J_2 | CWP - Chilled water pump |  |  | Leak on primary pump in PPR 10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623822&prj=630&rqi=0eAIhud4JUvKLCXIc3HNzbK8a5
GI-066 | c2ebaa95-977c-4690-8c0c-b1942e360340 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [7 empty] | Leak on TT08 in PPR08 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623827&prj=630&rqi=qilK2yeFWChIGlYsJYdzyrijGr
GI-057 | 45abfd59-51cb-4db3-a686-69bb481751dd | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [7 empty] | PPR 09 Power socket not live in the CGM | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623817&prj=630&rqi=5YjwEOcYwWD45e9fbY0cql11j6
GI-058 | 3e8fd254-021c-4d1b-b22c-7ec9b34483db | FR08-3 | 630 | N-EMEA | Closed | P2 Medium CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1_CWST_12_CWP_K_2 | CWP - Chilled water pump |  |  | PPR 15 - Leak on the airvalve on the primary pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623818&prj=630&rqi=6IaZ9qQDOxt6FypDkfrCfAVKS3
GI-049 | e7797b8d-4815-467f-9b0e-4e5594f98d1e | FR08-3 | 630 | N-EMEA | Closed | P2 Medium CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | [7 empty] | UV lamp defect on Jaegii HDAC PPR 09 HDAC 09 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623805&prj=630&rqi=eITdUzVsliNATwJWVRDTA3mrf8
GI-050 | 137d433f-5ffe-4ba8-b510-3d98a35ea8ae | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | [7 empty] | UV lamp defect on Jaegii HDAC PPR 10 HDAC 10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623806&prj=630&rqi=GpuXm1TDoLUrQQpvaKoA0F6Eh5
GI-064 | 32db1b30-840d-4dbd-9240-4d8bedec2275 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [7 empty] | Leak on Temperature Gauge in PPR15 near to TT07 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623825&prj=630&rqi=hSJeQC0PeoLc0iZMJRjZK4u8d3
GI-065 | d5cd2fba-85c2-467d-8df0-25a57a87abd0 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-06-03 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning | [7 empty] | Leak on Temperature gauge in PPR08 near Primary pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623826&prj=630&rqi=NK2LNtzaVe2867x9UIGmeRt4FY
GI-048 | 5198ae93-d6e1-4f3f-8a1c-0039bada44a9 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-05-22 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Not Correct | Commissioning | [7 empty] | Data Hall CRAH communication cable had been squeezed too tightly to the tray. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622778&prj=630&rqi=5Xie5gLYjYxjWh4byf8pCoObhQ
GI-040 | 44ded381-a55a-4b45-93b4-b925c09a730c | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Torque required | Commissioning |  |  | equipment type |  |  |  |  | Torque marks are not valid, as the cables have not been properly torqued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622394&prj=630&rqi=IVYv94dYNdw2DOYjxR8GzgHWhh
GI-041 | 86d373af-c7c6-44f8-a978-e2a00f89a1ec | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | Cabinet door earthing cables are either missing or damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622395&prj=630&rqi=etP0GcINKu6nsJ6ENhwcZ3ZITf
GI-039 | dcf5cbd4-d261-4b5e-8824-39861e2d5a6e | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | On all battery cabinets, the covers are either damaged or missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622393&prj=630&rqi=32LSTHlo1ADayPVbfa4BNzhwnG
GI-045 | aa359cbc-d06d-4714-a3e2-d108a634f1d9 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1_UPS_Y | UPS - Uninterrupted Power Supply |  |  | DC battery cables are not double torque-marked. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622399&prj=630&rqi=e42etXXvMFDfG0B5JwRvxM4biU
GI-047 | 902a9a2d-3646-487c-a32a-22128054842a | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1_UPS_Y | UPS - Uninterrupted Power Supply |  |  | Covering plates are missing. The Plates under the MSB / UDP are opened and they needs to be closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622402&prj=630&rqi=hYvoU9jVt7WYJDOoGSbEpqb1cs
GI-044 | 0ef60422-6009-48ab-be74-e04e493adea8 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1_GCP_Y | CP - Control Panel (Generator) |  |  | End clamps are missing for the complete breaker series, resulting in breaker movement and insufficient securing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622398&prj=630&rqi=x5i6FIuvfAxZkom3hogZiF7UMF
GI-042 | 5c30dbb3-bdf8-4e65-a2dd-447314af8e7a | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Correct | Commissioning |  |  | equipment type |  |  |  |  | On Cabinets 1 and 6, the DC cables are under tension. Please refer to the attached pictures. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622396&prj=630&rqi=ImsMt8o5gl2pemJj0ieOiolW1E
GI-043 | 261314c4-7336-45e7-994a-1c6c4913d334 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1_GCP_Y | CP - Control Panel (Generator) |  |  | Bone tags are missing on several internal and external cables. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622397&prj=630&rqi=xGlUbNkl5oAGGfpZ8vW6k5G6Gp
GI-046 | 8f0ffb5b-4709-41a9-8c43-987f3fdac944 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Correct | Commissioning |  | Electrical â€“ LV | equipment | 1_UPS_Y | UPS - Uninterrupted Power Supply |  |  | Cables are under tension. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622400&prj=630&rqi=7wYaWi3dCxvtz8fcyqCoRZYFsj
GT1ELEC-184-001 | 4686f724-0b98-4034-82cb-3399e45d21c7 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | tgates@global-cxm.com | 2026-05-13 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1_STS_J_5 | STS - Static Transfer Switch |  |  | Asset reference to be changed on DCOS and evidence provided, DCOS states 1_STS_J_10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621713&prj=630&rqi=DcjsoojM9GcJvawo9MzkvGKKQu
GT1ELEC-185-001 | 9576dff4-6a0d-4eb7-8aa2-6ac43b000c89 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | tgates@global-cxm.com | 2026-05-13 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1_STS_K_5 | STS - Static Transfer Switch |  |  | Asset reference to be changed on DCOS and evidence provided, DCOS states 1_STS_K_10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621728&prj=630&rqi=4sweAhnkhWvC2fKmnetz8SuBP8
GI-024 | 6cfcf774-2e4c-4152-99c3-3af06aff6c26 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1_CWST_08_CWP_L_2 | CWP - Chilled water pump |  |  | Armstrong pump - to be checked by Armstrong engineer regarding noise issues potentially with bearings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618830&prj=630&rqi=V59WHVigMfFmNYpzMoRalKRuQo
GI-023 | ec080c54-b900-4750-9796-40d6a4981699 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1_CWST_08_CHWP_L_1 | CWP - Chilled water pump |  |  | Armstrong pump - to be checked by Armstrong engineer regarding noise issues potentially with bearings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618826&prj=630&rqi=iJWVhrcbG2QmVzLMnpVcgEGOCq
GI-014 | 0903d8c6-7123-4824-8bb4-0ac36d84e81d | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-09 04:00:00.000 +0400 | VER - Vertiv |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1_BATT_H_09 | LIBATT - UPS Battery |  |  | Battery Cabinet DC Cable installation covers damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617664&prj=630&rqi=nngBluf8BehR24rb6Yqlyy4uXG
GI-013 | c52bf4a0-1892-44e4-8dbc-a296be52ec87 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-04-09 04:00:00.000 +0400 | VER - Vertiv |  | Installation Not Correct | Commissioning |  | Electrical â€“ LV | equipment | 1_BATT_H_01 | LIBATT - UPS Battery |  |  | DC cableing for UPS batteys needs to be cleated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617606&prj=630&rqi=M9Skz0ipbXH9w7WT4GIJ9AyJSM
YT1ELEC-222-001 | 1e46ff0f-4d8d-47fc-a8ed-16e121b18a09 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | tgates@global-cxm.com | 2026-04-09 04:00:00.000 +0400 | Construction Manager | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1_GCP_K | CP - Control Panel (Generator) |  |  | Earth bond on door needs to be re terminated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617648&prj=630&rqi=RErCMlniymnuP7ZOx3ZAeHrnu8
YT1ELEC-228-001 | 57b3c2da-cbe3-4ad4-b854-708850861a11 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | tgates@global-cxm.com | 2026-04-09 04:00:00.000 +0400 | CMM - Cummins | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1_GSB_R3 | GSB - Generator Switchboard |  |  | Shutters behind the ACB are faulty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617614&prj=630&rqi=OltvrXr3E6idlr1NLrbNlsUANW
GI-009 | 91af253b-3b95-4115-bbcf-c65f720561fc | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1_GCP_R3 | CP - Control Panel (Generator) |  |  | no bone Tags on the cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617551&prj=630&rqi=Aag4Oxo8walbLQzFLo9Mfi5poK
GI-008 | 40890ff5-5ed3-4e6a-b2cb-846da50754fb | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1_GCP_R3 | CP - Control Panel (Generator) |  |  | Cables are shorts and in tension according to VDE needs to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617550&prj=630&rqi=zA6lgirp7xAy5cur58OnnBYKU5
GI-011 | 63c773ee-2ce8-4fd6-ab2e-1d87411f5859 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1_GCP_M3 | CP - Control Panel (Generator) |  |  | Cable cover is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617555&prj=630&rqi=Zsr7k29a680b9muT1ur2G8pCAJ
GI-010 | 6591c6a8-7b9b-4485-9a57-7fe517089f83 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1_GCP_M3 | CP - Control Panel (Generator) |  |  | no bone tags on the Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617554&prj=630&rqi=hKTBM1IrskLtoQazaArwzsL2I2
GI-012 | 743bb16b-3718-4f4b-9e7f-6684ee7c1e26 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1_GCP_M3 | CP - Control Panel (Generator) |  |  | GCP Door Handel is broken not functional | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617556&prj=630&rqi=isefqczpZQ1Yw0Vt55A5aocJHL
GI-007 | e39238b2-1890-41a9-b416-551b1fccfbb2 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-03-26 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1_STSSB_L_2 | STSSB - Static Transfer Switchboard |  |  | 2 MCCB breeaeker handles damaged on site. Need to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616536&prj=630&rqi=3jSpLtPgVp5eFgsCDH4Z5c0pkn
GI-006 | 79eee96d-ec69-449b-8392-875f01814294 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-03-25 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Commissioning Issue | Commissioning |  | Controls | equipment | 1_HMI_J | HMI - HMI Panel |  |  | HMI J faulty software & not for the designed Board | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616354&prj=630&rqi=WcqWAiwUjBQ1DfjoKa1mn6oPhX
GI-003 | f3edc550-5981-49f9-9c0d-650d71d803ab | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-03-23 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | ARC Flash protection been broken / Damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616193&prj=630&rqi=s0sRCjtqh389TiPRzhrNA7BFPB
GI-002 | f98bd431-6b05-46c6-b365-d308794c1bb3 | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-03-09 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1_EB_PPR_09 | ERTH - Earthing |  |  | FR8.3 STS L2B Armstong appear to have missed installing the Modbus TCP module ST300 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615124&prj=630&rqi=FlNsgdYlwxh1aQqafbypFC7Pko
GI-001 | 17ba1af0-4266-4d01-8dba-73c933dd9cbb | FR08-3 | 630 | N-EMEA | Closed | P3 Low CX | jyusufi@global-cxm.com | 2026-03-05 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Commissioning Issue | Commissioning |  | Controls | equipment | 1_HMI_L | HMI - HMI Panel |  |  | Damaged HMI Display | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614804&prj=630&rqi=KCeak56wIJLJmdu92ALYcyeU9j
GI-214 | 502b8ec2-b68b-426e-9ad3-f16a2ea32087 | FR10x-1 | 378 | N-EMEA | Closed | P2 Medium CX | cjjones@global-cxm.com | 2026-02-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | SUDB_3_Q07 - 1_MVTB_R2 (Q01) Incorrect circuit ref on torque report Torque report not signed Sign off dates incorrect | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=139154&prj=378&rqi=EzcCJ9v1j0EBB5CzDToBsKjwtu
GI-005 | 60e5cd16-39d8-45dc-85d7-3f6efcbc3246 | FR12-1 | 692 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1MVTB_M4 | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633612&prj=692&rqi=WGobXZYMVRv5tuzcqXRNP83YrJ
GI-004 | 6be8866b-aa65-4a5e-b342-1ce384b644c1 | FR12-1 | 692 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1MVTB_M1 | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633611&prj=692&rqi=ZBeA0CZfT90ltndBcl8T8Iq8JR
GI-003 | ff44cd85-3690-447e-ae59-1d4e2715dd32 | FR12-1 | 692 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1MVTB_L | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633610&prj=692&rqi=UB91UP0n9F3cim09yB73HX6Maz
GI-002 | 1fe8c901-8ad6-453c-a0ea-075986190bbb | FR12-1 | 692 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1MVTB_D | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633607&prj=692&rqi=nhTShReEQBynrlOMD6ZotMzrtj
GI-007 | c00ba5f9-d482-47cb-87f2-d57b5bacc380 | FR12-1 | 692 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1MVTB_R1 | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633615&prj=692&rqi=4fhhY2hTW1VjP4PwSCl2exYTcl
GI-001 | 95885c55-9fb6-48c6-8e88-4d0424d85fa2 | FR12-1 | 692 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1MVTB_C | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633605&prj=692&rqi=VFQsMCd8i5Nzhtx4gV9MBErQ3O
GI-006 | 05ce5aba-b008-4763-8b64-a7a1a47c87b2 | FR12-1 | 692 | N-EMEA | Open | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-08-13 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1MVTB_N | MVTB - Medium Voltage Transfer Board |  |  | Please find issues raised by the GC during FWT below: 1. Interlocking between MVTBs needs clarity the are saying its done electronically but I think we can switch to earth by mistake 2. Chamber references 101, 012, 103 and 104 we need these to identify the correct chamber 3. Cable sizes and conformation that the cleats are sufficient in the back of the MVTB 4. Interlock was wrong as schneider had the wrong drawings needs to be sent through to them 5. Spare barrel / interlock with SS3 6. Earth bars looked to be missing marks in the MVTB we witnessed 7. Gen interlocking as currently you can close all chambers 8. Panel bolts missing torque marks chamber 102 same bolt torqued in other chambers 9. Switch torque marks 10. Schneider drawing update required as its in correct 11. Storage conditions for MVTBs 12. Require the link for there uploaded documentation as we could start reviewing now | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633613&prj=692&rqi=U65iL0nhhvL6PBJH8Gxa9r5DJv
GI-010 | 61d9fa76-e7ea-404e-b7e2-8f0a28515c24 | FR13-2 | 563 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Graphics Issue | DCOS | [7 empty] | RMU B not visible on DCOS during mains failure test. Port issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352273&prj=563&rqi=Pw9WV4QelLG4tOdiWkBX0LO4TO
GI-011 | f2711157-f7ba-4c34-9dbf-dc8881325627 | FR13-2 | 563 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Graphics Issue | DCOS | [7 empty] | 2 breakers on UDP B showing tripped when on | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352276&prj=563&rqi=lXPLfq9tMYPrYClclbIIBrHjqh
GI-013 | 02ddedef-1b5a-48b3-b8ef-98f3bd839afa | FR13-2 | 563 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | General Design issue | Design | [7 empty] | When lose of power to fuel pumps you have to restart manually. To be discussed with EQX design and RHK (recommend UPS backed supply) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352278&prj=563&rqi=DZuxzKUhdFBdAocyWyKkhBUiiv
GI-015 | 252797fd-ff16-45e5-83be-8b105156a4a7 | FR13-2 | 563 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | General Design issue | Design | [7 empty] | RMU Tx breaker tripping on in rush B, D, A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352280&prj=563&rqi=nafgOE3RTpQYSWWBoZkk5HbW4F
GI-012 | 0e47440a-1bd7-49dc-8f50-c9c29e9eac03 | FR13-2 | 563 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning | [7 empty] | Fuel system using low level bulk tank instead of high level bulk tank - Sigma to come and investigate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352277&prj=563&rqi=AfT5X0Jp3xGjaUjcgKDu8SR1hV
GI-014 | 31837e02-396f-4fce-8f36-2b8ee698fecb | FR13-2 | 563 | N-EMEA | Closed | P3 Low CX | drobertshaw@global-cxm.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Graphics Issue | DCOS | [7 empty] | Generator breaker on MSB C not showing as closed on DCOS graphic | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352279&prj=563&rqi=chQlmGMTE4CIQJjgi2xJGbjMMF
GI-009 | d2261f61-f7d3-4bcc-a694-cc826159dfa7 | FR13-2 | 563 | N-EMEA | Closed | P2 Medium DCOS | Alen.Francis@eu.equinix.com | 2026-02-13 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCIM Sync Service Issue | DCIM | [7 empty] | We are unable to verify all expected objects upserted to DCIM. System Integrator/ GC needs to update the DCOS/DCIM delivery time on when this will be completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199201&prj=563&rqi=Lkfi1NcSs8ejc6nLnoBHtDt4cJ
GI-028 | 4fc5248e-c620-4557-84e5-8f4fc9892045 | FR6 - Liquid Cooling | 685 | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-08-10 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | TCS/SFN-01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | Opened from a previous IRL. On the SFN some bolts are Carbon Steel and not Stainless Steel. Bolts are to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632976&prj=685&rqi=JSvGitgNBuhWe2xMxcn4wRZrOi
GI-027 | 51456f9e-38c9-4e1c-847e-8ff060c07b91 | FR6 - Liquid Cooling | 685 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-05-26 04:00:00.000 +0400 | Owner |  | General Design Issue | Design |  |  | equipment type |  |  |  |  | Temp sensors on the racks does not show accurate readings, as the sensors are surface mounted and facing the CRAH supply air flow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623135&prj=685&rqi=1QCsEqAuu9qs2Opkkmu5TVQ96u
GI-025 | 32943ebc-99c1-4425-8bab-fea08c3772ce | FR6 - Liquid Cooling | 685 | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-05-18 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | Missing Valve Tag Number on the SFN | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622163&prj=685&rqi=ThS1y1TBIqmh8KrpHPv3JTNJIQ
GI-026 | fbebdcd8-b910-4ece-b144-78ef56487f8d | FR6 - Liquid Cooling | 685 | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-05-18 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | Missing Torque marks on the SFN. Torquing has been done but missing the marks | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622173&prj=685&rqi=TU4x9zyBpmT6lD3aunf1do26Y4
GI-024 | 2a3dffd1-0653-49f4-8e17-302ac814603d | FR6 - Liquid Cooling | 685 | N-EMEA | Closed | P2 Medium CX | sdreik@global-cxm.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/ Equipment Failure | Commissioning | [7 empty] | Control Valve on the CDUs suppose to hold last recorded position after power failure. However, when the controller is starting the control valve is driving back to the lowest % set | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620495&prj=685&rqi=VAcUsZ9rTWbW3SreIO3628ke2k
GI-023 | f55ff5a7-0f29-46af-90a2-73fb7d7f2e5c | FR6 - Liquid Cooling | 685 | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-05-05 04:00:00.000 +0400 | Owner |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | Leak detection schematics are to be updated to include the new SFN area. the alarm is working and has been checked. only schematics to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620487&prj=685&rqi=D69ebeYhthxKWicTP125PijNa1
GI-022 | 18b265bc-4cb8-4f7b-86a1-c31f37270557 | FR6 - Liquid Cooling | 685 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [7 empty] | CDU Internal tanks to have a label specifying the PG25 manufacturer sticker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619684&prj=685&rqi=KSbR1RSpbnvm0BBdghbRJdEpEw
GI-021 | 63067dc7-ae4f-4ad3-951e-0902c26b725c | FR6 - Liquid Cooling | 685 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | text to be unified when losing a power source on the graphics | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619537&prj=685&rqi=77QhOFP3Wyad6D3TD80OgVTftW
GI-017 | ab1bd4a9-94bc-4daf-9dba-ea686d66dec0 | FR6 - Liquid Cooling | 685 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Template Issue | DCOS |  |  | equipment type |  |  |  |  | Text to be fixed not to cover the Graph | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619532&prj=685&rqi=1sZ0MbvhSoKABDohjJf7w6h8Rc
GI-015 | 37005224-06ca-4f4b-b6a3-3485753bd978 | FR6 - Liquid Cooling | 685 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | The below alarms are not visible on DCOS graphics: - Secondary DP Setpoint - Critical Alarm - Non-Critical Alarm - High Secondary Supply temp Alarm - Low Secondary supply temp Alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619527&prj=685&rqi=2T3uDeuxiha3a5np8v3tPXkcaf
GI-016 | 23f54db2-2cf8-4cbe-8e70-60b76fece354 | FR6 - Liquid Cooling | 685 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Template Issue | DCOS |  |  | equipment type |  |  |  |  | Text to be fixed on the Graphics | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619529&prj=685&rqi=N62X8HvyxsNKHH5ms1RbCGQ48h
GI-018 | f805ead6-2672-42da-9381-e32ed5e2d5ae | FR6 - Liquid Cooling | 685 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | Units to be unified between CDU HMI and DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619533&prj=685&rqi=6VIFfWSCkjcVBoCy8quogiaFjp
GI-020 | 2f82858d-5939-4528-9c66-6c520dc21738 | FR6 - Liquid Cooling | 685 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | on the CDU HMI, Filters 2 and 3 shows reading together not as separate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619536&prj=685&rqi=wdT99YD3pynyjww8TYQ0hduP3h
GI-019 | af64f291-2575-4e09-b7b9-a94bb3d630e4 | FR6 - Liquid Cooling | 685 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-26 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | Leak Detection alarm not available on the CDU graphics | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619534&prj=685&rqi=7FXnPnKMJU8G4h9tNUKDSLD8Kx
GI-010 | a47b9732-b3bc-4bb5-89e1-ca740de0bb70 | FR6 - Liquid Cooling | 685 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | ATS status showing on the graphics as a text. this should be amended to change or identify when a source is lost with an alarm and which source is still available | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618857&prj=685&rqi=hYjFg6TCnhVRrQc4oEU5L8S8lx
GI-011 | d20a3a9b-bb99-441d-a469-f7cbcd9d37d2 | FR6 - Liquid Cooling | 685 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Comms Issue/ Fault | DCOS |  |  | equipment type |  |  |  |  | When a comm alarm is generated on the CDU. alarm is showing in the alarm section and incication around the HL point. However, nothing shows on the CDU DH graphics, meaning ops will not be able to see that we lost comm until they go into the CDU graph | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618860&prj=685&rqi=FAZioQ6sxHo8l5wYmuO4wt9jQm
GI-013 | 22767412-1d0a-4bc8-a492-0d02f47f5ef6 | FR6 - Liquid Cooling | 685 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Bolts installed on the SFN are short and cannot be fully torqued as the bolts does not even reaching to be flushed with the nut while it should be 3 threads exceeding the nut | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618911&prj=685&rqi=j5G7vZPaKL9rUMrcLfqjMNWXRI
GI-014 | fda8217b-eab5-4fdd-a7ba-cc333f599798 | FR6 - Liquid Cooling | 685 | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | General Contractor |  | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | 2 valves handles are damaged and cannot operate the valves. at the moment the valves are kept open, but cannot be closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618986&prj=685&rqi=2VH3PT72eVzTl7Gfpn7WRhRPgM
GI-012 | 19ba0c5a-14b0-4b81-bb6f-81f011b20f0a | FR6 - Liquid Cooling | 685 | N-EMEA | Closed | P2 Medium CX | sdreik@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | Owner |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Missing Flushing Valves on the SFN pipe work installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618906&prj=685&rqi=qapupAy5Afwnc7pIO2uzClZnin
GI-005 | c7fda3be-9a39-4836-9a42-0158e6274816 | FR6 - Liquid Cooling | 685 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-20 04:00:00.000 +0400 | Owner |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Pressure test was achieved on the SFN without installation of the By-pass valve. as discussed with designer, the system will be functioning without it. Once installed a pressure test is to be conducted on that section and closed with a protocol | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618752&prj=685&rqi=QjN2WpLTm7JDqtSVL69lY08xKe
GI-007 | 46a49637-2b7f-402b-b262-b815612bbff9 | FR6 - Liquid Cooling | 685 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-04-20 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS Template Issue | DCOS |  |  | equipment type |  |  |  |  | The DCOS template shows 10 racks while the latest DWG shows 12. this is to be amended | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618759&prj=685&rqi=PaILCzcTzNz82OJ6grpTBClzQU
GI-009 | a916f991-8ef3-4134-a1c5-83671e6ae201 | FR6 - Liquid Cooling | 685 | N-EMEA | Open | P3 Low CX | sdreik@global-cxm.com | 2026-04-20 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | TCS/SFN-01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | SFN missing Pipe identification labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618764&prj=685&rqi=vZO4FSCYt8ZQJE2aS7FtUdXJ9C
GI-002 | 65b25783-be94-4259-a102-10c78351b62c | HE7: Liquid Cooling | 659 | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-26 04:00:00.000 +0400 | Equinix Ops |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | Leak Detection | LEAK - Leak Detection |  |  | Leak Detection System installation not complete or L2A/L2B/L3/L4 commissioned. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352230&prj=659&rqi=0hrHQxbskHuudhwZ3aF6U5mRWG
GI-001 | 8b20e2ec-24d8-4ebb-ae4e-69106b0db1af | HE7: Liquid Cooling | 659 | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-25 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | TCS/SFN hoses supplied by Refcon are designed for steam with pinpricked outer membrane. EQX COE requires the hoses to be changed for hoses specifically designed for PG25. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352227&prj=659&rqi=4d3MxRYHuAgep7HgRklqcdz1cT
GT1MECH-4-001 | a9eb9e2b-fc48-45d5-be60-0186d9413086 | HE7: Liquid Cooling | 659 | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-19 04:00:00.000 +0400 | Equinix Ops | L3 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Temperature Sensor High Alarm does not remain red when coming down from a High High alarm, but it if you simulate a High alarm from normal temperature it changes red. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199567&prj=659&rqi=XW2LogZrj6xoTA237vPmQBQtHf
RT1MECH-4-005 | 9f65c9e1-6210-72d7-3aae-c44cd98c077d | HE7: Liquid Cooling | 659 | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-19 04:00:00.000 +0400 | Mechanical Contractor | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Return joint under CDU02 not installed as per manufacturers recommendations as there is not proper "pad to pad" contact on both sides of the joint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199530&prj=659&rqi=xMBoLM9GaUU4NBWda8ATxoo2Ge
YT1MECH-5-002 | ad8f1f7c-20e6-c7c3-5573-5babab0c95ba | HE7: Liquid Cooling | 659 | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-19 04:00:00.000 +0400 | Equinix Ops | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | No earth bonding on TCS/SFN. EQX to confirm Finnish design requirements on TCS/SFN pipework bonding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199545&prj=659&rqi=xrMV9Zifd8Gq3BksTV2frq6OUP
GT1MECH-4-002 | cf502519-33c8-43d1-86f7-6544a1536093 | HE7: Liquid Cooling | 659 | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-19 04:00:00.000 +0400 | Equinix Ops | L3 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Temperature Sensor Low Alarm does not remain red when coming up from a Low Low alarm, but it if you simulate a Low alarm from normal temperature it changes red. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199568&prj=659&rqi=4tbTskjhGqGYDuPpukJneaKqYq
YT1MECH-5-001 | 40da5f74-55b4-5efb-3015-f2ff72cb33ea | HE7: Liquid Cooling | 659 | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | Mechanical Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Rack 101 bypass hose and valve are weeping | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199363&prj=659&rqi=zycgOo34AaoqkuBHkcUSFFhBcQ
RT1MECH-4-003 | 467f4549-3770-2ee0-7010-1ba2defcafcc | HE7: Liquid Cooling | 659 | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | Equinix Ops | L2A | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | All TCS/SFN temperature sensors are labelled with temporary stickers. Permanent labels to be installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199353&prj=659&rqi=syyFIV0qUdkaHpHTadxbPGsJj6
RT1MECH-4-004 | 08859962-39f7-e728-8a6c-91ef071bb20a | HE7: Liquid Cooling | 659 | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | Equinix Ops | L2A | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | All TCS/SFN valves are not labelled with ID tag/label. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199354&prj=659&rqi=jDPt6au4VgwK8nOg6uUjvR3ewT
RT1MECH-4-002 | fc1113ea-d7d1-93dd-55ab-934b229fc91c | HE7: Liquid Cooling | 659 | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | Mechanical Contractor | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Rack 101-105 connections supports are compromised by existing electrical containment. Rack 105 support in particular needs attention/additional supports. Pipework and Valve not level. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199352&prj=659&rqi=z23Zn4o85BNu9ucifiB1yuSSG5
RT1MECH-4-001 | 092389e0-961b-882f-4ace-88b6b16cf0e2 | HE7: Liquid Cooling | 659 | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | Mechanical Contractor | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Some TCS/SFN joints are not installed as per manufacturers recommendations as there is not proper "pad to pad" contact on both sides of some joints. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199351&prj=659&rqi=9sqDf6w4G2n5ImaLlnPB7oj03F
RT1MECH-4-006 | bfb450ec-0540-4dda-b35e-8df2c881fe56 | HE7: Liquid Cooling | 659 | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-05 04:00:00.000 +0400 | Mechanical Contractor | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Thread tape used on the brass drain valves and gauges installed on the TCS/SFN. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221141&prj=659&rqi=sNj3tQrWgQ7aWW9Yu6xGiRLMf7
RT1MECH-4-007 | d9dedcb1-43c0-4dce-94b5-0b1fdd0be379 | HE7: Liquid Cooling | 659 | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-02-05 04:00:00.000 +0400 | Mechanical Contractor | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | HE7-Zone 3D - TCS/SFN 01 | TCS - Technology Cooling System |  |  | Brass drain valves and reg valves installed on the stainless TCS/SFN. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221142&prj=659&rqi=TPPXYRBOLgLn4sVz4aUbjseT3f
GI-295 | c8fc951c-6da9-47a2-8f27-deb914cdd5fd | HK06-1 | 501 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | 12/F LVSB Rm - emergency lighting installation to comply with FSD requirement and within 2m of any FSI installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617730&prj=501&rqi=93wc116rkGsRrmUHfLRKNGZTxT
GI-294 | d327eb0d-c24c-47b2-baae-904e6407311c | HK06-1 | 501 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | R/F -Failure of the Battery discharge test for 4 nos. of emergency lighting | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617729&prj=501&rqi=UkhHVAmQwfFJfIGcA7BLv1BZRh
GI-296 | 2c870b8e-a180-4b70-aec9-1a63bd5d76cc | HK06-1 | 501 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | 13/F LVSB Rm - emergency lighting installation to comply with FSD requirement and within 2m of any FSI installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617731&prj=501&rqi=a3LhViOIUZlBjwmnsjeAajorTV
GI-297 | a0ab4c09-4dc2-4abb-9c81-dec21a268851 | HK06-1 | 501 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | 15/F LVSB Rm -emergency lighting installation to comply with FSD requirement and within 2m of any FSI installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617733&prj=501&rqi=cPPZFyaKIg38HRgRD8XexLQI2d
GI-293 | a6b74506-a474-4c25-8cf0-08f2cabe3497 | HK06-1 | 501 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-04-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Task Uniformity (Min./ Avg. = 0.014) of R/F the Luminaire Schedule by NV5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617128&prj=501&rqi=ldwf8ZqJ0oaYOgzqatN0rREJVL
GI-288 | 806f990d-8212-41d2-add0-01a1449f0577 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | CAM 00054 have not been tested as it has not been installed due to requiring conduit installation through CLP-controlled room. CLP did not give permission fpr access. Currently under NV5, GEM and EQX discussion. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616819&prj=501&rqi=T3WFQunB9ofCyucxNBLR0bkw6N
GI-289 | 7efde0cd-224e-4ec7-84ed-13cd9b84c11e | HK06-1 | 501 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | CAM 00024 has not been tested because it has not been installed. The installation requires conduit to be run through a CLP-controlled room, and CLP has denied access permission. The matter is currently being discussed by NV5, GEM, and EQX. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616820&prj=501&rqi=CbtpiF6bfQY3keEDhoag9HYIvr
GI-292 | 4cb1420b-8bd7-4cd0-bfe9-fd97ffde56ba | HK06-1 | 501 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | R/F - Emergency lighting discharge lower than 2 lux. (measure from floor) at the beginning of battery discharge. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616860&prj=501&rqi=YN368KFdneDU0Mby8O9LCu0g0R
GI-291 | 7258bffc-bb1c-4da4-b48f-ec57db1ace03 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Door 20 (D20) have not been installed due to damaged door frame. EM Lock, Keypad Reader, and Break Glass Unit have been tested without door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616822&prj=501&rqi=M1WAzylPTB9mj6xUXk6MfkxBbP
GI-290 | bf80d7ca-1f39-4ea6-9c34-779aa6c18aa4 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Door 28 (D28) will be replaced from double-acting doors to in-swing door with EM Lock upon completion of BD inspection on Apr 7. EM Lock, Keypad Reader, and Break Glass Unit have been tested without door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616821&prj=501&rqi=04BZWSGqCrhONzMdk7Xt5Jy39I
GI-287 | 21e5baf7-cbf7-4251-b784-80a9a51bf4a6 | HK06-1 | 501 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Electrical | system | Electrical System |  |  |  | Task Uniformity (Min./ Avg. = 0.30) of 17/F Lounge cannot meet the Luminaire Schedule by NV5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616648&prj=501&rqi=Pua9wEH3ZNlRYmAaeI21n7nzyS | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-284 | 5c9e9d68-a1c7-4f42-98b1-7c5a0ec79229 | HK06-1 | 501 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Electrical | system | Electrical System |  |  |  | emergency lighting installation to comply with FSD requirement and within 2m of any FSI installation" & "Emergency Lighting cannot fulfil the FS COP Requirements | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616639&prj=501&rqi=Lfb2oU7Ov6jquqAGQJgzBJK4ob | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-286 | ff7013eb-93b2-43aa-bfde-ee6901387521 | HK06-1 | 501 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Electrical | system | Electrical System |  |  |  | Avg. Lux Measurement of 17/F Customer Kiosks cannot meet the Luminaire Schedule by NV5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616647&prj=501&rqi=et3pVqfICiZUo2yPLksEWa6kY6 | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-285 | 63b30c74-37da-4545-ad92-c50d6c739f0f | HK06-1 | 501 | APAC | Closed | P3 Low CX | ShirleyLeong@commtechasia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Electrical | system | Electrical System |  |  |  | Avg. Lux Measurement cannot meet @of 17/F Customer Kiosks, Main conference room, at lounge | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616645&prj=501&rqi=EykV1pxVPcNTAMqoYlc9DOnocR | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GT1DCOS-13-001 | dfd1f523-f25a-4890-8f41-bb868adff3da | HK06-1 | 501 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-20 04:00:00.000 +0400 | General Contractor | L3 | Component/Equipment failure | Commissioning |  | Controls | equipment | 1DCOS_LCP_17 | DCOS - Control Panels |  |  | 1041 FER Room TT sensor showing inaccurate from calibrated device. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616065&prj=501&rqi=u1nfC5aDBmWZ2HwOmlo3vwW13m
GT1DCOS-13-002 | 2c1c822d-29f7-456a-84a3-2260eb195704 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-20 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning |  | Controls | equipment | 1DCOS_LCP_17 | DCOS - Control Panels |  |  | Unable to check points for flow (items 5 to 12 on point list / test record) as flow meter installation is pending for Water Department approval. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616067&prj=501&rqi=jcCtTG0eGfhpME0MsWlkYEQz4B
FPT-478-008 | 3d8892a0-df94-41c5-b2dc-cc048aaf07b5 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Fire Detection | system | Fire System |  |  |  | Pre-action panel manual operation function cannot be tested since the base building sprinkler pumps are malfunctioned. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615902&prj=501&rqi=iors9BPHUaR5CKau1NgNQKReZk | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-003 | e2b61765-54a0-4436-a057-2c50853eda7b | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Fire Detection | system | Fire System |  |  |  | Time synchronization issue for FS main panel and repeater panel (Has 1hr and 5mins discrepancy) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615892&prj=501&rqi=jxZvb9AMgI7OJdm4i3OYlGozHA | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-007 | 0757339e-4879-4e14-bc3d-7cdb07e20e88 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Labelling | Commissioning |  | Fire Detection | system | Fire System |  |  |  | Permanent label for damper bypass control panel to be provided (typical) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615901&prj=501&rqi=Y4NOWr6rrDhlxRBW3hlxwRpXSl | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-006 | dc02a5ac-3b93-4546-b560-1312dd7260b6 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Fire Detection | system | Fire System |  |  |  | (Typical for 12/F, 13/F, 15/F and 17/F) Genset did not receive "Remote E-stop" after fire signal triggered and therefore genset did not stop and MSFD also did not closed. Fuel supply system PLC did not receive "Fire Signal" to close the valve logically. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615900&prj=501&rqi=IwoRfJDsNV1vuaD5qYVPoLT45r | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-010 | 1e27ac44-f8df-4629-978d-1a9aec457b76 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Fire Detection | system | Fire System |  |  |  | 24V power supply to gas suppression system module is not available. Corresponding test for 17F gas suppression system cannot be conducted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615904&prj=501&rqi=ij3JTcxHAMhZtJaO7m9pTpfvKy | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-004 | 858a2238-f29d-4bd1-9c17-ab8415a8b5a4 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Fire Detection | system | Fire System |  |  |  | Gas suppression system at 13F module does not receive MFSD feedback status; MFSD is actually closed onsite. After jumping the MFSD feedback signal, the corresponding module was triggered and then NOVEC logical function worked properly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615895&prj=501&rqi=cVs20nJdrx2wT1GTPcSyxUM51I | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-001 | ad72da57-825e-4511-9099-ef1ab536d037 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Fire Detection | system | Fire System |  |  |  | (ACS)(Typical for 12/F, 13/F & 15/F) Mantrap near passenger lift lobby interlock function malfunctioning ; door release function (by fire signal) works properly in FIST | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615889&prj=501&rqi=DlK6ABqJoPOr4wIgAlkbYLFWqX | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
GI-283 | c903e68e-8951-44cf-8045-088494a62620 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [7 empty] | Unitary mode for chiller keeps coming on during IST2 on 17 March 26 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615907&prj=501&rqi=KkilMeydrPNZqyCWkyIu3WVvi0
FPT-478-009 | 18e68929-b421-419e-89db-6a93c182b007 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Installation not complete | Commissioning |  | Fire Detection | system | Fire System |  |  |  | "Evacuate" flashing light box inside genset room 12/F & 13/F were not properly fixed. The light boxes were embedded into the promat board wall, and the wall opening was not properly sealed or backfilled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615903&prj=501&rqi=ZFUhZi61omaxr3gGHg7CTlfh4j | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-002 | 86d03174-f305-4696-bbb1-8bf54d734f61 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Fire Detection | system | Fire System |  |  |  | Gas suppression system signage at 15F to be checked. The flash light effect is different from other signage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615890&prj=501&rqi=GG4s11OerTPCdoYIPJHGylynnj | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-478-005 | 4d9f4c62-de96-46a7-86f9-8b43bf032db7 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Fire Detection | system | Fire System |  |  |  | Missing label for 13F gas suppression system module | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615897&prj=501&rqi=QnOauBEQn4EQJGqy1AhhX8qO9f | https://equinix.facilitygrid.co.uk/x/project/501/system/13021
FPT-479-012 | a7f643ac-0346-4a49-9d3e-effed21e9193 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | 07:29AM 13040 TER Room, 1TT_01 sensor showing 0C, with a low temperature alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615744&prj=501&rqi=UR8CBUiDtgDd6fDYX5bXeZbv1Q | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-013 | 67125b3c-5ee9-4876-bd64-d2e77269d6dc | HK06-1 | 501 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | 09:10AM UPS_A2 Alarm triggered momentarily. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615748&prj=501&rqi=S7zLkrencDb81ACGNRO5oOrLXz | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-014 | e83e0a53-9923-4c06-9ae2-a69d426dd7b9 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | 10:45AM After failing CHWP-01 at string 1, the DCOS programme still counting for reset after 5 mins | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615751&prj=501&rqi=GK2zVt6k6hk2JY1QdGHgPezy1L | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-007 | 5681c571-0693-4d05-80e6-e777826a8da9 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | 03:52AM When PCP_01 was failed, PCP_02 became the primary unit, but "Power Supply Common Alarm" alarm was triggered for PCP_02 instead of PCP_01. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615643&prj=501&rqi=ay4KlfLnWaxpuZsFLJMWi6Zdhg | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-485-003 | 9c557d7b-24fa-4124-ad2f-5957398c6e81 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider MV | L4 | DCOS Graphics Issue | DCOS |  | Electrical | system | Electrical System |  |  |  | During the IST 2, at 14:35 - During the UPS_M1 is on maintenace bypass mode, the UPS PQM on DCOS is showing -0kW in effect a warning has shown. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615679&prj=501&rqi=ntJUjd1QLrVADCb5LBvNqorj9S | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-479-004 | 0dfd3faf-1d3e-473b-b77b-7f76687d120b | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | CHWSTR1 DPT-04 loss communication alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615640&prj=501&rqi=28UkI5MqMUDLo2GBIlGOQcGol3 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-010 | b9d0eaa6-32f0-442c-95f1-527232a50afd | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | 04:27AM After failing CWP-02 at string 2, WCC & CHWP staged down. String 2 still received command on in D2SD, the cooling tower remained on. 13/F Data Hall 2 CRAH_AR1_14's supply air temperature reached 27C. Data Hall SLA temperature was maintained within SLA range. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615646&prj=501&rqi=KYP6629qs6hjVaZmE2NXMK1hHX | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-006 | ebf9048b-ee92-4148-8d58-2ba0ad16a86e | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | 03:52AM When PCP_01 was failed, PCP_02 became the primary unit, but "PLC Stopped" alarm was triggered for PCP_02 instead of PCP_01. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615642&prj=501&rqi=nBk2G6E99m0qNVF7WD5OniX6PN | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
GI-279 | 43a33a4b-8f2f-4fa6-bbde-6f9799c54a52 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | ychoong@ap.equinix.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [7 empty] | Fuel Control Panel has no alarm when the panel is down with no power | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615660&prj=501&rqi=9bpLYFPe9ZYgQ9LZw7aDuTJlKn
FPT-482-032 | 396f79a5-986b-4d5f-88f3-bd40168dd424 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | Vendor- Manufacturer | L4 | Commissioning Issue | Commissioning |  | Electrical | system | Electrical System |  |  |  | During IST 2 EIST-01, the PLC panel for the fuel system riser is found to have burnt fuse. This affect the riser from changeover when a fault is detected for the riser | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615681&prj=501&rqi=2Fsm3JeLSu37xVnWJSStxvWDaW | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-479-008 | c9c48890-0182-48a0-aa9b-cfb18def5fed | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | 04:07AM When PCP 02 was failed, "Hot Standby Status" and "PCP Status" did not show on DCOS graphics, all greyed out. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615644&prj=501&rqi=jqzyFvkDgbdSExcW2KVynfC6pg | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-009 | e4899751-d4fe-4ed5-bb83-1efeb6ed7827 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | 04:07AM When PCP_02 was failed, "Power Supply Common Alarm" alarm did not trigger for PCP_02. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615645&prj=501&rqi=XzIoaXxiHbsEcq5F9kxNeE3urG | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-485-004 | 3f4bfe15-02dd-44f7-bc96-87dcb8bcfe8c | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | Vendor- Manufacturer | L4 | Commissioning Issue | Commissioning |  | Electrical | system | Electrical System |  |  |  | During IST 2 EIST-01, when the generator is started because total power failure is applied from the SUDB side, the fuel system on riser B is found to have fuel leakage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615680&prj=501&rqi=QMtjS4Foju3veQBZhYkh7mopHQ | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-483-021 | 1c81a71e-20bb-4313-a97d-5623c44f88c4 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS |  | HVAC | system | Mechanical System |  |  |  | HLT-1(HLT2) 3/14/2026 11:00:00 PM 1UPS_A1,A2,B1,B2 had high output current, kVA and kW alarm on DCOS. Alarm configuration to be clarified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615674&prj=501&rqi=PKIB065YqTLo4CwicZKJUM2I5k | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-482-004 | 17a46291-f2a4-43bc-8dad-9cf112414ad5 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | ychoong@ap.equinix.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS Graphics Issue | DCOS |  | Electrical | system | Electrical System |  |  |  | DCOS graphic for MV network. -11kV voltage is shown on SUDB even when the main switch is opened. - Amps is shown even when no load is applied - Energized line and non energized line are wrong | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615658&prj=501&rqi=U25Dn2NSkPzCLUJuehCKhMqZPj | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-483-023 | 060d6b01-0a3f-4a00-a9ae-9b29c4f78e65 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS |  | HVAC | system | Mechanical System |  |  |  | 3/14/2026 HLT-1(HLT2) 11:00PM 15F Battery Room had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615676&prj=501&rqi=G1IFNCaPtj2iGIQtR4e8YGiYxy | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-005 | d525247d-a3d5-4323-af4a-cc26314f8099 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | 03:49AM PCP-02 Module Present Status alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615641&prj=501&rqi=Wtt9C2wDHo2CFbAW70nHcw0DnC | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-022 | cd22de1c-327b-44fc-85b5-cde4dcd5d048 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS Graphics Issue | DCOS |  | HVAC | system | Mechanical System |  |  |  | HLT-1(HLT2) 3/14/2026 11:00PM 13F Tx Room had high temperature alarm triggered. Alarm configuration to be clarified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615675&prj=501&rqi=o2Mx3AIboKsSJ2eMoBaCbdpPs3 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-024 | 19f6939b-3c09-4f54-86a4-50ba0a8b0a7e | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS |  | HVAC | system | Mechanical System |  |  |  | 3/14/2026 HLT-1(HLT2) 11:00PM 17F Lv Switch Room had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615677&prj=501&rqi=bUfCxSDRLL4F1PqGrTsXrv5voE | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-479-011 | bfa66338-a655-4c86-be66-e88fd6c6574f | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | PerryLee@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | 04:27AM After failing CT-02 at string 2, the WCC, CHWP, CWP all remained running. String 2 was still receiving command on in D2SD. WCC_2 shown off on DCOS but WCC_2 was running normally on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615649&prj=501&rqi=VPelbNotYO9bFZ75BH9xkjfBCL | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-018 | 11cbc6d4-22fd-4211-88f6-973a5379d04e | HK06-1 | 501 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | 04:16AM For 13/F Data Hall 1, after Chilled Water Riser C was failed, "High Return Air Temperature" alarm was triggered for CRAH_AR1_01, 02, 03, 06, 7, and 17. Data Hall temperature was maintained within SLA. Pentagon to clarify the alarm dead band for "High Return Air Temperature" alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615629&prj=501&rqi=JaTcdT4MWJtSikpmxt9cZGNZ0I | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-016 | c9893f23-8980-4190-9dfe-c28f69efbd4f | HK06-1 | 501 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT2 L12 & L13 02:18AM After ATS changeover of 13/F CRAH units, it was observed that CRAH_AR1_01, 03, 08 chilled water valve command went to 0% and fan command went to 50%. 02:19AM 13/F Data Hall SLA temperature sensors exceeded 27C. Pentagon to clarify why power source changeover will cause fan speed command and valve opening command to drop. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615627&prj=501&rqi=lxzSYikezvenCGulPUGdSnJ0bW | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-017 | 3ba2e0ff-6721-4f9f-a61e-9e27b6bb9b71 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | 03:56AM After closing the return and supply valves of Chilled Water Riser B, DCOS was still showing ~4.5L/s of water for Riser B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615628&prj=501&rqi=2iuCUkgS6xM22DNUeFZPOHQmKE | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-019 | 8a39e98b-684c-4326-9637-b5d6ca611b84 | HK06-1 | 501 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | 04:45AM For 13/F Data Hall 1, after Chilled Water Riser C failure reinstate, "High Return Air Temperature" alarm was triggered for CRAH_AR1_04, 05, 08, 09, 10, and 18. Data Hall temperature was maintained within SLA. Pentagon to clarify the alarm dead band for "High Return Air Temperature" alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615630&prj=501&rqi=gZe4gFndkxDowfHC5v9eLiZuJr | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-015 | 45762e21-22a4-4e4d-adef-2b76452cda79 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT2 L12 & L13 01:56AM After ATS changeover of 12/F CRAH units, data hall temperature sensors exceeded SLA upper limit. It was found that the chilled water valves of the CRAH units closed, causing the supply air temperature to rise. 01:58AM Data Hall temperature dropped back within SLA range | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615626&prj=501&rqi=IxmJoy0XobqvMC8qSsTnXG0O8Z | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-485-001 | eb9b8a76-2832-451e-bfaa-e551c3920a64 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS Graphics Issue | DCOS |  | Electrical | system | Electrical System |  |  |  | In EIST-01, during the total power failure scenario where SUDB_1 & SUDB_5 Q01 incoming breaker is opened, the power line logic is wrong. It displays wrong graphic and response. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615634&prj=501&rqi=To8RLZ4M3QMbZD6BpHHqkm8qrs | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-479-003 | 618524e7-845d-4f5d-9e4f-f2cf99eb4ac0 | HK06-1 | 501 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Electrical | equipment | 1ATSMI_M1R1_25 (1ATSMI_M1R1_32) | ATS - Automatic Transfer Switch |  |  | 01:41AM "Emergency Source Not Available" triggered for ATSMI_M1R1_23, 25, 27 Emergency Source. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615639&prj=501&rqi=OgPvwwLEAiub98hGmCKJ7hEhEP
FPT-479-001 | 5b25c3c1-035e-479e-bde0-ee7729bff71a | HK06-1 | 501 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | HVAC | equipment | 1EF_B_3 | EF - Exhaust Fan |  |  | 1EF_B_3, 1SF_B_2, 1EF_A_2 and 1SF_A_1 communication match alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615637&prj=501&rqi=m2Aa1tbqvDMQm2WAeN05hjil3L
FPT-483-008 | bb6e37d9-74a7-4823-9729-b3cc347f89bc | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Electrical Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT2 Test - 05 L12 & L13 UPS A2 Alarm triggered. After checking by vendor, it was found phase A was overloaded. After adjusting the loading, the alarm was cleared. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615618&prj=501&rqi=k4EOkHMrkx8zORm0SbqiFj8U0W | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-002 | 77e897ad-1e99-4940-8821-84bc94dee170 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT2 Test-01 L12 & L13 00:17AM When increasing the data hall load from 0% to 25% for 12/F Data Hall 1, "High Supply Air Temperature" alarm was triggered for CRAH_BR1_01 to 10, and 17. Data Hall temperature was maintained within SLA, no pre-alarms triggered for SLA sensors. 00:20AM The "High Supply Air Temperature" alarms auto cleared once the supply air temperature dropped back below the alarm setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615612&prj=501&rqi=SeehdJgbKmN22vjcmAJ81Z5V04 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-010 | 6dd81143-4178-463d-b12d-256e8b917cc7 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT2 Test - 05 L12 & L13 10:45AM For 13/F Data Hall 1, after CRAH_AR1_18 was failed, "High Supply Air Temperature" alarm was triggered for CRAH_AR1_04, 05, 08, 09, 10, and 18. Data Hall temperature was maintained within SLA. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615620&prj=501&rqi=UZ83PbeQd9non6YqLJaNhYiv5N | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-005 | 47c4cc62-8be3-42e0-948d-abb71bffcb2a | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS |  | HVAC | system | Mechanical System |  |  |  | HLT2 Test-04 L12 & L13 DPT-04 in CHWSTR_1 lost communication | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615615&prj=501&rqi=c76lVMeWReCDSBwTLVqz0Ois2B | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-009 | fa059781-589b-4a1b-b5b0-40405db47354 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT2 - Test 05 L12 & L13 06:09AM When increasing the data hall load from 75% to 100% for 13/F Data Hall 1, "High Supply Air Temperature" alarm was triggered for CRAH_AR1_04, 05, 08, 09, 10, and 18. Data Hall temperature was maintained within SLA. 06:15AM The "High Supply Air Temperature" alarms auto cleared once the supply air temperature dropped back below the alarm setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615619&prj=501&rqi=oSYTr25hy7QdDUigWTUcyDVyG1 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-012 | 3b671157-3741-4fd4-a601-b39411fc07f4 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT2 Test-10 L12 & L13 11:40AM For both 12/F and 13/F, it was noticed that for CRAH units that triggered "High Supply Air Temperature" alarm, the alarm is held even when the group temperature has dropped below 25.7C. Pentagon had to power reset the units with the alarm to clear them. Pentagon to clarify why the alarm is unable to clear. Also whether there are any delays, and what is the alarm deadband. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615622&prj=501&rqi=WpR7iiLHBiqfpAhqr8CAtIy3gW | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-010 | bbce96c8-828a-40ec-a007-05640020a9f8 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT 3 - Test 22 11:40 Observed CRAH_AR1_13 stop operation during riser failure scenario. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615609&prj=501&rqi=KV9kzK8brQJ9QDz7ahy86eKvFb | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-012 | f2635be4-e3cb-4d12-94fc-0bfee870e40e | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS |  | HVAC | system | Mechanical System |  |  |  | HLT-20 (HLT1) 3/8/2026 CHWBT_4 TCV-03 valve had mismatch alarm triggered. (Typical) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615591&prj=501&rqi=S1p3VHTe1ZSxIO7RWfiV2Db8yW | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-004 | cd805c66-d963-47f5-9311-797aa0fcc070 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 1 13F battery room high temperature alarm. Sensor replaced. Observed around 2 degC difference between actual measurement and DCOS reading. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615602&prj=501&rqi=k2zPblHUhTubwWyDbuLNOhe9Jx | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-011 | 0552c778-6179-4b0f-b46c-4c22e8f5d83b | HK06-1 | 501 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT-17 (HLT1) 3/8/2026 WCC- Compressor had discharge superheat warning repeatedly triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615590&prj=501&rqi=nWGntSCNVOLDwFfbjjQTReEiON | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-013 | 040cc80a-1ce6-484f-8ce7-a1127ccbd32c | HK06-1 | 501 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT-2 (12F & 13F) Test 11: CRAH Failure at Data Hall 1 at L12 and L13. 3/14/2026 12:46 MAU_M3R2_1,2,3 had communication alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615623&prj=501&rqi=xIqOPWwJpsl4GDr11wMkwE4VpV | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-003 | 912f75bf-8853-4da8-bbec-2a939f65c8ae | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT2 Test-01 L12 & L13 00:30AM When increasing the data hall load from 0% to 25% for 12/F Data Hall 1, "High Supply Air Temperature" alarm was triggered for CRAH_BR1_04, 05, 08, 09, 10, and 18. Data Hall temperature was maintained within SLA, no pre-alarms triggered for SLA sensors. 00:33AM The "High Supply Air Temperature" alarms auto cleared once the supply air temperature dropped back below the alarm setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615613&prj=501&rqi=Ej3g6O0H1gbWqyUNVPeruFRA6Z | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
GI-275 | ff183441-123f-40e1-a0a1-1676c5e2664c | HK06-1 | 501 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | HLT-05 L12 & L13 10:45AM For 13/F Data Hall 1, after CRAH_AR1_18 was failed, "High Supply Air Temperature" alarm was triggered for CRAH_AR1_04, 05, 08, 09, 10, and 18. Data Hall temperature was maintained within SLA. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615550&prj=501&rqi=ZDqSxGbvsEDG4hxY1LCOr0y2Cp
FPT-483-006 | a9a88434-fa3f-493a-b8b3-a6791f52357d | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT2 - Test 5 05:39AM When increasing the data hall load from 75% to 100% for 13/F Data Hall 1, "High Return Air Temperature" alarm was triggered for CRAH_AR1_01 to 03, 06, 07, and 17. Data Hall temperature was maintained within SLA, no pre-alarms triggered for SLA sensors. 05:42AM The "High Return Air Temperature" alarms auto cleared once the supply air temperature dropped back below the alarm setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615616&prj=501&rqi=o1VoVeZUaUcymUSopS4nkEYg2Z | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-011 | 026c10e3-15fa-4f4f-93ab-564fd784db5f | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT2 - Test10 L12 & L13 11:04AM For 13/F Data Hall 01, after failing both CRAH_AR1_08 & 18, SLA sensor 80_TT_04 reached 27C and triggered the SLA upper limit alarm, momentarily. It was floating between 26.9C and 27C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615621&prj=501&rqi=d0oZ06xpa8kMTrbGnO2SqPAImJ | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-004 | ddf8a51a-7ee9-433b-b95e-1346ae167d35 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS Graphics Issue | DCOS |  | HVAC | system | Mechanical System |  |  |  | HLT2 - Test 03 1RPP_B2R1_2_01 graphic mismatch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615614&prj=501&rqi=TaG9PK2CEnKbDzjlmeU3TQHjye | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-013 | bc660784-a89b-41d9-b25d-40d7652fb50a | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | DCOS General Issue | DCOS |  | HVAC | system | Mechanical System |  |  |  | HLT-10 (HLT1) 3/8/2026 MAU_2 and MAU_3 had incorrect fan speed reading on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615592&prj=501&rqi=BiRaXtKnEYSCDlOVLNYU9xzP4r | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-001 | 63e8067e-7950-44fb-b946-65f4308308a0 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT2 Test-01 L12 & L13 00:00AM When increasing the data hall load from 0% to 25% for 13/F Data Hall 1, "High Supply Air Temperature" alarm was triggered for CRAH_AR1_01 to 03, 06, 07, and 17. Data Hall temperature was maintained within SLA, no pre-alarms triggered for SLA sensors. 00:12AM The "High Supply Air Temperature" alarms auto cleared once the supply air temperature dropped back below the alarm setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615611&prj=501&rqi=ABIwUiuafLMvNm30yBOu64W4ud | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-009 | 0d25aeb6-cb0e-4b6f-9214-153b341015b8 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT3 Test 3 - 09:56 Observe bleed off pump common alarm on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615608&prj=501&rqi=W4qsnNKZbeE1j1NlXtPC3OiPco | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-003 | 2a2ef8b4-c73c-4e4d-a4f4-2bfb3ac975ca | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 1: 0% Data Hall load: 12F Tx Room receives low temperature alarm(25.1degC) at 17:42 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615601&prj=501&rqi=L18PhAEciyDeCdPr0E4rzC3gPz | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-483-007 | 22ae2b75-ce25-4a38-86fd-296c40f08bc6 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | VincentChung@commtechasia.com | 2026-03-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT2 Test-05 L12 & L13 05:55AM After the data hall load was increased from 75% to 100%, CHWSTR_2 chiller was called to start, but it was not able to stage in. DCOS chiller received an external fault, but no alarm was found at the chiller HMI. Fail to start alarm triggered on CHWSTR2. String 2 then staged in under free cooling mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615617&prj=501&rqi=LpK0GbXh5IwQDWaFGuFIXOuaHa | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-008 | 8e616e32-13df-4645-833a-4b67cceabbd0 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS |  | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 17 SE to clarify 1RAS_06 (Input 3) still having flowrate reading (~4L/s) after shutting off riser B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615607&prj=501&rqi=IA9nNSpQb5rtywMnQcR8ZfWiK5 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-007 | eb376c6c-dcae-42f2-a9a3-45ae26ca361b | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | Mechanical Contractor | L4 | DCOS Graphics Issue | DCOS |  | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 13 Pentagon to clarify why after remote air temperature sensor failure, some units will show 0C, but some will hold last status. 12/F: CRAH_BR1_11 sensor 1 shows 0C, CRAH_BR1_14 holds last known. 13/F: CRAH_AR1_11 & 14 sensor 1 holds last known | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615606&prj=501&rqi=o4sxZQC2PEqQqs9AfQeMGR217o | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-011 | d9c19fe7-b981-4d57-9399-a362a5723775 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT 3 Test 22 - Mechanical failure scenario. CHWSTR1 changeover to CHWSTR 2. Observe CHWSTR1 fail to start alarm on D2SD. CHWSTR2 operates normally after changeover. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615610&prj=501&rqi=Q9mbSHdVgMLQ7e1Lg6GwHa6Eav | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
GI-266 | 5b53dbb2-73fd-48f6-b4fd-46d7c17c01c5 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | ShirleyLeong@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning |  |  | system | DCOS |  |  |  | SE to recheck and troubleshoot the system settings and parameters because SE uploads new software/firmware for the chiller/DCOS when unauthorized software upload is allowed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615518&prj=501&rqi=ptdZfzgZFsNIK0o7B88DF2mJoP | https://equinix.facilitygrid.co.uk/x/project/501/system/13006
FPT-484-006 | 21cde2f9-2e7f-45a5-bb03-0c29cd37b4fa | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | Mechanical Contractor | L4 | DCOS General Issue | DCOS |  | HVAC | system | Mechanical System |  |  |  | HLT3 - Test4 12/F and 13/F No feedback status for CRAH ATS status | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615605&prj=501&rqi=8odBgh2kUJDkEF3ZhQhGNbU76Z | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-001 | bc8df8d6-e4d4-4145-a381-c2f81daaf2fe | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 1: 0% Data Hall load: 17F Lv Switch Room receives low temperature alarm(24.8degC) at 17:39 17F Tx Room receives low temperature alarm(24.3degC) at 17:39 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615597&prj=501&rqi=HD7hDLgeRYdH81c1mT9UozRvLV | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-002 | 383aff02-61fe-49f4-9143-cc81a1d99397 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS |  | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 1: 0% Data Hall load: 15F 1EF_R1_6 receives command mismatch alarm at 17:40 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615598&prj=501&rqi=oH6cJWXmZGgWQ0MzO6KmTIrDlZ | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-484-005 | 29ffb230-c2c2-4a53-8bff-47227f406fd7 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT3 - Test 2 19:10 13/F DH2 exceed SLA during ramp up IT load. Unload to retest. 19:19 start again to ramp up load. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615603&prj=501&rqi=NT6m3EfeTvRJRUTPWOK4d8xwXC | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
GI-253 | 640e58da-4c80-477a-bc24-a0b11690ebca | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [7 empty] | 1RPP_B2R1_2-01 graphic mismatch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615378&prj=501&rqi=ihV71VZGEvNIh5ub35UwcTo1Cs
GI-239 | 2dc4c5f0-66a1-44a6-b03d-85b5334deb25 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Pre-HLT L12 and L13 13/F Data Hall 2 80_TH_04 exceeded SLA limit, it recorded 27.1C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615313&prj=501&rqi=REQZdfk6GrIN6SwAuS8MQc1PWH
GI-243 | 5be936bf-e11c-4ffe-a90d-d5abb735a5ee | HK06-1 | 501 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | During functional tests of water leak detection system, it is observed that for panels connected to leak detection cables AND point-type sensors, when simulating a specific leak test, the panel and DCOS read distances well above the accepted criteria. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615334&prj=501&rqi=5eSJ9ozSKCCh3wy2oaVdGyJFe4
FPT-482-029 | 09e67c1b-4154-43be-837d-3de97edc26dd | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | SCH - Schneider MV | L4 | Commissioning Issue | Commissioning |  | Electrical | system | Electrical System |  |  |  | 11:40 - 1SUDB_5 was triggered with battery tripping unit alarm during block R1 was failed on DCOS. It resumed automatically after block R1 is supplied by generator. GEM team confirmed on site that no alarm were triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615348&prj=501&rqi=nuNwGld35fJaMJ7dxkpwEKgbhu | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-240 | ec5ee1ff-8b2f-4d6b-b1f4-72424f807600 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Pre-HLT L12 Test 11 12/F Data Hall 1 80_TH_04 exceeded SLA limit, it recorded 27.7oC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615315&prj=501&rqi=wSXoS3XVBHK3SodaIjY013UjuW
GI-241 | 44e71d43-b133-4d8e-81a0-109ab6488e9c | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | PerryLee@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Pre-HLT L12 12/F Data Hall 1 CRAH_BR1_02 loss of communication alarm, unable to reflect status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615316&prj=501&rqi=J54midXp3R4B9wofVUFjuUqdCo
FPT-482-030 | f4af222e-de3f-4890-839f-eb909d88bec4 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Electrical | system | Electrical System |  |  |  | 11:46 - During the power changeover for R1 block, some ATS that has R1 block as emergency source did not show emergency source not available. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615350&prj=501&rqi=s7Q2QRy8tuiRlGeQWZPqVEYlLN | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-242 | 7799f307-77af-4daf-8621-fe4e62007bec | HK06-1 | 501 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | During L3 of Water Leak Detection Point-to-graphic test, it is observed that point signals incredibly high value when not detecting any leak. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615323&prj=501&rqi=KQQxW5J7yYc4Pc4lxrmxZCEcPv
FPT-482-031 | 392103c7-03e9-4397-818e-d6051ef10a06 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | SIE- Siemens MV | L4 | DCOS General Issue | DCOS |  | Electrical | system | Electrical System |  |  |  | 11:34 - During the power changeover for R1 block, MLTX_M1 was triggered with communication alarm. It is confirmed by GEM that the MLTX_M1 is online during the changeover and no M1 equipment undergo changeover. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615351&prj=501&rqi=ODa5V2BCtYsmWWpngogXtwWNkC | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-238 | d7b6cd4e-e254-4e79-95df-0936ce5816d5 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Pre-L12 HLT Failure CRAH_BR1_08 and 18 12/F Data Hall 1 76_TT_02 exceeded SLA limit, it recorded 29.1C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615312&prj=501&rqi=SuSaKJCaJsm1lrMsuRWn1OBz0A
FPT-482-028 | 37151fee-337c-45fa-9bfd-7126500351cd | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS |  | Electrical | system | Electrical System |  |  |  | 11:17 - 1MSB_B Q06 is detected with communication alarm during EIST-12 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615346&prj=501&rqi=SxvJ7oWTrJSW2M0CfGoFp0wjgy | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-482-010 | 60ebeb2a-496e-4252-9da0-2e851368f2aa | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Fire Detection | equipment | MSFD-13-14 | MSFD - Motorised SmokeFire Damper |  |  | 15:10 - MSFD-13-14 located at he generator set in 13/F generator room was found to be closed abnormally due to the flexible link is loose and resume at 15:20 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615276&prj=501&rqi=eIucl3C9zqMlAzvk8entiXiHe2
GI-237 | af486856-5c1b-4f71-a310-275d3cf06615 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | L12 & L13 Pre-HLT Day 1 Hot spot identified near CRAH-AR1-05 and CRAH-AR1-10, which caused exceed SLA limit on L12 Data Hall 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615299&prj=501&rqi=zemV21ovS0n3vNFEfDsv74dm5N
GI-201 | c42662ab-233e-489d-ab13-2ea4ddac82e0 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [7 empty] | MIST-12 When PCP 02 was failed, "Hot Standby Status" and "PCP Status" did not show on DCOS graphics, all greyed out. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615169&prj=501&rqi=SY9SEH3YtXs0fcrazP48ohOWVx
GI-205 | 1d2e3581-a3f4-4cd7-83fd-72ca1cf62117 | HK06-1 | 501 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning | [7 empty] | CRAH_LR1_01 to 14 triggered "High Supply Air Temperature" Alarm, Data Hall SLA sensors were all within SLA range. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615173&prj=501&rqi=Kc4hy13xWhxuQN7CFQn08e77uf
GI-203 | a73d149a-55b1-40c4-9a77-e193890db647 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [7 empty] | CHWBT_5 Bypass valve mismatch alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615171&prj=501&rqi=JD13B5FP9ET8xdj1qp24gJEnrG
GI-211 | 19499aa9-cdb0-45f0-9d31-9a7cecd20886 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | Point to graphic test is conducted on graphic template from SFAT. Gammon to confirm the point schedule with EOR and provide SICD for VRF system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615203&prj=501&rqi=aBdBaAOTC2Q3h7zdAuuyi43EbE
GI-209 | be62c122-a989-405a-8fb2-ccd1890cb003 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | During non working hours, when the room temperature exceeds 30C, the FCUs would operate. This logic is not available. Please clarify this logic with vendor and NV5 and which room is applicable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615195&prj=501&rqi=mNlJsA39wvTuNstheHF11eP5wv
GI-202 | 96509b25-e5fc-4c4b-afa2-bc7569c3e21c | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [7 empty] | MIST-12 When PCP 02 was failed, "Hot Standby Status" and "PCP Status" did not show on DCOS graphics, all greyed out. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615170&prj=501&rqi=wqk7RMACvQFImlW6vYnDiQilSV
FPT-482-020 | 648238b4-3499-4a5a-84e7-e07ca282c63f | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS |  | Electrical | equipment | 1UDP_B2 | UDP - UPS Output Switchboard |  |  | 16:17 - 1UDP_B2 "communication alarm" is triggered when block B changeover from generator source to main utility source. It is confirmed that the MOXA has UPS power backup. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615286&prj=501&rqi=mgg3ye3EUKCliQjpDIaNoUTzP1
FPT-482-007 | 3f93864c-1c65-4f52-b6e4-81ccae7c4e54 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | Electrical | equipment | 1UDP_B2 | UDP - UPS Output Switchboard |  |  | 12:08 - During the load is ramping up to 50%, DCOS recived "Communication alarm". FSL confirmed that the breaker did not triggered any lost communication alarm on site. SE DCOS should rectify this matter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615273&prj=501&rqi=BRJPV1Ny6kkJTFJ4zaIA96qW2n
FPT-482-005 | 21d99c86-97d9-4601-8f6d-593a62c33c87 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | 11:27 - Before the EIST start, DCOS received "ATS id no. ATSMI_M1R1_30, 04, 03" Emergency Source Not Available alarm. GEM confirmed that the essential power was healthy on site. GME shall clarify the mismatch between actual status and DCOS status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615271&prj=501&rqi=TtCxmI36tCj1NI9iChtzfxOLab
FPT-482-019 | 9512d96d-7664-4bdc-ae52-53eb1a7eaee6 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | 16:11 - When the STS is showing alarm from the event log, the STS icon beneath UDP did not show any alarm or surrounded with any color of border line. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615285&prj=501&rqi=GU4djlTAuixOR29ibGACFCuFbn
FPT-482-022 | d0a1a12a-91ef-46c2-af16-ffb2686e5840 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Electrical | system | Electrical System |  |  |  | 17:15 - For SLA sensor 01-07 in the 15/F big data hall, it received communication alarm from 15:31 to 17:38. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615288&prj=501&rqi=3hKCRgQUUHGJQFwqXcwyDwwoCm | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
FPT-482-021 | bde23282-fc86-4695-b8c7-e435059f19b1 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | 16:45 - CT occur with vibration fault causing the chiller to change string during the power resume for block M1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615287&prj=501&rqi=wvSxtIhIml7IHVoTMRV3OKesfd
FPT-482-012 | 263ce351-80d6-4db2-9381-98355af5d71b | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Electrical | system | Electrical System |  |  |  | 15:24 - During the changeover for M1 block, normal power light in 17/F command centre and LOCC room were found and it was not resumed when generator power has kicked in. The power resume after around 5 minutes. GEM EL team claim that there was light work ongoing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615278&prj=501&rqi=itMP0DHrDDjxf7yqDNdfGtSDLO | https://equinix.facilitygrid.co.uk/x/project/501/system/13749
GI-210 | b227aca7-897e-4ba9-93c2-169b7499be45 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | During unit sensor fail, operating unit will be switched off and other unit will run in 100% to cater the load. Please clarify logic for this scenario for the battery room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615196&prj=501&rqi=ESvAtyQIWxhz6UUDleZjiU3n0w
FPT-482-023 | 3ffbbb47-cacc-4d23-ae5f-26ef0ccf508b | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | 17:38 - CRAH in the 13/F LVSB room did not show which source is it on before the power failure started on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615289&prj=501&rqi=qpGfC8TEF8I2e94BqiV3F0W7K9
FPT-482-016 | 7d239548-bca1-4841-be6c-849aa2df43f9 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Electrical Contractor | L4 | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | All "input breaker open" alarm is triggered when the battery is discharged. It is confirmed that the UPS input breaker is not opened on site and on the graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615282&prj=501&rqi=HRYwutToDnuXVRPzc5AxmceUkJ
GI-213 | a308fb91-491a-4e86-bdac-5ce84167d0c6 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | During power failure test for VRF indoor unit, it is observed that there is no alarm on DCOS and it keeps showing last status on the graphic. Gammon to confirm the point schedule with EOR and provide SICD for VRF system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615206&prj=501&rqi=EClMcaRwySfKfRyp3PFXBuTZUR
FPT-482-006 | c9ff7abb-cbf4-4e23-bcea-5091695c36af | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Mechanical Contractor | L4 | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | 11:52 - During the load is ramping up to 25%, DCOS received "summary alarm" with red border line, this indicated as a "high high alarm" were triggered for all the CRAH in 15/F DH1 & DH2. STULZ confirmed it is "high supply air temperature alarm". | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615272&prj=501&rqi=GkbQGWi4z0SxPxf2rMF2W0PSza
GI-212 | 321cc3fd-f69e-479f-aca0-e3275e3446b5 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | VRV Alarm priority to be clarified. Gammon to confirm the point schedule with EOR and provide SICD for VRF system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615205&prj=501&rqi=4VtjGa9PhmC5qJJyIVCwtzGTKe
GI-208 | 798cb09f-b6b7-48c3-beac-cdc4072f1e84 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | When one FCU has power loss, the other FCUs connected to the same outdoor unit will also receive the fault code and trip. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615193&prj=501&rqi=H0U3YCbzQ8BAvyrHyuh22SG2HQ
GI-206 | 97429a8b-0ead-409b-97f9-11d1027ca7f0 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [7 empty] | TCV-03 for CHWBT feedback and common mismatch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615174&prj=501&rqi=Pos8huVjLM8Xii4FB7yZB3FDwN
GI-200 | 2c310316-7d1e-47c4-9029-1339411a4ef0 | HK06-1 | 501 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | MIST-03 (Failure of CHWP) MAU2 Compressor 1 fault alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615167&prj=501&rqi=0LuoWXp3sLpZWTpgDfD5rngtGt
GI-207 | 1760cc5a-ae8e-4729-997c-b284ac509f34 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | When one outdoor unit was failed (via E-Stop), the standby outdoor unit cannot stage in automatically. It has to be staged in manually. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615192&prj=501&rqi=XItuhf8ekc2SL0Fo27iLU7PrPJ
GI-199 | 88deba30-9025-42b6-a481-efc506349a7b | HK06-1 | 501 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | L15 MIST MAU 2 Loss of Communication Alarm due to R-Block no power | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615161&prj=501&rqi=7TQjGmX3rfAzh1lXmFpYTiweEn
GI-204 | 2c2a8e87-4f7d-44ae-9c9b-9375045c754d | HK06-1 | 501 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | After CWP was failed and when STR 2 WCC stages in, the run status of WCC 2 would flicker between On/Off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615172&prj=501&rqi=9OjLyKYjUMTyuGwzUfLV2wQ3wv
GI-160 | 7de558ff-8758-4390-a882-1c08fe908d7d | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning | [7 empty] | During the whole Pre-EIST for 15/F, all the CRAH in DH 1 and DH 2 on 15/F, the high supply air alarm is triggered on their control panel and summary alarm is triggered on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615031&prj=501&rqi=KHPQqXbUPwJedHlzQiAlWrqYSI
GI-166 | e4456d09-b849-45ca-8f14-525ed2dae80f | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [7 empty] | Before the Pre-EIST, for all the SUDB that is not under this phase, MCB common fault is active and triggered on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615045&prj=501&rqi=lUKMpIhWEe9V19SD1MFJ19EEoe
GI-165 | 4a155664-c375-4431-a916-df1526cfb79a | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | [7 empty] | During Pre-EIST day 2, when we are ramping up the load to 75% (16:14), 12/F electrical room room temperature is below low limit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615044&prj=501&rqi=hTACBaRmIEgfPlyy0Eq2syedYq
GI-197 | 5bea584e-155e-4087-8188-2d530f6fc12d | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | ychoong@ap.equinix.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [7 empty] | During Pre-MIST, PCP 01 was failed, PCP 02 took over but "PLC Stopped" alarm was triggered for PCP 02. Redundancy Fault error alarm and PLC were also triggered for both PCP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615112&prj=501&rqi=tYMEJmJquywa8OfZWxa37ZVDgO
GI-152 | 6d143e73-40d6-4fe6-8464-d7d8e493602a | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Block B receive an overvoltage issue during the Pre-HLT, causing the changeover happen between main utility and generator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615006&prj=501&rqi=LegqJXZfoUmtOHFLRg5qMo2u71
GI-162 | b767b6d1-17b3-400f-af45-fa1de40e7a35 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS | [7 empty] | Before the Pre-EIST started, all MSB are receiving priority 2 alarm and priority 1 alarm on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615037&prj=501&rqi=CNsVwCpYjAOGCCGqQ4TpIAtksF
GI-168 | 6cce94d7-7033-46b6-b694-d61e62c19a77 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS | [7 empty] | During the Pre-HLT, unit individual reading should be shown on DCOS graphic and group control temperature should be | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615053&prj=501&rqi=At8bQtsmVNhOFYZ1VtkdfkBuTa
GI-198 | fea115a1-c117-404a-b45d-2939559fb2f6 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | ychoong@ap.equinix.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [7 empty] | During Pre-MIST, When PCP 02 was failed, PCP 01 took over but "PLC Stopped" alarm was triggered for PCP 02 Redundancy fault error alarm and PLC were also triggered for both PCP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615113&prj=501&rqi=amEGB9iwQrjHbNw2MdJnlFqS9H
GI-155 | cc21be17-489a-4012-86ca-aa3df35eee27 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | [7 empty] | MAU triggered a fault alarm on DCOS but on site the MAU does not have any alarm shown during Pre-EIST | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615018&prj=501&rqi=BEsmyDq27fAOEB4cKetIuJa8QH
GI-167 | 9abaa813-b88e-48a6-97ac-25b51daa2cd2 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | [7 empty] | During Pre-HLT (HLT-3), when the data hall is on 50% load and maintaining for an 1hr, the 13/F battery room has high temp alarm triggered | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615052&prj=501&rqi=WZEwtMxYvKFTYNdiBb9AOzfFhZ
GI-192 | f6537d45-1b1d-477d-8fb2-9fa6c759ab25 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | [7 empty] | The name specified in approved drawings is "FCU_M3_24" but the name of master panel shows "FCU_R2_24". Please clarify and rectify with correct name shown. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615083&prj=501&rqi=9t10yYUMW6JQGsqbseHAwnsGBu
GI-169 | fc987873-5506-4c6b-998d-58f4daa78a99 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | During HLT-10 (CRAH failure at Data hall 1 and Data hall 2), GW88_TT05 and GW94_TT06 reach high temperature after reinstate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615054&prj=501&rqi=JJzO9AXEcW7cjeiKNiYeiXFsIg
GI-153 | 269207c5-20cc-44d7-969d-3bc3912d9f21 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment type |  |  |  |  | Communication alarm for ATS is at MSB-M1 triggered during Pre-EIST when load was at 50% no switching was occuring at that point. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615015&prj=501&rqi=PymfLBtg8CVisD577wEi6wWDfV
GI-157 | f2c1bca6-6cf0-4020-81d5-40eb81de5a02 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [7 empty] | RMU_R1 is showing red-dotting line on DCOS, however no alarm can be acknowledged on the RMU_R1 side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615021&prj=501&rqi=uBpis1A5lDbEMgCUYZMfS1M49R
GI-161 | 7c7c604f-5be3-4114-8fdf-845f75b74d56 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [7 empty] | During Pre-EIST (EIST-15), for both of the UPS in 17/F LVSB room, external bypass breaker is closed but both of the UPS did not show it is on external bypass mode on the UPS HMI panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615033&prj=501&rqi=27DSXHN2eYgZdfts7BJsW9fpLB
GI-179 | 91a925f8-e639-401f-a9c1-007097cc0fe3 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | DCOS panels cannot emit fault signal for room temperature sensor for testing ICUs function for temperature sensor fault. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615070&prj=501&rqi=4BY9vzzg8V0gEqljrEKsNhAGFB
GI-159 | d36e01da-0396-4a65-966b-e25539dee9e4 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning | [7 empty] | During the EIST-12, when the changeover occur between mains utility and generator, both CRAH in the 17/F LVSB room is showing source 2 unavailable instead of source 1 unavailable (R1M3_1, R1M3_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615028&prj=501&rqi=XBfJIQ9mlV76e8UqTDXV02BzSS
GI-196 | 22bb7df5-0ce0-40e6-9cd3-ed9dd156cf67 | HK06-1 | 501 | APAC | Closed | P3 Low CX | ychoong@ap.equinix.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | During Pre MIST - ChWP changeover/failure, both halls 1&2 exceeded 27degC SLA but return normal within 1 min. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615111&prj=501&rqi=jGpSh3D4RhnYS2Qn1Go6F8ivQg
GI-191 | cb803221-27ff-4efd-beec-5e153e490c24 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning | [7 empty] | For all the FCU in 17/F office rooms, E-stop not yet tested. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615082&prj=501&rqi=lWvuTk0oIKJfeGVvRVO1lrRr2Q
GI-188 | 7df2a5d5-3f8c-4afe-96c3-f8408795fb5c | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning |  | HVAC | equipment | 1VRFOD_M3_5 | VRF - DX Unit Variable Flow System |  |  | 1VRFOD_M3_5 CHW flow speed and return temperature higher than design rating, Calibration cert out/dated for water temperature sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615079&prj=501&rqi=y6K2UnetdjdoIlSG3Lh7qX9O2I
GI-154 | a6335624-d0f5-486f-84b5-d9cf220e4915 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning | [7 empty] | STSSB communication alarm is triggered during Pre-EIST | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615017&prj=501&rqi=ytrKFtWnvuPSEI857OCiug2JLz
GI-190 | 27f27a8f-c08c-45bb-9855-d39146dcc9ee | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning |  | HVAC | equipment | 1FCU_M3_17 | DXID - FCU/DX Indoor Unit |  |  | FCU_M3_17 controller air speed button broken. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615081&prj=501&rqi=r3QozPfgPu6Vo9SbPRBg0zuQO9
GI-158 | 1a78c1f9-b75e-478e-a7d2-4959124807a6 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | UPS is triggered with high limit alarm on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615024&prj=501&rqi=b3JjoYbImxvifgzju9ll6Sld99
GI-170 | 62b1ebf8-3d1f-4726-946f-68c401f75c09 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning | [7 empty] | During HLT-12 (CRAH sensor failure at data hall 1 and data hall 2), Data hall 2 reached 29.25 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615055&prj=501&rqi=vloEG8xOB5APSnEfYGpRD1xr3d
GI-171 | c01ba8d4-e3f5-4a0f-8ff5-7b72c86075a0 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning | [7 empty] | During HLT-13 (CRAH sensor for remote temperature, failure at data hall 1 and data hall 2), data hall 2 exceed SLA temperature high limit of 27 degree. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615056&prj=501&rqi=BJxgv8iEVGh2PSpQyHh0OYi7N2
GI-164 | a11c4d54-2c47-46cb-ae5a-77572bb0e62a | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [7 empty] | surge protection device failure alarm is still receiving and active on DCOS for all MSB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615042&prj=501&rqi=M803T7kov0RKUxOIjxJk96OVo3
GI-189 | 8861d329-29cc-43da-90fd-dff3c5284b34 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Construction Manager |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | All indoor units supply air temperature lower than temperature set point at controller (set point: 16oC, measured: ~22oC). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615080&prj=501&rqi=d0e6jMBZGu8BHbOoQqM6J5Iqag
GI-193 | 0850d837-f3db-4bbb-86ef-916881dd8ade | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS | [7 empty] | STSSB_B2R1_1 and STSSB_A1R1_1 communication alarm is triggered | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615084&prj=501&rqi=xbyBtPzu8LbJH4cmnlduZu4zMb
GI-195 | f97f201f-93ec-400e-a2ce-9329b9e798d3 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | ychoong@ap.equinix.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | During Pre-MIST, MAU 01 found to be not runing. "SA Dewpoint High" was found on unit HMI | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615110&prj=501&rqi=tI2xSO1K0CovaOAVF6fNCFYcQF
FPT-481-014 | 2ebe2267-63d1-4aa6-89ea-2c26a6c6634d | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT-10 (HLT1) 3/8/2026 GW94_TT06 high temp 27.1 and drop down to 26.9 within sec @05:25 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615593&prj=501&rqi=NGcsMdiCB39aPk8nbs9B5OcW6a | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-009 | b329f0a7-4ac1-4df4-bd62-f797624ad85f | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS |  | HVAC | system | Mechanical System |  |  |  | HLT-1 (HLT1) 3/8/2026 CRAH_LR1_15 &16 had lo/lo temp alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615588&prj=501&rqi=1pdmtC9L4JeQhOkqW3BQXo0TtA | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-010 | 56664b92-a521-4e56-a242-d902d793d21c | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS |  | HVAC | system | Mechanical System |  |  |  | HLT-1 (HLT1) 3/8/2026 1EF_R1_6 had common mismatch alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615589&prj=501&rqi=ZxAzBxbxAkGL3F6HNo37hWT8ir | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-015 | ee67a9d3-78d9-47d8-9754-c7b57e258cbe | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS |  | HVAC | system | Mechanical System |  |  |  | HLT-21 (HLT1) 3/8/2026 After Estop the WCC, CHWP can keep running for 2 mins. However after 2 mins, reset estop WCC and reset string 1, but string 1 cannot be reset to resume operation (string 2 was in maintenance mode). SE to clarify whether it fulfills the design intend. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615594&prj=501&rqi=hiw2Uzb1xZoCDQUoI0iRfh7WHb | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-006 | 607e4be7-ed90-488a-8a8b-930bfbde86fc | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT-3 (HLT1) 3/6/2026 12F Tx Rm LVSB Rm; 13F Tx Rm, LVSB Rm; 15F Tx Rm and Batt Rm; 17F LVSB Rm 2 had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615585&prj=501&rqi=9ewCfb6XJuci53FvIxx71zloDm | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-008 | 2516c8a3-6c37-4bf9-aaac-da187a51a5ca | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT-5 (HLT1) 3/6/2026 12F Tx Rm, 13F Tx Rm, 15F Batt Rm, Tx Rm and 17/F Tx Rm, LVSB Rm had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615587&prj=501&rqi=XoRJle2nkKPDv7MHo5VjdhWtu3 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-004 | bf35e275-229b-4550-8a77-fa240828ab68 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT-2 (HLT1) 3/6/2026 13F Batt Rm, Tx Rm, LVSB Rm; 15 Tx Rm; 17F Lv Switch Rm had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615583&prj=501&rqi=TfhvmJi47z0DsXH9Tg6MdrXbWz | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-003 | e25120d0-745a-4a17-8398-aba490b055a8 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | High supply air temperature alarm for DH2 CRAH were triggered at 03:32 and resume at 03:32. Datahall keeps maintaining SLA range. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615582&prj=501&rqi=lJaQ8VvrJ3b1uvBzR8xi3L5GI2 | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-002 | d92c6146-5f2a-456e-b46d-0ce4b8c8b8c6 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCOS General Issue | DCOS |  | HVAC | system | Mechanical System |  |  |  | Tuning the bypass valve min flow delay to 20s at 02:38 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615578&prj=501&rqi=KHZ7NRANDL2Y9e1enGl0G5U7Vk | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-001 | ccd27a10-c757-4de2-ba3a-1fb63a09d2d2 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT-1 (HLT1) 3/6/2026 12F LVSB Rm, Tx Rm; 15F Tx Rm, Batt Rm;17 LVSB Rm had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615574&prj=501&rqi=hxWFQDNHhuy6qfxrESZT1AHJvo | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-007 | c546e2ed-a4f8-4299-9cce-8560f9baddcd | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT-4 (HLT1) 3/6/2026 12F Lv switch room had low temperature alarm triggered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615586&prj=501&rqi=rvCNJZgxBmTFBJzjODoIAKsnQT | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
FPT-481-005 | 7d426c34-9a58-4e4f-bf33-deb4e19c9d6f | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | HVAC | system | Mechanical System |  |  |  | HLT-3 (HLT1) 3/6/2026 DH1 CRAH 04,05,08,09,10 had high supply air temp alarm triggered at 04:18 and resume at 04:19 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615584&prj=501&rqi=hkcaQFGpoEOKP91foUYFS5iBoC | https://equinix.facilitygrid.co.uk/x/project/501/system/13748
GI-151 | 1af6ac47-c72a-4d66-92c7-08e6d7b8aa01 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | JosephHalim@commtechasia.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | MAU overview page showing Static Pressure (Pa) - to change to Fan Flow (l/s). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614792&prj=501&rqi=wDgsISPcyxZOdj36pGk1CqqQuC
GI-150 | c7171d2a-80cd-4223-8d90-bdf709d951fb | HK06-1 | 501 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-05 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | During heating mode, 1 outdoor unit will run. If it fails, it does not changeover to the remaining units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614790&prj=501&rqi=P5EuZl66y6z2HopTPdQnnMAQEI
GI-149 | a13ea97f-e7cb-4dd7-b709-0a8269cea503 | HK06-1 | 501 | APAC | Closed | P3 Low CX | keymanchan@commtechasia.com | 2026-03-05 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | 16/F Chiller Plant - Emergency lighting discharge lower than 2 lux. (measure from floor) at the beginning of battery discharge The possible reason is chiller block the path of light. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614773&prj=501&rqi=xsDpsp1vtU9iJW6V0BMZP94HrI
GI-147 | 177df66e-0dc5-4a21-9877-a82c518d47be | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Fan flow not showing correct reading on DCOS for MAU 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483403&prj=501&rqi=KKAbCz34E61ciBhmhGveQIcj1g
GI-142 | f09939ba-d8c8-4114-998c-7934e667aa42 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | Gammon to clarify with NV5 the design intent and control logic for CHW Valve under Free-cooling mode. Whether it operates as pre-treatment or not under free cooling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483398&prj=501&rqi=O6g7N8mvb8Ps9I0QrhFflsnJgL
GI-148 | 825f3fc9-07f6-46d9-9eae-aa2484a8cc15 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | GEM and SE to coordinate and ensure all setpoints put on DCOS are according to approved settings as alarms were not activated during testing due to incorrect setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483404&prj=501&rqi=qTqopl4TA3wqXYMd8Z0mbpKuMy
GI-146 | 7c3b82c5-c638-492f-a5aa-fd3ce2b26508 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | Compressor #3 icon not showing running / not running status on MAU 1 & MAU 2 DCOS Graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483402&prj=501&rqi=qLJBWAMYMmk6C7SACrKB61b5Gp
GI-145 | f4ae0306-4ee1-4080-aa89-f7838318c99a | HK06-1 | 501 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | GEM to coordinate with Saiver and SE DCOS to rectify DCOS-autoON function for MAU unable to automatically restart upon power failure resuming. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483401&prj=501&rqi=NJTm38eGSg7PUta1Y0LiPEoTDz
GI-144 | be1e1a8a-0fb7-474a-a266-e1f64c5677cd | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Gammon to clarify with NV5 the design intent and control logic for CHW Valve under heating mode. Whether it operates as pre-treatment or not under Heating. To clarify and update SoO. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483400&prj=501&rqi=4DFaEN49J5Ujvd9YNdPqDJQcPt
GI-143 | fb314a61-8599-4981-804f-05b5431e11f0 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JosephHalim@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Gammon to clarify with NV5 the design intent and control logic of outdoor unit activation under different cooling mode temperature. If it is solely controlled by off-coil CHW temperature reading, or if airflow is also considered. To clarify and update SoO. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483399&prj=501&rqi=7MuOffpH1mL1koeL1KGQ1C1TKa
GI-141 | 5f919cb0-c132-4a29-95c0-8d800964f322 | HK06-1 | 501 | APAC | Closed | P3 Low CX | PerryLee@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning |  | HVAC | equipment | 1CHWBT_5 | CHWBT - Chilled Water Buffer Tank |  |  | TCV_03 for CHWBT_4 and CHWBT_5 mal-function | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483390&prj=501&rqi=WI8VYwjOftPn92Yv1J7bBvO3yr
GI-140 | 34738cbc-91fd-447f-91d8-2cccc5de28b0 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JosephHalim@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | Control logic deviation from SoO: After 20 minutes (1200s) of exceeding the high SA temperature dewpoint, MAU should raise a high SA temperature alarm and shutdown. However - only alarm appears with no shutdown sequence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483389&prj=501&rqi=0j5HLkva4HuedJSvKlfUJoaVJk
GT1DCOS-23-001 | fa0b420c-e29e-4d84-aa92-34ecb2bdd114 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_GWP_28 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352266&prj=501&rqi=6MoXbxoepA1r7cT7VDmvGRx4uB
GT1DCOS-26-001 | ca44d2d9-b5e9-4c65-a10b-b6902f870223 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_GWP_31 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352263&prj=501&rqi=B9YBwZdOHm7LJH1hATj3OF7Ynz
GT1DCOS-28-001 | 393ecc84-dbc9-4bf3-a130-743e77fd502d | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_GWP_33 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352265&prj=501&rqi=NRMJ0L8e8eU391fdtDBPbAh76E
GT1DCOS-24-001 | de0d582d-c3da-4e0a-b306-2871ab6390a9 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_GWP_29 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352267&prj=501&rqi=mcrA4HJC6XFdgDP0Fr3jfg1nUy
GT1DCOS-25-001 | 31ad0995-8502-4d7a-a282-518cfc855ae7 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_GWP_30 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352268&prj=501&rqi=coSTBRVd0iIUdOu4FZvxsfO5ct
GT1DCOS-27-001 | 8048c3f6-68d5-46ae-a720-e1fbe0b5f4d1 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_GWP_32 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352264&prj=501&rqi=gFcTVTsyOqc3Qt9UCHjdKqcjdq
GT1MECH-2-013 | 17b47dcd-c415-4c3a-8cd6-39b6e100a160 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS |  | HVAC | equipment type | AHU - Air Handling Unit | AHU - Air Handling Unit |  |  | All MAU unit / EC fan Auto status not able to be shown as operating on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204118&prj=501&rqi=eCv0l5Dj1D5Jn2WRyNVWGXO7CV
GT1MECH-2-009 | 62364426-ee2c-4e2e-aa37-0df77bedbd52 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS |  | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Outdoor air damper command to be clarified. It shows in 'percentage' on GUI and functions as "Read" point which deviates with point schedule. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204113&prj=501&rqi=bVVtUvuQmqFGq0lSXSuphZ9wwi
GT1MECH-2-001 | 518ec07a-31a6-4b91-87e1-5266f852429a | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS |  | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Decimal for Supply air fan flow and Air flow sensor range to be checked with GC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204105&prj=501&rqi=cG19ky56zrwqadach3GAO9AhWo
GT1MECH-2-006 | c26e960a-0eeb-48ea-9ab6-1a7066c73fe7 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS |  | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Humidifier control signal to be clarified. It functions as "Read" point which deviates with point schedule | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204110&prj=501&rqi=t47rDJpQbUESHPhVMAGAuso8rN
GT1MECH-2-003 | cf07a1ad-29e5-414b-817b-c57adceb3bab | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS |  | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Low temperature detector alarm is not available. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204107&prj=501&rqi=A80H5vBPUJaCTCWmnALboE6fRn
GT1DCOS-29-001 | b8fcde34-0b32-4cee-b3c6-b4f19c0332e2 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_GWP_34 | DCOS - Control Panels |  |  | Full point-graphic report outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221094&prj=501&rqi=3Lk4ISgCpImZdUx1SSAXJfmPpO
GT1DCOS-31-001 | 146cac95-09bd-4eeb-8453-35f76e00fa68 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_GWP_36 | DCOS - Control Panels |  |  | Full point-graphic report outstanding. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221097&prj=501&rqi=IveujTSJGW6HRdIfSe3sc28xm4
GI-121 | a61ec776-3bd9-4327-8211-f6b1cad5d98f | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | ATS alarm log description should be aligned with the graphic description. Normal source available (Rename as normal source not available) Alternative source available (Rename as alternative source not available) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204088&prj=501&rqi=cynhDpjPOH7R7CuoVFd1vcQqTC
GI-117 | 04be25b5-887c-4ab3-9aca-46fbfcd36ec9 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS |  |  | system | eWall B |  |  |  | DCOS power line issue - Some power line is not shown with color when it is energised, some is showing with color when it is not energised. In general, the DCOS power line graphic for each equipment has variation to the real-time situation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204083&prj=501&rqi=WlIcp2Lw9EGZ34wu6hL33bjIWX | https://equinix.facilitygrid.co.uk/x/project/501/system/13008
GI-124 | 7d2340e6-eb0b-4dac-a465-5f6a98c347f3 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | It is observed that there is no status update under column "Total" and "Active". Please clarify any status when unit is running or having alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204095&prj=501&rqi=47LMl3nuYnHjCxfNCqhDPymSRZ
GI-137 | becfb79b-c181-472e-b108-71de6823e5b4 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  |  | system | DCOS |  |  |  | It is found that Environment sensor alarm cannot be shown in the alarm log (Area Hierarchy) Issue found on room temperature sensor at floor 6,9 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221089&prj=501&rqi=Da0yO8IEDTyWACxvcAOqu2cJJ5 | https://equinix.facilitygrid.co.uk/x/project/501/system/13006
GI-119 | 2a55df18-4c43-419e-812f-00d62ff1f044 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS |  |  | system | Rblock R |  |  |  | DCOS power line issue - Some power line is not shown with color when it is energised, some is showing with color when it is not energised. In general, the DCOS power line graphic for each equipment has variation to the real-time situation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204085&prj=501&rqi=hzvjVSFm5fTWPOR9emoBSEEaUc | https://equinix.facilitygrid.co.uk/x/project/501/system/13010
GI-136 | cda0aca0-b572-44e3-9f0a-93a0bd5510f3 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  |  | system | DCOS |  |  |  | It is found that SLA sensor reading have disconnection issue on DCOS. Please double check the configuration. Issue found on SLA sensors at 15/F DH1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221088&prj=501&rqi=xhqQH0qubHx2OSf26MMb3dqwg9 | https://equinix.facilitygrid.co.uk/x/project/501/system/13006
GI-127 | e2036ab7-4017-4435-819b-aa888198186b | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | Mechanical Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | It is observed that ATS alarm description is different with point schedule. Please clarify deviation with point schedule Normal source available (Rename as normal source not available) Alternative source available (Rename as alternative source not available) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204098&prj=501&rqi=YMtHV9ytGBCsnXZMFdRriwrYLx
GI-130 | 31cfa116-8839-4e8a-82ab-158c4f3907a4 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  |  | system | DCOS |  |  |  | Some SLA sensor faceplates are mal-functioning which is normal during the point-GUI test before. Issue found on SLA sensors at 15/F DH1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204123&prj=501&rqi=AW0a3FNSHx90AhPRomNuXj3H5Y | https://equinix.facilitygrid.co.uk/x/project/501/system/13006
GI-118 | 084b0310-9e9d-499c-b98a-d2da55756f9e | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS |  |  | system | meWall M1 |  |  |  | DCOS power line issue - Some power line is not shown with color when it is energised, some is showing with color when it is not energised. In general, the DCOS power line graphic for each equipment has variation to the real-time situation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204084&prj=501&rqi=Ynz2wFLmuzhQOxISDckIN7qOs6 | https://equinix.facilitygrid.co.uk/x/project/501/system/13009
GI-131 | 0a303dec-106f-4a4b-8ffc-1b31a90368de | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  |  | system | DCOS |  |  |  | It is found that SLA range is incorrectly set. Please confirm the setting and rectify it. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204124&prj=501&rqi=VxPQ6DsAqwBi1moo0hCS2qw1iA | https://equinix.facilitygrid.co.uk/x/project/501/system/13006
GI-128 | 4d136b1b-eaa4-42e6-8c8b-0e9d211ebdd0 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | It is observed that no command point is available on DCOS. Please clarify deviation with point schedule Chilled water valve command Return air temp setpoint Supply Air temp setpoint Supply Fan speed command | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204101&prj=501&rqi=VYzhcoybPcIkeKwTsHGJPUdfJX
GI-129 | 5df673a3-2533-4852-aaa9-2a673c608321 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | It is observed that these points are not available on DCOS. Please clarify deviation with point schedule Entering Water Temp kW Leaving Water Temp Supply fan command | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204102&prj=501&rqi=4Bm8wdBCQ4lxZl9eQc3lU9QRbH
GI-125 | 618f2ec7-5592-400e-a134-adb29e3b26bb | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | It is observed that no reading under column kW. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204096&prj=501&rqi=R9bsRQRwJcrpJFqg44SQUdJqPP
GI-123 | 65f4888f-d9f8-484a-a8d5-09ee2f0ea70b | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | It is observed that CRAH ATS on alternative status is off when normal source is resumed and ATS is counting down to transfer back to the normal source. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204094&prj=501&rqi=jE68dD3BtfKtMv4Ckc6kD8sBXp
GI-126 | d980ce4b-1185-4a8a-961e-804d767a05c4 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | It is observed site legend shows critical, high, medium, low alarm. In DCOS SICD document for CRAH, alarm severity is shown as urgent, high, low, inform. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204097&prj=501&rqi=9aMKc1L8aWPbqwhoX7FmeFOYdG
GI-122 | 678c7599-9fd8-4c9b-90b5-dcf4db0e55fd | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | It is observed that CRAH ATS alarm normal source not available alarm stay active even though normal source is resumed. Alarm returns to normal status after ATS transfer back to normal source. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204089&prj=501&rqi=AMJwAZd3YXvHANSCXRpXwXFjDt
GT1DCOS-30-001 | d0086fa9-607d-4f08-a9e3-8c67cefea78b | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_GWP_35 | DCOS - Control Panels |  |  | Full point-graphic report outstanding. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221095&prj=501&rqi=LzelQuUroI28sUOiwfmjz3oqsl
GT1MECH-2-002 | 4853ee91-118b-413c-afb5-c1c2f9f36e07 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS |  | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Supply air static pressure is showing supply air flow rate reading. Please clarify the deviation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204106&prj=501&rqi=NNvasMaZOGR4SvzJHagseRfnIR
GT1MECH-2-011 | a47f967c-d173-46c3-b482-4b542a4dbf88 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS |  | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Smoke detector alarm mapping mismatch. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204116&prj=501&rqi=9qPqBdbxYntrqVn3Bf0LquzE7E
GT1MECH-2-012 | c4315932-1a0d-4d31-9926-fac47e6d86b9 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS |  | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Supply air temperature setpoint is not available. MAU is controlled by supply air dewpoint temperature. Please clarify with GC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204117&prj=501&rqi=iXmgsrxM2vBfKXMQLYxmB70MMz
GT1MECH-2-005 | fa48123e-5903-42d9-a75a-a47851fedfa0 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS |  | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Humidifier command to be clarified. It shows in 'percentage' on GUI and functions as "Read" point which deviates with point schedule | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204109&prj=501&rqi=iBi0KgijFiC36rvVDZwUH04ODo
GT1MECH-2-008 | 7f16bf06-f6aa-496a-9156-cc90a5080299 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS |  | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Humidity setpoint is not available on DCOS. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204112&prj=501&rqi=vOihJvUxNhGh8lKcGuBAVtsGpZ
GT1MECH-2-007 | 60f46a33-a142-4a20-9806-eff2a8439830 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS |  | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Humidifier running status to be clarified. Individual running status should be provided on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204111&prj=501&rqi=a5qvBOyepcisk6oZpVJFenvSNq
GT1MECH-2-004 | c888c78d-e94a-445d-8cc9-2d4a2169788a | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS |  | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Chilled water valve command to be clarified. It functions as "Read" point which deviates with point schedule | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204108&prj=501&rqi=8KHTst0ZMV7IWaUPRIBGl1470R
GT1MECH-2-015 | cf25eee6-9d52-4506-a1c0-d93e3763006c | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS |  | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | EC fan kW unit to be checked. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204120&prj=501&rqi=wqNEgzTUfN13Ytk7WcRgxQsita
GT1MECH-2-010 | 64a7de86-a2cc-40e6-9acf-38ebb4b60417 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS |  | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | Outdoor air damper feedback to be clarified. It shows in 'percentage' on GUI which deviates with point schedule. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204115&prj=501&rqi=Jq8xJsrGb3WPa9aVzyGvkN2PoO
GT1MECH-2-014 | 20799dc6-d07d-45ad-a491-776d3a661273 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS |  | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | EC fan DC bus voltage is not available on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204119&prj=501&rqi=69jRGKo4xM5DL03A1OAB5VZtgm
GI-082 | 3b483903-3e89-4b16-bec4-adca4ba7b7fd | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | It is observed that CRAH ATS alarm cannot be reset by "acknowledge" button after power resume. Please double check the logic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199728&prj=501&rqi=6yO3lkuiGfv124asgU6CV6ilVx
GI-085 | 9bb08fd2-9f7e-49fe-8c60-c9665177fac5 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | FCU DCOS issue - further clarification required where one point on DCOS is not done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199731&prj=501&rqi=ax8wxQxKd42MP4rRM865km3S5u
GI-081 | 8a452b4e-6d71-4c88-9f56-b13268c9604e | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | Electrical Contractor |  | General Design issue | Design | [7 empty] | Fuel pump system SOO issue - during scenario where more than 8 generators sent signal for refilling fuel and a fault occur, pumps were not able to start up or changeover | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199725&prj=501&rqi=Xc4vrsCe6YNgpdT67Nku8RXz3H
GI-087 | 2d21e5d2-1055-43ed-9849-bbb1a692584b | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | BTMS DCOS communication issue - server is not ready and point is not checked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199734&prj=501&rqi=dxDMBmpT64FfOH4gWPrXYpIoAL
GI-084 | b3d323bd-71d8-41f6-8cb2-f5d2ac63700c | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | VRV point to graphic issue (control card issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199730&prj=501&rqi=vTgN2YrsDuMtn1sP83QToFOegX
GI-083 | 36c499e4-291a-43e0-96dd-13e69721305d | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS | [7 empty] | MAU graphic is not ready and self test has not done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199729&prj=501&rqi=iF3xOf2kdaTW9wTj1eNw9AOoPb
GI-086 | c6dadce5-3777-49f9-90e2-177a37128fea | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | VER - Vertiv Electrical |  | Commissioning Issue | Commissioning | [7 empty] | RPP DCIM point mapping issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199733&prj=501&rqi=9kmPHYoWqpcZ7xMez5xHtFll0d
GI-088 | 1d93b1ce-5601-49f8-a86d-932a6bc363e0 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | JeffChan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [7 empty] | Chiller logic on DCOS is not ready - some of the logic is not following the SOO even though it can run in auto mode | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199735&prj=501&rqi=HunBXNpKSeLVSs5Q58fnKCCuPc
GI-079 | 68123c9a-f6c8-4a60-a33c-c627f6ea2c08 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS |  |  | system | eWall A |  |  |  | DCOS power line issue - Some power line is not shown with color when it is energised, some is showing with color when it is not energised. In general, the DCOS power line graphic for each equipment has variation to the real-time situation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199630&prj=501&rqi=liJ1dl4FYaFFd5EKwegCSw4isR | https://equinix.facilitygrid.co.uk/x/project/501/system/13007
GI-080 | 0f9d8a9a-3485-436c-8307-ebc98f766674 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Fuel pump system Cx L4 - A total of 8 to 15 nos. of Genset hall fill requests, the full system cannot be operated if A1 & B1 of the pumps have a fault. - The full system cannot be operated if Special Changeover scenarios (Already 2 Pump Running, Possible request more than 3 Pump). Because the logic can let both pumps A1 & A2 run or both pumps B1 & B2 run. But it cannot operate any swap combination pattern, both pumps A&B running together. The system will be in â€œHungâ€ Status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199632&prj=501&rqi=rbBpGf5DUGjS9ybvr4oPImmPnt
GI-075 | 856c1dcf-6ca6-4f67-8254-1ea8a8519d1f | HK06-1 | 501 | APAC | Closed | P3 Low CX | keymanchan@commtechasia.com | 2026-02-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | BTMS (Busduct temperature monitoring system) 's DCOS part outstanding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199257&prj=501&rqi=IetCqIKAbsV5HuNzDP6z7nF6Ds
GI-074 | 226e331b-f3fc-4231-b054-73ff254bde37 | HK06-1 | 501 | APAC | Closed | P3 Low CX | leocheng@commtechasia.com | 2026-02-16 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | STSSB test report DCOS cap screen not fully completed. Pending Vertiv to coordinate with Schneider to collect all cap screen to finished test report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199253&prj=501&rqi=7WGNEmGAw2xMbqQMNOGvq6Vqnj
GI-070 | ebb56537-f180-4696-8539-45db603d4004 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | It is observed that there is no status update under column "Total" and "Active". Please clarify any status when unit is running or having alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199235&prj=501&rqi=g4g0bks3ZoWxW3y8kK41P7c6Fi
RT1MECH-3-001 | 76f38c81-3e63-4ac7-a6e1-f17d6bf0987c | HK06-1 | 501 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | HVAC | equipment | 1MAU_M2R1_3 | AHU - Air Handling Unit |  |  | Nameplate of 1MAU-M2R1-3 is showing different model number to the approved material submission. Approved model: A1(C)1330H-1050W, while onsite model number on nameplate is showing A1(C)1330H-1200W. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199229&prj=501&rqi=dRumjo2dXz1u6LjCgJKkZsnSZR
GI-069 | eb6e7ee5-d9a8-4dfd-8eb9-2d5f0115a753 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | ATS alarm log description should be aligned with the graphic description. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199233&prj=501&rqi=ea9on8PBQIMb4m50c6ZhxTcI3z
GI-072 | 8940438c-cb32-4c4e-8a36-e7a109ee8882 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | General Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | It is observed site legend shows critical, high, medium, low alarm. In DCOS SICD document for CRAH, alarm severity is shown as urgent, high, low, inform. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199237&prj=501&rqi=7zlwZxtQvBxVHsbhaQH96Rqtb1
GI-071 | 56d93240-c723-4df9-b536-6a877c88f0af | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | It is observed that no reading under column kW. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199236&prj=501&rqi=sA5t2hbDuOM2BxNAsWPp9ikqdG
GI-068 | ce864cb6-4ed5-4b1b-974b-3ef45f38e971 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | It is observed that CRAH ATS alarm cannot be reset by "acknowledge" button after power resumption. Please double check the logic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199232&prj=501&rqi=qDb78XZFU09MCLk8i82UiNAZJy
RT1MECH-2-001 | cfc63eab-f084-47a7-b3de-a7479a5f15b9 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | HVAC | equipment | 1MAU_M3R2_2 | AHU - Air Handling Unit |  |  | 1MAU_M3R2_2 panel affixed with un-updated equipment ID: 1MAU_M2R1_2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199234&prj=501&rqi=PVzBW9Yy9WsuUh83wQqEccUKJC
GI-073 | 82f3d6f2-ca92-47b6-8f2d-fc4e5c3b1ed9 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | VincentChung@commtechasia.com | 2026-02-14 04:00:00.000 +0400 | Mechanical Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | Entering Water Temperature kW Leaving Water Temperature Supply Fan Command Normal source available (Rename as normal source not available) Alternative source available (Rename as alternative source not available) Please provide clarification and confirmed with EOR for any changes | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199238&prj=501&rqi=TFBvhvvT8IjQ8uKSXRCzJ22hB8
GI-067 | ce11dd2b-3298-49ab-ba45-563aec4afdf3 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-13 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS | [7 empty] | Gen set L3 Fuel pump system point to point test & logic test issue 1. Is the global design graphic for the "Main Tank X lockout" point and alarm show in the pump information? Please clarify. (image 1) 2. In the DCOS graphic during whole fuel pump logic test & point test, all fuel running path are outstanding (image 2, image 3) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199208&prj=501&rqi=O0YmYED7Lt0zYKfm9xhGuHtiSu
GI-066 | 935914fe-9631-4e00-a71e-92bffc2fd17e | HK06-1 | 501 | APAC | Closed | P3 Low CX | JosephHalim@commtechasia.com | 2026-02-13 04:00:00.000 +0400 | General Contractor |  | Component/Equipment failure | Commissioning | [7 empty] | During dummy load test, dummy loader failed to startup. Was first reported that the unit control power shut down during testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199177&prj=501&rqi=WLosW4ZwDY5Fgh0CzwBwBly6nQ
GI-065 | 5d5aa247-defb-4a4b-bca6-a538c3f48f39 | HK06-1 | 501 | APAC | Closed | P3 Low DCOS | PerryLee@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | HVAC | equipment | 1EF_M3_7 | EF - Exhaust Fan |  |  | The exhaust fan type of 1EF_M3_7 in SOO not align with approved fan equipment schedule. In-line fan type approved in equipment schedule, however EC fan type approved in DCOS fan SOO | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199113&prj=501&rqi=ZLTxxjGdSHQwJB62ia3jDFwtcs
GI-063 | 130f9662-a033-4972-a960-7f7d839ab68c | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS | [7 empty] | RMU power path is incorrect. During Cx L4 testing for the RMU, when both of the incoming VCB is open, the power path connecting between both of the RMU is showing to have power floating, whereas the RMU is also shown to be energise to the downstream. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199102&prj=501&rqi=JyrO7eGGJRii13KttahnfmFLcA
GI-064 | 710b8b53-ac22-4d18-8b0c-5879ef82bfde | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [7 empty] | BTU 24 hr discharge test were not able to follow as per the playbook intention. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199105&prj=501&rqi=3HDgoR941RvO3zv5CkjviT5n8R
GI-061 | 62fd3599-a4b6-4e0e-8afe-9a6850b6d3c9 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | PerryLee@commtechasia.com | 2026-02-11 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning |  | HVAC | equipment | 1CHWSTR_M1R1_1_CWP_1 | CWP - Condenser Water Pump |  | Ebara | WCC and CHWP fail to start but fault alarm not triggered on DCOS due to incorrect set point | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198976&prj=501&rqi=omh17DHpiqJjVwGM16RN1DXlBk
GI-060 | 26fcfa4a-ad68-483c-9e7c-089e47db5557 | HK06-1 | 501 | APAC | Closed | P2 Medium DCOS | JeffChan@commtechasia.com | 2026-02-06 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS General Issue | DCOS | [7 empty] | DCOS graphic for chiller is not ready, immediately fix and solution must take action | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198686&prj=501&rqi=X6C4C1VWgsD03FJJUswuwtmzvN
GI-059 | 65e0a5ee-6022-465c-abb7-5eef5c4729be | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS | [7 empty] | RMU point has issue during Cx L4 During the Cx L4 test for RMU, when one of the VCB is opened, the DCOS graphic for the RMU went offline. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198474&prj=501&rqi=JCxrApTGBTmEekBwKE1G3l1ffJ
GI-056 | 0b40a51d-b099-46ac-995b-ca8d4d018d71 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [7 empty] | DCOS and the network is super slow which it has slowed down the T&C process | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198319&prj=501&rqi=VSU6gjGlkhFcu455pZGK4tSjUp
GI-058 | 10be260a-19cd-4db6-aa44-326ce656ad94 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [7 empty] | UPS did not exit ESS mode when it is performing 0% to 50% step load | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198323&prj=501&rqi=tVVXQOmJdv0aSlkpTudChjYCcV
GI-057 | f120c68e-a60b-4f6f-af89-2908e1ac5a0d | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | SCH - Schneider MV |  | General Design issue | Design | [7 empty] | BTU for SUDB not able to do 24hr discharge | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198320&prj=501&rqi=fwTIdKwEr2AnZbHd7ypGw6maZR
GI-049 | 40415ac7-b6ec-43de-a395-0fa064b56c33 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | As per SOO, remaining fan will ramp up to maximum speed. It is observed that CRAH unit in group control mode will be ramp up to maximum fan speed and stop running afterward when single fan within CRAH is failed. Please clarify the discrepancy. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198224&prj=501&rqi=2s613a1cxQn2OCZ1cBaFzpgSlj
GI-041 | 86b9ab87-9c0f-4f69-87b0-1d3b39d6da2a | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | General Design issue | Design | [7 empty] | When the transformer is de-energized with high temperature trip, power loss to the transformer control power because the incoming control power is coming from one of the DB in MSB which does not have any UPS power back up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198186&prj=501&rqi=Pidls5OLmQur0kK5wS7U6Su8Vm
GI-047 | bcab08be-7d1d-4b37-b260-f6b74c9770bf | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | It is observed that CRAH unit in group mode consider highest RAT and SAT reading for fan speed and valve control. High / low return air temperature and supply air temperature alarm activation also follow the same logic. Please clarify whether it fulfills design intent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198221&prj=501&rqi=10ty1XmMdExfCDcts0gjy73hi1
GI-045 | 8b51043b-a7e0-41a6-8e03-c1f6204188c5 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | It is observed that CRAH supply and return air temperature in group mode is showing the group control temperature on DCOS(All units have the same reading on DCOS). Individual CRAH unit temperature reading cannot be shown on DCOS. Please clarify whether it fulfills design intent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198217&prj=501&rqi=pSH4w7t7qGQrGkgA4DwXwY0lOI
GI-055 | 20052c29-b852-4ac1-a426-1ab3448593c1 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | It is observed that CRAH ATS on alternative status is off when normal source is resumed and ATS is counting down to transfer back to the normal source. (DCOS) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198233&prj=501&rqi=9LZ41MssmvQSeYJ8GVDV0awcHk
GI-040 | e6a8c9d1-97f3-4a69-982f-2099f1d0230d | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | Missing cover for remote air temperature sensor for CRAH. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197702&prj=501&rqi=uZiBas6KDBmgJZJtH4NQhfvd48
GI-052 | fcc0ef47-89bc-40cf-a5cc-78cb80ee9d29 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | As per SOO, CHW valve will be opened to Vmax position. It is observed that CHW valve will close after lost of command signal. Please clarify the deviation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198229&prj=501&rqi=vkJID1XI0XPcbM8L7dRwvVJKPv
GI-043 | e254ee53-72b3-4ea4-afbc-634bdccaddb1 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | Please confirm remote temperature setpoint in UPS Room. As per SOO, the setpoint is 27degC. It is observed that CRAH in UPS Room is operating at 60% at low load conditions. Return air temperature (from remote temperature reading) is around 25 degC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198215&prj=501&rqi=YfxXxN037iaVBG8ZrXWZ28m6iy
GI-046 | dbef0dc9-9cf1-45af-8626-a484528316ad | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | As per SOO, CRAH equips with in-built return air temperature sensor in Lv Switch Room and in-built return air temperature sensor with humidity in DataHall. It is observed that in-built return air temperature reading is excluded. Please clarify whether it fulfills design intent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198219&prj=501&rqi=gklrWIQqIV2MnOQlJdYBKZNfD0
GI-048 | 4cd1969d-f6e0-493f-b8b3-0c7dadbb08a6 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | As per SOO, fan speed will ramp to meet the setpoint if remote temperature reading is higher than setpoint, vice versa. It is observed that fan speed will ramp when remote temperature is getting closer to setpoint. Please clarify PID / proportional band setting for CRAH fan speed control and update equipment setting table for fan speed control. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198223&prj=501&rqi=9V5oAdcD0gjfV3wGFyUykzhvU1
GI-051 | f42dd3b5-5401-433c-8054-f8d3231eeeff | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | It is observed that CRAH unit requires a close contact for VAC trip while â€œNOâ€ contact is a common practice for fail safe purpose. Please clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198228&prj=501&rqi=INBovAiThriMgaQhARs8luBw4O
GI-054 | bd77682c-f12e-48eb-8965-4d2c11a1abb7 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | It is observed that multiple CRAH units supply air grille are damaged and the condition of SAGs are deteriorating. Please provide a schedule for replacement work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198231&prj=501&rqi=yWvVvE6WeUaLT4KLmaAQDr6MNB
GI-042 | edbd07cf-b6cb-49e1-a9f4-107007cd7825 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | Please confirm ATS setting for CRAH in UPS Room that is not supplied by UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198208&prj=501&rqi=Wpr01ZRXMuS5t9Wg0ae3IfQFbB
GI-050 | 5ac33730-e8e5-492c-b4f7-ec66c4e8c651 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | It is observed that no alarm will be raised on controller under dual power failure condition. It is deviated with SOO. Please clarify the discrepancy. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198227&prj=501&rqi=h3FpZ6aRPLApSBJCyuZFeidQba
GI-044 | 115c7544-4404-4e67-9524-4ff96e82b5d7 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | CRAH fan speed is controlled by return air temperature reading while return air temperature consider highest CRAH unit average remote temperature reading in group for calculation. Please clarify whether it fulfills design intent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198216&prj=501&rqi=5zugaZtRjUT2IQkwIwjuOaS0Y7
GI-039 | ea71c16b-20a4-4341-a00f-eb635b295c6c | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-01-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | DCOS network is not stable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197602&prj=501&rqi=rZaLq7llrqgyxQDBo0GnxrhjZn
GI-038 | b33b2198-f94b-4d66-9e5a-b5b608cd3797 | HK06-1 | 501 | APAC | Closed | P3 Low CX | JeffChan@commtechasia.com | 2026-01-26 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [7 empty] | UPS physical damage for UPS L12, L13, L15, L17 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197553&prj=501&rqi=Rzoi0vCthRxPBqfZjZ3ZK6Ec7M
GT1ELEC-36-001 | 31010eb3-78b8-4ea3-a71b-ed1ab0769544 | HK06-1 | 501 | APAC | Closed | P3 Low CX | lawkwokfai@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Construction Manager | L3 | Commissioning Issue | Commissioning |  | Electrical | equipment | 1ATSMI_M1R1_27 (1ATSMI_M1R1_34) | ATS - Automatic Transfer Switch |  |  | ATS ID number do not match DCOS; B-C & A-C have 54V shown on display and DCOS when power off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197442&prj=501&rqi=hcaSUFtpXMNKbiCrgWegwv8Khl
GT1ELEC-32-001 | e6e27edc-d124-46a4-9822-c6c2a05c7a00 | HK06-1 | 501 | APAC | Closed | P3 Low CX | lawkwokfai@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Construction Manager | L3 | Commissioning Issue | Commissioning |  | Electrical | equipment | 1ATSMI_M1R1_26 (1ATSMI_M1R1_33) | ATS - Automatic Transfer Switch |  |  | ATS ID number do not match DCOS; B-C & A-C have 54V shown on display and DCOS when power off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197441&prj=501&rqi=80erVR6J7dN7z8WRQZxwKivNuF
GT1ELEC-30-001 | c4e98927-3f89-4a35-ab58-1065eb9dde7c | HK06-1 | 501 | APAC | Closed | P3 Low CX | lawkwokfai@commtechasia.com | 2026-01-21 04:00:00.000 +0400 | Construction Manager | L3 | Commissioning Issue | Commissioning |  | Electrical | equipment | 1ATSMI_M1R1_24 (1ATSMI_M1R1_31) | ATS - Automatic Transfer Switch |  |  | Communication alarm test with DCOS fail, device name matched drawing and FG but not match DCOS, B-C and A-C have 54V shown on display and DCOS when power off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197306&prj=501&rqi=qhRZucn17wS4ySO2O7ntjesUFx
GI-037 | 7a903662-3c55-4b1e-98c1-b80a72fbefd5 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | It is observed that ATS Alarm - Normal source not available and alternative source not available alarm was shown on DCOS graphic which are deviated with point schedule. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197243&prj=501&rqi=7ybUtm1MczASfhpiZhwMWGe2LG
RT1MECH-211-001 | 2307f6e0-7e18-4f78-bd54-397192818f4e | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning |  | HVAC | equipment | 1EF_L_2 | EF - Exhaust Fan |  |  | Installation of motion sensor will be verified at Cx3 after completion of fitting out work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197098&prj=501&rqi=I3MLoUKRRBrW5CEEqTu5Egx4rD
RT1MECH-210-001 | 9c3506aa-82a2-4e80-a326-e869c0e34c33 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning |  | HVAC | equipment | 1EF_L_1 | EF - Exhaust Fan |  |  | Installation of motion sensor will be verified at Cx3 after completion of fitting out work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197097&prj=501&rqi=MRMfF1KOuw5xqyAcYUY7ndc81C
RT1MECH-102-001 | 5385d7dd-dcf1-4889-ad36-c10eeae30a45 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning |  | HVAC | equipment | 1EF_A_1 | EF - Exhaust Fan |  |  | Installation of motion sensor will be verified at Cx3 after completion of fitting out work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197096&prj=501&rqi=x44q9S8BPzi6sECQFgZ1yA7udF
GT1ELEC-31-001 | de2a3dbd-7c11-4aed-b726-3d683f4845c6 | HK06-1 | 501 | APAC | Closed | P3 Low CX | lawkwokfai@commtechasia.com | 2026-01-16 04:00:00.000 +0400 | Construction Manager | L3 | Commissioning Issue | Commissioning |  | Electrical | equipment | 1ATSMI_M1R1_25 (1ATSMI_M1R1_32) | ATS - Automatic Transfer Switch |  |  | Communication alarm test fail, device name match drawing and FG but not match DCOS. B-C & A-C have 54V shown on display and DCOS when power off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197312&prj=501&rqi=oKHNSQf3rep6cydKfWR5B3UTh6
GI-036 | 1a34f78a-ac3f-4159-9059-1c438b290df6 | HK06-1 | 501 | APAC | Closed | P2 Medium CX | JeffChan@commtechasia.com | 2026-01-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | 1. ATS equipment ID not aligned between DCOS and on-site layout. 2. Communication alarm only response when both sources is detected with 0V which it should not be the case. 3. When the main source of the ATS is simulate with lose of power, main source still detect with around 50V on phase to phase, this happen same to the alternative source of the ATS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197062&prj=501&rqi=hEyBrRxXA8Sg9kekrROSMWUKKf
YT1MECH-237-001 | eee45921-c553-42db-a06a-31158182ca31 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-02 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | HVAC | equipment | 1FCU_R2_54 | FCU - Fan Coil Unit |  |  | Scratches were found on LMCP casing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196249&prj=501&rqi=T9yxqN1vXnHtYM0YCEtWOPNPaf
YT1MECH-247-001 | f81515ee-3f51-497d-825e-b09d5d427fe6 | HK06-1 | 501 | APAC | Closed | P3 Low CX | VincentChung@commtechasia.com | 2026-01-02 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | HVAC | equipment | 1FCU_M3R2_53 | FCU - Fan Coil Unit |  |  | Scratches were found on LMCP casing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196248&prj=501&rqi=Bkbvvy5Qm5wHTNhcHdl0uUajiB
YT1ELEC-419-001 | dad8176b-8fe4-49f2-80e5-238c3525a80a | IL03-1 | 609 | S-EMEA | Open | P3 Low CX | o.alemdag@core-group.me | 2026-09-15 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | Trace Heating (Chilled Water) | TRACE - Trace Heating |  |  | L2b_Elec_OA: There are defects on this panel as follows. Pictures are also attached. * Cables routed on earth bar * Two cable lugs connected at a single termination point * Deep cleaning required * Missing bolt connection * Missing cable tray covers * Missing covers at panel bottom * Sealing issue identified * Missing torque marks on connections * Improper cable lug installation * Earth cables must be yellow-green | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638086&prj=609&rqi=rvBQ05Q74IfJmq9PX5LW0A4IMh
GT1MECH-378-001 | 1d455098-7821-460e-8170-5eac4bac8c58 | IL03-1 | 609 | S-EMEA | Open | P3 Low CX | s.collier@core-group.me | 2026-09-15 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | General Design Issue | Design |  | Electrical | equipment | 1HWS_C_1 | HWS - Water Heater |  |  | The access to maintain HWS C1&3 is very limited and may need ceiling removed to replace the Heater if required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638114&prj=609&rqi=h1pOALEan7s2gXcQlJRH3PldS1
GT1MECH-136-001 | 7d6b0797-3512-41b0-9f83-f6d22198b9fe | IL03-1 | 609 | S-EMEA | Open | P3 Low CX | k.erbay@core-group.me | 2026-09-03 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Installation Damage | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_R_01 | CRAH - Technical Room CRAHs |  |  | The ventilation grille's louver is damaged and the mounting screws are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636649&prj=609&rqi=u1qgLz0Y2BYS7VSvofZ82gLX0f
GT1FS-222-001 | 5001d912-dd6b-4db5-99d4-9c69635819d8 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | o.alemdag@core-group.me | 2026-08-18 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Component/Equipment Failure | Commissioning |  | Fire Suppression | equipment | 1MFD_C_62 | FD - Fire Damper |  |  | L3_Electrical_OA: There is an issue during L3 test, C _62 damper open-close status could not be completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634100&prj=609&rqi=S8ec3tpUavpPUFl6o84yrqte5F
L2L3 Sun-159-002 | 3ebfb877-6430-43fb-a4ff-b6dcecd466c1 | IL03-1 | 609 | S-EMEA | Open | P3 Low CX | o.alemdag@core-group.me | 2026-08-18 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning |  |  | equipment | PAVA Main Equipment Rack | PAVA Main Equipment Rack |  |  | L2b_Electrical_OA: During L2b inspection, following issues are found the PAVA panel in the security room. * Panel fans, some bolts and covers are rusted. Please check Image 1. * Battery connections are not completed. Check Image 2. * There is still un-terminated cable in the panel. Check Image 3. * There is high dust, foreing objects inside and around the panel. * Cable entry from above is not sealed. Covers in bottom side of the panel is not completed. Check Image 4. * Panel humidifier or thermostat setting must be set as per required value. Check Image 5. * It is not clearly visible which cable connection is done each zone. There is no label on the panel racks etc. Check Image 5. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634095&prj=609&rqi=pO21NbWfpqyJL9RhatHzzS0NZa
YT1SEC-37-001 | 3b40187a-27b9-47a3-b0aa-5fb559416a9a | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | o.alemdag@core-group.me | 2026-08-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning |  | Electrical | equipment | NIRB.0101 | ICT Racks |  |  | L2B_Electrical_OA: Missing equipment ID tags especially AV sockets etc. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632728&prj=609&rqi=QzWxVOYsnLdD6tMgolDslsPtYV
GT1MECH-44-001 | 72ad9c9e-2a2a-45f5-a6c3-844a72424862 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-08-03 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_A_17 | CRAH - Technical Room CRAHs |  |  | The equipment label on the CRAH unit is damaged and partially illegible. It needs to be replaced. This applies to the CRAH units listed below. -1CRAH_A_17 -1CRAH_A_18 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631994&prj=609&rqi=vLQNnYAOtO33zplMspvUhYckmV
YT1ELEC-34-001 | a09f48b1-fd23-4ea4-8005-dff7c4d1e30a | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | a.tuysuz@core-group.me | 2026-07-20 04:00:00.000 +0400 | CMM - Cummins | L2B | Component/Equipment Failure | Commissioning |  | Electrical â€“ MV | equipment | 1-GEN-B | GEN - Generator (MV) |  |  | During the MV route checks from 1-GRMU-C to 1ZZTRMU_A, cracks were observed on the MV termination kits (Euromold type) installed at the incomer connection from the Gen-B alternator to 1-1GRMU-B. The MV cable connection between the generator alternator and the GRMU incomer shall be thoroughly inspected. The cracked termination kit shall be replaced with a new approved termination kit and the cable shall be tested following the replacement. A cable test report shall be prepared and submitted for all generator-to-GRMU incomer cables. The report shall include, at a minimum, two clear photographs demonstrating that the cable termination kits are installed correctly and are free from defects. This comment is applicable to all Generator sets and their respective GRMU incomers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630007&prj=609&rqi=mT0c0OPnWucBPGW7mmjmZTzF3G
RT1ELEC-32-005 | 5ed6e492-4438-4a48-8c2b-f621b948fdac | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | a.tuysuz@core-group.me | 2026-07-08 04:00:00.000 +0400 | CMM - Cummins | L2A | Design not as specified | Design |  | Electrical â€“ MV | equipment | 1-GEN-A | GEN - Generator (MV) |  |  | Regarding the ARUP / Generator Earth Bar technical submittal and the design correspondence below dated 07/07/2026 at 10:17 AM, the earth bar inside each genset container shall be rectified in accordance with the approved technical submittal and the requirements outlined in the email. This requirement is applicable to all Gensets. "The removable link shall be incorporated into the generator earth bar arrangement as indicated in the approved Cummins shop drawings. This requirement was raised during the QA/QCâ€“FAT visit, formally noted, and subsequently reminded. To remain fully aligned with the design intent, the incomer connections originating from the transformer room, local earth rods, and the serial bonding conductors between generator earth bars shall be terminated on the opposite side of the removable link, as shown in the shop drawings. This arrangement is necessary to maintain compliance with the approved design." | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628430&prj=609&rqi=vazeUkQarcOBoegr6WbvuHrgKU
RT1ELEC-32-006 | 0e6dc3f3-0bce-484b-84a9-92e4ca525c94 | IL03-1 | 609 | S-EMEA | Open | P3 Low CX | a.tuysuz@core-group.me | 2026-07-08 04:00:00.000 +0400 | CMM - Cummins | L2A | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1-GEN-A | GEN - Generator (MV) |  |  | Regarding the ARUP exit signage and emergency lighting fixtures used in the GEN-SET area, and with reference to the correspondence below dated Thursday, 21 May 2026, at 3:47 PM, please note that the lighting fixtures inside the containers shall be fully replaced with self-contained emergency luminaires,And external lights to be provided over all acces doors. This requirement is applicable to all GEN-SET containers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628431&prj=609&rqi=kEbnMdCi4Q1ScawLsLdtdaBVTq
L2L3 Sun-159-001 | 057f0274-4eea-40b6-95f6-3cfb1a5c007a | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | w.tavares@core-group.me | 2026-06-26 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning |  |  | equipment | PAVA Main Equipment Rack | PAVA Main Equipment Rack |  |  | During the L2B inspection it was found that same PAVA speakers need to be replaced, and the Cleaning has not been Completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627061&prj=609&rqi=Ss457l14zrGPqVlAeGdjMTv1lW
GI-027 | b629bc2d-c49d-4d11-bf8e-7dc7b1bd8956 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-19 04:00:00.000 +0400 | SCH - Schneider MV |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Closing interlock logic in C264: mismatch between software and wiring. There seems to have been a wiring change in the C264 interlock output contact (change from NC to NO). These wires have different labels than factory wiring. Now the latest software update in 264 matches the original wiring Even the drawings are confusing. On one page there is NC contact, on another page is NO contact. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626239&prj=609&rqi=NP8BQTLFPpfdUoZmu3I6aL40vt
GI-024 | 1559c193-0574-35b4-3368-f3eb2ae0fe17 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-17 04:00:00.000 +0400 | General Contractor |  | General Design Issue | Design | [7 empty] | Personel cannot be evacuated safely in case of an urgent, rapid evacuation. if someone goes out rapidly from the gemerator enclosure it would find itself trapped on the plantform, on the side without ladder | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625750&prj=609&rqi=DXnn5G70rPpGxZ459whdUPmyFI
GI-023 | 0b80dc3d-9d2b-7847-257d-a0d0534d85f6 | IL03-1 | 609 | S-EMEA | Open | P3 Low CX | i.vasilescu@core-group.me | 2026-06-17 04:00:00.000 +0400 | CMM - Cummins |  | Installation not correct | Commissioning | [7 empty] | MV cable tray is not secured against seismic risks. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625749&prj=609&rqi=zf0rx59EMeFxiRUuT11Dh4IkFk
GI-022 | 9bb19e7a-bfc5-4128-bc63-e62ca6511b85 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-17 04:00:00.000 +0400 | SOC - Socomec |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Internal STSSB power connection found not torqued during ispection. (section right after the bus bar flange - see attached picture). This was torqued and marked during the inspection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625585&prj=609&rqi=RsWS0Wg7LV2wJJeV1QtWsI55NM
GT1ELEC-15-005 | be22ac84-a175-4810-b1f9-c280af25472f | IL03-1 | 609 | S-EMEA | Closed | P1 High CX | m.yerkoylu@core-group.me | 2026-06-16 04:00:00.000 +0400 | SCH - Schneider MV | L3 | Component/Equipment Failure | Commissioning |  | Electrical â€“ MV | equipment | 1PUSP_2 | PUSP - Primary Utility Supply Panel |  |  | The L3 phase connection to the Voltage Transformer (VT) experienced an arc flash event. The VTs appear to remain structurally intact; however, arc flash marks were observed on the top surface of the L3 VT and around the L3 cable boot. The protective top cover at the L3 cable termination on the VT side was found dislodged following the incident. The VT enclosure sustained mechanical damage, with localized outward bending of the panel, but no internal components were exposed. Inspection of the L3 VT secondary wiring revealed no apparent damage to the cables themselves; only the protective sleeving showed signs of arc flash damage. It should be noted that the L3 VT and its associated cabling were factory-installed, terminated, and tested by the MCE vendor, and were delivered to site as a complete assembled package. No personnel were present in the room at the time of the incident, and no injuries were reported. Photos are attached. MCE/GC to provide RCA accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625471&prj=609&rqi=6p5HZxy0ZwduqA9CsvhLRvIJNK
GI-021 | 768ec73d-6ca2-df6e-c181-df033629fe47 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-11 04:00:00.000 +0400 | SCH - Schneider MV |  | General Design Issue | Design |  |  | equipment type |  |  |  |  | MV commissionability: trip signals should be made available through the test block. otherwise, with each maintenance these wires will be tampered with | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625308&prj=609&rqi=u3YRK5934Vv5ZVgJ28MUo3IgGm
GI-017 | 6569b3f0-1c51-9835-36f5-196a13a258b7 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  |  | equipment type |  |  |  |  | TRIP OUTPUT needs to LATCHED! | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623668&prj=609&rqi=GxzEQRULTrfnqS1LnLfLY9fGPk
GI-016 | 317d1598-8629-ecfb-ae3d-d53930504182 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  |  | equipment type |  |  |  |  | this contact needs to be NO. to be modified in PUSP1 as well. attach picture with evidence to close it | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623667&prj=609&rqi=bYtpWPW9csiAeFS8eNbcTvOltH
GI-018 | db22a03f-2508-0b1a-c76b-f77a09dd6550 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider MV |  | Incomplete Connections | Commissioning |  |  | equipment type |  |  |  |  | trip circuit supervision inputs are both active when according to schematics only one should be active (return path through CB position) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623669&prj=609&rqi=D6AT89JejRoKDVHJ7yjLZWGvjK
YT1MECH-412-001 | 4e418272-b89e-4a32-a3a9-cdfabafc2514 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-06-02 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Design correction needed | Design |  | Fuel | equipment | Fuel -Oil System-GEN-R | FFIL - Fuel Fill System |  |  | Access to the daily fuel tank is inadequate. The piping/valves structures installed in front of the access area restrict maintenance access and should be reviewed against the clearance requirements specified in the approved drawings. In addition, sufficient access is not available to fully open the louvre doors on the generator enclosure. A permanent access platform shall be provided to ensure safe operation, inspection, and maintenance activities in accordance with HSE requirements and the manufacturer's recommended clearance requirements. Applicable to all GEN Sets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623642&prj=609&rqi=9t5FrMvICmrI4TtfbxHg9H3jpW
GT1ELEC-15-004 | f8b5ed60-835a-315f-1750-0baba36652ba | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider MV | L3 | Design correction needed | Design |  | Electrical â€“ MV | equipment | 1PUSP_2 | PUSP - Primary Utility Supply Panel |  |  | spare contact for trip lockout is wired to a NC contact. this should be wired to NO contact. change in PUSP1 as well | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623666&prj=609&rqi=0onrJ6JcbF6PP9zOECwigyJZgc
GT1ELEC-15-003 | c470b99b-759e-ac45-5fdc-2aa1e6cdad91 | IL03-1 | 609 | S-EMEA | Closed | P3 Low DCOS | i.vasilescu@core-group.me | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS Design Issue | DCOS |  | Electrical â€“ MV | equipment | 1PUSP_2 | PUSP - Primary Utility Supply Panel |  |  | this "alarm" needs to be properly defined. at the moment, with cb open, the alarm changes its status just by changing the disconnector | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623665&prj=609&rqi=yQTi6CprdLtD0PptaYUm4yinUi
GI-014 | 8f5ff649-5be4-136c-e81a-8d398d333d19 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-21 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  |  | system | MV System |  |  |  | Cables from Control circuits need the have their screen earthed on one end. attached, in the picture, are current measurements from SUDB. to PUSP. its screen is not earthed on any side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622687&prj=609&rqi=P0lofEGBsOVr05QU7d7Cb162Bf | https://equinix.facilitygrid.co.uk/x/project/609/system/12241
GI-012 | f19b5a63-8e31-6415-431a-0c188d77a6e5 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-21 04:00:00.000 +0400 | SCH - Schneider MV |  | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1PUSP_1 | PUSP - Primary Utility Supply Panel |  |  | current measurement cable cannot be of a colour identical to grounding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622675&prj=609&rqi=LQ5OdQ3re4qtVfyHbHegVgnXbc
GI-013 | 61c21d71-9237-e556-0001-565dc1847577 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-21 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  |  | equipment type |  |  |  |  | Current measurement circuits need to have one point of earthing on star point. currently, the circuits coming from SUDB to PUSP is not earthed. a temp link has been made in PUSP1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622686&prj=609&rqi=S9rZpYLZXDODl690uW5ugXmGkl
YT1MECH-49-001 | 2ea7041e-523c-4396-a918-c2c8b8ac6984 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_A_18 | CRAH - Technical Room CRAHs |  |  | The left panel/cover of the CRAH unit was damaged (see attached photo) and needs to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622539&prj=609&rqi=XdWXX6Me0J8vyk0fEyx0Y7hR4d
YT1MECH-48-001 | 3efdb1a4-02b8-48a5-bcd5-9c156dd17f77 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation Damage | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_A_17 | CRAH - Technical Room CRAHs |  |  | The grilles of the CRAH unit was damaged (see attached photo) and needs to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622541&prj=609&rqi=fOHR3AiE9EIfASg3IfVsi5sLGK
YT1ELEC-35-001 | 7ef521dc-4605-498f-a63d-f9d5c985cfed | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | a.tuysuz@core-group.me | 2026-05-18 04:00:00.000 +0400 | CMM - Cummins | L2B | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1-GEN-C | GEN - Generator (MV) |  |  | During the L2B inspection of 1-GEN-C comments are listed below. 1- GEN SETs pressure test reports for pipework and day tank shall be added to the L2B documentation. (Previous phase test document is attached.) 2- Pressure gauge calibration certificates shall be added to the L2B test documentation. 3- Sleeves shall be installed at the each MV cable tray joints, and the sections which is contact on MV cables shall be cut/trimmed accordingly. 4- The gap between the deck ladder and the walking platform shall be closed. 5- The GRMU MV cable glands shall be tightened at the bottom. 6- Floor openings shall be closed. ( General comment ) 7- It was observed that particles are present inside The batteries and alternator.Cleaning is done not enough. 8- Rusted IMC conduits shall be cleaned in accordance with the applicable procedure/standard. 9-Emergency lighting fixtures and signage have not been installed on the doors.( Please provide tech submittal ) 10-LV and ELV cables shall be properly rectified, as the current installation is not sufficient. 11-General and detailed cleaning of all equipment parts shall be completed. 12-Equipment (lighting switches, power outlets, etc.) shall be labeled according to the DBL circuits, not according to the cable schedule. The items listed above are applicable to both 1-GEN-C and 1-GEN-B. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622152&prj=609&rqi=RG3h5yXqgR3niOAvT5GZYOIsIy
GI-008 | d8e8ca38-754f-41ff-b687-dc530902d700 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Design correction needed | Design |  |  | equipment type |  |  |  |  | PUSP - Tx Feeder- Isolator Switch Position is not present in DOCS Every HV equipment position needs to be present in DCOS one way or another | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621864&prj=609&rqi=7H1SgOC80c8TycTIzlc4v77czN
GT1ELEC-14-002 | e61547a7-8c09-48b5-beb9-0c4e28d1610f | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS Graphics Issue | DCOS |  | Electrical â€“ MV | equipment type | PUSP - Primary Utility Supply Panel | PUSP - Primary Utility Supply Panel |  |  | PUSP Power Meter shows a frequency alarm when the line is simply disconnected. Alarm should be filtered if it's out of range during operation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621854&prj=609&rqi=aw6iMVhWwkJBFO28DmNtGRxyxv
GI-009 | 88a10366-5a23-44cf-9e67-049687526843 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1PUSP_1 | PUSP - Primary Utility Supply Panel |  |  | PUSP - Feeder - current measurement cables don't have labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621865&prj=609&rqi=GwkU5om5ZRXnGWZ5KJo18Rzn2m
GI-004 | 01bafade-a94a-4374-a90c-74c392900f10 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  |  | equipment type |  |  |  |  | P643 Current circuits: 34kV outgoing cable Core Balance CT is not wired as per relay manual. NER CT not present in the design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621792&prj=609&rqi=5aXGIIT5oIESEVGLP8Jo0V8CTK
GI-003 | f1935978-36c8-41c5-bf89-3820861bd9d2 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Three wires are are not permitted in the same terminal. RON should get in contact with SCH and ARUP to check the two options: - add extra terminals in PUSP control panel (preferred method) - use a 4wire measurement circuit. A ready for verification status from RON should be set once an answer from ARUP is obtained | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621790&prj=609&rqi=ZlwKA9F6NnZ3plso8I0XgH2NVt
GI-010 | 02633ca9-e5b6-4adb-bc8c-4150a79442a2 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  |  | equipment type |  |  |  |  | PUSP - TX Feeder - Local/Remote button not wired into relay, can't be made available in DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621867&prj=609&rqi=SsmNcStpT4tWRuu7K2FS0gbrrS
GI-011 | ecbe32e5-901a-44f3-85d9-3cd6ed5e8839 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | PUSP - Trip Lockout signal is not latched in the relay. DCOS status won't show if a relay tripped the Circuit Breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621870&prj=609&rqi=OFeMloyhjHjLedrQp10nZVdl6G
GT1ELEC-14-001 | d3e70229-22dc-4ada-9ecf-6a4e59b2867f | IL03-1 | 609 | S-EMEA | Open | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV | L3 | Installation Damage | Commissioning |  | Electrical â€“ MV | equipment | 1PUSP_1 | PUSP - Primary Utility Supply Panel |  |  | Pendant CB status not working (light bulbs are missing) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621853&prj=609&rqi=u4DCdscagZnISWBqzQSLz0gVZX
GI-002 | 63997db5-c8f1-4985-abd2-88e790284581 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | The wires connecting the Current Transformers from SUDB to PUSP have a cross section of 2.5sqmm and they might be too thin (but as per design IL031-RON-ZZ-ZZ-SH-E-POWR-6103). Schneider to confirm that the used wire on site is the correct one by updating the IL31 - MV Network CT/VT Calculation document (IL031-SCH-ZZ-ZZ-CA-IC-MVSWGR-7009.pdf). At the moment this situation is not covered in the design. Add a calculation chapter for the CT connecting SUDB to PUSP., prove calculation with a 2.5sqmm and the length from SUDB to PUSP is within limits | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621786&prj=609&rqi=XrSGBKTSySsWfjI6PKwRS0MTCY
GI-006 | d91096fd-2547-4c5d-b930-136846003f91 | IL03-1 | 609 | S-EMEA | Closed | P3 Low DCOS | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS |  | Electrical â€“ MV | equipment | 1PUSP_1 | PUSP - Primary Utility Supply Panel |  |  | PUSP Bay numbers (Q01, Q02) don't match the ones from DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621857&prj=609&rqi=9W9d0JV3T6vyAeQKY9As30EkNh
GI-007 | b56b4586-0441-41c9-8d20-5fc9d9c4c912 | IL03-1 | 609 | S-EMEA | Closed | P3 Low DCOS | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | PUSP - "Alarm" The tag of this signal should be changed to be self explanatory. It is supposed to be voltage presence. Both alarms are active if the Voltage Transformer is not energized - Bus without voltage. As a minimum, the "Alarm" should be changed to "Bus voltage absent". Need to clarify the actual function of this button | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621859&prj=609&rqi=X0x2Y44aZCnWINO2dzP4PFli9x
GI-005 | e7f470ea-783f-4f67-a13e-52c2c33f9ec6 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | i.vasilescu@core-group.me | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider MV |  | Design correction needed | Design |  |  | equipment type |  |  |  |  | Breaker failure protection functionality in PUSP is reversed. Incomer sends trip to Feeder, when it was supposed to be the other way around. (executed as per drawing) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621852&prj=609&rqi=rUxEOatiQkMhgbJOv7yPeDM74M
YT1MECH-405-001 | a35471e3-35a8-41bf-81b0-3b84bff5cf4f | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-05-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Design correction needed | Design |  | Mechanical â€“ Water | equipment | 1TST_1 | CHWBT - Chilled water buffer tank |  |  | It was observed on the buffer tank recharge line that a sudden reduction from DN200 to DN80 may create an excessive increase in velocity and pressure loss. In common site practice, a maximum reduction of two nominal pipe sizes is considered acceptable. For larger reductions, a staged reduction is recommended. Confirmation by the EOR is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620694&prj=609&rqi=sIs6CpsvLTzhGsFZsm1yLSDnsa
YT1FS-94-001 | 9bfb2e29-8f2c-4024-8a48-c43588cb768b | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-05-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning |  | Fire Suppression | equipment | 1MFD_C_1 | FD - Fire Damper |  |  | Permanent asset label is missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620354&prj=609&rqi=N8UtYwXHxuNDVkYY4TUslVN2Ye
RT1ELEC-332-001 | 7517b89b-9f36-bd10-8f5d-a1299e8e8bf3 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-04-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | LD-FO-GEN-B | LEAK - Leak Detection (Fuel) |  |  | Carry out full visual inspection of panel and found that metal gland shall be installed prior to the final connections of the tubes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618376&prj=609&rqi=E3fTxc9gBncYjY78aaMszn4pwk
RT1FS-260-001 | f633b95d-7d06-4da4-a81a-36bd58435496 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-04-15 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Component/Equipment Failure | Commissioning |  | Fire Suppression | equipment | 1MFD_LB_04.4 | FD - Fire Damper |  |  | It has been observed that the fire damper cannot be opened manually. This must be rectified prior to the L2B inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618196&prj=609&rqi=sWAPUJR1WzYoYoLiDMlCbUt6ko
RT1FS-259-001 | 202f8920-1700-4961-9222-3de35b41989e | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-04-15 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning |  | Fire Suppression | equipment | 1MFD_LB_04.3 | FD - Fire Damper |  |  | The duct connections of the fire dampers do not comply with QA/QC standards and are applicable to all transformer room dampers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618194&prj=609&rqi=Tv5ndFMCC90XJuE0xNVtNob0yq
RT1FS-180-002 | c37beca5-abc1-4c5c-9cf9-9c4719e87ab0 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-04-02 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning |  | Fire Suppression | equipment | 1MFD_R_8 | FD - Fire Damper |  |  | The open/closed position labeling on the fire damper actuator is missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617135&prj=609&rqi=x48Cl9L2K2lkbo3FMcS39Y0MDX
RT1FS-180-001 | 162c093f-32d6-440f-acf3-39588b38fe5b | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-04-02 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning |  | Fire Suppression | equipment | 1MFD_R_8 | FD - Fire Damper |  |  | The damper does not open due to a clash between the duct elbow and the damper blade. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617134&prj=609&rqi=1GxSKg99LEJrqA7qH19wjyHJuK
RT1FS-257-001 | b647d307-3954-4ed5-91ac-ff64220bdac5 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-03-31 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Design correction needed | Design |  | Fire Suppression | equipment | 1MFD_LB_04.1 | FD - Fire Damper |  |  | Inadequate maintenance access in LB-Transformer room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616923&prj=609&rqi=ibUhoZ67gbTyIiRYnn7eDj63cX
RT1FS-255-001 | 3fba29ab-7913-44a4-82ca-ca52bde2b314 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-03-31 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Missing Components | Commissioning |  | Fire Suppression | equipment | 1MFD_LB_02 | FD - Fire Damper |  |  | Missing component. Kit WE has not yet been installed yet. Applicable to all LB fire dampers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616922&prj=609&rqi=DwG0J4EPPaTtV1pHdvxNX9Jfik
RT1MECH-385-001 | 9bce6c85-e25a-4efa-be33-ca8b99a40abb | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-03-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Incomplete Connections | Commissioning |  | Electrical | equipment | 1HWS_C_5 | HWS - Water Heater |  |  | Equipment should be installed complete with reinforced flexible connections. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615223&prj=609&rqi=CINqhXlmIEf5LyZ4vZJWK08HPe
RT1FS-53-001 | 3269c3c7-8dcd-441d-8a1d-ceeab0755ec7 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-02-25 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning |  | Fire Suppression | equipment | 1MFD_A_62 | FD - Fire Damper |  |  | Fire damper installed has not been supported in accordance with the approved benchmark details and project requirements. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204131&prj=609&rqi=U8t26oT0xdSKmsdJIlBHfzorEE
RT1FS-4-001 | 8258fdb1-4d28-4b42-861a-f47cd13197ea | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Fire Suppression | equipment | 1MFD_A_5 | FD - Fire Damper |  |  | This installation of the following MFDs: 1MFD_A_5, 1MFD_A_62, 1MFD_A_75, 1MFD_A_76, 1MFD_A_77, 1MFD_C_30, 1MFD_C_42 and 1MFD_E_02 are not as per the approved BENCHMARK. The installation of these MFDs shall be rectified to proceed for the L2A inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204130&prj=609&rqi=p2BWhAfjrPz3ZDKcY9MAip3OCf
YT1FS-119-001 | 16a19806-8cb9-49c2-abe9-01d410c62c9b | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-16 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Fire Suppression | equipment | 1MFD_C_28 | FD - Fire Damper |  |  | Earthing cable is connected the MFD support system. However, bonding between the support system and the MFD body is not yet done. GC to complete the installation of the missing bonds. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199270&prj=609&rqi=gHNWFxzXeaof3pvrzmDGeDqhCC
RT1FS-81-001 | cd172227-8171-4436-a4cc-5334b32575f9 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-16 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Fire Suppression | equipment | 1MFD_B_27 | FD - Fire Damper |  |  | 1MFD_B_27 is not accessible due to its installation above the busbars (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199264&prj=609&rqi=rISGDhZD6QvsUUf8z1RQWxMOgU
YT1FS-29-001 | 210a4daa-a292-44a9-a29c-8c99ccd5e1cc | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-06 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Fire Suppression | equipment | 1MFD_A_31 | FD - Fire Damper |  |  | Body bonding is not installed. This case has been identified in many of the MFDs installed. GC to re-inspect all the MFDs and make sure that bonding is installed as project specs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198687&prj=609&rqi=x8XgoHiXnCI96wkO3xjwGgp2it
RT1MECH-122-002 | 901e3d50-41bc-4b37-acbd-d4d0b706dbc5 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation Damage | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_18 | CRAH - Technical Room CRAHs |  |  | One of the bottom covers of the CRAH unit is damaged and must be repaired or replaced by the GC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198222&prj=609&rqi=Ya4Wc76CzFsvXskzMYF7VTpz3l
RT1MECH-122-001 | 6eaad900-6f67-49fc-8d3a-c64634aae5be | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_18 | CRAH - Technical Room CRAHs |  |  | One seismic cable is in direct contact with the C channel support of the cable tray installed above the CRAH unit. The C channel support shall be relocated by the GC team to ensure proper clearance for the seismic cable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198220&prj=609&rqi=QE9w0mvATvZniI43q8Qw9EO5Z1
RT1MECH-121-001 | 8260d097-72c0-4885-baba-7aca01c22e8c | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-03 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_17 | CRAH - Technical Room CRAHs |  |  | The seismic bracing cables installed on 1CRAH_C_17 at four corners do not conform to any single one of the four installation alternatives provided by the seismic design supplier. Instead, the current installation is a hybrid configuration combining elements from both Alternative 1 and Alternative 2. Vertiv is requested to provide official confirmation on whether this mixed installation is acceptable and approved by the seismic designer. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198209&prj=609&rqi=nKWQCZqV292n5XnKJKm1LES2WV
RT1MECH-121-002 | b95763ee-c9bc-4322-b95a-0833f2d0f87e | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | j.abdo@core-group.me | 2026-02-03 04:00:00.000 +0400 | VER - Vertiv Electrical | L2A | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_17 | CRAH - Technical Room CRAHs |  |  | 1CRAH_C_17 has a visible gap between the structural frame and the black protective sheet attached to it. This defect requires correction or replacement by Vertiv. (Please refer to the attached photo for additional clarification.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198212&prj=609&rqi=rppe5Z9Ufsof7sVlnvenmGmcpl
RT1ELEC-15-008 | 6b55af02-3f62-4ba6-bd94-2d87eedf6c37 | IL03-1 | 609 | S-EMEA | Closed | P2 Medium CX | m.yerkoylu@core-group.me | 2026-01-28 04:00:00.000 +0400 | SCH - Schneider Electric |  | Missing Components | Commissioning |  | Electrical â€“ MV | equipment | 1PUSP_2 | PUSP - Primary Utility Supply Panel |  |  | SF gas level is found low. Close to critical level as per gauge. To be rectified prior to power on. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197726&prj=609&rqi=5ZMRH7nyDQWENtEnws7nEApxCS
RT1FS-176-001 | ac3e1c3b-d608-4c85-bac9-a215c585081f | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-01-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning |  | Fire Suppression | equipment | 1MFD_R_4 | FD - Fire Damper |  |  | The firestop label should be applied to both sides. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197246&prj=609&rqi=smivko2NsJLX2NBkBnaDfKQ1tw
GI-001 | 7c522e84-f801-4c68-9bda-a429f7fb920f | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | m.yerkoylu@core-group.me | 2026-01-12 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning | [7 empty] | Damaged MV Cables (2 nos) observed at PUSP-2. GC to investigate further and propose the way forward. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196679&prj=609&rqi=hXvr1erqnEwxUeFLhVVjoaBM2E
RT1ELEC-35-005 | 3fdb43df-b2b7-43c1-aa61-4e03640ecc26 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | t.marculet@core-group.me | 2026-01-05 04:00:00.000 +0400 | CMM - Cummins | L2A | Installation Damage | Commissioning |  | Electrical â€“ MV | equipment | 1-GEN-R | GEN - Generator (MV) |  |  | Generator container has a dent by the door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196318&prj=609&rqi=cQ5JLk3rs9hJUq0zxqc8Owdpot
RT1ELEC-32-004 | 20f130e3-2082-4e0d-bd26-1957d297ad37 | IL03-1 | 609 | S-EMEA | Closed | P3 Low CX | t.marculet@core-group.me | 2026-01-05 04:00:00.000 +0400 | CMM - Cummins | L2A | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1-GEN-A | GEN - Generator (MV) |  |  | General issue for all Gensets - Earthing cables missing from the starpoin connection to the local earth bar. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196317&prj=609&rqi=h5QEsIeIxlQSmEJCY2HDOWARYe
YT1MECH-40-002 | 317428f4-1254-4059-8012-61c80e225cb7 | IL03-P1 | 625 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-09-01 04:00:00.000 +0400 | CMM - Cummins | L2B | Installation not correct | Commissioning |  | Fuel | equipment | Fuel -Oil System-GEN-E | FFIL - Fuel Fill System |  |  | During inspection, it was observed that the tension cable of the fire safety fusible link valve system is in direct physical contact with an adjacent metal support bracket (as highlighted in the attached image). The bracket is obstructing the free movement and direct path of the cable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636415&prj=625&rqi=I0sUB7bOtnk7WIXUstP0IYUYg9
YT1MECH-40-001 | 530f171c-f3c9-47b8-be9d-76950e39c9db | IL03-P1 | 625 | S-EMEA | Open | P3 Low CX | k.erbay@core-group.me | 2026-09-01 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Design correction needed | Design |  | Fuel | equipment | Fuel -Oil System-GEN-E | FFIL - Fuel Fill System |  |  | Access to the daily fuel tank is inadequate. The piping/valves structures installed in front of the access area restrict maintenance access and should be reviewed against the clearance requirements specified in the approved drawings. In addition, sufficient access is not available to fully open the louvre doors on the generator enclosure. A permanent access platform shall be provided to ensure safe operation, inspection, and maintenance activities in accordance with HSE requirements and the manufacturer's recommended clearance requirements. Applicable to all GEN Sets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636414&prj=625&rqi=tdtx0z8VZfz8vlDve7zvOWN4Vy
GI-001 | f1bb03ab-00a0-4f9c-b803-5f18bcae81cf | IL03-P1 | 625 | S-EMEA | Open | P3 Low CX | j.shaw@core-group.me | 2026-08-24 04:00:00.000 +0400 | TRN - Trane |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Cap ends missing from pipework on Chillers. This could lead to accidental drainage of the system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634889&prj=625&rqi=YIf1vS9Q1WHGdpDjEJhQyfjoDr
RT1MECH-34-001 | 35634de1-dce8-4fc7-a15e-43566fb34a0a | IL03-P1 | 625 | S-EMEA | Closed | P3 Low CX | k.erbay@core-group.me | 2026-06-28 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation Damage | Commissioning |  | Mechanical â€“Air | equipment | 1EF_E_03.2 | EF - Exhaust Fan |  |  | The fan panel door mechanism is damaged and must be repaired. Scratches and paint defects on the panel door shall also be rectified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627220&prj=625&rqi=ZnHuMMTAL6ukHMmLc6c5QwYzWc
GI-279 | 366fd129-5d65-4e45-a325-816cefac66a5 | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | junkaichan@commtechasia.com | 2026-09-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | Calculation for Riser kW is wrong - pending confirmation of correctness of TT sensors. - this affect Total Cooling Load capacity summation value. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638639&prj=632&rqi=ahvYc3I8SQskluH2AmdWsgFd0s
GT1MECH-465-001 | 9bc09bf0-0b23-4b15-94f6-867b297e8cdd | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | KaiJetSim@commtechasia.com | 2026-09-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Incomplete Connections | Commissioning |  | Fuel | equipment | FPPUMP1 | FPMP - Fuel Pump |  |  | FPPUMP1 While polishing process with selected FBulk_1 as supply, neither of the pump (Pump_1 / Pump_2) trip, another pump (Pump_2 / Pump_1) able to takeover. However, while polishing process with selected FBulk_2 as supply, the changeover does not happen. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638456&prj=632&rqi=t48MZVjPrknvdw5ayNvsSE9ftT
GI-278 | 2255b073-3e41-4681-8f81-84aeb50412be | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | junkaichan@commtechasia.com | 2026-09-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Doubtful Input power reading on JCI Chiller Control Panel. Observed WCC is reading 40kW input power at 30% motor amp on JCI chiller controller. This value is illogical and different to FWT result of 110kW input power at 31% motor ampere. Action: Please correct the reading on all JCI controller. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638065&prj=632&rqi=vJia8JX7sL1I1fytaC3HtTHnIx
GT1ELEC-177-002 | c50437cd-feb1-4a80-8b67-2d5f979c6261 | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | charitysamar@commtechasia.com | 2026-09-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | Pending DCOS point-to-graphic verification for Q16. DCOS is unable to monitor Q16 voltage (AB, BC, CA, AN, BN, CN), current (A, B, C, N), power (kW, kVA, kVAR, kWh), and power factor due to a communication/connection issue. Power meter communication interface/components require replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638077&prj=632&rqi=QYEPbjXLxTVsfhya7m5qtH3Akq
YT1MECH-532-001 | 1c6ca6ef-eb89-4652-ab2c-0e928cbcb98b | JH02-1/2 | 632 | APAC | Open | P3 Low CX | KaiJetSim@commtechasia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Fuel | equipment | FPPUMP1 | FPMP - Fuel Pump |  |  | FPPUMP1 No pump labeling and rotation direction on pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637871&prj=632&rqi=g1pUqgaIireeT3zygFSH4CCRxU
YT1MECH-533-001 | fd9fb817-3b8f-435b-8b30-05300719bf60 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | KaiJetSim@commtechasia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Fuel | equipment | FPPUMP2 | FPMP - Fuel Pump |  |  | FPPUMP2 No pump labeling and rotation direction on pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637873&prj=632&rqi=sCLsGpEv1i1af0Lt7Dmz5qvyEI
YT1ELEC-225-001 | ef9a734b-d227-48a5-88f3-f64125685e83 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-09-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1RPP_F1R1_2_1 | RPP - Remote Power Panel |  |  | 1RPP_F1R1_2_1 Incoming cable and earth cable not attached with label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637562&prj=632&rqi=fDCQUNH4OjgB0sK5dDzjLgYGLk
GT1DCOS-10-001 | 1f36a7cf-fac5-422c-bc51-52b71aa4fe3c | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Controls | equipment | 1DCOS_RIO_1 | DCOS - Control Panels |  |  | TT sensor mapping on graphic is wrong. when plug out sensor 1, both sensors 1 and 3 give out alarm. this is identical for other sensor inside the chw loop. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637410&prj=632&rqi=aM86hpsI8rlnNjBr2efgLh9QxL
YT1MECH-257-001 | a7effed9-d9ba-4ec6-ae7f-9c2809fcaa1c | JH02-1/2 | 632 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1EF_M1_10 | EF - Exhaust Fan |  |  | 1EF_M1_10 calibration certificate serial number for cable test on Accesstech side is not tally with the one mentioned inside checklist. Please take a necessary action. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637440&prj=632&rqi=70L5MWsPoxVXyqd6VMzVoeYV2o
YT1ELEC-116-001 | 056efdb2-ec6a-4f80-877f-fa9e2bb35995 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | charitysamar@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STS_D1R1_2 | STS - Static Transfer Switch |  |  | Remove white paint splashes from the STS panel door and clean the affected surface. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637432&prj=632&rqi=iuAvgSLudblMrjCiN3fbpRp2Oj
GT1DCOS-10-002 | 1941d342-a609-469d-b69f-c86335455586 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Controls | equipment | 1DCOS_RIO_1 | DCOS - Control Panels |  |  | DPT mapping for ewall riser 01 and 04 is wrong. onsite the dpt is connected to different riser not as per mapping. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637411&prj=632&rqi=kAAHdDoxB3ffZ3KXCf4avaIIBI
GT1ELEC-127-004 | e27b6bea-1668-47e7-9147-168ecff4aaee | JH02-1/2 | 632 | APAC | Open | P2 Medium DCOS | AliHazmeerHamdan@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | UPS_A1 - Refer to DCOS graphic, some item / equipment not fully configured or still shows undefined value. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637139&prj=632&rqi=CvUC3w6QJfW7B82bAjmoCLeNJq
GT1ELEC-104-001 | 271ab856-9868-4d90-9298-bfd112591baf | JH02-1/2 | 632 | APAC | Ready for Verification | P2 Medium CX | charitysamar@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STS_E2R1_1 | STS - Static Transfer Switch |  |  | During the STS (Static Transfer Switch) Functional and Burn-in Test, a significant load discrepancy of approximately 60 kW was observed following the transfer from Source S1 (E Block) to the alternate Source S2 (R Block). The observed discrepancy is considered abnormal and requires further investigation. Contractor shall investigate and identify the root cause, verify the accuracy of the load measurement/metering and associated power distribution, and implement the necessary corrective actions to rectify the issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637145&prj=632&rqi=2cEtQnOgtXkiRkygU9ipuUCk2H
GT1ELEC-127-006 | 28131ab7-832f-4d45-833c-bacd64c197c0 | JH02-1/2 | 632 | APAC | Open | P3 Low DCOS | AliHazmeerHamdan@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | UPS_A1 - Line animation still not fully configured correctly. Honeywell to rectify and ensure the animation accurately reflects the actual system status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637142&prj=632&rqi=tEV02yRajxaRg9UPwON9IfJlj6
GT1ELEC-127-005 | 932cdad6-6cc0-4a28-8a84-b71617c27343 | JH02-1/2 | 632 | APAC | Ready for Verification | P3 Low DCOS | AliHazmeerHamdan@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | UPS_A1- Eaton shall provide the applicable threshold or range values to Honeywell to ensure that the displayed values are correctly configured and identifies any out - of range conditions or abnormal status indications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637140&prj=632&rqi=cvWD5BukbRZLtBYIrmnnMdR3bQ
GT1DCOS-3-006 | 640ab303-d109-4788-924b-3ef71a47dc83 | JH02-1/2 | 632 | APAC | Open | P2 Medium DCOS | MuhammadHaziqZakaria@commtechasia.com | 2026-09-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/Equipment Failure | Commissioning |  | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | DCOS graphic for FCV_03 keep flicking On and Off when the feedback is at 0%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637066&prj=632&rqi=jCR0ocZ3oEv7XFpylRwWw0Ew04
GT1ELEC-5-001 | fe57f6a8-7eee-4ee2-bed5-6533c9255793 | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | charitysamar@commtechasia.com | 2026-09-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_R | RMU - Ring Main Unit |  |  | The RMU ring circuit breaker position is currently not indicated on the DCOS monitoring interface. Honeywell shall configure and integrate the circuit breaker position (Open/Closed) into the DCOS for remote monitoring. (This applies to MV Overview, see attached photo for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637057&prj=632&rqi=tpBh4GxO68rJtky5VkMuapoMxZ
GI-268 | f4dbf6f5-6a7e-4ae3-881e-46400091b28a | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | junkaichan@commtechasia.com | 2026-09-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F1 | UPS - Uninterrupted Power Supply |  |  | During Cx3 Testing for UPS F1 for 10. UPS OVERLOAD - (SINGLE) - LB ramped up to 1400kW for 10 mins to trigger Static Bypass transfer (L2 overload alarm), after Static Bypass transfer immediately L3 overload alarm triggered and offloaded the UPS. Action Required: To preform investigation and submit RCA. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636944&prj=632&rqi=Zm3NhNXrC2OLiDDhft8kaD2Tek
GI-270 | f0463110-ebf6-4808-8593-cad0670c6ae3 | JH02-1/2 | 632 | APAC | Open | P3 Low DCOS | junkaichan@commtechasia.com | 2026-09-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_A | MSB - Main Input Switchboard |  |  | Phase-N signal of voltage and current show on graphic as per required in SPL, but designed breaker is TPN. Action required: HW please confirm with EOR to remove these unnecessary items on graphic. and attach final screenshot to proof this is removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636949&prj=632&rqi=7kDzGkqrBTRwf6FjR8MIeENlou
GT1MECH-172-001 | 89922357-f9c2-48f4-b4b4-f66f45d23034 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-09-04 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Component/Equipment Failure | Commissioning |  | Mechanical â€“Air | equipment | 1EF_M1_05 | EF - Exhaust Fan |  |  | During Cx3 Temperature Validation, found the temperature sensor for 1EF_M1_05 show (37.1Â°C) which is a different reading (31.3Â°C) from a calibrated temperature meter. The different is higher than the acceptance tolerance (Â±0.5Â°C). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636798&prj=632&rqi=0ysB3Hpe9tqWutLCs4ajGVq2DG
GT1MECH-165-001 | 4201d992-330e-4de8-9a30-75aea23129d4 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-09-04 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Component/Equipment Failure | Commissioning |  | Mechanical â€“Air | equipment | 1EF_M1_06 | EF - Exhaust Fan |  |  | During Cx3 Temperature Validation, found the temperature sensor for 1EF_M1_06 show (27.7Â°C) which is a different reading (29.3Â°C) from a calibrated temperature meter. The different is higher than the acceptance tolerance (Â±0.5Â°C). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636801&prj=632&rqi=8T74aK7iB8LmXQRFh7TEqNHkzB
GT1MECH-137-006 | 52463bb0-5c8f-4188-941d-6f4d5da99d25 | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | All CRAH units fire cable yet to be terminated to the units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636677&prj=632&rqi=cgwGIzB7JEWTrN6VEFeibT8V8I
DCIML2B-1-001 | 1a7be075-4597-419e-a1d8-36afed3bb9c3 | JH02-1/2 | 632 | APAC | Open | P2 Medium DCOS | sganeshmahadik@ap.equinix.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L2B | DCIM Maximo Issue | DCIM |  | Controls | system | DCIM |  |  |  | Maximo and Location Vectors list is not ready as Cx activities are going on. It's essential to DCOS/DCIM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636679&prj=632&rqi=1Y0nih7NzmiZvA9PSzFPHWB5d8 | https://equinix.facilitygrid.co.uk/x/project/632/system/12791
GT1MECH-137-005 | 31efec13-24c4-4b95-ad53-6dc6a66b78e1 | JH02-1/2 | 632 | APAC | Open | P2 Medium DCOS | samintarajarujunan@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | Supply Fan Command Mismatch alarm unable to simulate. SE does not have fan feedback data provided to DCOS. This point is DCOS calculated and based on the onsite testing it was found that this point unable to be simulated for testing. Please recheck the logic and get the point tested to close this issue. Applies to all CRAH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636675&prj=632&rqi=Lr7ENglgpqKMNvS31cc6T5Ii5J
GT1MECH-137-003 | 06c688fc-732c-432e-a9e5-c941ae5f4e79 | JH02-1/2 | 632 | APAC | Open | P2 Medium DCOS | samintarajarujunan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | Num of Units in Group is still computed based on the configuration point. This means the number is based on how many units has been configured in a group rather than a live value. During testing one of the grouping cables has been removed to observe the change in number units in group. However, found that it does not reduce. The only way to reduce the number of units in group is to configure a different value from the CRAH HMI. Applies to all CRAH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636389&prj=632&rqi=fjJoykaP7Etl7KfuGtiBc8vUfn
GI-266 | ba78bf9e-c711-434c-95bc-222089cc8fbd | JH02-1/2 | 632 | APAC | Ready for Verification | P2 Medium CX | junkaichan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS |  | Electrical â€“ LV | equipment | 1STS_A1R1_1 | STS - Static Transfer Switch |  |  | There is a list of boolean points informed by CSPM cannot be tested at P2G due to Socomec controller do not have simulation function. Please confirm with manufacturer with official letter confirmation on which point unable to be simulated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636427&prj=632&rqi=1vgs6MV6XV8dwGfYwNNsWRMGsl
YT1ELEC-108-001 | 9cd8c469-65ef-46c6-a954-70f68508d94b | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | charitysamar@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STS_F2R1_2 | STS - Static Transfer Switch |  |  | Damaged STS ventilation/insect mesh at roof support. CSPM to rectify and reinstate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636393&prj=632&rqi=NbU8liicwAwonOq1y2QOeRgDjX
GT1DCOS-3-005 | 1af10a0b-bf08-4a29-8c39-a677e432bd87 | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | imanuddinhamdan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS |  | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | Line animation and buffer tank mode is wrong when the open the FCV 03, the buffer tank mode is not changing. Line animation also | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636483&prj=632&rqi=rsnwSr0uH2e1vecmos1Gddtquu
GT1MECH-137-004 | 6f348767-eea7-48fd-abd6-97ed1c16e529 | JH02-1/2 | 632 | APAC | Open | P3 Low DCOS | samintarajarujunan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS |  | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | The Command screen has 2 submit buttons. Apply to All CRAH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636392&prj=632&rqi=iGW9vDQ5CveYHzCchdVQc0XaA2
GT1MECH-137-001 | 844a7317-6f7f-4615-98ac-d490bad0cddb | JH02-1/2 | 632 | APAC | Open | P2 Medium DCOS | samintarajarujunan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | Resilient and Resiliency Vote Calculation to recheck. Once 1 of the Units from the group receive summary alarm, all the units in the group loses its resiliency vote. however, based on the approved calculation, resiliency vote is calculated individually for each unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636386&prj=632&rqi=4mG25kQOxuZ68q5hPuf86T0raI
GT1MECH-137-002 | 7a265bd3-4316-4a39-9e65-7e84fc3a05ad | JH02-1/2 | 632 | APAC | Ready for Verification | P2 Medium DCOS | samintarajarujunan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | Valve Mismatch is a DCOS calculated Alarm. 30s delay has been added however during testing it was identified that the mismatch still be triggered on multiple occasion. To recheck the programming on the implementation. Applicable for all CRAH Units | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636388&prj=632&rqi=Jfy0y44tUUSU6apHeNyIxmPnYd
GI-265 | 8523006c-06c8-4814-a1fa-6c2942d48754 | JH02-1/2 | 632 | APAC | Closed | P2 Medium DCOS | junkaichan@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS |  | Electrical â€“ LV | equipment | 1MSB_A | MSB - Main Input Switchboard |  |  | MSB_A DCOS PQM unable to communicate during official P2G witness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636171&prj=632&rqi=6i5n7fKcvkE2fyp4qAhYjhM25h
GT1DCOS-3-001 | 9220d638-1949-481e-90f7-184f339edde9 | JH02-1/2 | 632 | APAC | Open | P2 Medium DCOS | junkaichan@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | CPR1 - DO - CT1 and CT2 share same start/stop command from DCOS graphic - whichever faceplate of CT1/CT2 give command start/stop, both CT1 and CT2 will run/stop together - confirm with HW EOR if this is intended design (P2-HW) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636218&prj=632&rqi=bZC5Z3a5GCRHYoR65QpIBZMlqu
GT1DCOS-3-003 | 2ea19e7d-dc7f-4f45-9ee4-dd6e48e65e4c | JH02-1/2 | 632 | APAC | Closed | P2 Medium DCOS | junkaichan@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning |  | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | CPR1 - AO - CT VFD speed command not working - DCOS can't send out command signal to VFD to control pump speed (P2-HW) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636224&prj=632&rqi=Kp6ge4W4SXgBDsw24JFDuttsSl
GT1DCOS-3-002 | 103db7f2-a865-41e4-8793-1985d8f64a5f | JH02-1/2 | 632 | APAC | Open | P2 Medium DCOS | junkaichan@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | CPR1- AI - FT-01 on site not performed flowrate verification and P2G - no flowmeter ready by HW. (P2-HW) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636223&prj=632&rqi=NQFIlg6WH1eRBlP7tYUnk07GeO
GT1DCOS-3-004 | bd454481-7176-4dce-a998-b6e4a457c6be | JH02-1/2 | 632 | APAC | Open | P3 Low CX | junkaichan@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning |  | Controls | equipment | 1DCOS_SCP_1 | DCOS - Control Panels |  |  | CPR1 - All Belimo valves in chiller plant no proper tagging, and some with wrong tagging. ACT to rectify based on approved schematic. (P3-ACT) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636225&prj=632&rqi=s2JH0Fus5WjXIMNrgapbyVuVas
GT1ELEC-95-001 | cbe5d701-6f9c-43b2-bc89-d4fe807662c7 | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | charitysamar@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STS_A1R1_2 | STS - Static Transfer Switch |  |  | During the STS Point-to-Graphic Test/Functional Test, no DCOS line animation (energized/white indication) was observed on the STS Source 2 Bypass path while the system was in S2 Bypass Mode and STS Q42 breaker was in the Open position. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636216&prj=632&rqi=UZjYaPrLctn9FKcmUXFPv1By3D
GT1ELEC-215-001 | 9c02cd71-0271-4b0f-bce3-aa9ab97a7560 | JH02-1/2 | 632 | APAC | Closed | P1 High CX | charitysamar@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LBSB_1 | LBSB - Loadbank Switchboard |  |  | Water ingress into the Load Bank Switchboard occurred due to incomplete cable installation associated with the Mobile Generator. Contractor shall provide an Incident Report identifying the root cause, extent of water ingress, and corrective actions taken. Contractor shall also assess and confirm which electrical tests are required to be repeated prior to re-energization of the switchboard and resumption of load bank testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635215&prj=632&rqi=RXG0rb1ChBQtVo6CfzZaqU2HIb
YT1MECH-308-001 | 035b8673-9998-4b08-9803-05fe435bf1fc | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_5 | FPMP - Fuel Pump |  |  | The cable from 1FP_M1_5 to Overflow Pump connected to the single phase circuit has been installed 3 phase color identification (RYB). the cable color arrangement does not comply with the required single phase identification, which should be Red (L), Black (N), and Green (PE) . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635231&prj=632&rqi=r61xh213xmGCcuokTVNose3gNc
GT1ELEC-128-001 | 7278857d-96a6-4be4-8dcc-51fe27d4bb15 | JH02-1/2 | 632 | APAC | Ready for Verification | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-08-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_A2 | UPS - Uninterrupted Power Supply |  |  | During the load slowly increase until 100% (1200kVA) for UPS_A2, the UPS generated phase C Overload alarm at HMI. The overload event was triggered phase C (Blue Phase) only, while the overall UPS load remained below the configured overload threshold. the configured overload setpoint is 106%, however, the Phase C Overload alarm was triggered when measured load was still below 106% setpoint, this event occurs shows the phase is unbalanced. In addition, the DCOS did not receive or display any overload of phase unbalanced alarm from UPS_A2 when the alarm was active on the UPS HMI. The DCOS alarm indication is critical for operational operation. Any abnormal or protection event detected by the UPS should be correctly transmitted and displayed on the DCOS to alert the Operations team. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634558&prj=632&rqi=wqlmDjoAJpzdDb0aDKushz0IQb
GI-263 | 79e5f0c9-9e23-498f-87d3-b7b97c163abd | JH02-1/2 | 632 | APAC | Ready for Verification | P2 Medium DCOS | AliHazmeerHamdan@commtechasia.com | 2026-08-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Comms Issue/Fault | DCOS | [7 empty] | The trend logging for the electrical system, particularly for the UPS systems, has not been fully configured in DCOS. The trend logs for the UPS and overall electrical system parameters are still incomplete. This limitation prevents DCOS from properly recording and trending the electrical parameters during the UPS Burn In Test. Honeywell required to complete configured and setup the trend logs for all UPS system and the overall system in DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634559&prj=632&rqi=i9KyhMAi7drxi9FxPBwTZusMB7
YT1MECH-216-001 | b495ae96-9e18-4e9a-a5aa-75cc19b350c2 | JH02-1/2 | 632 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_D_1 | EF - Exhaust Fan |  |  | Found the tagging for DCOS cable is not tally between its own pair and the cable name inside checklist. Please do the necessary rectification to close the issue. Please check on all EF before close issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634571&prj=632&rqi=c6OjnN7Xb45rHzcDe7zKqGmRz1
GT1ELEC-135-004 | 295cb114-7cd9-42a2-a28c-6ea44a84f002 | JH02-1/2 | 632 | APAC | Ready for Verification | P2 Medium DCOS | AliHazmeerHamdan@commtechasia.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_E2 | UPS - Uninterrupted Power Supply |  |  | During UPS_E2 Burn in Static Bypass, DCOS graphic just remain at Double Conversion (online mode). The graphic does not reflect with UPS status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634164&prj=632&rqi=FAX0lyHacVASGYQSapFTvRWAzF
GT1MECH-193-001 | e700e1ff-acbb-4c47-9ae5-f5bf1477b0e0 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-08-18 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_M2_2 | EF - Exhaust Fan |  |  | Fan running time and time taken to trigger is not tally for all the fans. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634045&prj=632&rqi=kcqMY295mCxfHL93GuxURkQCDS
GT1ELEC-135-003 | 455751c9-3d55-4513-9679-6df3b3a773da | JH02-1/2 | 632 | APAC | Ready for Verification | P3 Low DCOS | AliHazmeerHamdan@commtechasia.com | 2026-08-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_E2 | UPS - Uninterrupted Power Supply |  |  | The breaker status Q01, Q08 and MSB_E_PQM displayed on the DCOS is incorrect. The status indication needs to be checked and rectified before proceeding with the Gen Source transfer testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634115&prj=632&rqi=BJKxWyFP1ohGialtJJtuTJpNkM
GT1MECH-194-001 | bd06d67b-6436-47a5-b575-9c66954592f5 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-08-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_M2_1 | EF - Exhaust Fan |  |  | When fire alarm is triggered at the M2_1 , M1_1 also triggered the fire alarm. Same goes to the refrigerant leak simulation same fan triggered as well. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634021&prj=632&rqi=H0l4nnTvg6B4I4skMJySiwWj8C
GT1ELEC-133-001 | 7d7d91b8-7e84-483c-a625-3085a74da544 | JH02-1/2 | 632 | APAC | Open | P2 Medium DCOS | AliHazmeerHamdan@commtechasia.com | 2026-08-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_M1 | UPS - Uninterrupted Power Supply |  |  | The DCOS is displaying an incorrect value for Gen_M1, and the breaker status is also not being reflected correctly in DCOS. Please verify all the points at MSB Graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633914&prj=632&rqi=UOSRNcQ6IhiEzKs9FHNfE6aZg7
YT1MECH-237-002 | 754bbeef-93ef-413b-afb3-64e16cb40ed8 | JH02-1/2 | 632 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_M1_03 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found there is missing terminal block inside panel for 24 VDC and possible missing cable termination since SLD and GA drawing mention for 24 VDC. Please clarify the issue and close the issue immediately. ISSUE APPLIED TO ALL EF | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633869&prj=632&rqi=iELwsbqFbk5d5fuO1e0H0CqLmR
YT1MECH-237-003 | a8d40556-8e02-45ae-a929-fdd04daea0a9 | JH02-1/2 | 632 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_M1_03 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the cable tagging for DCOS is not tally as per checklist. Please refer photo attached for the discrepancy. Understand the one from checklist is the correct one. If so, please change accordingly. Please do check for other cable as well. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633871&prj=632&rqi=PuyezzztATa2w9Rfq9xTR7ss8u
YT1MECH-229-002 | 965eee7c-f33d-487b-ab91-930453bc410a | JH02-1/2 | 632 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_R_1 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found there is missing terminal block inside panel for 24 VDC and possible missing cable termination since SLD and GA drawing mention for 24 VDC. Please clarify the issue and close the issue immediately. ISSUE APPLIED TO ALL EF | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633868&prj=632&rqi=gkESiTOz8zzyRhN9OSr55ZRrgs
GI-261 | 8d90fdd8-0059-4bd6-abd6-c5c229fa3073 | JH02-1/2 | 632 | APAC | Ready for Verification | P1 High DCOS | AliHazmeerHamdan@commtechasia.com | 2026-08-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS | [7 empty] | Issue: DCOS/CPOS graphics development, deployment, and validation are significantly behind schedule. SFAT-validated graphics and database evidence are no longer valid, requiring substantial rework. Multiple graphics remain incomplete or contain errors, trending configuration is not fully implemented, equipment integration and handshaking activities are outstanding, and no consolidated tracker exists to monitor completed versus pending works. These deficiencies are preventing chiller plant testing, sensor validation, TAB verification, burn-in testing, and other commissioning activities from progressing as planned, creating a significant risk to the project RFS milestone. Honeywell is required to provide a comprehensive recovery plan, resource allocation strategy, outstanding works register, and milestone-based schedule recovery actions. Impact: Delay to Cx activities, inability to complete planned testing, risk of repeated testing effort, and potential RFS schedule slippage. Required Action: Honeywell to submit RCA and execute a detailed recovery plan with clear ownership, resource augmentation, daily progress tracking, and prioritized completion of critical DCOS/CPOS graphics and integration activities. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633763&prj=632&rqi=Nnq7JVKCfYFVrXy6QVCK4l3nM8
GT1ELEC-132-002 | 711f092d-bedb-4799-8961-bb5effb55ed9 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-08-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_R12 | UPS - Uninterrupted Power Supply |  |  | The reading shows at MSB_R_Q_04 for KW and PF are still incorrect. The Value required tally with DPM MSB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633761&prj=632&rqi=HXf3UWGf812idSlfHveVept87y
GT1ELEC-132-001 | 44d67b6a-4595-4c5b-80f2-a9669fcd730f | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-08-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_R12 | UPS - Uninterrupted Power Supply |  |  | The line animation on the DCOS graphic is not fully aligned with the actual system status. Please verify and rectify the animation accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633760&prj=632&rqi=CHl2NAtFjkTo2NncrKbECwvC62
YT1ELEC-607-001 | 1d7ea6e6-0abb-4c3c-bf82-13583be50d0f | JH02-1/2 | 632 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_D_1_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q04 to "SPARE". Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633188&prj=632&rqi=uqo7CFjIpMg8VaL0xxnmPhzaGY
YT1ELEC-606-001 | 34b9264e-3414-47b9-89f6-3908e4a8d511 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_C_1_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q04 to "SPARE". Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633191&prj=632&rqi=men4TtMa0Xo404hAyHf83k8WwW
YT1ELEC-152-001 | ac01502e-7238-4e49-8fcb-cb698227b1ba | JH02-1/2 | 632 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_C_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q09, Q10, Q11 and Q12 to "SPARE". Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633192&prj=632&rqi=uuuitLzoN7XTsSkXEvYgnrbfEC
YT1ELEC-608-001 | f0b28dd6-e3c3-4885-b57e-dcc342571078 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_F_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q02 and Q03 from "SPARE" and Q11 from "SPACE". Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633194&prj=632&rqi=SkB55Q66RfS0WgIWR3mfJ1QPRt
YT1ELEC-607-002 | 3342e8c7-376a-43ae-a8db-082a59832b50 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_D_1_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q04 to "SPARE". Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633189&prj=632&rqi=J50bzWAakWvfXcGSN1fMHV003B
YT1ELEC-367-001 | eae8449d-7cc4-437a-a962-c87d66476489 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | charitysamar@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_M1_27 | LVSB - Low Voltage Switchboard |  | i-Box | Update the as-built drawing to incorporate the changes and place the approved revised drawing in the designated document pocket of the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632989&prj=632&rqi=R2LUlC9Pvtrfxy1epk9wksc27M
YT1ELEC-389-001 | bf1c1771-5e39-47a9-80fa-70e52c272d2b | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | charitysamar@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_C_06 | LVSB - Low Voltage Switchboard |  | i-Box | Update the as-built drawing to incorporate the changes and place the approved revised drawing in the designated document pocket of the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632994&prj=632&rqi=nOHkX5doXofj4eiJLgS8F9Rufw
GT1ELEC-177-001 | 50799918-b367-4019-8cc6-ba2756b675c7 | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | MSB_R. During simulate utilities failure (Open Breaker). The Gen_R breaker at MSB not automatic close and the genset not kick in to start. The UPS_R1 in discharge Mode (Battery Discharge). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632831&prj=632&rqi=lBqk2UEB0Iny85qyFaMIRBUfZv
GI-259 | 35f8c48c-29db-4935-ba77-5d851201e3a1 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-08-07 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D | MSB - Main Input Switchboard |  |  | HMI panel already install by GC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632701&prj=632&rqi=AteDl2kZxESFl3Gwuuj420Ej9N
GT1ELEC-135-002 | 854f5f27-6719-4994-85be-2b2c6fcfc3ae | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_E2 | UPS - Uninterrupted Power Supply |  |  | During the Burn In test UPS_E2 (Double Conversion), UPM 2 and UPM 3 experienced an overtemperature trip due to the elevated supply air temperature from CRAH system. The high CRAH supply air temperature resulted in an increase in the ambient temperature around the UPS, causing the UPM operating temperature to exceed the allowable limit. Please verify and confirm the condition of UPM 2 and UPM 3 following the overtemperature trip event. Kindly check whether the event has caused any abnormality, derating or impact the UPM efficiency and output capacity. I believe this UPM can operate 0â€“40-degree Celsius without derating based on technical specifications. it would be appreciated if Eaton could provide the UPM temperature history or trend prior to the overtemperature trip, including the final temperature recorded before the trip. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632709&prj=632&rqi=ABwkAm8yTWRJkfqs6rlmLejwlC
GI-260 | d2bc8621-ba47-48e8-8d86-10a6821c7aa2 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-08-07 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F | MSB - Main Input Switchboard |  |  | HMI panel already install by GC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632704&prj=632&rqi=yxFvh0eP2xw1w4aOWTPB8yXrhU
GI-258 | 46c5dfb8-e32a-4fc0-8c65-f510dc05e4c3 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-08-07 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | HMI panel aready install by GC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632696&prj=632&rqi=WvuTUMuyj5rXFFptrl9V4ymsEG
GI-257 | 8f342cc0-6d42-4147-bddc-12fbedfad212 | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | junkaichan@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_R11 | UPS - Uninterrupted Power Supply |  |  | - load up UPS to 35%~420kw - â engineer check for meter verification between PQA and UPs HMI - â found imbalance current at UPS HMI (output meter -blue phase) while PQA showing healthy reading Please submit RCA report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632500&prj=632&rqi=gvDo0zHe3fUq00bf2zawfwPq52
GT1ELEC-135-001 | bd55c5f0-2c7d-4680-a99c-a8db6e5f0e99 | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-08-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_E2 | UPS - Uninterrupted Power Supply |  |  | The UPS_E2 HMI current indication is abnormal. The blue phase current reading is significantly lower than the red & yellow phase. R = 175A, Y=172A and Blue=86A. Please verify the current measurement and CT wiring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632265&prj=632&rqi=h2AA0IslZCSuL67Sp5GCj7Eo7K
YT1MECH-199-001 | 2545c459-06f5-4605-8261-0fa43ca15cb0 | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-08-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_A_1 | CRAH - Computer room air handler |  |  | To complete installation of field sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632070&prj=632&rqi=YBtfEOptvoYQIdSjVCuXL932WL
GT1ELEC-180-001 | 0914e91f-046b-4365-8559-195b39a255da | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-08-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_M2 | MSB - Main Input Switchboard |  |  | Test 27- Flex initiated transfer to Fixed Generator (Closed Transition). The Generator started and the utilities breaker were in closed position. However, the system did not receive the Sync Ready status signal. As a result, the synchronization sequence could not proceed, and the transfer to the Generator source was inhibited. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632082&prj=632&rqi=LLPRF5VmFZYDZngHXOVDilwfrw
YT1MECH-227-002 | b364c700-89b2-4427-994a-0b9ded2f961d | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_M1_06 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the end of fire cable is left hanging from the junction box. Please complete the fire cable installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631963&prj=632&rqi=6obaDL7rMiLudSsOAGowjIagZL
YT1MECH-227-003 | f4e4424f-f89e-428f-bc93-d2e37f232b29 | JH02-1/2 | 632 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-02 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_M1_06 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the TS glass cover is broken. Please rectify to close the issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631964&prj=632&rqi=xjcjK3K2ug4amDCvVPrMp1YEdN
YT1MECH-227-001 | 85c812a8-c413-4e69-b157-91629be4d99f | JH02-1/2 | 632 | APAC | Open | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-08-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_M1_06 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the cable for DCOS is missing however the DCOS is mentioned inside the SLD. PIC claims the drawing is wrong. Please attached any relevance document to show proof DCOS cable is not to be terminated on this panel. Please amend the drawing if necessary. APPLIED TO ALL EF | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631962&prj=632&rqi=Q8IhxFt4PYN1FEdGKH5100ULeM
YT1MECH-260-001 | 38e17513-921c-46ef-9e24-d22db1aa47f4 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1TEF_M1_1 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, noticed fire cable is missing from the drawing attached inside the pocket drawing. Please discuss with relevance party to clarify the fire cable termination. Issue for panel LCP_1TEF_M1_1&2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631716&prj=632&rqi=0UwLO9bwtGDKY10M58uQUv6LHz
YT1MECH-230-001 | 7649d41d-1ed3-4fb4-981b-912051f7cb79 | JH02-1/2 | 632 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_1 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the breaker size is larger than SLD and GA Drawing. On site breaker install 20A while in all drawing mention breaker size is 10A. Please verify and amend as necessary. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631359&prj=632&rqi=GzRKmyrQuvzg9awxNQMkI16c3J
YT1MECH-229-001 | 17442369-074b-4ca7-816b-797735189a52 | JH02-1/2 | 632 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_R_1 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the breaker size is larger than SLD and GA Drawing. On site breaker install 20A while in all drawing mention breaker size is 10A. Please verify and amend as necessary. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631361&prj=632&rqi=9wJoiUnfVjEroLhAZK7hqqLEte
YT1MECH-236-001 | 74cf5e1b-be66-44a0-aa3d-79312f012af7 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-30 04:00:00.000 +0400 |  | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_A_1 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the breaker size is larger than SLD and GA Drawing. On site breaker install 20A while in all drawing mention breaker size is 10A. Please verify and amend as necessary. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631349&prj=632&rqi=xVwQQyDkFALmXugxBHMWQL8DAk
YT1MECH-237-001 | 6969ae92-2f0f-422f-ae6a-cd50c8810e32 | JH02-1/2 | 632 | APAC | Ready for Verification | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_M1_03 | EF - Exhaust Fan |  |  | During Cx2B YT inspection, found the breaker size is larger than SLD and GA Drawing. On site breaker install 20A while in all drawing mention breaker size is 10A. Please verify and amend as necessary. APPLIED TO ALL EF | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631357&prj=632&rqi=pcRPJJWf6iHToexQKVZnorqd7Z
YT1MECH-223-001 | 4846b46b-f6b8-4e76-a7a4-1d55a87fbfaf | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | junkaichan@commtechasia.com | 2026-07-29 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_E_1 | EF - Exhaust Fan |  |  | Signal cable from fan control to LiB Block E (E_ 1-7) and (E2_1-7) is not installed, tested thus termination at LiB is incomplete. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631123&prj=632&rqi=WIyymyNGYLYkejL2BlV3VhdcZC
YT1MECH-177-001 | 8ccf742d-7a50-4fcf-a9ce-8a5c1663ddaa | JH02-1/2 | 632 | APAC | Open | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_E_1 | CRAH - Computer room air handler |  |  | Pressure Testing and flushing documents are approved on Project Portal and attached to the correct section of Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630831&prj=632&rqi=kWCYfWALSW10FnEVgGvVUE35IN
YT1MECH-183-001 | ee6ef885-5529-4a4d-bd6b-0103fba7cf9b | JH02-1/2 | 632 | APAC | Open | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_1 | CRAH - Computer room air handler |  |  | Pressure Testing and flushing documents are approved on Project Portal and attached to the correct section of Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630833&prj=632&rqi=TWe9FFH7UHZpb3aBh7B6xctOU8
YT1ELEC-154-001 | f4e839b0-8a13-47cb-984e-057a3d54ee3c | JH02-1/2 | 632 | APAC | Open | P3 Low CX | charitysamar@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_F_1_1 | MDSB - Mech Distribution Switchboard |  |  | Update the load tagging of outgoing breaker Q04 from "SPARE" to the correct load. Submit an approved revised shop drawing reflecting the correct load designation and update the as-built drawing accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630655&prj=632&rqi=0psQg4ENxNU0ui50W53QBBdzLt
YT1ELEC-107-001 | 1e175f22-77f4-4d7a-8d70-1c2609860861 | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | charitysamar@commtechasia.com | 2026-07-23 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STS_F2R1_1 | STS - Static Transfer Switch |  |  | The tagging at the busduct connection point to the STS does not correspond to the tagging on the busduct body. If the discrepancy is limited to the busduct body tagging, a continuity test should be conducted to verify the connection, and the tagging shall be corrected afterward. However, if the discrepancy is at the connection point, the busduct will need to be modified to ensure the correct connection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630513&prj=632&rqi=TAFFyeBCy9FQZX3jsj2j0K59ik
YT1ELEC-370-001 | 662a6004-88d7-4a17-99cd-97db242dd5ab | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_M1R_38 | LVSB - Low Voltage Switchboard |  | i-Box | 1LVDB_M1R_38 RCCB for each phase, to be swapped out for 2 pole MCB as confirmed by NV5 to avoid nuisance tripping. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630218&prj=632&rqi=1knaJnrkQWayOBuGvPct6T8SP1
YT1ELEC-106-001 | c6b0cd8e-a22a-40d3-a490-f7a26b271b30 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | iau@cspm.com.my | 2026-07-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1STS_E2R1_2 | STS - Static Transfer Switch |  |  | White Glove Report is approved on Project Portal and appended to the document section of this checklist | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629708&prj=632&rqi=vlUIE5adPgPfIP8NGgz6yGFcZS
YT1ELEC-103-001 | e0e2a267-e1f9-4168-ab4c-f64b13a03f57 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | iau@cspm.com.my | 2026-07-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1STS_E1R1_1 | STS - Static Transfer Switch |  |  | White Glove Report is approved on Project Portal and appended to the document section of this checklist | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629712&prj=632&rqi=Q1GsUzu7PJDVqZZ8y8NFxePqpD
GT1ELEC-129-001 | 91d10ced-43b5-4e12-a3f0-07e39d140e42 | JH02-1/2 | 632 | APAC | Ready for Verification | P2 Medium CX | charitysamar@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B1 | UPS - Uninterrupted Power Supply |  |  | UPS DCOS SPL not in Honeywell Points List during Cx3 Testing: -DC Ground Fault -DC Over Voltage Shutdown -Input Current Unbalance -Maintenance Bypass Breaker Closed -Maintenance Bypass Breaker Open -Output Breaker Closed -Output Breaker Open -Over Temperature Shutdown -Overload Shutdown -Resiliency Vote -Resilient -Static Switch Disable -Synch Enable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629341&prj=632&rqi=OAjhjPvM8R8amTSYfXrojTLkWt
YT1ELEC-365-001 | a21092ea-4709-4cd8-925e-115ba5777eee | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | charitysamar@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_M1_25 | LVSB - Low Voltage Switchboard |  | i-Box | Please attach/provide the calibration certificates for the exact test instrument used. The Cable Insulation Resistance Test conducted on the cables on July 13, 2026, was performed using a Kyoritsu test instrument with Serial Number E8528764. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628833&prj=632&rqi=UEIj3v404aFaH6Zwxo5NEWKi9k
YT1ELEC-603-002 | 82548ddc-4f73-4893-9bda-b466792367a0 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_R_28 | LVSB - Low Voltage Switchboard |  | i-Box | During YT inspection with GC and vendor, found the termination for contact is not as per drawing. Drawing show termination from only 2 MCB (Y3 & Y4) while on site termination is connecting from 3 outgoing MCB to contactor C2 (1L2-21, 1L2-22, 1L2-23). Please advise. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628641&prj=632&rqi=tWZFFy4yqA5uA4qjyGVBW6tY9l
YT1ELEC-555-001 | ea384072-a3ac-4f9d-a7b9-592bd5439810 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1ATSM_M1R_27 | ATS - Automatic Transfer Switch |  |  | During YT inspection, noticed the quantity for fuse inside the panel is not the same as in the drawing. Total quantity for fuse inside drawing is 9 nos while the total quantity inside the panel is 10 nos. Please confirm the nos of fuse and do some amendment if necessary. This issue is applied to all unit 1ATSM panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628642&prj=632&rqi=ZH25SHi9TYZKgpKIBEoFHsAdaD
GT1ELEC-178-001 | 8cc678b4-7e8a-4e47-9c4e-02362ed87946 | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_M1 | MSB - Main Input Switchboard |  |  | During the UPS_M1 Failure Mode Test Under Utilities Supply (Failure of UPS Batteries for 5min). The LiBattery breaker was switched OFF. Initially, the UPS transferred to Static Bypass mode. After the LiBattery breaker was isolated, the UPS transferred to Double Conversion mode. During testing 50% load. Approximately 1-2 mins later, the following breakers tripped due to Ground Fault Protection: 1) Incoming from Tx (Q_01) : Tripping A (1200A) : time (0.00sec) 2) Incoming for UPS_M1 (Q_10) : Tripping A (600A) : time (0.00sec) Additionally, the time and date settings in the micrologic protection units were not configured correctly, preventing accurate identification of the trip sequence and confirmation of which breaker operated first. The vendor shall carry out the detailed troubleshooting to the determine the cause of the Ground Fault Trips. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628638&prj=632&rqi=S5GFIhSMhfVyiK5XWudzWo6gZm
YT1ELEC-364-001 | 5e1f139c-d2cf-479d-a929-9ef1ff5f73b1 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_M1_24 | LVSB - Low Voltage Switchboard |  | i-Box | During YT inspection, found 1 of the timers that located beside the contactor inside panel is not turn on. All the timers T2 and T3 is turn on while T1 beside the contactor C1 is turn off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628640&prj=632&rqi=wuXvJfHFboX0AGDQaS7k3f0CDJ
RT1MECH-277-001 | 5e2ccedf-5fb5-4907-afd8-3f1dadbd6ace | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_M1_07 | EF - Exhaust Fan |  |  | Permanent equipment labels affixed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628634&prj=632&rqi=JX9w2oACMpmYFI4GKH4FjAjZJ6
YT1ELEC-603-001 | 608bbe72-d50a-4b9b-9cee-f7c06ad02806 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_R_28 | LVSB - Low Voltage Switchboard |  | i-Box | During YT inspection with GC and vendor, found the termination for contact is not as per drawing. Drawing show termination from only 2 MCB (R3 & R4) while on site termination is connecting from 3 outgoing MCB to contactor C1 (1L1-21, 1L1-22, 1L1-23. Please advise. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628637&prj=632&rqi=nkdJoFPU9jQbEigxoK1CNUZYQA
RT1MECH-625-001 | 51f31807-9583-4d9d-918a-0492418e66f6 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1LEAK_C_1 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628687&prj=632&rqi=GEZDtpa6XbDfZ6DdGEzAuKhAf5
RT1MECH-621-001 | 242a0eee-5d3d-4b6a-a0d9-5ef34e58305a | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1LEAKZ_D_3 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628509&prj=632&rqi=HKTsr1uHb2ShLj9CTlnQuY0bX0
RT1MECH-616-001 | 455bdb7f-1f51-464e-98d4-3e9066df73df | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1LEAKZ_C_4 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628502&prj=632&rqi=3gPYAJ3rTLJPIPQPfAIUYAacxS
RT1MECH-607-001 | 498205d0-ab5d-452e-9358-01da0aea56f6 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1LEAKZ_A_4A | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628467&prj=632&rqi=xxkwHe9i4VyGLP1cZ7tjlTj0DG
RT1MECH-615-001 | eeea2b6b-c88a-4fa3-aaaf-f9f0369b3996 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1LEAKZ_C_1 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628495&prj=632&rqi=7O9RqaMAGBWpCygJwdrOdHxNmf
RT1MECH-608-001 | 25339196-be04-4b29-b035-36a25dfb0d03 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1LEAKZ_A_3 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628470&prj=632&rqi=EoUGhkJCSeZNLkvr8NhoUq7Xst
RT1MECH-611-001 | ad1728cb-e1cc-4724-a9b7-277bb9251c2a | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1LEAKZ_B_3 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628493&prj=632&rqi=GFDP7dTixHymffijGHNOo0R7L5
YT1ELEC-5-002 | a97d5002-62cf-43aa-b2af-530b12d20098 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | charitysamar@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_E | RMU - Ring Main Unit |  |  | The shielding cable has been cut and rejoined using a bolted connection (bolts and nuts). Confirmation from ABB is required to verify whether this repair method is acceptable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628515&prj=632&rqi=gZYwQfGzOsKCW8UZj4tq3FpyFL
RT1MECH-624-001 | 31ffd198-6794-407e-8930-bc1555d50bbe | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1LEAKZ_M1_1 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628507&prj=632&rqi=EE0yxhh5yJHzbN0TQkqY0Jn0y1
RT1MECH-619-001 | 242a5936-04fb-4d12-a899-d6035b715673 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1LEAKZ_D_1 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628503&prj=632&rqi=Lrf3LuYFvgYdBSYjE9iaUvtP25
RT1MECH-620-001 | c184e4ae-d4a0-46bf-bc2e-80948cbd11bd | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1LEAKZ_D_4A | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628506&prj=632&rqi=XSt0ig8qiid12yr4DPfOhtoSfg
RT1MECH-623-001 | 633a9cbd-43a3-40e0-823f-88a476b8a1e4 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1LEAKZ_D_4 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628505&prj=632&rqi=WXFjbTCOrf0B1Y6HrE1KVtmOtm
RT1MECH-614-001 | eeab89af-0676-4a1f-9260-a46ccb7f3708 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1LEAKZ_B_4 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628494&prj=632&rqi=vfrrIufU1otnNc7vTLmEbmGKhM
RT1MECH-622-001 | 253bac59-359d-4a43-98c8-29a3775dd1c0 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1LEAKZ_D_2 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628504&prj=632&rqi=wqgvMlG5TCucQ7JcAXp8h7xWMK
RT1MECH-613-001 | 6e3d5eb7-2ad4-48ee-bd2f-7e2be726f5eb | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1LEAKZ_B_2 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628492&prj=632&rqi=aetA3XULD9QyRrckHftXuHG3kL
RT1MECH-605-001 | 42df937d-d9d8-4768-8af3-4827730aace7 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1LEAKZ_A_2A | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628269&prj=632&rqi=326wbTbVfi82LfS9OgVdFteayv
RT1MECH-612-001 | 4300f951-1233-455e-ade8-350647e7807f | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1LEAKZ_B_1A | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628267&prj=632&rqi=kYiBeMTnZVyPrDmFLYW2a5PQPX
RT1MECH-610-001 | b4d6844a-702c-47af-ada6-a2e42e346208 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | samintarajarujunan@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1LEAKZ_B_1 | Water Leak Detection |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628266&prj=632&rqi=bfqrHEqJRmOgQCebIIzCLJVMhb
YT1ELEC-130-001 | dba698b8-ef74-4311-8dbd-97b697de982c | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B1 | UPS - Uninterrupted Power Supply |  |  | GC need provide Photo Evidence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628112&prj=632&rqi=D4TMDU39M1poCleRk5RlOi9V7K
YT1MECH-306-003 | 35c8b31e-765f-4972-b615-7ed14d9ccaab | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | The wall penetration is still not fire sealed. This outstanding work is preventing us from issuing yellow tag for PUMP ROOM 1 & PUMP ROOM 2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628166&prj=632&rqi=lErxNzcTEzmfJYwuMxwsfQmqok
YT1MECH-306-004 | c35c8240-2a2b-4d22-a476-1e6372300bb0 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | The earth chamber still not tested yet & kindly place the labelling or tagging at Earth Chamber follow the Earthing Main Schematic labelling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628167&prj=632&rqi=VGDExZukGsPyf74bhGYtp372FX
YT1MECH-307-004 | 2fb5ffd0-f9ab-4150-ac30-add1c6934bd1 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_2 | FPMP - Fuel Pump |  |  | All permanent earthing not complete installed & labelling in PUMP ROOM 1 & PUMP ROOM 2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627957&prj=632&rqi=l1in6Mbv152I0vmbc5nEFn5ado
YT1DCOS-12-001 | d3e62d56-8fe7-ee27-cf45-63b4222fd820 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Controls | equipment | 1DCOS_RIO_3 | DCOS - Control Panels |  |  | Wrong power source tagging. supposed me 38-B6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628264&prj=632&rqi=ZW5oxPgQDhBbZVRwxKZviYmh4M
YT1DCOS-10-001 | b52958b3-4a0e-9ceb-2dd0-6d2ff0c402f7 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Controls | equipment | 1DCOS_RIO_1 | DCOS - Control Panels |  |  | Wrong tagging for power supply. Supposed to be B1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628263&prj=632&rqi=TFm7dYEhciFNVVSjgXMnnLKylh
GT1ELEC-127-001 | 310cf2f0-63f4-4f92-ab3a-1db600cffcfe | JH02-1/2 | 632 | APAC | Closed | P3 Low DCOS | ahmadfuad@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | Battery time remaining status on DCOS to recheck formula as it does not indicate correct time as per UPS HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627490&prj=632&rqi=9aDq3kikCxUwpmh50h3tVz4pDo
GT1ELEC-127-002 | 7af7fcd1-e902-43a9-ab62-97c41c6b8f4b | JH02-1/2 | 632 | APAC | Open | P3 Low CX | ahmadfuad@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | UPS is showing kWh/day status on HMI, however DCOS is using kWh as per approved SICD. Eaton to verify if the correct HMI status with per day status should be there or to be revise to kWh | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627491&prj=632&rqi=fA8eAh4PcR3j3If97HmrWbQRoj
GT1ELEC-127-003 | 7c051973-3586-4a45-b5a0-db582331af38 | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | UPS has been verified with latest new firmware version CSB : 5.12.342. Eaton to ensure the latest version update is incorporated in new setting revision and submit to design consultant for approval. Please attached new approved setting document for record purpose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627493&prj=632&rqi=4zjsv57nvCuRARkKZ0SjX7AyGO
YT1ELEC-7-001 | 4afc4881-e76e-4c23-b094-cef59f1a9f96 | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_A | RMU - Ring Main Unit |  |  | During preparation of UPS_A1 load, test it was observed that RMU_A1 trip due to earth fault trip to Q_03 outgoing breaker to MLTX_A1. Further investigation, it was found cable shield for the 3C phase cables were found to be outside of ZCT. RYB to seek clarification via email from ABB. As for the solution to bring the cable shield inside the ZCT is acceptable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627190&prj=632&rqi=ydTDuG89FYznfRsLwxSsQ4hcvb
GI-253 | bf52e7ac-6750-4dab-b7de-244911a5ef8c | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | junkaichan@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | CRAY Isolator installed right below water flexible hose connection - risk of damage/safety during maintenance/accidental water leakage. Suggest checking with design team if the isolator design is acceptable or any modification required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626444&prj=632&rqi=AkzRrVFDfxaII51dlDlcDpXEdu
YT1MECH-210-001 | 9cdc909d-91ed-43f2-b5a8-386b2c3dc2bd | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_M2_2 | CRAH - Computer room air handler |  |  | Confirm that Chilled Water has been pre-commissioned, flushed and treated to approved Method Statement and witnessed by GC/CxA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626306&prj=632&rqi=cP38HcJvkqCQMBHCelumlaZPGc
YT1MECH-209-002 | 43327fd0-0b7c-4cf1-b787-88ad06d6e3d4 | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_M2_1 | CRAH - Computer room air handler |  |  | Pressure Testing and flushing documents are approved on Project Portal and attached to the correct section of Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626305&prj=632&rqi=8GBONrRxQ8WnhURCT0CLgASnU1
YT1MECH-209-001 | ccdb663d-7caf-48a1-8d03-fdc71f3033ed | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_M2_1 | CRAH - Computer room air handler |  |  | Confirm that Chilled Water has been pre-commissioned, flushed and treated to approved Method Statement and witnessed by GC/CxA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626304&prj=632&rqi=ZMEp3jJxRppYeTuYw32evFenWj
YT1MECH-210-002 | f7c2ee81-595b-4312-b466-accb6e581ee4 | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | samintarajarujunan@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_M2_2 | CRAH - Computer room air handler |  |  | Pressure Testing and flushing documents are approved on Project Portal and attached to the correct section of Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626307&prj=632&rqi=YsOGM3Rgrxnn3BKsH8hjKmxET1
RT1ELEC-241-001 | 542ae0f7-fe6d-476e-90b0-474343b02b9f | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1FOLDZ_M1_3 | LEAK - Leak Detection |  |  | The panel no permanent tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626281&prj=632&rqi=hOtdyjhKzcW9SWBhjs4mpL2lql
RT1ELEC-242-001 | 3bb7a09f-65fa-4f13-8ca0-f5aa16c35a88 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1FOLDZ_M1_4 | LEAK - Leak Detection |  |  | The panel no permanent tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626282&prj=632&rqi=guLudLa0dOnRUkk7xpMutrAzM8
RT1ELEC-246-002 | 8712c2c6-7f6c-4a0e-acd4-d0fa7d83cdf9 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1FOLDZ_D_1 | LEAK - Leak Detection |  |  | The panel alignment requires adjustment as it is slightly slanted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626288&prj=632&rqi=szOp9OqAKWh2nr4zc1QuCIxtWO
RT1ELEC-245-001 | 7f52e3c4-818a-4b6a-9a99-a87891bf3d7a | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1FOLDZ_C_1 (L1 near DG) | LEAK - Leak Detection |  |  | The panel no permanent tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626285&prj=632&rqi=XmpwcYVFF3BmFMNIWoEq0EFko8
RT1ELEC-240-001 | 989e769c-31bf-4c3b-9815-317a858e9897 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1FOLDZ_M1_2 | LEAK - Leak Detection |  |  | The panel no permanent tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626280&prj=632&rqi=krR9wMxYoFGC8jRWslkuI9ckjy
RT1ELEC-243-001 | 1a929e29-9b50-4c01-acff-0ae23f6526ad | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1FOLDZ_C_2 | LEAK - Leak Detection |  |  | The panel no permanent tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626283&prj=632&rqi=2A4rcwnn5tRtWliZ5CUc6S7q6C
RT1ELEC-248-001 | c86ed473-891b-4419-90b3-14872d193606 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1FOLDZ_B_2 | LEAK - Leak Detection |  |  | The panel no permanent tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626290&prj=632&rqi=CKrsDEDttskyZDND1U8djyUmJK
RT1ELEC-247-001 | 0bb92103-1d98-45b6-91e2-587dd5c30336 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1FOLDZ_A_2 | LEAK - Leak Detection |  |  | The panel no permanent tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626289&prj=632&rqi=BwhMb25l6qVET6BxZWnVjczLYG
RT1ELEC-244-001 | 8209ff48-cc73-4684-bef5-da90310c2c83 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1FOLDZ_D_2 | LEAK - Leak Detection |  |  | the panel no permanent tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626284&prj=632&rqi=Z4UMfTKQ8jiYP9HH4CVH7LOfYl
RT1ELEC-239-001 | 69bd9601-e669-48d1-a3ce-2426091d40f2 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1FOLDZ_M1_1 | LEAK - Leak Detection |  |  | The permanent labelling not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626278&prj=632&rqi=89gOsTuLAYI4XMpzJGA8YCnH9b
RT1ELEC-246-001 | 2eb2a579-d07b-4dbc-8e98-6c39aa006d69 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1FOLDZ_D_1 | LEAK - Leak Detection |  |  | The panel no permanent tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626286&prj=632&rqi=sz1DLiW51FW37PDSLBFKNFt4DQ
GI-250 | 5911c537-404f-49f5-aff5-eb791c36ef52 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_M1R_03 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_M1R_03 bottom cover of the busbar section dented. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625741&prj=632&rqi=l6XY9Me0FzXCDRC0ES3shpNxZp
GI-249 | 2f9e94f8-0797-4255-b05a-7ef80c8ff087 | JH02-1/2 | 632 | APAC | Open | P1 High CX | pauljohnson@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_M2 | RMU - Ring Main Unit |  |  | 1BTU_M2 side of the unit is damaged and the door now not aligned to close. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625740&prj=632&rqi=1Sl3N4SHNTUYSNtJ3OEDoIoAva
GI-248 | 57fd8f4e-6f92-4add-8b39-00591e67cc14 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | junkaichan@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1MWP_M1_1 | DOMW - Domestic Water Set |  |  | coiled up cable in MCC cabinet not terminated - to be clarified the purpose. if unused to be wrapped up the exposed termination. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625589&prj=632&rqi=NzZVYwQgtpiMCQymi6cD8MnAXc
GI-247 | 219ce8ef-1954-4889-bc4a-fad0f54f241d | JH02-1/2 | 632 | APAC | Open | P3 Low CX | junkaichan@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1MWP_M1_1 | DOMW - Domestic Water Set |  |  | Pressure switch control cable no label. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625588&prj=632&rqi=9pFJw78l8cy1PecRmCsMVJDJWG
RT1ELEC-201-002 | 8a104557-e4c6-4a21-8549-6a88ce138071 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-06-16 04:00:00.000 +0400 | Commissioning Authority | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_R_4 | MDSB - Mech Distribution Switchboard |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625415&prj=632&rqi=tlbHCXJZmyft4iyRXFOvO0wQ4M
YT1MECH-306-002 | 8c96d065-7639-4167-bfd4-f5c30abe36d4 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | Cable missing the tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625420&prj=632&rqi=07zIBws0OlD2366rvo2sm84SM1
YT1MECH-306-001 | 118c93cc-37ed-466c-a3fe-21c2e0e9216c | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | Cable entry at the Fuel Pump Panel (bottom) of the panel is not properly gland and the cable need flexible conduit before entering the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625412&prj=632&rqi=1S8EO3OX4edcqBgMigECK4HExl
YT1MECH-307-002 | 6ca444c8-d84a-4222-8a10-cbdf301296b8 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_2 | FPMP - Fuel Pump |  |  | The cabling missing tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625418&prj=632&rqi=uqALqukSeBza06BnmgDpJTeEAK
YT1MECH-307-001 | ea7b689a-3cd2-44f4-8cfc-73e96cfccb64 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_2 | FPMP - Fuel Pump |  |  | Cable entry at the Fuel Pump Panel (bottom) of the panel is not properly gland and the cable need flexible conduit before entering the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625417&prj=632&rqi=5y3T00yAjyIpoTpAAuEZoAz2wi
YT1MECH-307-003 | c7999563-8092-4ec2-a6d3-20b45eb8a81a | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_2 | FPMP - Fuel Pump |  |  | Cable dressing is not acceptable. Cable ties have been at the cable bend, causing excessive bending. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625419&prj=632&rqi=vxEAIpbzlYn3pHoPpwdAu6irs2
YT1MECH-310-001 | 7c250783-5a88-4c92-b687-7389f61b5638 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_4 | FPMP - Fuel Pump |  |  | Cable entry at the Fuel Pump Panel (bottom) of the panel is not properly gland and the cable need flexible conduit before entering the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625430&prj=632&rqi=TtzdiAV5M2s6MGyRNgWSl2qgTt
YT1MECH-310-002 | a47f8d49-1501-443f-ba59-d67468e54106 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_4 | FPMP - Fuel Pump |  |  | the cable missing tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625431&prj=632&rqi=G0VBJKQiZhfh2435nin5HRSRbK
RT1ELEC-201-001 | 7d83a9d4-5a9e-4272-8075-bb973b8e6bb2 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-06-16 04:00:00.000 +0400 | Commissioning Authority | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_R_4 | MDSB - Mech Distribution Switchboard |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625413&prj=632&rqi=eS4vkTa47vbUg0TvzrWC76mTsm
YT1MECH-309-003 | 8aaf6760-3187-41d4-adcd-5d3728c54856 | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_3 | FPMP - Fuel Pump |  |  | Cable dressing is not acceptable. Cable ties have been at the cable bend, causing excessive bending. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625429&prj=632&rqi=8CFg8qP8s0hLMzgGOgkxWbfeg0
YT1MECH-309-002 | b066b60c-4841-4cf8-875d-27287190b8fa | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_3 | FPMP - Fuel Pump |  |  | The cable missing tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625428&prj=632&rqi=Uyu5U0PjWBKMOEVoe17ItmEPUs
YT1MECH-309-001 | 5591fe9b-d60c-40e2-81cb-95a2f629c20a | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_3 | FPMP - Fuel Pump |  |  | Cable entry at the Fuel Pump Panel (bottom) of the panel is not properly gland and the cable need flexible conduit before entering the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625427&prj=632&rqi=ZiObMJnoGZn0XhKxtLhZteeOiI
YT1MECH-200-001 | 472e00e0-03c5-0e12-d0cb-48e5f3c4271d | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_A_2 | CRAH - Computer room air handler |  |  | Conduit for fire is tear | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626191&prj=632&rqi=fyzv0mMkQzhntkHnLHIvYMfTP3
YT1MECH-200-002 | 7aa20574-f9bd-59fd-e7de-ffeee59a284c | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_A_2 | CRAH - Computer room air handler |  |  | isolator for power source to be label to differentiate power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626192&prj=632&rqi=q0VN4PthUkB2hDoQLz38I7jSSK
YT1MECH-200-003 | 13820512-bb62-3c47-a77f-d03972e2c235 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_A_2 | CRAH - Computer room air handler |  |  | Conduit to be labelled serving whats trade/service | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626193&prj=632&rqi=guXP0zaqP1CJEDjPnLCiSXb3Aw
GI-245 | 770dc9bb-6ab2-46fc-83f9-5623759979e1 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_M2R_7 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624918&prj=632&rqi=5qhqPIhI86qvnmRz6bmeIZgrS6
GI-241 | 250683ee-e167-46da-8d37-66cc9f82ef29 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_M2R_2 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624912&prj=632&rqi=FyclmQQX4ktnRrao9aZUtXPMqf
GI-242 | dbfe7a16-87c0-4a18-8d55-a7c5a2ec205d | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_M2R_3 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624914&prj=632&rqi=Haj9rgXcHWrYQfViuud489P57h
GI-244 | 11733d14-a34a-4d15-9cc4-55355841ce8e | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_M2R_6 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624917&prj=632&rqi=TD8wXyAnMdxPb4lG5utP7fCfxX
GI-246 | 7d7ffee3-7207-4597-9534-24c1178df558 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_M2R_8 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624920&prj=632&rqi=oB5PbZDbIeoronfAZE0qCRLz8j
GI-243 | 7c10400e-c727-4a4f-9e04-de838ecc492b | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_M2R_5 | MDSB - Mech Distribution Switchboard |  |  | Tagging & SLD needs to match the Chiller ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624916&prj=632&rqi=BspA43UOy1HXm3kLooqdAYQnxR
YT1MECH-202-001 | d60ceada-3c7c-77ff-dac9-2b916971cbfc | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_A_4 | CRAH - Computer room air handler |  |  | tear conduit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624819&prj=632&rqi=yuFnIbvOaELtqRRnGmtQPhFJG5
YT1MECH-201-001 | 9ee246c4-312a-3ef3-3180-a9225a8883b7 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_A_3 | CRAH - Computer room air handler |  |  | isolator to be label at A and B source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624820&prj=632&rqi=fezu4alepj3zelJAM86VnBq6xS
YT1MECH-203-001 | d42c8bc3-c927-92d2-6f19-497d409928b8 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_A_5 | CRAH - Computer room air handler |  |  | Conduit to be done properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624821&prj=632&rqi=LbUW7soG3ZX23zSDX1nYYvBSak
GI-240 | 534f138b-39a7-48b9-86dd-d31f0e046764 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-06-10 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_R_15 | LVSB - Low Voltage Switchboard |  | i-Box | Closed issue panel warning sign sticker refer photo attachment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624632&prj=632&rqi=uVkWFYaRo4BIoWpXXMSijAsqik
GI-239 | ffaa4af8-e78b-4fc6-aa18-3261dfe1b116 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | jefferygo@gsm.com.sg | 2026-06-10 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_M1_15 HVAC DB | LVSB - Low Voltage Switchboard |  | i-Box | Closed issue Panel warning sign sticker refer photo attachment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624631&prj=632&rqi=zS1ozksrS7GgN7BqWtbsNvzcKm
YT1MECH-294-001 | 64be47f5-28ea-ba50-99d7-ce285445cac5 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_1_CHWBT | CHWBT - Chilled water buffer tank |  |  | valve clashing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624294&prj=632&rqi=PEN9q4mBYo3EIcnl5taYRK2JYH
YT1MECH-295-001 | 7884e4cb-b1dd-0873-0841-f19a201cddf6 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_2_CHWBT | CHWBT - Chilled water buffer tank |  |  | Valve clashing with tank | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624293&prj=632&rqi=RjnazAPLENTu74TGO1hoMxCE5L
YT1MECH-299-003 | c8c1f244-701d-6456-a714-01a0bd3fe855 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_6_CHWBT | CHWBT - Chilled water buffer tank |  |  | flow direction label to be install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624291&prj=632&rqi=3PuQl4P7XPeTqMe5roCWxUOz7i
YT1MECH-299-002 | 500c8e1a-1048-2ef9-9bea-3ad537eb08f4 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_6_CHWBT | CHWBT - Chilled water buffer tank |  |  | insulation to redo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624290&prj=632&rqi=rWoMEOhBmCCrIi8pDIlDRrqcQZ
YT1MECH-300-001 | d6fcedb1-fc4e-40a9-53c2-c4f068979c52 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_7_CHWBT | CHWBT - Chilled water buffer tank |  |  | Accesories not intalled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624292&prj=632&rqi=vFN06W9WfYkKsn7zJXtFkZXgOY
YT1MECH-299-001 | b941585c-ed74-725b-79db-28dd3fc46c07 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_6_CHWBT | CHWBT - Chilled water buffer tank |  |  | Valve clashing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624289&prj=632&rqi=eB1RL1x1WXVKLUjY8AXkrBurxv
YT1ELEC-214-001 | 9df0ca35-6974-43b5-8d79-e51d2ba4d0ea | JH02-1/2 | 632 | APAC | Closed | P1 High CX | ahmadfuad@commtechasia.com | 2026-06-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_M2R_9 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_M2R_9 was energised prior obtaining Conditional Yellow Tag (CYT) or Yellow Tag (YT) given to the panel which deviate from the established Cx process and EQIX playbook. GC to submit RCA detailing the sequence of event and the corrective action plan to prevent same issue occurring again in future. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624228&prj=632&rqi=LZlyrxsDn3FGTfeeXqsuzqXbbb
YT1ELEC-450-001 | f37e9e63-a2b9-48e3-90f5-fe7fb0b02512 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-06-06 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_R_03 | LVSB - Low Voltage Switchboard |  | i-Box | Circuit tagging missing on plastic cover. To install circuit tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624229&prj=632&rqi=PyUfQ2aoNbJj6pyQVIa5l2qxU6
YT1MECH-192-002 | da344701-b459-ec95-476b-5eda7da7f7f6 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_R_4 | CRAH - Computer room air handler |  |  | Comm cable is not properly tagged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624274&prj=632&rqi=f8qQdxxLHpBKD6bObbhYwcPERu
YT1MECH-192-005 | bc7365e8-5837-60f2-8af0-08a7a7b659ea | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_R_4 | CRAH - Computer room air handler |  |  | Tear conduit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624277&prj=632&rqi=Hr625DHo62QlNQTc2FeuhrYg8c
RT1ELEC-378-001 | cbe718c6-3d28-445f-8891-9ced9fba9193 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_M1_15 HVAC DB | LVSB - Low Voltage Switchboard |  | i-Box | Panel warning sign stickers are missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624101&prj=632&rqi=Lbi4sn2HfhRsnDEvTaD0rX5Bsx
YT1MECH-192-003 | 3c24baf4-1e8e-556d-51ec-3e36812d2658 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_R_4 | CRAH - Computer room air handler |  |  | Isolator to be labelled power source And B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624275&prj=632&rqi=403Eh6gwlZpZMMScyovbbQIxXV
RT1ELEC-472-001 | cca81c49-2433-4da4-b1c6-d1e54c3348ef | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_R_15 | LVSB - Low Voltage Switchboard |  | i-Box | Panel warning sign stickers are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624104&prj=632&rqi=cRnoFXqr7t7Sy7Ji2n5mghrpc8
YT1MECH-192-001 | 273ee4f9-331b-0b0a-71a1-f77b7cc7f288 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_R_4 | CRAH - Computer room air handler |  |  | Fire cable not terminated per standard and unlabelled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624273&prj=632&rqi=ThrcWyOLTea9ASzUk8wBhj8f83
YT1MECH-192-004 | c5dfbba9-865e-8fd2-a390-4ed968ad36da | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_R_4 | CRAH - Computer room air handler |  |  | equipment is coated with dust and cleaning to be done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624276&prj=632&rqi=6ikUAe7imqgDqVUx323xNxHAaC
YT1MECH-271-001 | 882d4d06-f293-db5d-e1d5-41de95f0a8a9 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_M1_6_CHWP | CHWP - Chilled water pump |  |  | DCOS and Xinnetwork conduit not labelled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624014&prj=632&rqi=Q6fghQQ4ankWXkJpWuhM914inh
YT1MECH-272-002 | 702d6318-39b5-7508-4c2d-e78bd3b73e22 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_M1_7_CHWP | CHWP - Chilled water pump |  |  | torque mark misaligned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624021&prj=632&rqi=YJIdHJKXU5s5b9ufGN6zElbZCo
YT1MECH-271-002 | ddb883bc-572e-4028-e4b1-56645548c71f | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_M1_6_CHWP | CHWP - Chilled water pump |  |  | cabel tag missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624015&prj=632&rqi=LwMSR2jQWmk2Jtk6QLKv7ZEpOO
YT1MECH-272-001 | e7c79c8f-51e9-c052-e9ce-e68ef67153c8 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_M1_7_CHWP | CHWP - Chilled water pump |  |  | conduit to be labelled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624020&prj=632&rqi=qpNz2tCjvFRvuSDmugKQcM8ozf
YT1MECH-272-003 | 0f959880-5733-06b7-0577-afc8b83af7fa | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_M1_7_CHWP | CHWP - Chilled water pump |  |  | missing cable gland | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624023&prj=632&rqi=Af42Oa6Zz8aJnxvYV8wAZ5byvu
YT1MECH-268-001 | 376713a4-799e-dd82-040d-0f53d8d0b9cc | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_M1_3_CHWP | CHWP - Chilled water pump |  |  | labelling for trunking and conduit to be done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624011&prj=632&rqi=PifbikU9Ne0pCGLLzvEx1PWBm0
YT1MECH-276-001 | df570829-c993-eea6-04fa-2481a473d5af | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_M1_4_CWP | CWP - Condenser Water Pump |  |  | isolator cover missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624030&prj=632&rqi=LCqeRyIRverVQmcBCt6nUcWXJt
YT1MECH-279-001 | 24662461-eb23-2f4b-0c37-197f768d507a | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_M1_7_CWP | CWP - Condenser Water Pump |  |  | missing cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624024&prj=632&rqi=D2XO3PzwRReyfjdyxgoc7gm6mW
YT1MECH-268-002 | 3786a35a-c9ca-cabb-92d1-1cd8a51cf647 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_M1_3_CHWP | CHWP - Chilled water pump |  |  | Torque marking not done properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624012&prj=632&rqi=0Ue3C4PJmnTr1TPcGZFqYFROKy
YT1MECH-268-003 | 40aa2508-192b-457c-d068-d5c328f74ed9 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_M1_3_CHWP | CHWP - Chilled water pump |  |  | cable tagging missing xinnetwork | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624013&prj=632&rqi=Noe3hmFnjBM6MtTeBGq0M1FD8X
YT1MECH-269-001 | c3b8daa7-f620-9981-96b4-7d74eb26c4e2 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_M1_4_CHWP | CHWP - Chilled water pump |  |  | cable tagging not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624031&prj=632&rqi=9IXWl49bpa8A7U25bnWhX1dBRI
YT1MECH-271-003 | b9929c20-0f2e-6e6b-0076-7c01fa8aa2ac | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_M1_6_CHWP | CHWP - Chilled water pump |  |  | no cable gland | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624017&prj=632&rqi=uWxWIJzN9TRI9EdoWaTKSNgT2L
YT1MECH-246-003 | 2803e729-3e2f-4036-0869-aaf752792e04 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1PF_M1_7 | EF - Exhaust Fan |  |  | cable labelling is wrong and swapped over damper and mv fan | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623882&prj=632&rqi=0XMIWvDLct7gpdSfisMmI6EwMB
YT1MECH-244-001 | faf07551-d856-c3d3-ef01-03775f9ec218 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1PF_M1_4 | EF - Exhaust Fan |  |  | isolator IP rating compromise | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623874&prj=632&rqi=tqWKbkpp4qdPoCk9WYzWMtIari
YT1MECH-246-002 | 4ab9ed9f-78b0-39a6-22f4-1b4c31a52e10 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1PF_M1_7 | EF - Exhaust Fan |  |  | Isolator not labelled serving to which panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623881&prj=632&rqi=9A7XE3316ocyagfBVr9ASn6tCG
YT1MECH-246-001 | 57f12996-a8b3-94da-d213-0c4f61e35669 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1PF_M1_7 | EF - Exhaust Fan |  |  | Ip rating compromise since coring on isolator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623880&prj=632&rqi=3SvnuGEjC3CXBVRjxVtY5RRFgK
YT1MECH-243-001 | 49bbe950-3b1d-e77f-6d4e-eccb001b2b79 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1PF_M1_3 | EF - Exhaust Fan |  |  | Isolator IP rating compromise | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623879&prj=632&rqi=Dknp9lDcBprryUey2GaUnyYGrZ
RT1MECH-317-001 | 8b9e7340-97e2-17ff-ac0f-ed1c86425a31 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1TEF_M1_1 | EF - Exhaust Fan |  |  | GA and SLD not tally onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623756&prj=632&rqi=0grW9jmCcHfJzeoEg47BYmUIAb
YT1MECH-296-001 | 2dac4eaa-ff23-4654-897a-7ea0ed993a48 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_3_CHWBT | CHWBT - Chilled water buffer tank |  |  | Valve clashing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622619&prj=632&rqi=nrVkRmliJ0VMyJYnET9RmMzTpg
RT1ELEC-488-001 | f10edc35-4f5f-4324-ae8a-663eaa2dea31 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVSB_M1R_5 | LVSB - Low Voltage Switchboard |  | i-Box | The outgoing breaker tagging (Q_04, Q_06, Q_07) at 1LVSB_M1R_5 panel on site is not tally with the latest revision (Rev 02) of the SLD drawing. Please check and amend the drawing based on site condition. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622579&prj=632&rqi=K8zJ9STrbzpHwtAN9Er30jSyN8
YT1ELEC-392-001 | 265bd164-bba2-4664-ae97-e310e4be1ce2 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_CR_09 | LVSB - Low Voltage Switchboard |  | i-Box | Electrical wiring drawing does not tally with FCU layout drawing. Electrical drawing has CCT R1 to FCU_A_30, but FCU layout has this as FCU_A_25. (All other circuits are the same as this) Electrical drawing & LVDB SLD to be red-lined (updated) as per the FCU layout drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622358&prj=632&rqi=3kX93boPaZZucAGowOBtrFtUll
YT1ELEC-461-001 | 9f7f109d-77a9-4a16-ac2e-001eab4b0588 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_AR_09 | LVSB - Low Voltage Switchboard |  | i-Box | Electrical wiring drawing does not tally with FCU layout drawing. Electrical drawing has CCT R1 to FCU_A_02, but FCU layout has this as FCU_A_04. (All other circuits are the same as this) Electrical drawing & LVDB SLD to be red-lined (updated) as per the FCU layout drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622213&prj=632&rqi=ZAaM7xcg4rKKXRY8gGq2xgYUrq
RT1ELEC-213-001 | 48b43bc2-a88e-450e-a7db-15ec4b9e863e | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-05-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_M2R_4 | MDSB - Mech Distribution Switchboard |  |  | Outgoing breaker tagging Q_02 (To 1CHWSTR_M2_9_CWP) and Q_03 (To 1CHWSTR_M2_9_WCC) need to be revise to follow CWP (To 1CHWSTR_M2_3_CWP) and WCC number (To 1CHWSTR_M2_3_WCC). Typical to all 1MDSB_M2R_2 to 8 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621923&prj=632&rqi=E9M7TCtzqP7wgrpimg8gAHK8vI
YT1MECH-275-002 | 3310121c-d13b-4671-8f4e-d7d382edb004 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_M1_3_CWP | CWP - Condenser Water Pump |  |  | isolator box to change and label. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621773&prj=632&rqi=iZ63GtLNILtk3YQyx9yBdqr3Z5
YT1MECH-278-001 | 4ade87ff-e03a-00cd-d69d-a50e31f56c42 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_M1_6_CWP | CWP - Condenser Water Pump |  |  | no cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621778&prj=632&rqi=CBZqavlyUyJoC5xqv9gTfhA6DM
YT1MECH-275-001 | ff3eb201-ebf3-17da-80f2-fae6a21a0378 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_M1_3_CWP | CWP - Condenser Water Pump |  |  | no tagging at cat6 cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621772&prj=632&rqi=vQsySSmYLaepcGllwRH1M8OvGQ
GI-230 | b75524cd-7059-4a9f-970f-b193d84d37c3 | JH02-1/2 | 632 | APAC | Ready for Verification | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | it was observed that all pipes in Pump Room 1 & Pump Room 2 are not labeled, identified and painted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620183&prj=632&rqi=kskH1gMCc7aIs3HNom5qdLeNDj
GI-229 | b2e1c230-f260-44fc-9bdd-462c1ad91c03 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-05-04 04:00:00.000 +0400 |  |  | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | The pressure gauge, test point and flow switch are missing at Pump Room 2 & Pump Room 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620182&prj=632&rqi=KQofmsJauuiWZzHJzjtK20oGiG
GI-231 | b49256a1-09c1-4a8e-a2c9-16957c542fb2 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | All bolted connections are not torque tightened and some pipe support brackets are not completely installed. Applied to HSD Yard, Pump Room 1 and Pump Room 2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620184&prj=632&rqi=wR7ARUFcpODtNd7Y4hlvCjy1HK
GI-232 | 21bb0e82-07e1-478b-8adb-8243cc6b866d | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | AliHazmeerHamdan@commtechasia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FP_M1_1 | FPMP - Fuel Pump |  |  | it was observed Check Valve (FR_CV2 & FR_CV3) are installed in the wrong direction. Applied in Pump Room 2 & Pump Room 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620186&prj=632&rqi=nmBt2MbZGCGtgPeBU5zvBM0Sda
GI-233 | 2b8b7634-016d-4932-af9c-46af0a6b08be | JH02-1/2 | 632 | APAC | Open | P3 Low CX | AliHazmeerHamdan@commtechasia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Fuel | equipment | FPPUMP1 | FPMP - Fuel Pump |  |  | it was observed all pipes are no labeled, torque tightened, identified and painted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620188&prj=632&rqi=Z7Ywk7RzwbLNgDbQIrB6QbFoyx
YT1ELEC-65-001 | 517da5b8-3a13-4ee7-94c5-92803ac957aa | JH02-1/2 | 632 | APAC | Open | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1ATSM_M1R_02 | ATS - Automatic Transfer Switch |  |  | It was observed that there were no DCOS monitoring to 1ATSM_M1R_01 till 07 (supplying to CHW pumps). Honeywell to recheck with EoR and confirm if these ATSM panels supplying to CHWP require to be monitored or not in DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619676&prj=632&rqi=X4JXNpOEenNOu1iVTrPoTaewfQ
RT1MECH-186-001 | b08d9b95-fbee-ab81-7543-7fbc59ccfc55 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-24 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1AS_B_11 | FFU - Air Scrubber |  |  | isolator blocked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619443&prj=632&rqi=NwM7UOSsNBJsLJB7CbJFq4zLkA
RT1MECH-182-001 | 0a3a9fa4-4ee8-5221-1232-d2ddd9b5e3ad | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1AS_B_09 | FFU - Air Scrubber |  |  | fan clashing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619444&prj=632&rqi=jPxXCax2ElTqX4SqfylSvsGYgq
RT1MECH-208-001 | e2fd3697-029b-c26e-2fa2-4316a1933c87 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1AS_B_01 | FFU - Air Scrubber |  |  | faulty isolator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619438&prj=632&rqi=zineuvqMRG7auA0Jp2m7M3QC6b
YT1ELEC-212-001 | fc312109-dce9-4704-85c7-e9aaa3962402 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_M2R_4 | MDSB - Mech Distribution Switchboard |  |  | Outgoing compartment Q_03 nameplate shows to 1CHWSTR_M2_9_WCC. Actual on-site outgoing goes to 1CHWSTR_M2_03_WCC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619159&prj=632&rqi=sJFY8vIWLx38NfU2ew3FHHtYIs
RT1ELEC-372-001 | 6f5557b0-39f7-4cf3-a996-f7cb736bd7b9 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_M1R_33 | LVSB - Low Voltage Switchboard |  | i-Box | Permanent equipment labels missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619162&prj=632&rqi=Gs7UiAILmqhRXUYe8isyNtzPye
RT1MECH-210-001 | 99ae6a50-cb45-dc17-5c26-e9af7fe57074 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1AS_B_02 | FFU - Air Scrubber |  |  | Cement marks on unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619439&prj=632&rqi=jc8EFuEpkK96N9kwMvg0J5yV1G
RT1MECH-212-001 | f609052c-1a0d-feb2-086e-8cbfca895803 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1AS_B_03 | FFU - Air Scrubber |  |  | cable management to be done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619440&prj=632&rqi=DjDXIU6KwYKBHpll0WTk0QgrHM
RT1MECH-200-001 | 93561cf8-5e1c-012c-09b5-3b7ac8cf4ca2 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1AS_A_04 | FFU - Air Scrubber |  |  | power isolator blocked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619441&prj=632&rqi=m9MUBP9MyNvd9ONGF6RhmnFjK3
RT1MECH-229-001 | 15beb699-d1e0-f0e3-2a50-b19c041a190d | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_D_2 | CRAH - Computer room air handler |  |  | Confirm clear access is available to all CRAH components and that sufficient withdrawal space has been allowed for maintenance, removal and replacement of parts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619163&prj=632&rqi=K4cNktGwvQ9JXTgwFdH7rs5ihe
RT1MECH-243-001 | 7c8cd844-6559-1ca6-d73a-eb460c3baeae | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | imanuddinhamdan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_4 | CRAH - Computer room air handler |  |  | Valve bracket damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619168&prj=632&rqi=3HukVMvAnxTczNZd4QdTXhSZej
RT1MECH-232-001 | 623b1154-0168-7212-6bfe-bf62c842d4be | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_D_5 | CRAH - Computer room air handler |  |  | Confirm clear access is available to all CRAH components and that sufficient withdrawal space has been allowed for maintenance, removal and replacement of parts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619166&prj=632&rqi=hy3VS9I9EF17mKppt9JWxaKLX4
RT1MECH-230-001 | 0fcfb1cd-fe35-7c99-eb1e-80c476eee109 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_D_3 | CRAH - Computer room air handler |  |  | Confirm clear access is available to all CRAH components and that sufficient withdrawal space has been allowed for maintenance, removal and replacement of parts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619165&prj=632&rqi=MCsNNRwWQZPBdR4p1MBVnqf0d4
RT1MECH-228-001 | 098988d4-e01c-c81d-db78-32d34bde4000 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_D_1 | CRAH - Computer room air handler |  |  | Confirm clear access is available to all CRAH components and that sufficient withdrawal space has been allowed for maintenance, removal and replacement of parts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619164&prj=632&rqi=wCCRkAgqNaPdxH0aMeyTcOq7ng
RT1DCOS-42-001 | 301f84af-2f9f-4391-b37e-16f2c2fb09d4 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Controls | equipment | 1DCOS_CP_1 | DCOS - Control Panels |  |  | Neutral bar only provided for protected earth ( power earth bar). No functional earth (signal earth bar) provided for the panel. Other panels PCP, SCP, RIO, LCP has both functional. HNY to get confirmation from EoR. Aoolicable to all CP panels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618967&prj=632&rqi=n7oaPn7lSNweCInzxCI2OX8O28
RT1MECH-320-002 | f50bf378-d5e0-447d-95e9-21502d5fed51 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1MAU_M1_1 | AHU - Air handling unit |  |  | The equipment labelling has not been fixed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618004&prj=632&rqi=oQEa7VpIwsx5tAguRHx2ShYiM4
RT1MECH-320-003 | b6438b1a-da4e-43c6-8ff7-015a331bc54c | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1MAU_M1_1 | AHU - Air handling unit |  |  | To provide relevant project piping specifications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618005&prj=632&rqi=yha8FCSNRlxvl0bNnejM9YjPZY
RT1MECH-320-001 | ea9efbb3-42f7-4b4c-8712-669cf9d169e6 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1MAU_M1_1 | AHU - Air handling unit |  |  | Observed dents and scratches on the bottom plate of the MAU. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618001&prj=632&rqi=uXdCJVy6kTWxXPRyWYx7cDXHsF
YT1ELEC-122-001 | c6aab292-f87f-4b77-988c-e797f5fb52c0 | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | As per understanding from Siemens, the earthing from the TX to earth system, it should be 2 earths from the TX room earth bar to the TX LV side and 2 earths from the TX room earth bar to the TX MV side. Current onsite installation has all 4 earths from TX room earth bar to TX LV side. GC to confirm with vendor (Siemens) and NV5 that this is an acceptable installation method | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617768&prj=632&rqi=4jQvlEKXE2NtbALFUBmEa8Tgnf
RT1ELEC-382-001 | aa934e22-2cbf-44c5-bd12-439ff4ba1e3b | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | MuhammadHaziqZakaria@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_R_27 | LVSB - Low Voltage Switchboard |  | i-Box | Missing permanent nameplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617598&prj=632&rqi=8CMRYGOrYFtpBn7GB1ZDTatxit
RT1MECH-374-003 | 1db0b016-ed9d-4a8d-996d-ea136cbd6b4d | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1DWBP_M1_1 | DOMW - Domestic Water Set |  |  | No Tagging for Pump and Panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617613&prj=632&rqi=ebqTZcBVc2PXIrb4r89seycGaK
RT1MECH-368-001 | 6ceb4a3c-f85a-4152-b130-7bec154d915f | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1MWP_M1_1 | DOMW - Domestic Water Set |  |  | IP Rating for Panel to be updated with supporting letter from Supplier | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617290&prj=632&rqi=VovX7QyzeunKaIGmQ0jYIPhSpC
YT1ELEC-93-003 | 95c7d34d-6403-4386-8137-d3c5b192388e | JH02-1/2 | 632 | APAC | Closed | P1 High CX | ahmadfuad@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1SUDB_1 | SUDB - Secondary Utility Distribution Board |  |  | During energisation site walk conducted on Friday (3/4/2026), it was observed that there is a potential SF06 gas pressure issue at K01 Outgoing Feeder of 1SUDB_1. The SF06 pressure gauge indicates the reading is outside of the acceptable (green) range. ABB to investigate and determine the root cause of the issue whether it is due to gas leakage or instrument faulty. ABB to submit RCA for the issue to outline the findings corrective actions and preventive measure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617355&prj=632&rqi=q3JUfP8jQmfrABoDvZ4NASAshg
RT1MECH-368-003 | 57f52cf8-1eb5-4408-a73b-3f22028249bf | JH02-1/2 | 632 | APAC | Open | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1MWP_M1_1 | DOMW - Domestic Water Set |  |  | Missing Labelling for equipment and warning sign | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617294&prj=632&rqi=5tui0UkT4OMOYfSUc8HigSbDKg
RT1MECH-374-002 | c62468c7-f64d-434c-add3-d01c6db94950 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1DWBP_M1_1 | DOMW - Domestic Water Set |  |  | SLD Drawing to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617338&prj=632&rqi=gnydbdTUMQQzv81r2m9pecdnOE
RT1MECH-378-001 | f10f1f93-2cf3-4877-9240-59c19fc0ff9b | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1RWFP_M1_1 | DOMW - Domestic Water Set |  |  | Panel IP Rating to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617332&prj=632&rqi=cdr1P6bmfo9xKlC2ralhJXXEfK
RT1MECH-251-002 | f58246a6-8f2c-40a7-9d4f-3236b586d0d2 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_2 | CRAH - Computer room air handler |  |  | Tagging for equipment is not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617289&prj=632&rqi=xhD4hCVvIhcbz4EKylaVFrcIFk
RT1MECH-294-001 | 86e3f04e-d182-4cbb-bbe2-d9691f7ec05d | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_M1_03 | EF - Exhaust Fan |  |  | Exhaust fan duct support bracket is installed in a slanted and improper alignment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617303&prj=632&rqi=laGcXR8D30U9Dmtn2vprtR6Q1R
RT1MECH-376-002 | be009754-f797-42c1-a361-43e7ace11e6d | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1TWSP_M1_1 | DOMW - Domestic Water Set |  |  | Panel tagging and Pump Tagging to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617336&prj=632&rqi=whcNM0iqp6ABRpE2Iiwz8ptFmd
RT1MECH-378-002 | c0029bc1-f2fa-4c66-bde6-912d8173ef87 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1RWFP_M1_1 | DOMW - Domestic Water Set |  |  | Panel naming and pump tagging to be updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617334&prj=632&rqi=n71NWPyDTul38pURyzmbvK2sfd
RT1MECH-374-001 | 3936c3cd-97cb-4ba2-97c4-258cc5196393 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1DWBP_M1_1 | DOMW - Domestic Water Set |  |  | Panel IP Rating to be clarified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617337&prj=632&rqi=0Y7ed1pcHyoxrKxoy0e2fUL1Jq
RT1MECH-368-002 | 04358bb7-fd06-4216-903c-8160fd6a688a | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1MWP_M1_1 | DOMW - Domestic Water Set |  |  | MCB Rating to be clarify. Drawing shows 40A while however onsite shows 32A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617291&prj=632&rqi=ZHEqJSn33wL5u05ioenbfsP9Me
RT1MECH-251-001 | 7a691905-7e4e-44aa-adc6-7afaf53f7a76 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_2 | CRAH - Computer room air handler |  |  | Internal tagging for the sensor to be updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617285&prj=632&rqi=upLt9fbGR6t5n4sFfBI7luPOJR
RT1MECH-255-002 | 0587ad3f-e930-499c-b06a-039b7f02a96e | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_6 | CRAH - Computer room air handler |  |  | No Permanent Tagging Installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617288&prj=632&rqi=DmL77jtudAU7iqq7H2Qcrvhb5U
RT1MECH-255-001 | a9558748-829d-49a2-a8a1-c53cc5e94096 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_6 | CRAH - Computer room air handler |  |  | Internal Tagging for equipment to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617287&prj=632&rqi=MV1T78m8VajlAANMK0XghOTKpB
RT1MECH-376-001 | c24e57c2-57ed-478b-a5cf-d2bc2ea3f47f | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | imanuddinhamdan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1TWSP_M1_1 | DOMW - Domestic Water Set |  |  | Single Line Drawing to be updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617335&prj=632&rqi=DxYvE6MfPvq2ugbAZLNzH48diC
RT1MECH-296-001 | 819ce44d-4ebb-4514-8f90-f3ca3494bbfe | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_M1_04 | EF - Exhaust Fan |  |  | Exhaust fan support bracket is in contact with the cable tray. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617214&prj=632&rqi=jgFe465pG3zzl0YqBLTnccCPpW
RT1MECH-292-002 | c9697208-b112-4250-9473-e8d40eb941ce | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_3 | EF - Exhaust Fan |  |  | Drawings missing from the panel. Applicable for all exhaust fan at Pre Action rooms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617218&prj=632&rqi=TG29C7Y1E4Pn1vXMViJDtw6k9O
RT1MECH-292-001 | cf56d94a-4fe6-453e-afae-bc33b3fa4c94 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_3 | EF - Exhaust Fan |  |  | Equipment layout drawing needs to be updated as the panel name shown is incorrect compared to the onsite panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617217&prj=632&rqi=bapT0Svc4KMRL6Hd6jgixEQvCk
RT1ELEC-495-001 | 276454a8-6a9f-4040-ab10-cbd5c9b9afa8 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVSB_M1_1 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign is not affixed to the panel. Applicable to all panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617000&prj=632&rqi=zLFcTETuF9toreepBMI8916X8a
RT1ELEC-592-001 | 70c19718-6d1a-4ab4-8ee8-205275cb2ebb | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_M2_10 | LVSB - Low Voltage Switchboard |  | i-Box | Panel nameplate is damaged. Applicable to 1LVDB_M2_10 and 1LVDB_M2_12 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616785&prj=632&rqi=Mgh4LjRTUIe9ttGxdTAridoN5I
RT1ELEC-486-001 | bd0aae8f-3bf5-486e-88f9-f20de1d70380 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_M2_06 | LVSB - Low Voltage Switchboard |  | i-Box | General arrangement and schematic Drawings not in the panel. Applicable to 1LVDB_M2_06 and 1LVDB_M2_07 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616783&prj=632&rqi=mURfrcJWkc7n78W0GBKcrkazXv
RT1ELEC-486-002 | 19913ab6-302e-4e52-9490-e44e0405b093 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_M2_06 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign is not affixed to the panels. Applicable to all panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616784&prj=632&rqi=31urFNb2IRhaTyMwA5poRaXTf4
RT1ELEC-593-001 | 815447f0-f401-4abb-9aba-d85ddb255993 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_M2_11 | LVSB - Low Voltage Switchboard |  | i-Box | Panel door knob is broken. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616786&prj=632&rqi=zNQrmKILk2RuLq9bpQRKUdUVyL
RT1MECH-351-004 | d1ef81ca-c543-485d-ab60-df70e9644718 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_1_CHWBT | CHWBT - Chilled water buffer tank |  |  | Permanent equipment labels not fixed. Apply to all Buffer Tanks. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615931&prj=632&rqi=Lcv9rE0t4mYgWbkkOk7MiJhOmO
RT1ELEC-145-001 | 0795da20-a3c6-47c7-85cc-769fc327625b | JH02-1/2 | 632 | APAC | Open | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D | MSB - Main Input Switchboard |  |  | HMI not yet positioned and installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615495&prj=632&rqi=ihdA8Jtfr9252rjzEA4ZMYBlvj
RT1ELEC-144-001 | c186d803-e64d-4c90-82a8-d2669bd22568 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | HMI not yet positioned and installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615493&prj=632&rqi=wiUbe5EtJ4vqTEZL2V6oyGYQif
YT1ELEC-13-001 | 6502f40b-1e49-4fe5-a1b6-ecd2c5446034 | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | pauljohnson@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | CT for L3 phase is to be replaced and to be tested once installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615490&prj=632&rqi=ib2dKStQD4mSD1oYDQ9XYM8IoK
RT1ELEC-146-001 | d187e04c-4c96-4b24-bd21-fe8a8c054979 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F | MSB - Main Input Switchboard |  |  | HMI not yet positioned and installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615499&prj=632&rqi=yAPE4H3znz7TYSYEBQvSv39jNM
RT1ELEC-37-001 | 58b6ff3a-e579-400f-8393-a8cb91b9ee9c | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1ATS_FR_02 | ATS - Automatic Transfer Switch |  |  | Panel door is unable to close properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615498&prj=632&rqi=l9pn7TkXgzuDaQzEFW2baP2C1J
RT1ELEC-33-001 | c6e32397-d585-4916-b495-1268d4ce9663 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1ATS_DR_01 | ATS - Automatic Transfer Switch |  |  | Dual power supply sign is not affixed to the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615494&prj=632&rqi=YiGdOhzBwUgMqLKyqI6dXmbK3B
RT1ELEC-366-001 | 7552a600-843f-443e-bc73-cbcad431b337 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_M1_25 | LVSB - Low Voltage Switchboard |  | i-Box | Latest revisions of both the General arrangement and schematic Drawings missing . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615497&prj=632&rqi=bEVjTpZs9VoANFJTdzDUce8Hai
YT1ELEC-11-001 | 8f8da18a-ab39-415d-a048-71e5fd9c10bf | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | pauljohnson@commtechasia.com | 2026-03-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | CT for L3 phase is to be replaced and to be tested once installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615491&prj=632&rqi=wlWH4nXKgEmjQdwWZkz1fCBN29
YT1ELEC-128-001 | 43665bf6-3abb-4ecc-9f0c-06bb6218686b | JH02-1/2 | 632 | APAC | Closed | P1 High CX | ahmadfuad@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | During busduct Cx2A was conducted between 1MSB_A to 1UPS_A1, it was observed the earth bar on UPS compartment and busduct N bar is too near to each other. It was observed that the spacing is less than 5mm spacing. GC to evaluate and make adjustment to ensure the safe gap of more than 25mm in between. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615338&prj=632&rqi=1LJ8fGEVDpodlCVYMnojyhGScf
RT1ELEC-13-001 | 1fa90cb9-a36a-4240-b7bb-e73b425ba943 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615090&prj=632&rqi=DNG1XGPCjrkL87eX5AFRREazin
RT1ELEC-12-001 | 82c4de83-d171-4267-8b61-1f341c27fe21 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615093&prj=632&rqi=L4ZC5vr262AWekRe5znw1e7hWn
RT1ELEC-5-001 | f2eea627-5186-4b3c-8109-4ab941c34bb4 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_E | RMU - Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615091&prj=632&rqi=vlZGXQPl50b8XttGuYwlnDfEch
RT1ELEC-11-001 | c08c399d-07a2-4fc9-9498-d58efd8fb7c8 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615089&prj=632&rqi=ufw3fZHJI0cREZCglOlY3PfRco
RT1MECH-330-001 | 956ddabb-84e0-41e3-8ee1-9d6f30f9b825 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_M1_1_CWP | CWP - Condenser Water Pump |  |  | Danger warning sign is not installed on panel. Apply for all CWP panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614869&prj=632&rqi=HCRf877nCPzAYnexMeLkcfejja
RT1MECH-323-001 | a03a67fa-bc37-402a-b882-5f0671d09bc2 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_M1_1_CHWP | CHWP - Chilled water pump |  |  | Danger warning sign is not installed on panel. Apply for all CHWP panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614787&prj=632&rqi=FwoeM58tAC5gI04wFdlrQqtE8b
RT1MECH-351-001 | d35669f0-e62d-49d8-ac83-1c5f419d0073 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_1_CHWBT | CHWBT - Chilled water buffer tank |  |  | Tank painting micron indicated 50 micron for external layer and 150 micron for internal layer as per document specification. GC to provide prove on painting micron. FAT document didnt shown the information. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614745&prj=632&rqi=8DMCDwvm8SLhU81Onwebulw47x
RT1MECH-351-003 | 4a4ec968-0a6e-4bc7-8890-d73dd268cbbe | JH02-1/2 | 632 | APAC | Open | P3 Low CX | ahmadfuad@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_1_CHWBT | CHWBT - Chilled water buffer tank |  |  | maintenance ladder to buffer tank stop short at plinth. However no access provided from ground to plinth. Suggest to extend the ladder to the ground. GC/ACT to confirm maintenance feasibility. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614748&prj=632&rqi=V3gbR1YDQtpLsL3E7qRdhLqmgn
RT1MECH-351-002 | e778b6fe-e87b-4144-8e7d-3a83782d7407 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_1_CHWBT | CHWBT - Chilled water buffer tank |  |  | Bolting at the floor and end connection did not indicate torque mark. To ensure all bolting have torque mark and demonstrate to CTA on site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614747&prj=632&rqi=6qe1useaHi1Q936F3fJpPmA74w
RT1ELEC-404-001 | 3c7c5587-122b-4e1d-ad47-ce50dc3e3ab6 | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_DR_8 | LVSB - Low Voltage Switchboard |  | i-Box | Proper circuit number tagging to install. Current installation is not acceptable. Refer to the sample as per attached. Typical for all LVDB panels. Please do one sample for review before proceed for other panels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614680&prj=632&rqi=wpzmQLJLEXuupqtMA0MgTNZLYt
RT1ELEC-96-001 | 5115504d-d866-4bfe-b057-fe8b23728139 | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STS_A1R1_1 | STS - Static Transfer Switch |  |  | FAT report provided is without the Primary Injection test on ACB breaker. As per Cx playbook, PI test is require to be conducted on site for breaker >250A. CSPM to arrange manpower to complete the testing on site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483514&prj=632&rqi=tAQXm2ZholQkYHMVK7qhzSeNjn
RT1ELEC-129-004 | 02420052-7792-4f7d-b6f3-796ed1cf407b | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | fazdliabdulmubin@eaton.com | 2026-03-02 04:00:00.000 +0400 | Commissioning Authority | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | Pictures of equipment in final position are taken and on Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483517&prj=632&rqi=aLuzHVmoF4cgmXL7upwckp6VZI
RT1ELEC-129-005 | cc2573b6-762c-4913-b7d5-6d4caa142d23 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | fazdliabdulmubin@eaton.com | 2026-03-02 04:00:00.000 +0400 | Commissioning Authority | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | Installation checklist from MCE completed (signed off) and attached to this checklist as a document (where Applicable) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483520&prj=632&rqi=M7qwr1xTP6N70KLTovkI0qXORY
YT1ELEC-179-001 | cf72b3cf-af1b-4e6b-ae75-2377054edf28 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-26 04:00:00.000 +0400 | Consultant | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_M1 | MSB - Main Input Switchboard |  |  | Q14 incorrect settings for the short time. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352255&prj=632&rqi=Q0wVxmsbAPgGQ4oIIzFY7UlszE
RT1ELEC-178-002 | 34a45b6f-0260-434e-a4c6-9eed2d1819cf | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  |  | HMI not yet positioned and installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204138&prj=632&rqi=G0BxDTkA0bQKymGBCOvLupbk95
RT1ELEC-181-001 | c1f9bd84-38f5-43c9-80a2-13aa7333c5b7 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  |  | HMI not yet in position and wall mounted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204140&prj=632&rqi=mjaGJ7y4OqN148v6Hz6pUN7g0I
RT1ELEC-180-001 | b7bf4197-832e-45e0-abd2-511d7357ffec | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_M1 | MSB - Main Input Switchboard |  |  | HMI not yet positioned and wall mounted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204143&prj=632&rqi=gtdPwME1lgGfYLYHzLCZkZrTGN
RT1ELEC-177-001 | 29e47899-9135-4951-97cd-af8f31afc96f | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_A | MSB - Main Input Switchboard |  |  | HMI not yet in position and wall mounted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204141&prj=632&rqi=gfRpXVcRjmCIVaFWaHHMIgP4bs
RT1ELEC-129-003 | d6e9550a-efc2-4f3e-aa03-7ffe22f2209e | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | Missing equipment tag for UPS to install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199815&prj=632&rqi=20htprIlI0A7w6cIyOdZil2Hnh
RT1ELEC-129-001 | fa066746-9e96-4c42-b18b-e0298037e627 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | DC+ and DC- busbar to tag '+' in red color and '-' in black color. Current on site missing color tag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199812&prj=632&rqi=lmvBoK20JZaeGTikiLKzGRF56s
RT1ELEC-129-002 | c4a07585-f3fd-4e6a-8149-120d19f069a4 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_A1 | UPS - Uninterrupted Power Supply |  |  | Missing drawing pocket to install infront of cover plate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199814&prj=632&rqi=5QZvX1A6qPSjEZukbPAMj6xnXo
YT1ELEC-177-001 | 71c4bc12-19dc-4431-874c-958408e29f70 | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | pauljohnson@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  |  | For the eWall Earthing Schematic, the schematic shows MSB, Transformer Room & Generator As a TNC (should be TNC-S) with a Neutral Earthlink shown inside the MSB. Also the schematic shows the LV cables from the TX & Genset as a PEN (Protective Earth & Neutral Combined) conductor. Current onsite LV cabling doesn't tally with the schematic and TNC set up, as cables installed have 14 earth cables from the TX to the MSB. GC to confirm with design. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198962&prj=632&rqi=G1GZy4M6r0u2efk2DUGc5LYIWF
RT1ELEC-158-001 | 7a28a595-0196-4d31-a304-31a19bd14372 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_M2R_8 | MDSB - Mech Distribution Switchboard |  |  | Control drawing missing in the pocket drawing. Control Cable tagging for control unable to check. Typical for all 1MDSB_M2R_2 to 8. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198963&prj=632&rqi=WReGj4qEdNz9765WVNWrVlbO6e
RT1ELEC-179-003 | ed1efe9c-5704-4806-b8c8-0c2af6c7a744 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | MSB_R HMI panel not yet installed as part of MSB Cx2A. Arrange with GC to expedite this installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198573&prj=632&rqi=pQMKh6ZEwxNDoBwuIp7TjX6bLO
RT1ELEC-520-001 | 7d1ae636-6240-7da0-2847-509fea9695b4 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_R_11 (40A) | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign is not installed on panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198567&prj=632&rqi=hAJjg8u8rPtqSLLkXFPIrGtrID
RT1ELEC-405-001 | c6abc23e-1ec4-bb85-6fee-56c1f439f460 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_DR_9 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign is not installed on panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198571&prj=632&rqi=3y2ieDNskyvTXJFhj1v2Wn178p
RT1ELEC-397-001 | edaaea85-f123-4710-811f-47c74803bbe9 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_C_13 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198578&prj=632&rqi=52hx9iB2wVczFULYjHTq5JXcjR
RT1ELEC-60-001 | 328eaa82-1e1d-4713-aa64-ba0b5e2d02a6 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1ATSM_DR_02 | ATS - Automatic Transfer Switch |  |  | Danger warning sign and dual supply warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198582&prj=632&rqi=PaMwuxekhCXrVKHJ79ttKLCjGf
RT1ELEC-178-001 | 115763b8-1a6c-4b5a-9ebc-d8c400245a76 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  |  | MSB_B HMI panel not yet installed as part of MSB Cx2A. Arrange with GC to expedite installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198576&prj=632&rqi=SRZwdEclY57cSoJeIF0deOfhcO
RT1ELEC-409-001 | 5e95c0c4-36b9-7301-26d0-4f54762207e4 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_D_13 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign is not installed on panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198562&prj=632&rqi=IJzP2Z3yNYWPLtIQAcVH9D270y
RT1ELEC-393-001 | ba088f30-ff35-4cbb-be30-089595cf8f3e | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_CR_09 | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning is not installed on panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198575&prj=632&rqi=YIyTEsvn8h4sfZEj3A0JOWnU8G
RT1ELEC-56-001 | 11636603-2e12-429e-995f-5bc4b23fb0ac | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1ATSM_CR_02 | ATS - Automatic Transfer Switch |  |  | Danger warning sign and dual supply warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198583&prj=632&rqi=msvZSwhbAEvID2onXVkH3NkBsp
RT1ELEC-521-001 | 21e870b7-de01-422d-886e-2da75338c9d8 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_R_12 (40A) | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198581&prj=632&rqi=1VLjH5LHH7UDaCiZjdxLk4yW2q
RT1ELEC-519-001 | cebfa613-40ad-455b-b72d-f8bbbcb61130 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_R_07 (40A) | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198579&prj=632&rqi=yhEwdYaC8upFdQiHdMf9aCLh5L
RT1ELEC-518-001 | 2279d425-2c7b-4e3f-ac14-03351bdcb10c | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | KarthikReddy@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_R_06 (40A) | LVSB - Low Voltage Switchboard |  | i-Box | Danger warning sign not installed on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198577&prj=632&rqi=QZhk0M4HuVIU5p64Ke1EP7Z3g2
RT1ELEC-473-001 | 5412370d-393a-4bc4-b959-7d766a9f3405 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_R_09 | LVSB - Low Voltage Switchboard |  | i-Box | Verify Permanent equipment labels affixed and are as per approved colour scheme. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198289&prj=632&rqi=0jwTx3nbkSeJ6VMUD6vRITeCP8
RT1ELEC-30-001 | 612f8398-4371-42d7-9554-75d2d9194d01 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1ATS_AR_02 | ATS - Automatic Transfer Switch |  |  | Permanent equipment labels are affixed and are as per approved colour scheme. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198288&prj=632&rqi=Okg5gI9oyMTS3lc5y6f21ybXb9
GI-228 | 70d14078-4d37-449f-b33b-61f92d455c86 | JH02-1/2 | 632 | APAC | Closed | P1 High DCOS | ahmadfuad@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Controls | equipment | 1DCOS_PCP_1 | DCOS - Control Panels |  |  | (FWT) During DCOS and CPOS SFAT, it was observed that minimum testing readiness was prepared by Honeywell. The test was deemed Not Acceptable and re-SFAT required. Line animation and basic graphics requirement were not presented due to unreadiness. These items are mandatory and required to be tested during SFAT. The configuration is not based on signed off SICD. The DCOS HMI graphics were only presented for one typical set of equipment, which does not comply with the MOS requirement that 100% of graphics must be ready and tested. Finally, no proper Internal test report and QA/QC report with graphic screenshot were not provided before the SFAT date. Honeywell to submit RCA for detailed failure root cause and corrective action plan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197901&prj=632&rqi=OQPaXXManqKz2cLxBNCwJUUHkS
YT1ELEC-93-002 | 3cc814f7-2870-41ff-8012-316b5297b625 | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1SUDB_1 | SUDB - Secondary Utility Distribution Board |  |  | 1BTU_1 Battery Charger have two charger namely Charger 1 and Charger 2. Incoming power for Charger 1 identified is from LVSB_M1_35 R2. However, no incoming cable identified for Charger 2. Please recheck with design EOR to confirm power source for Charge 2. Typical comments for 1BTU_2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197324&prj=632&rqi=noj7x550VEw6zCiGuvQhz5d3sC
YT1ELEC-488-001 | b33b2ef8-1bed-4a76-9fd4-9c6b63b9566a | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVSB_M1R_2 | LVSB - Low Voltage Switchboard |  | i-Box | LV cables connection to isolator for LCP-1EF-M1-13 and LCP-EF-M1-12 to redo cables termination due to bending radius not acceptable. As per PB 5.1 Equinix allow a min bend radius of 12-15 times the cable diameter | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197322&prj=632&rqi=HDPrNwA4iVQAkNpRxr2mk8wXEY
RT1ELEC-216-001 | e98fd3e8-4418-44b1-88c7-0f520a84da20 | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_M2R_10 | MDSB - Mech Distribution Switchboard |  |  | Discrimination setting. Refer marked in yellow changes from R4. To finalise setting with design consultant and update sticker where required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197172&prj=632&rqi=5E5HQVvKDtWeuDmq0034CcT8Oh
YT1ELEC-199-001 | cc2930c8-3adf-44ae-918e-0777d90b8f38 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | pauljohnson@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_R_3 | MDSB - Mech Distribution Switchboard |  |  | Confirm all labels and safety labels are present | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197153&prj=632&rqi=cmWQS5BtB8d6RgQB2NV2QGC5CB
YT1ELEC-199-002 | 6dc7973c-dc1b-44d2-a901-03be5b4b3968 | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | pauljohnson@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_R_3 | MDSB - Mech Distribution Switchboard |  |  | For MCCB's Q02, Q03, Q04 & Q05 Discrimination study for instantaneous and ground faulty doesn't align with the Breaker Frame Size (In) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197154&prj=632&rqi=c1jf3rsAb3x28HW9Klh90AIyhK
RT1ELEC-215-001 | d21c8792-2b42-4299-96f2-d8b88be4e1a1 | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | ahmadfuad@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_M2R_9 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_M2R_9 Q_06 breaker size onsite is 160AF/40AT. Discrimination Study for Q_06 show 100AF/40AT. Breaker size installed on site correct as per SLD. To reconfirm with design consultant which to follow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197163&prj=632&rqi=tQv7JH3eOB8kxNdsax9lYxojBL
YT1ELEC-204-001 | 1eeb5c7d-8170-4073-99d6-7501c000dda4 | JH02-1/2 | 632 | APAC | Open | P3 Low CX | pauljohnson@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_M1_04 | MDSB - Mech Distribution Switchboard |  |  | Confirm all labels and safety labels are present | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197141&prj=632&rqi=UifQBhlCqq3bSPlSfgQbYnevlC
YT1ELEC-204-002 | b524b342-66e3-4fa6-b4e0-f86b0915d8cd | JH02-1/2 | 632 | APAC | Closed | P2 Medium CX | pauljohnson@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_M1_04 | MDSB - Mech Distribution Switchboard |  |  | For MCCB's Q02, Q03, Q04 & Q05 Discrimination study for instantaneous and ground faulty doesn't align with the Breaker Frame Size (In) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197146&prj=632&rqi=h6NLUFuGKue09ERec2xwG7dAAI
RT1ELEC-182-002 | 37a2b4b2-15e0-42f5-8a67-c9c07f96c472 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_M2 | MSB - Main Input Switchboard |  |  | Tagging for switches K01 to K05 pending installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197178&prj=632&rqi=xLcyi90WK8Zb35BFlZsDEMSCuh
RT1ELEC-182-001 | a1adae7f-44a3-4f1b-86a8-c37dc2e98708 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_M2 | MSB - Main Input Switchboard |  |  | MSB_M2 HMI panel not yet installed as part of MSB Cx2A. Arrange with GC to expedite installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197175&prj=632&rqi=9yTibqvCNHIIYXPwmSXBw2NRpu
RT1ELEC-10-003 | b75b381b-05af-4c23-8c82-8fb5701f1970 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Permanent ladder or movable ladder or platform are required to be position inside the RMU. Current testing was conducted using temporary ladder. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197102&prj=632&rqi=Fl0ePpRtKhiDyNzW0NdxenwGTU
RT1ELEC-10-002 | d9754ba1-4adc-4eed-8dd7-cb490d8b443f | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | ZCT and Moxa BMS card pending installation inside RMU. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197101&prj=632&rqi=KDSG61wFeRs8Yd1IkZuXJ7sPFu
RT1ELEC-10-001 | 0c2f00b7-dc6c-48bd-8a0e-78ac2a2e2bf0 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | 1RMU_B panel tagging pending installation. Typical for 1RMU_M1, 1RMU_M2, 1RMU_R and 1RMU_A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197100&prj=632&rqi=ElzDW22kkJJ0sr9SSSJToeKQJE
YT1ELEC-94-001 | d9bfc72d-338a-43f7-b25f-9f1d0d10d958 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1SUDB_2 | SUDB - Secondary Utility Distribution Board |  |  | Current Setting for below was tested on site without actual setting. However, to confirm if setting require to be set on site and If required please confirm the setting with design consultant. Typical comments for SUDB1 and SUDB2. 27- undervoltage 59- Overvoltage 81U - underfrequency 81O - over frequency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196867&prj=632&rqi=mrlVq5WkiLKXVePa01MfVyM6px
YT1ELEC-93-001 | d6d2f521-1e0a-4527-b9b3-b2d09491b4f1 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1SUDB_1 | SUDB - Secondary Utility Distribution Board |  |  | Current Setting for below was tested on site without actual setting. However, to confirm if setting require to be set on site and If required please confirm the setting with design consultant. Typical comments for SUDB1 and SUDB2. 27- undervoltage 59- Overvoltage 81U - underfrequency 81O - over frequency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196866&prj=632&rqi=tMBpmvjHYVGbw2qIICp5zkKMP5
RT1ELEC-94-001 | 09a0d04e-1cbf-48f5-ba85-96a16635bd49 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1SUDB_1 | SUDB - Secondary Utility Distribution Board |  |  | Approved Schematic drawing SLD yet to place inside SUDB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196759&prj=632&rqi=8CCbDdWFUFmtJKNPZ43LFBDLFu
YT1ELEC-372-002 | c83a32e7-7017-4898-9601-f5fc6485675a | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_M1_34 | LVSB - Low Voltage Switchboard |  | i-Box | Pending incoming cable test Cx2B. To expedite cable installation and testing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196557&prj=632&rqi=UouutNQvj9wWfn79NHfVj4kYQw
YT1ELEC-198-001 | 1490536d-d27f-4bcf-b7b7-f659d71f332e | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_R_2 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_R_2 discrimination setting not tally with PDC report 1) Q_02 Please confirm I Instantaneous should be (6.0 x 100A (breaker frame size) = 600A) instead of 240A from discrimination studies. 2) Q_02 to 05, 07 to 12, 16 to 20 setting Ground fault at 0.4 x 100A = 40A which typical to trip setting? Otherwise, should this be typical to Q_01 which is 0.2 x 100 = 20A setting? 3) Q_14 I instantaneous 6.0 x 160A = 960A however setting shown is 600A. Please confirm Once NV5 revert, to update and retest accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196556&prj=632&rqi=FhXMFjjmp4aazuKE3oUiRG6M17
YT1ELEC-372-001 | 64f872f0-e2e9-40b0-b213-c702ff747739 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LVDB_M1_34 | LVSB - Low Voltage Switchboard |  | i-Box | Incoming cable test pending installation and Cx2 document signed off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196544&prj=632&rqi=a0iIa52grUKB0ND1SjqRc5CR5M
YT1ELEC-178-001 | 592a061e-8b7f-4f6b-b024-53821d59a33b | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | HMI_R is yet to position and start Cx activity. To expedite wall mount installation and start Cx2A and Cx2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196555&prj=632&rqi=c9c4NYQhJB2X1tqOMooa8vjU8p
RT1ELEC-179-002 | 5d75c039-41a8-f6fd-4b10-20def62eed37 | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | HMI R have yet to position and start Cx2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196416&prj=632&rqi=SmIIdegA0fhzx7YRKnYPtXg6Fa
RT1ELEC-179-001 | 6f847539-6cf2-4817-b7f9-adfc58ff962c | JH02-1/2 | 632 | APAC | Closed | P3 Low CX | ahmadfuad@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_R | MSB - Main Input Switchboard |  |  | Key switches tagging missing on panel to install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196305&prj=632&rqi=bpc2LQ3yaehVR9KykElkKrCNfX
RT1ELEC-1-012 | 1a62ff31-57cc-4beb-a353-463020809b81 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-11-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Nameplate found rusty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615404&prj=626&rqi=DUjzKnUedPfKBD6r798OBRMx96
BT1FD-6-001 | 1221ea70-9fed-48c1-a80a-6cdb61e91f42 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-09-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | During the 1st alarm simulation, there was a delay in alarm signal detection/indication at the DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638410&prj=626&rqi=bfiNoDZZL835Var9iWetoo7NNL
BT1FD-4-002 | a6d61433-855b-44ee-8130-34b5dfcdf2be | JK01-2 | 626 | APAC | Ready for Verification | P2 Medium CX | wellyjulian@commtechasia.com | 2026-09-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | During General Alarm, the motorized fire damper at the fire riser did not open. MFD FOH B panel indicated Floor 6, whereas it should indicate 4 dampers. LCP indication showed Floor 4 MFD ON. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638416&prj=626&rqi=MpqcgxvT9pLbhwqoIVf9l6cF7N
BT1ELEC-4-001 | d148a8e2-605a-4c28-b5d0-74f1af94f1bb | JK01-2 | 626 | APAC | Open | P1 High CX | fauzanfikri@commtechasia.com | 2026-09-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | During test generator under 100% load condition, abnormal noise and vibration were observed at the generator exhaust. On second start-up attempt, the generator was found hunting condition Testing could not be continued and further investigation from Altrak is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637827&prj=626&rqi=MiM5PtieSBKwbvxHzMCA7OmKu6
BT1FD-5-001 | c05be585-421e-4e7c-8b28-5ca9795489a4 | JK01-2 | 626 | APAC | Open | P1 High CX | wellyjulian@commtechasia.com | 2026-09-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_5.01 | PAV - Pre-Action Valve |  |  | During 1st Alarm simulation, SAP Fire Panel L5 indicated â€œCARD 3 LOOP 2 â€“ CARD MISSING/FAILED,â€ resulting in failure of the required interlocks, including CRAY ramp-down and other systems, following the General Alarm sequence. Orient to provide RCA and confirm whether card replacement or troubleshooting is required, followed by full re-testing of the interlock sequence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638412&prj=626&rqi=08vfTqPFw1A7cDfUpyWGOyLNZo
GT1FD-39-001 | 5cce3f53-1d77-4133-a3fd-df3f3c95924b | JK01-2 | 626 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-09-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS |  | Fire Detection | equipment | ASDSP-7.10 | VES - Vesda |  |  | During P2G with DCOS, Description in alarm shows ASDSP-7.09 instead of ASDSP-7.10. DCOS team to fix this issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637728&prj=626&rqi=cMwh5zzU1lPTsEVfrBeLrwcCfZ
BT1ELEC-5-001 | 7cec6bac-fb52-49ac-b331-b0b4b29e13a6 | JK01-2 | 626 | APAC | Open | P1 High CX | fauzanfikri@commtechasia.com | 2026-09-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | During CxL4 testing for scenario â€œEarthing Switch State Checking for Maintenance 1RMU,â€ the earthing switch coil on 1RMU_B was not working. This is second time the same issue has occurred. The same issue also happened previously when 1RMU_B was energized | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637764&prj=626&rqi=zZ0S0VwrEMxR9LPV05jrmqbjJa
BT1ELEC-38-001 | 591ea6f0-0fa6-4550-8cf8-c264759025a3 | JK01-2 | 626 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-09-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Component/Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | CxL4 â€“ 1MLTX_F can't be performed due to an issue with temperature control component. In addition, the communication cable to DCOS is still showing communication loss (commloss) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637790&prj=626&rqi=Hu18hQp4X8U2rcn65IfvROXS3I
GT1ELEC-155-003 | a772db1e-d1f4-4ec7-ab79-07784d99c29b | JK01-2 | 626 | APAC | Open | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Controls | equipment | 1PANEL_I/O_Motorized Damper | CP - Control Panel |  |  | GC need to perform Air TAB for MAU and provide report Air TAB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637453&prj=626&rqi=j7VHHadZaj9l0DeNhZTmT1D8i3
GT1MECH-81-001 | 3810fc7b-1823-43fd-96c5-bf1395a4f703 | JK01-2 | 626 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_6.01 (Existing) | PAV - Pre-Action Valve |  |  | Seismic Bracing not yet installed and will be planned to install asap by GC. (This issue for all floor) Ensure that when installing those, there will be not affect piping and support pipe. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637418&prj=626&rqi=FsCzeMT6I0Flw0dSCtpofen8V3
GT1ELEC-155-002 | bcb373c3-e912-4e9e-86ea-fbb59d76b03a | JK01-2 | 626 | APAC | Open | P2 Medium DCOS | DimasKurniawan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Controls | equipment | 1PANEL_I/O_Motorized Damper | CP - Control Panel |  |  | DCOS have to provide additional register (regarding new SoO of MAU Motorize Damper) that need to integrate to DCOS monitoring: - High Temperature Alarm - Bypass Damper Fault - Room Damper Fault Level 2-7 (Cool Spine) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637448&prj=626&rqi=GkdlPiq47FkwqKmdqAFVsdsJ0C
BT1MECH-57-001 | c67eacaf-9024-40e5-ad83-64fcdba1b62c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | During the Fire Alarm Signal Test, the fire alarm status on the LCP HMI remained "False." | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637250&prj=626&rqi=s9QvcFPhAGMWhIRC8HeYLBYqKm
BT1MECH-60-002 | 7a23207e-57f7-4f53-9c76-a4aea766c2ff | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | There is a discrepancy in the Hâ‚‚ sensor reading. The value displayed on the HMI-LCP is 1, whereas the sensor indicates 0. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637251&prj=626&rqi=q1VfsoG89MHX2ybc6ZOiP55ftD
BT1MECH-60-001 | e1b3c412-5bd6-4328-b781-8c31aa6ca581 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-08 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | During the Fire Alarm Signal Test, the fire alarm status on the LCP HMI remained "False." | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637249&prj=626&rqi=4lhniYERcbMNzvr4HfYHLJqkiU
BT1MECH-67-001 | 14c4c136-7241-417c-85c7-613fb4dd7de3 | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | MulyaSitanggang@commtechasia.com | 2026-09-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | There is a discrepancy between the room temperature sensor reading and the temperature displayed on the DCOS graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636795&prj=626&rqi=5FmRKwkjDEN7eBRBicCbMzvsz6
BT1MECH-64-001 | a495780c-f6b2-4778-9e21-fae386ca80b7 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-04 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | During the manual ON/OFF on HMI operation, when the selector switch is moved to Manual, the unit immediately starts running. However, according to the SOO flow for Manual Mode, the selector switch should first be moved to Manual, followed by pressing the Start button on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636785&prj=626&rqi=PCr4Xxt6NGw8c277Fp1NrxoCQN
BT1MECH-67-002 | 268bcc6f-b847-4829-825c-68a714258dd3 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-04 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | During the manual ON/OFF on HMI operation, when the selector switch is moved to Manual, the unit immediately starts running. However, according to the SOO flow for Manual Mode, the selector switch should first be moved to Manual, followed by pressing the Start button on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636797&prj=626&rqi=cK8Nb8rqRR7MmxznqgTfVSxSHK
BT1MECH-62-003 | f7d87452-625e-49d9-8f53-d8889197a3b0 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_C_54 | EF - Exhaust Fan |  |  | During the manual ON/OFF on HMI operation, when the selector switch is moved to Manual, the unit immediately starts running. However, according to the SOO flow for Manual Mode, the selector switch should first be moved to Manual, followed by pressing the Start button on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636655&prj=626&rqi=spsZyZ8o4cJBJ0gZKOY7JaMAlp
BT1MECH-62-001 | a498dbc5-69a0-4ba3-85cf-a8b4afb31130 | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_C_54 | EF - Exhaust Fan |  |  | There is a discrepancy between the room temperature sensor reading and the temperature displayed on the DCOS graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636652&prj=626&rqi=cDrEkD4fppcj43M2RegWKd8Yni
BT1MECH-61-001 | f8dc75f2-f7b0-46b1-a982-1dbd082ebedc | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_C_53 | EF - Exhaust Fan |  |  | There is a discrepancy between the room temperature sensor reading and the temperature displayed on the DCOS graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636651&prj=626&rqi=PfBw4HbiR2zPM5ZqATouj3DnO5
BT1MECH-62-002 | fb571c6d-30b8-4859-939a-1b80f6d63561 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_C_54 | EF - Exhaust Fan |  |  | The room temperature reading on the HMI LCP not fluctuating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636654&prj=626&rqi=EBRSlp7kyxndkL4JxI3kmsh69h
BT1MECH-58-001 | f2d1532c-6863-4cdb-87f8-580d1c5e3424 | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_31 | EF - Exhaust Fan |  |  | There is a discrepancy between the room temperature sensor reading and the temperature displayed on the DCOS graphic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636667&prj=626&rqi=FbAkdr2odY5nA7pBchPOpfCVpZ
BT1MECH-58-002 | ac4a12f3-3cca-4c1b-ab34-a479777000f7 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_31 | EF - Exhaust Fan |  |  | During the manual ON/OFF on HMI operation, when the selector switch is moved to Manual, the unit immediately starts running. However, according to the SOO flow for Manual Mode, the selector switch should first be moved to Manual, followed by pressing the Start button on the HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636668&prj=626&rqi=vwLxzNYTOjyUTNLAKSgSalBaQi
GT1ELEC-50-004 | e2182b60-5878-4131-805f-a083f721474e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | Please revise the graphic for STSSB_D_1 refer to STSSB_B_1, as they are one integrated equipment, not separate equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636453&prj=626&rqi=9LV7MYk4T7QxGJNorzJH3cS8NG
BT1MECH-50-004 | 291c6fec-8629-45fe-b523-9069aa993c81 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_D_22 | DXID - FCU/DX Indoor Unit |  |  | During Dx FCU Functional Test, when Simulate the space/room temperature Lower than current set point by changing the Setpoint at Thermostat, set point temperature does not trigger to Centralize LCP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636430&prj=626&rqi=waQUAYsbxoPpnAzyFZGerS5Gq5
BT1MECH-50-002 | 714e18df-92dd-41a9-94d3-f6249f31d26c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_D_22 | DXID - FCU/DX Indoor Unit |  |  | There was no change in the set temperature on the LCP and DCOS when the set temperature was changed on the thermostat. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636421&prj=626&rqi=is1X62oSTJ8yO6glTd4FSwcg2H
BT1MECH-50-005 | 96ccd864-d831-4ef2-a167-aa922d4346b8 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_D_22 | DXID - FCU/DX Indoor Unit |  |  | When Start Hot Standby Sequence test, Second FCU units in the same room are not operating normally (B_22) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636443&prj=626&rqi=V2Ujqb9vzipaqbWQFrxljQmTyW
GT1ELEC-52-003 | 20c45195-933f-402c-98a9-2fec8c5e050e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Please revise the graphic for STSSB_F_1 & F_2 refer to STSSB_B_1, as they are one integrated equipment, not separate equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636454&prj=626&rqi=jAqcmWXc72Bkim8HpR3nOgJWdQ
BT1MECH-50-001 | d776cffb-3048-4b51-8094-8d8cc0ef6a44 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_D_22 | DXID - FCU/DX Indoor Unit |  |  | During the compressor failure test, the compressor power was intentionally switched off. After the power was reinstated, the VRFOD did not immediately resume automatic operation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636409&prj=626&rqi=91cb0PiCqt0gOrxCWLysWWzehk
GT1ELEC-48-004 | a9d390c1-6041-4a5e-ae5d-4a6f3d3debfe | JK01-2 | 626 | APAC | Closed | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Please revise the graphic for STSSB_C_1 refer to STSSB_B_1, as they are one integrated equipment, not separate equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636447&prj=626&rqi=IcDQqFVw5ZwhOTygPxVrZvvk9S
BT1MECH-50-003 | 03a62475-7c77-4431-9d74-d7baa9a6c164 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_D_22 | DXID - FCU/DX Indoor Unit |  |  | During Dx FCU Functional Test, when Simulate the space/room temperature Higher than current set point by changing the Setpoint at Centralize LCP, set point temperature does not trigger to thermostat | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636426&prj=626&rqi=1TuImPjfHKeqGQhJT3ewATtG3S
GT1ELEC-49-003 | f17ea51f-d1d4-4fab-8dda-0d8844966949 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Please revise the graphic for STSSB_C_2 refer to STSSB_B_1, as they are one integrated equipment, not separate equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636452&prj=626&rqi=bg6KOUJ2cVlkYn5depiPtS35WS
BT1MECH-54-002 | a1178aa8-fad4-4eca-887d-b7610084198c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | There is a discrepancy in the room temperature readings between the thermostat and the LCP/DCOS (The readings on the LCP and DCOS are the same) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635569&prj=626&rqi=MImqD29fpoDh6nSOheSnnwtopg
BT1MECH-52-003 | af9fafc5-d8fe-45ea-9685-c27fedeea4e7 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_F_42 | DXID - FCU/DX Indoor Unit |  |  | There is a discrepancy in the room temperature readings between the thermostat and the LCP/DCOS (The readings on the LCP and DCOS are the same) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635587&prj=626&rqi=C48b2w0GSP4KtfQSo7qcypU6zU
BT1MECH-54-001 | 0cc9691f-d669-46ca-b216-7542d45a32a2 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | During alarm test, upon DXFCU power loss the alarm appeared for approximately 8 minutes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635489&prj=626&rqi=yVMZyH4W4S7Jz1dYS6ZuMhKUbs
BT1MECH-52-002 | eeca4de2-d564-4bfa-8a46-a76f4992b03b | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_F_42 | DXID - FCU/DX Indoor Unit |  |  | During Start Stop Sequence (Auto Mode) LCP unit cannot be switched to Auto Mode (Need To Confirm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635586&prj=626&rqi=qVguGpXN9qjT6Ghh5ttH0raEsn
BT1MECH-52-001 | 014c07a3-de9e-4574-bf18-04650ef44c1b | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_F_42 | DXID - FCU/DX Indoor Unit |  |  | During alarm test, upon DXFCU power loss the alarm appeared for approximately 8 minutes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635580&prj=626&rqi=kKhskixenDZcPaRM7x7HBnGxcU
BT1MECH-53-003 | c3eac548-0706-4500-be3b-9d17930089e3 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_B_41 | DXID - FCU/DX Indoor Unit |  |  | During Simulate power failure for PICV actuator by disconnect power supply to the PICV actuator from control panel. After re-connect power supply, PICV closed first then open again to last position. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635490&prj=626&rqi=2dp2lbjRKG9UWsa43xPZwgLV14
BT1MECH-53-002 | 0f0f9398-28dc-488c-9545-39474ea29fc6 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_B_41 | DXID - FCU/DX Indoor Unit |  |  | During alarm test, upon DXFCU power loss the alarm appeared for approximately 8 minutes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635488&prj=626&rqi=q3WTWplpYXqLKBkTKX16YYUAqh
BT1MECH-53-001 | fe9ce55a-f5c2-4046-bd06-424b5d2962bf | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_B_41 | DXID - FCU/DX Indoor Unit |  |  | During Start Stop Sequence (Auto Mode) LCP unit cannot be switched to Auto Mode In SOO mention can Auto Mode Operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635234&prj=626&rqi=gqaE2zpZWKvx0gWUebphIIjtz4
GT1MECH-87-001 | 0b023967-8d07-484d-acae-b1c5483f0afb | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Fuel | equipment | 1LCP_FPUMP_B2 | FT - Fuel Tanks |  |  | Actual test regarding existing Pump function cannot perform due to incomplete PRV setting. Once it already done and can be test, please invite CTA to witness | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635230&prj=626&rqi=2a3I2uVRTWHVdNqDIwz6g3OISI
GT1MECH-86-001 | f8afa15d-631d-40ee-8318-a4c0a51c9055 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Fuel | equipment | 1LCP_FPUMP_A2 | FT - Fuel Tanks |  |  | Actual test regarding existing Pump function cannot perform due to incomplete PRV setting. Once it already done and can be test, please invite CTA to witness | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635227&prj=626&rqi=egRa9d8cAOKPgAVlf6FfWDqVc5
BT1ELEC-41-001 | ee8c1eb3-a3d3-44ab-a46c-f1967ade0f71 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | During CxL4 1RMU_D, Power meter at 1MSB_D_1 shows an inaccurate kW reading compared to the actual load | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634714&prj=626&rqi=af7HRFtkcIMyKvXI22tlTLx2ND
BT1MECH-51-004 | 538271f9-f2b8-4be8-98b8-88978b734657 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | During Start Stop Sequence (Manual Mode) PICV water flow 1.5 (PICV water flow available (â‰¥1.6 lps)) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634362&prj=626&rqi=8zCLC2Me4Tm4WWmoJqNNm9I4ey
GT1FD-5-001 | d2bf5b9b-d013-4b8f-9c87-db8868e11bab | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Fire Detection | equipment | 1FAS_6 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634255&prj=626&rqi=t0Y7dtTbO5Nlh3UCTPKh5wxCOo
BT1MECH-51-002 | 1c2df634-e24f-4c8b-852e-61c911600e92 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | During Fail compressor by failing power to compressor. Verify Loss Communication alarm at DCOS. FCU remain running on site is off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634360&prj=626&rqi=I4KoMQlpwpElS6j2VOcrmSGKjX
GT1FD-1-001 | 5adb0659-0047-4e2f-92dd-526575806a1d | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Fire Detection | equipment | 1FAS_2 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634252&prj=626&rqi=8G6QHh6JLD2ubxnFb9IRdl1XQ7
BT1MECH-51-003 | b222a2fe-7d0e-4002-9f84-51d1eb4e92a0 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | During Start Stop Sequence (Auto Mode) LCP unit cannot be switched to Auto Mode In SOO mention can Auto Mode Operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634361&prj=626&rqi=IMXlol19R4JHftd57fFQJkBMQB
GT1MECH-26-002 | fbde8ac7-0efa-4790-8a91-8e5205980f68 | JK01-2 | 626 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634307&prj=626&rqi=4iSPF8osIDrdQS9B78tVBGosDp
GT1MECH-27-002 | dfc61aca-6d94-4dd3-be3e-f0c98e1cd4df | JK01-2 | 626 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634305&prj=626&rqi=hDMTcnEljH67iZCivWnoTmEKyO
GT1MECH-26-003 | 7756fb9f-9944-4023-8b57-cd03566b105a | JK01-2 | 626 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634308&prj=626&rqi=JMP1iEtA5SigKe0lwNF9OqeRBj
GT1MECH-24-003 | ac814471-8a33-4139-8e84-e60e72eff706 | JK01-2 | 626 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634309&prj=626&rqi=G3DHsZOdaRLfbweZAQpajzD6m2
GT1FD-6-001 | 7ce79a29-5710-4159-907e-667ecd45409b | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Fire Detection | equipment | 1FAS_7 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634256&prj=626&rqi=jaliEZZEffHqPfta1Ti970IFSN
GT1MECH-25-002 | 4324a628-b58e-4407-8de3-c612582f1cf2 | JK01-2 | 626 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634311&prj=626&rqi=7Dvkg9UTI6CfnmYIVGngwGkVJB
GT1FD-4-001 | 526cff01-2ac7-4098-b233-3b6cd23fdfd4 | JK01-2 | 626 | APAC | Ready for Verification | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Fire Detection | equipment | 1FAS_5 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634254&prj=626&rqi=k7gYFvZNTDBMcUbZsV06QXlWzZ
GT1FD-3-001 | 2e8c65c4-300d-49cc-9aa1-fe29e2bf4abf | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Fire Detection | equipment | 1FAS_4 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634253&prj=626&rqi=C3qelpOV8GikHSNkDr73nWVHP5
GT1MECH-25-003 | 8538a0b4-4c09-4fe7-bd46-16a3f50d606d | JK01-2 | 626 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634312&prj=626&rqi=cpY54be4ZcFCoZIRFntndGH2jG
GT1MECH-27-003 | 1cf6839b-0673-40c9-b10a-a8795ee5a832 | JK01-2 | 626 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634306&prj=626&rqi=mjpC5KaBDEI7PuknnEvVViyc0p
GT1MECH-24-004 | dd06d0bf-5638-4e27-81c2-e9084f3a8492 | JK01-2 | 626 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634310&prj=626&rqi=Da1FyVrKKocjGqV2voJzey7CY4
GT1MECH-79-001 | 07388389-7175-4ba9-9348-3106e7367623 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_2.01 (Existing) | PAV - Pre-Action Valve |  |  | Integrated testing with CRAY has not been performed when the 1st alarm, CRAY will ramp down. Orient to perform this test with Vertiv and make a report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634257&prj=626&rqi=BSEvt42sRqlWgB1aNHPaPnFzva
BT1MECH-51-001 | 256a3f3f-074d-457d-926e-61832d817ee0 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-20 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | During indoor trip alarms no alarm verified at DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634345&prj=626&rqi=vJCdhrJtzfgciMBYIUAfwE0aEn
GT1MECH-78-002 | dc8a2738-96fa-4ca1-a4b2-27c99c94a1dd | JK01-2 | 626 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634167&prj=626&rqi=aRj6fwpKJkDzYd6AbaFyjoES7I
GT1MECH-77-004 | 63650844-8410-48b5-b091-bcac5f3f103f | JK01-2 | 626 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634166&prj=626&rqi=uc16XFHsXPtFkcWy2cFuvRZAze
GT1MECH-75-002 | b1494caf-2332-4bb0-b34a-7b2fe335a255 | JK01-2 | 626 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634165&prj=626&rqi=gQ4hugyEyWIirp1UEnAU0znPrH
GT1MECH-35-001 | cec94237-1f9e-4b6e-9eca-3cf117303e51 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-08-18 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | During airflow measurement test, blanking panel beside Cool Array unit are bend / curved when running 100% fan speed of Cool Array test | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634048&prj=626&rqi=UFNj5s4LePK4xLoT3DRV0m9KKF
GT1MECH-76-006 | 21714227-6608-4a67-b4f3-c51424eb29a2 | JK01-2 | 626 | APAC | Open | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | Several outstanding P2G test by Orise will be conducted after DCOS integration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634080&prj=626&rqi=FojhhPZD6dzbS9WfHdr11Xs3wP
BT1FD-5-002 | 13e18494-7cc4-4e46-a302-343a0ecb9406 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_5.01 | PAV - Pre-Action Valve |  |  | During CxL4 (Water Discharge Test) some issues are discovered; - The LED indicator floor mimic panel doesn't ON during 1st & 2nd alarm (DONE) - There's a water leak/splash on water gong (DONE) - Need to add support for drain pipe at sprinkler Control Valve Room (DONE) - install flow direction sticker for fire pipe at some point (DONE) - Seismic Bracing not installed yet (DONE) - Wire burn in HAC & CAC will be test during IST (FYI) - Need to add installation isolation valve after flow switch (suggestion from FMG) --> for future maintenance (FYI) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638414&prj=626&rqi=qOuhNZrn6FIRwDYJ7JtmBzKFLD
BT1FD-4-001 | 9629e5df-de2e-4654-8758-f8a8fd506615 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | During CxL4 (Water Discharge Test) some issues are discovered; - Need to add support for drainpipe at the Sprinkle Control Valve Room (DONE) - install flow direction sticker for fire pipe at some point (DONE) - Seismic Bracing not installed yet (DONE) - After the test, leakage was found in 1st floor piping that makes Jockey Pump starts running continuously (DONE) - Wire burn in HAC & CAC will be test during IST (FYI) - Need to add installation isolation valve after flow switch (suggestion from FMG) --> for future maintenance (FYI) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638415&prj=626&rqi=dPKfA9zEvuyGtiSejLLXU2f4rT
BT1FD-6-002 | e8764bdd-14d6-454c-83ac-d5c96d0c9b70 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | During CxL4 (Water Discharge Test) some issues are discovered; - There's a water leak/splash on water gong 7th floor (DONE) - Need to add support for drain pipe at sprinkler Control Valve Room (DONE) - Install flow direction sticker for fire pipe at some point (DONE) - Seismic Bracing not installed yet (DONE, can check on RFI reports) - Wire burn in HAC & CAC will be test during IST (FYI) - Need to add installation isolation valve after flow switch (suggestion from FMG) --> for future maintenance (FYI) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638411&prj=626&rqi=vCxZkVUskfQxGeGmmDCljEW66z
GT1MECH-78-001 | 61a9a348-48d0-4024-96c6-fdfcaa361232 | JK01-2 | 626 | APAC | Open | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633410&prj=626&rqi=Vw2JIieE7Gdede5vyUL1EjLrHx
GT1FD-2-001 | dbe8b709-2ffc-449d-981a-0b43887c3b68 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Fire Detection | equipment | 1FAS_3 | FP - Fire Panel |  |  | The Sound Level tests for the horn strobe are still pending. These tests will be conducted during L4, with Orient committed to completing them during the L4 activity. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633417&prj=626&rqi=zTwZK7wXrsGVl8cB9Q7KODVNsZ
GT1MECH-75-001 | 1389ceed-0e8e-49e8-afd6-8023cc290088 | JK01-2 | 626 | APAC | Open | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633411&prj=626&rqi=tkz08ymUNFrL1sLOK4AT3MvmNh
GT1MECH-77-003 | 7a3f8628-db64-43d5-8425-61616900dfb5 | JK01-2 | 626 | APAC | Open | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633412&prj=626&rqi=hjfp7Pj7Yxku1iLsTd0lM6XQOd
GT1MECH-76-005 | 7e73441a-7df6-4096-be32-d29eae6ae9d0 | JK01-2 | 626 | APAC | Open | P3 Low CX | wellyjulian@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | Water TAB cannot be carried out yet, as it requires the UPS Mech A & G installation to be completed first. Then Water TAB will be carried out after the CR is released. Please note that this activity will require sufficient time for completion, which may impact the overall schedule. Therefore, CTA will push and prioritize this issue either before L4 or after L4, depending on the actual site conditions and readiness. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633408&prj=626&rqi=ZXVIIBV9RUPwgUPCjaMXrWGuQl
BT1ELEC-30-005 | 4fd94a76-3f26-4579-973b-62ade4a862e6 | JK01-2 | 626 | APAC | Open | P1 High CX | fauzanfikri@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Based on discussion between Aurecon, CTA, TnT, Altrak & GC regarding the phase unbalance issue during CxL4 1UPS_D_1, Altrak is required to investigate the issue and provide an RCA (Root Cause Analysis) for the phase unbalance observed when step load using generator source Issue related: During load step-up to 75% with Generator source, MSB panel detected a phase unbalance, causing power source automatically transfer from Generator to Utility. The same 75% load step-up was repeated using Utility source, and no phase unbalance was detected and remained stable at 75% load | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633390&prj=626&rqi=zkVF565DXGUqhvsUOrBI8K38Vn
GT1ELEC-155-001 | abed9a67-e125-4753-a800-08fecc917b01 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Controls | equipment | 1PANEL_I/O_Motorized Damper | CP - Control Panel |  |  | During the HRA activity for the MAU motorized damper programming and commissioning activity, the following items were identified: 1. Update the SoO flowchart to reflect the actual operating condition and obtain approval from the AE. 2. During a power failure, the actual motorized damper remains closed, rather than returning to the last position as currently stated in the SoO. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633221&prj=626&rqi=hKcbwjtpDLh38xIyiYm2z3fdcC
YT1ELEC-152-001 | 5084cc09-bbd0-4bc2-af33-ca4b6b9bf26b | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L4 | DB - Distribution Boards |  |  | ( Issue CxL2A Laying cable from DB_FOHA_4_L to DB_DALI_L4) Need install vinyl netral and grounding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633150&prj=626&rqi=ejL3BovD8CqQQy5RhHBUAjI3Gp
YT1ELEC-155-001 | 67e6aec9-ef4d-46fc-ba9e-3735e3dbc50d | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | ( Issue CxL2A Laying cable from DB_FOH_7_L to DB_DALI_L7) Need install labelling at FOH side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633151&prj=626&rqi=8QCKpdtRYh0WNaZqtKsOy5ffoi
GT1ELEC-8-001 | 7d6bf669-5d05-42eb-9417-1c97053a3658 | JK01-2 | 626 | APAC | Ready for Verification | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | For (FDAY) DCOS P2G verification related to Valve Command and Valve Feedback, GC need to coordinate with related parties to perform those tests. And after test already perform, Orise need to revise their report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633010&prj=626&rqi=izzqZbec8nDYqC7m4jICWHnbV9
BT1ELEC-40-001 | 0496f68c-5b45-4c8d-be23-f9d106280ee6 | JK01-2 | 626 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Key "K3" on Solenoid box can't take out during process reinstate the maintenance bypass for UPS, because UPS OFF conditions and thereâ€™s no power on HMI, so that can't send the signal to Solenoid box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633008&prj=626&rqi=YYOIw25YuTU8SXdfOMtt0NErMs
GT1ELEC-7-003 | 7b65ae52-867f-4a6f-ba54-8747246f11d4 | JK01-2 | 626 | APAC | Ready for Verification | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | For (FDAY) DCOS P2G verification related to Valve Command and Valve Feedback, GC need to coordinate with related parties to perform those tests. And after test already perform, Orise need to revise their report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633006&prj=626&rqi=znM2pTG4X9qT8WEWr0zU8r0jQ5
GT1ELEC-9-001 | 202b1a84-f21a-4d26-9dcb-2f3600a38df0 | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | DimasKurniawan@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | For (FDAY) DCOS P2G verification related to Valve Command and Valve Feedback, GC need to coordinate with related parties to perform those tests. And after test already perform, Orise need to revise their report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633011&prj=626&rqi=eHtk7rwDRlxLYQeikluWkJWNxP
GT1ELEC-6-001 | efb9e3f5-49cf-4545-9221-c62ed198613a | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | DimasKurniawan@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor | L3 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | For (FDAY) DCOS P2G verification related to Valve Command and Valve Feedback, GC need to coordinate with related parties to perform those tests. And after test already perform, Orise need to revise their report. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633009&prj=626&rqi=ZnybmNOMyoEPSrn07evrQo9q4v
GT1FD-7-002 | fd5caa30-66b0-4a18-97f8-62d40864e1cd | JK01-2 | 626 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-2.04 | VES - Vesda |  |  | Based on the current ASDSP point list, new loop-3 integration to DCOS points have not yet been configured and programmed. See the HLI Modbus List for reference. Be sure to retest after configuration. (Responsibility Orient and Orise, with escort by GC) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632821&prj=626&rqi=RfxEoPoBx6iNJpSEh7SkhiCnV1
GT1MECH-72-002 | f8f139c7-8d52-471f-9eda-be792e61e61b | JK01-2 | 626 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | (Only for Record) During the PASCV C&E Matrix testing, a smoke detector was triggered in the data hall. At that time, the CRAY team had not yet confirmed whether the CRAY unit would ramp down as expected. Therefore, Orient and Vertiv conducted an internal test and invited CTA to witness the test and close this issue. (Orient already installed the cable and module). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632817&prj=626&rqi=lCsWhXVLa19vFXx5BU7q8rRwWR
GT1MECH-74-003 | c6fb8890-55e9-4d3d-b719-5f4100959811 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | (Only for Record) During the PASCV C&E Matrix testing, a smoke detector was triggered in the data hall. At that time, the CRAY team had not yet confirmed whether the CRAY unit would ramp down as expected. Therefore, Orient and Vertiv conducted an internal test and invited CTA to witness the test and close this issue. (Orient already installed the cable and module). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632819&prj=626&rqi=vNOvLXfNT4yJHy4sEhoDn00l5P
GT1MECH-73-002 | d18e6d77-c2ae-438f-a2b2-e6cacad736b3 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_5.01 | PAV - Pre-Action Valve |  |  | (Only for Record) During the PASCV C&E Matrix testing, a smoke detector was triggered in the data hall. At that time, the CRAY team had not yet confirmed whether the CRAY unit would ramp down as expected. Therefore, Orient and Vertiv conducted an internal test and invited CTA to witness the test and close this issue. (Orient already installed the cable and module). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632818&prj=626&rqi=45JGIg5oYWsVZftY7zCiXXyCrr
BT1ELEC-32-001 | e3918468-d656-4280-acac-1baf078f607a | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | During CxL4 1UDP_F_2 testing, abnormal sound/noise was observed from UPS unit during operation at 100% load on inverter mode | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632777&prj=626&rqi=QU9jIDS01rXl5ds4XZJTH26UgM
BT1ELEC-39-001 | 6a128555-67c3-4a9a-9aaf-9cca9eda6b92 | JK01-2 | 626 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Key "K3" on Solenoid box can't take out during process reinstate the maintenance bypass for UPS, because UPS OFF conditions and thereâ€™s no power on HMI, so that can't send the signal to Solenoid box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632779&prj=626&rqi=nHIAuUyWkFz1g8I1Hoz45AFzrg
GT1MECH-73-001 | 0c1461be-e539-40d0-802b-04259e2cbed9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_5.01 | PAV - Pre-Action Valve |  |  | Need to touch-up painting pipe and install flow direction. Manual Call Point (Z3-MP-10) need to install ID tag. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632655&prj=626&rqi=IYfhzIOFnFSwsdQQe8dvQeuBRh
BT1MECH-6-001 | c3d3ba90-9def-4e71-86dc-e0cd328f817e | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | During Fan Speed Control (Group Control) Unit CRAH not response (Simulate the Return Temperature sensor set point lower than the current Return Temperature Sensor Value (Average sensor value) Fan speed does not increase | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632690&prj=626&rqi=ys5NlYpgxpH2MkuvInIlMPdd0u
GT1MECH-2-001 | 442fba81-d291-4050-b828-97f84f95426c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | Please provide report cable for sensor CH4, H2 and CO. And revise acceptance criteria (on the MoS) of these 3 tests according to Approve SoO. Attach photo once it done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632735&prj=626&rqi=PU1CnFmctbSwCyb1UY8q1r7LB9
BT1ELEC-26-002 | 309b8dfa-900d-4b46-bf49-1cd3088d145f | JK01-2 | 626 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Key "K3" on Solenoid box can't take out during process reinstate the maintenance bypass for UPS, because UPS OFF conditions and thereâ€™s no power on HMI, so that can't send the signal to Solenoid box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632752&prj=626&rqi=QA0Vk60aA0szUjQ02ulrge5gql
GT1MECH-72-001 | 16b8fec4-91aa-45f8-b0f1-78e4ccc77bb3 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | When the solenoid valve and PASCV are activated, the flow switch is active but the monitoring on the MIMIC and panel does not match with C&E Matrix. Need to check and retest and invite CTA for closing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632730&prj=626&rqi=w56yiuKkO54tACxTFaGdD4jJ9G
BT1MECH-6-003 | 06108571-836a-4c12-b8de-dfe6f7dd96c9 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | During Grouping Failure / Lost Communicationâ€ alarm not appears DCOS, and on CRAH display not have sign alarm, only sound alarm on CRAH Unit (STULZ) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632692&prj=626&rqi=GI62Ex7zdd20Ktu13vua1KuNBw
BT1MECH-6-002 | f9c81a2c-a00d-483b-9c2d-25d729cc76c7 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | During Fan Speed Control (Group Control) Unit CRAH not respone (Simulate the Return Temperature sensor set point higer than the current Return Temperature Sensor Value (Average sensor value) Fan speed not decrease (STULZ) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632691&prj=626&rqi=r6M0JZAMAmdFfNaubbBTBDemF7
BT1MECH-11-001 | 2b636355-d2bb-4f12-b84c-0e4b4c7264b3 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Component/Equipment Failure | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | During Water Leak Alarm test, the module sensor did not respond (usually the indicator lamp is on, but this off) Stulz to rectify this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632499&prj=626&rqi=rwP9BCg97v6OoyiOaJfWVHSEY8
BT1MECH-1-002 | 42af9b04-7cf3-4980-b0ac-6658160072a2 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | During Fan Speed Control (Group Control) Unit CRAH not respone (Simulate the Return Temperature sensor set point higer than the current Return Temperature Sensor Value (Average sensor value) Fan speed not decrease (STULZ) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632492&prj=626&rqi=QpvGyv0gr0gPPRbuq07xcMyX3T
BT1MECH-1-003 | d0ddad87-b466-4240-9c0e-ad7a90afec5e | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | During Grouping Failure / Lost Communicationâ€ alarm not appears DCOS, and on CRAH display not have sign alarm, only sound alarm on CRAH Unit (STULZ) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632493&prj=626&rqi=hTGCzOa1Q1V0jpbA0vKNVx7w8E
BT1MECH-1-001 | 6ced0246-238c-47ac-b43c-a1458d86f403 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-08-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | During Fan Speed Control (Group Control) Unit CRAH not response (Simulate the Return Temperature sensor set point lower than the current Return Temperature Sensor Value (Average sensor value) Fan speed does not increase | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632277&prj=626&rqi=xwoxRlAYBgOhhaOfw6gO0JElLd
BT1MECH-12-001 | 7b419cef-6882-4617-96a7-56b6300806e5 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-08-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | During simulate of supply air temperature sensor failure, CHW Valve cannot modulate open to Vmax | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632102&prj=626&rqi=RPRZKEPxLtoDDyVjXaVs8wEXxR
GT1FD-7-001 | 8add7470-b992-4816-965b-1b1967521246 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-2.04 | VES - Vesda |  |  | (For All ASDSP issues) During the L3 ASDSP testing, the ASD workstation was not ready, as an additional VHX 1200 module was required for configuration and programming. After the installation is completed, the vendor and GC shall retest the ASDSP functionality. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632820&prj=626&rqi=5sKDpdO9OB3o1EfC6IV5qXmYd9
GT1MECH-72-003 | 3d434370-2966-4c74-a94e-9264165033ad | JK01-2 | 626 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-08-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | During the low-pressure simulation, a discrepancy was identified between the actual panel status and the C&E Matrix Rev. 04. The actual panel status is shown as Supervisory, while the C&E Matrix indicates an Alarm. Please clarify the intended status and confirm the correct sequence. If the C&E Matrix requires revision, the updated C&E Matrix shall be reviewed and approved by the Design Team. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633020&prj=626&rqi=YwShbm1mEG32QHNJLWj3u2il0i
BT1ELEC-29-001 | 8c959fb8-de10-4dd3-9439-0e2109803cb2 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-08-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | On DCOS & HMI UPS input phase-to-phase voltage displayed phase-to-neutral voltage values | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631945&prj=626&rqi=3FSnlyTH6iuZpH0BvGoMHJOWMD
YT1ELEC-23-002 | 65dec1f2-306c-44c8-be78-ebd20b70221a | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_G_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A 1UPS_G_2 to Libattsys_G_2) Labelling cable is incorrect, please change from 1UPS_G_2 to Libattsys_G_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631753&prj=626&rqi=8r69ufXRqMV4aUQ1ceUdDqMxKl
YT1ELEC-14-002 | d4a288e0-01d7-4f75-b1b1-05559dd2569d | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_A_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A 1UPS_A_2 to Libattsys_A_2) Labelling cable is incorrect, please change from 1UPS_A_2 to Libattsys_A_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631741&prj=626&rqi=iEwl6SY5ti4H0k3agnp4lv78oF
YT1ELEC-120-004 | d0590faa-3ea3-4c48-8b39-53238b639cc7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Elevation socket outlet not align with shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631731&prj=626&rqi=LLYnxASfYkSMhel1hfoFaRBz3Q
BT1ELEC-30-004 | 343e3176-47d7-48b1-8f6b-5c2360ef443b | JK01-2 | 626 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Key "K3" on Solenoid box can't take out during process reinstate the maintenance bypass for UPS, because UPS OFF conditions and thereâ€™s no power on HMI, so that can't send the signal to Solenoid box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631944&prj=626&rqi=KkGasveEIh9aQEN0SBFSfMr1NV
YT1ELEC-23-001 | f1440f9d-0a9b-4a8d-bb27-1d3be770da4c | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_G_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A 1UPS_G_2 to Libattsys_G_2) Vinyl install for cable (+) is incorrect . Please replace it with the black color | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631751&prj=626&rqi=7HyJzpP6IuC9GYzEQaevMRaFXc
BT1ELEC-30-003 | 85d86be7-5550-4e10-ac7b-c387cb532c82 | JK01-2 | 626 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | During load step-up to 75% with Generator source, MSB panel detected a phase unbalance, causing power source automatically transfer from Generator to Utility. The same 75% load step-up was repeated using Utility source, and no phase unbalance was detected and remained stable at 75% load | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631943&prj=626&rqi=HSlRzEXrgfjKoTgyCpwjh3dDFm
YT1ELEC-14-001 | ea75c471-bd11-44a4-ba21-9dfed044210f | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_A_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A 1UPS_A_2 to Libattsys_A_2) Vinyl install for cable (+) is incorrect . Please replace it with the black color | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631739&prj=626&rqi=ckfzI2jzUwUlyIoucbmWMc0gGY
YT1ELEC-123-002 | 573a4f8c-1332-4def-8abc-59d0ce3441e9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | elevation socket outlet not align with shop drawing (refer attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631737&prj=626&rqi=rMVhxGANK3DJGDT2HVSg7xuKqs
YT1ELEC-123-001 | 0ca95623-de2b-4b87-b911-ebe18d64a109 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Discrepancy between drawing and actual labelling, need update drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631736&prj=626&rqi=0v9KQBz84l4cCL094FuYmN437D
YT1MECH-39-006 | 6745911a-46eb-4506-a2b9-09bede4e11ef | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | During Cx activity, found that one of support for return pipe (near PICV) are loose and not securely tight. Attach photo from same angle once already rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631727&prj=626&rqi=OMbWzeiZ7hjlR748C6LWuYhBT6
YT1ELEC-120-003 | 19143370-83c5-4abe-9c54-b458cdafaea5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-31 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Discrepancy between drawing and actual labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631728&prj=626&rqi=cjuBNy5fpfj3aJukhwaw337OkR
GT1MECH-74-001 | 70162dd8-3a30-4d7f-aa2f-7a642ec29c5d | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | During CxL3 activity, ID tagging valve for PASCV 7.01 are not installed yet. Pipe direction sticker also not installed yet, please provide. Once all been done, please attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631429&prj=626&rqi=16I6dM8tk2FeGjzynNa7gG3Zi4
GT1MECH-74-002 | 0a43a5a1-f0a6-4610-bfa6-eef288f18931 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | During Low Air Pressure Switch Function + 1st Alarm Test, Solenoid and Flow switch is not triggered, need to check and re-programming with latest Cause and Effect Matrix | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631443&prj=626&rqi=Y4kzGJ9ghoyxsbuTYlsbM0HDhq
BT1ELEC-33-002 | 62c45f5a-943e-4215-ae94-a66fd8a22add | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Inconsistent overload alarm threshold was observed between UPS units. UPS F2 (Mechanical UPS) triggered the overload alarm at 107% load (above 100% load), while UPS D2 (Mechanical UPS) triggered the alarm at 112% load (above 110% load). The overload alarm setting shall be standardized across all UPS unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631724&prj=626&rqi=oE8HGJdHYyzQCVQxjUxaUzMpgN
GT1MECH-64-002 | a7c2414a-9edd-4f4f-9ee7-1fa0cd78ea1b | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/Equipment Failure | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_41 | CRAH - Computer room air handler |  |  | During Waterflow Verification (PICV VMax) the HMI cannot show the value of Opening Chilled Water Valve, while in DCOS it appears. Stulz needs to rectify, attach photo once it already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631444&prj=626&rqi=SZe0YacK6YCtGwxwGGReaVi5IC
GI-031 | b9815a43-9f64-4b39-8130-998a3a78b84b | JK01-2 | 626 | APAC | Open | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [7 empty] | The gaps between CA need to be sealed off (for all floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631105&prj=626&rqi=ARPFvjqxyDCIYozfIkDEozGvZR
GT1ELEC-51-002 | 96b3168b-d871-4c4d-9b32-13ea01dd483d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631012&prj=626&rqi=sf6b3ddwcDjECWOyVrD3HmogOt
BT1ELEC-33-001 | 3194c4a4-f823-418d-9e20-f6c48e39a96d | JK01-2 | 626 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Status of operation mode UPS after Overload Test, UPS status is Static bypass (Load on Bypass in DCOS), but in DCOS shows Load on Inverter | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630835&prj=626&rqi=yANNkCmgYyc7GUcPpLzYhqb6JI
YT1ELEC-167-002 | 9d03e059-d074-4c00-80bc-b0b47a2a954e | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630863&prj=626&rqi=xrr5CmeA2boCsaRib9UwkNNr2G
YT1ELEC-171-003 | 410848a7-eede-45b1-8846-86a1b66e97c3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630875&prj=626&rqi=cQIOyqyxsVGJ84Ith6QMuH7lcj
YT1ELEC-169-008 | d1e8db77-20cb-4e0b-b007-9b840a6e7b10 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Rrom readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630873&prj=626&rqi=z4lF8WVwAgvxUavNPNf0aD4pjk
YT1ELEC-168-005 | 6c6ba497-fab9-448f-9914-eaf54a408ecf | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630868&prj=626&rqi=YuVONA6AtZY7u6K5SrfmUm4O6S
GT1ELEC-53-003 | 851aabeb-e51d-4820-aeaf-7d8f0d2685ca | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631177&prj=626&rqi=Z63DD7sIybxpWtTD8GYEDpv5K1
GT1ELEC-50-003 | cd5ad49b-276e-4750-9d75-042884c7f5ec | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631174&prj=626&rqi=rXKRc4hBR00sReSCDgroxvGrPc
BT1ELEC-30-001 | 325e5308-618f-44b0-bef1-1e57ddde4f37 | JK01-2 | 626 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | During 50% load step-up on Generator source, 1MSB_D_1 panel unexpectedly switched back to Utility. When trying to transfer the power source back to Generator, Breaker QE (Generator incomer) failed to close even though the Generator was running | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630998&prj=626&rqi=KoPfG0gPgNSiFPNtEa8FgZK5FS
YT1ELEC-170-003 | 51c17248-2b5f-4dbe-82b8-4c713bb52f92 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630874&prj=626&rqi=xPiQv02Ah5882RoUGLsUXh9ez9
GT1ELEC-49-001 | 276f09b8-02ba-418e-b131-5dadff0d4643 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631008&prj=626&rqi=RCJGLZmSfrfqOsQeMxL8ysTRVp
YT1ELEC-166-007 | f9fc1ab8-35bb-4d52-abd0-799e2a73c491 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630869&prj=626&rqi=l9rFn0Tx6e2aClBcPfyqG9YJm5
YT1ELEC-164-007 | d1ad5c64-c3b6-4724-bd10-e57cf813df87 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630864&prj=626&rqi=wzyf17i9divgl7rZDPzqffPllM
GT1ELEC-47-002 | 87b26c94-2c96-4abe-a371-f0bddd5bc73d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631005&prj=626&rqi=QmUUbvkPXmHHlCvzgt8gw1bhnl
BT1ELEC-30-002 | 7ff7595e-10ee-4688-a34c-423d87a594f0 | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | During UPS overload test, DCOS indicated "Battery Discharge" alarm even though the UPS was not operating on battery mode (ORISE) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630999&prj=626&rqi=bMEkGGdIlAbxp9HGavuNvZsliZ
GT1ELEC-48-002 | 96ba899e-817d-421b-a402-1647b43c1942 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631006&prj=626&rqi=ZfonbespjUjPf9KOnAFJ13xOAk
GT1ELEC-48-003 | 99848fed-0d3f-44b1-9230-29512be8b1e5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631007&prj=626&rqi=GlCGW99vc0MvH1SG10h3oSYbOr
GT1ELEC-46-001 | d65e2524-770d-4c5b-82ec-449b112b37a0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631002&prj=626&rqi=FjbP6JQWHeeinSywgbTnslcy7r
GT1ELEC-50-002 | 8577a5a2-6966-4da8-92d8-9501bb04f7b7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631010&prj=626&rqi=mPPhrWRjEaIJpBFeNb4ZIGEyQ8
GT1ELEC-52-002 | d5705862-0c69-4d6d-82a4-50285bd58f43 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631014&prj=626&rqi=1kArFCoqo3G1IzFWovG8kDdL3c
GT1ELEC-46-002 | e39af5e8-29da-4468-9779-e7ba5732ce30 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631003&prj=626&rqi=0WDniUDdA10M9M2C3yaSrzGYr5
GT1ELEC-52-001 | 2648cd8a-c1c3-4cc0-bbae-a10a0d5f21ab | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631013&prj=626&rqi=IRFVJ7K3mao7xqk33OAQKAgCIT
YT1ELEC-165-004 | 4454355a-2f2a-4ef2-89c1-c00cefddd26e | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Room readiness need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630866&prj=626&rqi=oDoq7hHqVCBDOKW6KKzqXZWMwb
GT1ELEC-49-002 | 95beed43-82d3-44cf-bc1b-f6ba16e6f8a9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631009&prj=626&rqi=xHMHyQ7Hxi8bgda824tSpdjnXg
GT1ELEC-51-001 | 7e55f149-e770-4104-8e4d-60a0806bb8e0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631011&prj=626&rqi=lUnjOP2mW3GoV2f2viANS42uAK
GT1ELEC-53-002 | 0c8a4d4e-3bc5-4c7f-8b01-a578cb7ba5ff | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631176&prj=626&rqi=9CAm2cEClmqf6SjLPk8TxKkxJE
GT1ELEC-47-001 | 990c3ce6-3101-48d3-8352-35289c30f961 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Breaker naming does not match with mimic diagram displayed on HMI. Please update the breaker names to ensure consistency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631004&prj=626&rqi=0WJzBcbzPGzdWQbeKFQVWHFw8i
GT1ELEC-7-002 | a942a23e-2de0-4e1b-bf71-6d7e18c12781 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Frequency Dip during Block Load Test 0%-100%-0% out of tolerance. 50Hz to 41.88 Hz (above 10%) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630675&prj=626&rqi=h72gdgmLoV8UAO64ydHWrZHfnw
GT1ELEC-7-001 | 0bdc1663-d073-4576-880d-cd9415442860 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Voltage Dip during Block Load Test 0%-100%-0% out of tolerance. 418 to 280 Volt (above 20%) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630674&prj=626&rqi=WG0nTNgk4PjVzTxomikGgWiCMu
GI-030 | a6bc02da-73bf-4bfd-a69f-97a2f8f42b37 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | All the sharp edges (which is in contact with the cable) need to be protected with rubber protection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630627&prj=626&rqi=dtfrJJF5ZWpH1kL4aqWYkPhLwU
BT1ELEC-28-004 | aefe0fcb-288d-438d-bf9c-bf69890f953b | JK01-2 | 626 | APAC | Open | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | During the Maintenance Bypass test, Key K3 at MSB solenoid box could not be released after switching sequence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630610&prj=626&rqi=ltZpInEErRMH9cI0tEr8kH3VxF
BT1ELEC-28-002 | 803b16ad-ea7d-4bce-98c1-408b6326a895 | JK01-2 | 626 | APAC | Open | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | During UPS transition from Normal Mode to Dynamic Mode, the DCOS graphic did not update. The operating mode remained displayed as "Load on Inverter" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630608&prj=626&rqi=m3pnkfvc2d85VvfuqnQ5odE9ji
BT1ELEC-28-003 | 567b18bf-c590-48bf-a97f-8d661e01d571 | JK01-2 | 626 | APAC | Open | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | During UPS overload test, Overload Alarm was not triggered even though the UPS load reached 110% of rated capacity | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630609&prj=626&rqi=fCHv5T2m9bVYDM3n6CKeNcLgLd
BT1ELEC-28-001 | 6d115420-eb0a-41b5-9af5-656d49151c14 | JK01-2 | 626 | APAC | Open | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-07-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | DCOS Graphics Issue | DCOS |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | During UPS transition from Normal Mode to Eco Mode, the DCOS graphic did not update. The operating mode remained displayed as "Load on Inverter" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630607&prj=626&rqi=4WqGprKSn0gOIpChYHMmPcYneT
YT1MECH-59-002 | 4f98143c-caa1-4107-9d6d-5155838cb256 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | Completed Termination Cable PICV | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630222&prj=626&rqi=TdT51fAq13B8lF7Yxujz7tiptk
YT1MECH-61-005 | 47caedb1-9080-4c64-8837-8e62b4a77a5b | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | Tidy Up Flexible Installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630233&prj=626&rqi=zUvajmx9Mpi12ZAY9dZ3Pd86IW
YT1MECH-61-002 | d7ea1ae3-4a16-49a7-8eb2-986ae926c1e5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | Completed Termination Cable PICV | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630230&prj=626&rqi=34I4bMNYgPraw4CzP8IFlx8epD
YT1MECH-61-001 | 3feded38-6b04-441a-876b-2d378fe06a4b | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630229&prj=626&rqi=pwJTk8wFzbAhYc9n53Qu4thX1j
YT1MECH-60-001 | 8929c7f7-8887-4f5b-8303-3c15e6b6dc61 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630225&prj=626&rqi=En0GN8mtnOvhMNeT7kkZVbK4Ez
YT1MECH-61-003 | 432be709-de0a-4abf-8638-d0e10a792131 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | Take Out Material Not Use | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630231&prj=626&rqi=G7fEyigxm3lDUgm6OSaogYeAWC
YT1MECH-61-004 | 1af2246c-dee0-472f-b179-6110424c8f81 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | Tidy Up Fire Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630232&prj=626&rqi=ixQ2mqyLSSdot5RXM4MjYs6Zih
YT1MECH-60-003 | b66544b4-db0e-484d-8898-51ed06f9e434 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | Take Out Material Not Use | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630227&prj=626&rqi=kXwbEyx7EybaBkT8gEIJHyh3LQ
YT1MECH-60-004 | 9296c97a-26e9-4cf9-bca6-2618d23fca12 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | Tidy Up Fire Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630228&prj=626&rqi=p1OoS4JMgXgnFGai0wsaPs6szC
YT1MECH-60-002 | b4ec3497-95c4-465f-b5b0-b07d7faed356 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | Completed Termination Cable PICV | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630226&prj=626&rqi=5or9mtXHrR7VpBvMWYygYgn0O5
YT1MECH-59-004 | 02706460-5f0b-43ca-a51f-827e503f9456 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | Tidy Up Fire Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630224&prj=626&rqi=QfuqIAaIJzUMDNSDGo8clBbhve
YT1MECH-59-001 | 393cf997-c8cb-476a-b32e-ea8d8c1132d1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630221&prj=626&rqi=ZIe0Hrg8vviaiHcMCxwtJeIIFa
YT1MECH-59-003 | a35be811-ffcc-4a5f-9a68-dd2d0d55d4fa | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | Take Out Material Not Use | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630223&prj=626&rqi=oFwhew96G0jXY4R5ql7AdnE5zs
YT1MECH-62-002 | cd09b20c-6691-49a5-9d73-ca68b6ee3a75 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | Completed Termination Cable PICV | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630237&prj=626&rqi=InXfQ2sfQkMVTBcH9iacO7zO4z
YT1MECH-62-004 | 170e3615-3f94-4087-8f18-c2845f8a71cb | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | Tidy Up Fire Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630239&prj=626&rqi=uDFowd8ekIgXJL2uFeirKqRpBY
YT1MECH-62-001 | 5a43eb2e-84e0-4cb5-963d-35aff9548378 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630236&prj=626&rqi=5VeZStuZ2JwjYC1CWubTizYHfR
YT1MECH-62-003 | c6047c4c-2340-4d52-8b2b-40b0aacb67d6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | Take Out Material Not Use | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630238&prj=626&rqi=fhyxt41rwzvSiX4BAXPIsIndQG
YT1ELEC-6-002 | aac142a9-9948-4cf9-97c4-298d8a32ac2d | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630310&prj=626&rqi=M6PTr9ZHS197pD04rscxldlg6G
GT1MECH-77-002 | 7575ddef-55f7-4706-95d7-35c1b99a9e77 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | During the verification of the flow reading between FM and the handheld tools, witnessed by CTA and attended by the Orifice Balancing principal, an anomaly was identified between the FM and handheld readings. GC shall investigate the discrepancy and provide clarification/ statement letter with principle regarding the observed measurement results. CHWP 4: FM: 43 l/s ¦ Handheld: -0.1 kPA (appx. 7 l/s) Compare with CHWP 2: with the same tools (the results are good and not much different) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630074&prj=626&rqi=Qp2K2QqykM06A0yotTma75hQM4
GT1MECH-76-004 | 80ee0f51-a833-41d2-8194-90f562121816 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | During the verification of the flow reading between FM and the handheld tools, witnessed by CTA. The flow readings from FM and Pump HMI are consistent. However, the handheld measurement at the orifice balancing point does not match and shows fluctuating results, indicating a potential issue with the orifice. GC is required to obtain a formal statement letter from the orifice manufacturer/principal to clarify and justify the discrepancy. Compare with CHWP 2: with the same tools (the results are good and not much different) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630095&prj=626&rqi=DvdrLMVPjzJgTyGIn0ONZ0RB7w
GT1ELEC-17-002 | 0a285847-1cde-4e04-9ef4-63a233f86659 | JK01-2 | 626 | APAC | Open | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Several points have not been tested: This includes all UPS units. - Output Overload - Output Alarm - Overload Shutdown - Rectifier Fuse - Total Output kW - Input Breaker Open - Low Battery Alarm - Battery Amps - Battery Time Remaining Status | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630169&prj=626&rqi=BqNIFxVAPIi7uJaz2GG0C9rAAo
YT1MECH-58-004 | f7257b55-d85b-4d45-96da-358aab9b14d9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | Tidy Up Fire Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629986&prj=626&rqi=BzJHZyPVxvG1delC9yVGnnviRh
YT1MECH-57-004 | 20c1c7c4-d308-434f-88eb-bd91efa046f7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | Tidy Up Fire Cable at CA unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629982&prj=626&rqi=bzUoO1mWZdE2RRIVevgKSLbGgv
YT1MECH-57-002 | aedd1a44-ab9b-4eef-bc78-d69eeb5d0022 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629980&prj=626&rqi=6XKmM3fifPug9HlqNFt7ji8DPX
YT1MECH-58-001 | cc16691f-e1ed-4027-958e-f78de3b399d2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | Completed Install Cable Sensor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629983&prj=626&rqi=WGzQaIFPtnLc2jTXUMeOgEgash
YT1MECH-58-002 | 7a4d7c52-bedf-45c7-b260-9ad2f7c34006 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | Completed Termination Cable PICV | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629984&prj=626&rqi=3ub4NxjaZnp8VEXJ5ULhSJtmNi
YT1MECH-58-003 | e056da53-82bb-4c3e-8530-49a4e1c76d8a | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | Take Out Material Not Use | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629985&prj=626&rqi=m3dyl994gdN9qUhIWJuzU8KFWE
YT1MECH-57-003 | 8c348572-e687-48fe-9059-199193ee4cf9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | Completed Termination Cable PICV Valve | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629981&prj=626&rqi=WzRjF6vkCqWma2O1XsSGri00ab
BT1ELEC-26-001 | 7e252afc-5713-4487-ba24-4e18900def85 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | During the preparation for the UPS B_1 L4 (Burn-In) test, a cable was found to be in contact with the busbar. Once finish burn-in, install additional rubber protection on the cable, as over time the cable may come into contact with the busbar again. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629978&prj=626&rqi=Dyxi5y2DaFzHxKSK0NTF9M0t5j
YT1MECH-43-003 | bfdf6f9b-639c-4747-a508-3c3cdc568d32 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Completed Install PICV Cable_CA Response in issue must take evidence each of equipment in Block D (5th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629354&prj=626&rqi=mp4K45hhr1pikcMA0o2m2SezXm
YT1ELEC-162-002 | b84309bf-efb3-47d2-8eea-2ca1622956ce | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | DimasKurniawan@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | General Contractor | L2B | DCOS Installation not complete | DCOS |  | Electrical â€“ LV | equipment | 1Fuel Leak_L3 | LEAK - Leak Detection |  |  | The DCOS cable hasn't been pulled to the panel, even though the drawing shows a DCOS connected to the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629412&prj=626&rqi=rVgjvt4sXIMmvVoVSQ5qVjf3yu
GT1MECH-76-003 | bae2019a-87e2-4824-985b-8860619ecee6 | JK01-2 | 626 | APAC | Closed | P1 High CX | MulyaSitanggang@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | A leakage has been identified on the CHWP-03 pipeline. Please provide an explanation of how this issue could have occurred, including a detailed Root Cause Analysis (RCA). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629352&prj=626&rqi=r5mZbFyYNMKYuClIHwrN2ITJBi
YT1MECH-43-005 | ced5fa8c-6096-4935-a753-1521f7cf7e93 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Take out material not Use_CA Response in issue must take evidence each of equipment in Block D (5th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629357&prj=626&rqi=g6fx1aJn0yRmBC2nPHoLtJDfJQ
YT1MECH-43-004 | 71f1c240-1f68-4b12-970b-344dfd524f11 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Completed Termination Cable Sensor_CA Response in issue must take evidence each of equipment in Block D (5th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629356&prj=626&rqi=9NO6ce4tZofbeh2m2vO1ON1i5o
YT1MECH-43-006 | d203c470-3539-4adb-8467-d80c22c737a7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Tidy Up Flexible Installation_CA Response in issue must take evidence (report) each of equipment in Block D (5th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629359&prj=626&rqi=VM1YYJoAwIH2asQOHxZGIC1KBV
YT1MECH-50-003 | 4e97299b-3730-452b-8890-8c27c4d1b9b5 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_C_01 | CA - Cool Array |  |  | Kindly Termination All Cable Installation at Sensor unit Response in issue must take evidence each of equipment in Block C (4th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628855&prj=626&rqi=fsaTUpDgnN4UHBkCfvjbpirROE
YT1MECH-50-002 | 6043ea6d-4144-4f4d-8c70-40d8ad509be0 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_C_01 | CA - Cool Array |  |  | Kindly Tidy Up All Cable Installation (Cable Sensor) Response in issue must take evidence each of equipment in Block C (4th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628854&prj=626&rqi=kCM2ufejxXs5QALoZ1TOENtY42
GT1ELEC-48-001 | a0e9c87c-f999-4527-8e23-8f76408b4ecd | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L3 | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Key interlock on ACB is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630617&prj=626&rqi=T8Zn0WFBK91ugHMs27GIVegFCz
GT1ELEC-53-001 | aaa99e98-cb5a-483f-ac80-cb04c6d8bc66 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L3 | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Key interlock on ACB is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630619&prj=626&rqi=SxBmtYGYYS8JKy0QDwUanN8bdW
YT1ELEC-9-003 | f3b950f8-8c54-41e3-9aaf-50c4732cd8c4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628852&prj=626&rqi=K1u4UnVanQGZZ78AJ5Z0q8u5cu
GT1MECH-77-001 | 33676f39-39f8-49b4-87cc-7780f2ed607d | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | During CxL3 Running Pump, leakage in connection pipeline | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628846&prj=626&rqi=BTtdXpVQUj8KSCgrNOUGLkdHcf
GT1MECH-76-002 | ec33bbad-d86c-4272-80fc-e10a062d0581 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | During CxL3 Running Pump, leakage in flange connection pipeline | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628844&prj=626&rqi=p5ob2f1HVc5HIhMuSEplhQP1tS
YT1MECH-50-004 | d56e617d-b733-4d5a-880c-81a6c14817c6 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | MulyaSitanggang@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_C_01 | CA - Cool Array |  |  | Kindly Provide Report for Installation Flexible pipe (completed sign off TNT and CTA) Response in issue must take evidence/report each of equipment in Block C (4th Floor) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628858&prj=626&rqi=f4OzyS2ksXuxEjKEhPzABdunF5
GT1ELEC-50-001 | 54b0dff6-7521-4e76-a89b-a7ee35a75f54 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-13 04:00:00.000 +0400 | General Contractor | L3 | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | Key interlock on ACB is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630618&prj=626&rqi=wC6tllqWqDihO4QJQii8kcvMgH
YT1ELEC-47-005 | 27d361fa-7e8e-4c29-a74e-49b6a86385f9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628736&prj=626&rqi=54g9aPLmYtwPmTfbQXNxYyL8DW
GT1ELEC-17-001 | 9f46597a-a461-421e-9163-1ed2afa0c380 | JK01-2 | 626 | APAC | Open | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Based on UPS Point-to-Graphic (P2G) test results, several DCOS points have not yet been tested. Please complete the testing for the following points: (will be verify during CxL4 ) 1. Battery Amps 2. Battery Discharge 3. Blower Fan 4. Alarm 5. DC Cap Fuse 6. Output Overload 7. Overload Alarm 8. Overload Shutdown 9. Rectifier Fuse 10. Total Output kW | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628675&prj=626&rqi=8tkHvX3zlTn07jxs3jIS4Sz0zN
YT1ELEC-46-001 | 58f8ea66-6729-4309-bc63-2983f5cc3a88 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628735&prj=626&rqi=MahNgWK09t4q9yJ366JwIWSnvt
YT1ELEC-165-003 | ca2ec2b5-418c-4284-a9ba-5766a493ff35 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Wrong cable termination location. The cable from 1MDSB_R1_2 to 1TOU_C_2 has been terminated at the wrong breaker Q1-6 at 1MDSB_R1_2 side. The correct termination point is breaker Q1-3. Please rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628706&prj=626&rqi=SG8AWfP5qRNzAIIh6j56ZEd2k8
YT1ELEC-7-002 | 72c178da-2fcf-4962-9d9f-ec4c41f2c606 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628725&prj=626&rqi=2NuAeJoMimEo3z8q0qmsiaAm4X
YT1ELEC-168-004 | c1a82d69-51ca-474c-bbab-d642615b5e27 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Wrong cable termination location. The cable from 1MDSB_R1_2 to 1TOU_F_2 has been terminated at the wrong breaker Q1-3 at 1MDSB_R1_2 side. The correct termination point is breaker Q1-6. Please rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628708&prj=626&rqi=FLYeVnJ8R6F59L2atslspO9iwf
YT1MECH-37-004 | 6b4da2f7-3bfc-4400-899e-cd3260445972 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_02 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628566&prj=626&rqi=AC9VHB5FpRD4wJtc2zqsux7cOl
YT1MECH-39-002 | 498c5c66-9fe2-4da4-8a1c-d0a70ffd26d9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628555&prj=626&rqi=IpJ7EW0rLTkokPDGkDc4PWTA6m
YT1MECH-36-003 | a6db96a6-2b16-4196-9af8-961f0f523eb0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628528&prj=626&rqi=CIldOeQc5tegO4itcOBurpFR52
YT1MECH-41-003 | 847c61b0-f96e-4c49-ada8-f21c71cb1acd | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628557&prj=626&rqi=LQ50fhYoojbWSItKmUQlScW4UY
YT1ELEC-18-010 | c0eb0f78-3a4f-443a-9c45-8cf0a1b26fed | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | kattyrachmawati@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | White glove inspection/FOD report not yet submitted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628491&prj=626&rqi=Szx29QiwkJouL1pCt1xRI06ovv
YT1MECH-40-005 | 61cd90f1-dabf-408b-870a-bd219fe91637 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_06 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628576&prj=626&rqi=q2G3H1JhLwMTMChlgBoPB68BLB
YT1MECH-38-005 | 9942b77f-860c-4384-9a4b-877308897d05 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_03 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628579&prj=626&rqi=nMf7wqzIKmuVKoXpVbRJQn0DtS
YT1MECH-41-004 | 12eefea2-fef9-48c1-ab5c-32f42c98448c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH are not yet pulled. When the cable already pulled, please do the installation properly and attach photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628560&prj=626&rqi=yVNrRMUFRMuGaRcQNPkK8DhExQ
YT1MECH-39-005 | d3b473fd-427e-43a6-9392-87614090f088 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628577&prj=626&rqi=IHQZuk2ii5XNhij9KmXHGzk0pH
YT1MECH-38-004 | 095b86a3-2458-469a-839d-add6309596f2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_03 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628567&prj=626&rqi=KbUgh8lXnJFg65wu1AVAhASiyO
YT1MECH-39-003 | 554d905e-5f24-408e-8fce-61d5cc814244 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH already pulled but need to tidy up and installed properly. Cable test also not perform yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628563&prj=626&rqi=v9iU7QyMamcVm6sCN8sUsZS1V8
YT1MECH-40-004 | 5e3af760-9c27-42d3-a9ec-483df3f4e7e5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_06 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628569&prj=626&rqi=OMMxpvjs5cpoTMjHNHAA1etSKC
YT1ELEC-8-002 | 5eccdd14-b9b6-4960-83ec-60f6d9c6e1a9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628548&prj=626&rqi=X6ko8vqSNMfLmDPKnrNWj1c2fl
YT1MECH-41-005 | 92246b0c-972b-4649-9abc-15216af1375a | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628570&prj=626&rqi=PYvX97WmlB883xHiUnBbkbFHpb
YT1MECH-37-002 | 309168cf-6eab-4219-a956-7aef864ab44b | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_02 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628552&prj=626&rqi=bX4jKPTZ3jHcdiSvyaiJjl670x
YT1MECH-42-004 | f48c4827-c6fb-41d3-a31d-39f8c9dfb3f5 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH are not yet pulled. When the cable already pulled, please do the installation properly and attach photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628559&prj=626&rqi=OycOLkGWDOTd0P70eKlQVuqfzQ
YT1MECH-38-003 | 994c6f25-73c2-42f8-9fe8-ef874be24395 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_03 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH already pulled but need to tidy up and installed properly. Cable test also not perform yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628564&prj=626&rqi=OIIwBayhtJOCen5emgQNIalvCK
YT1MECH-37-005 | f5d218fc-fed1-41f9-9e7e-121b5ba95400 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_02 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628580&prj=626&rqi=Cgz4rZm0acGS3wSmhyDDq0KxGq
YT1MECH-37-003 | 677611b7-5945-45ef-ad37-6a80e15839a8 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_02 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH already pulled but need to tidy up and installed properly. Cable test also not perform yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628565&prj=626&rqi=WcDwpbXfS6OywCzu9lriypTDYt
YT1ELEC-49-001 | 483073a6-2dae-4efb-bce6-697e382a2b91 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628550&prj=626&rqi=dVCWFrNLrjHqjjPqq1nv5MA2vl
YT1ELEC-51-004 | 0b441464-7886-44b3-9197-8698bfe03c3a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628553&prj=626&rqi=8ATggG8vfcHg3iGyItoUf2ddtc
YT1MECH-38-002 | c7195e2a-20f0-4fcc-b39f-4340d5be4f9e | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_03 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628554&prj=626&rqi=rwgdbkKkpt94qQ49DAl2W93VnE
YT1MECH-39-004 | ff3295fc-bd6d-4a4e-9f5d-000ae405f458 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628568&prj=626&rqi=QgyBO3765eW3r68c5bii1wNm83
YT1MECH-40-002 | ea70c7eb-f54f-4cf8-94e4-5d863c6c6b2e | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_06 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628556&prj=626&rqi=ILZ1mTWtG8B4DqW9PtF6yA0GmG
YT1MECH-40-003 | d34e4945-abfd-486a-92ec-12265b5bcabf | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_06 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH already pulled but need to tidy up and installed properly. Cable test also not perform yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628562&prj=626&rqi=JjbrTftZaI946v17IPpvUtyUmk
YT1MECH-79-002 | 7fbe7277-65ac-47a9-9abb-2d095c15d15d | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_F_1 | FFU - Air Scrubber |  |  | Completed Cable Installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628533&prj=626&rqi=eOrwfbytaUy0cB9d2SX81dfCCr
YT1MECH-79-003 | ad9d0157-4635-4e0d-bdff-8c92c3a409f7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_F_1 | FFU - Air Scrubber |  |  | Label Equipment Not Straight | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628534&prj=626&rqi=szgANo9T0ajTUb6Ofalfn8RFfL
YT1MECH-42-005 | 8829f976-342f-4f0a-815a-b9d890295442 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628571&prj=626&rqi=2bSnvtrAAb9QtoSUzCZm9VrKwu
YT1MECH-42-003 | 455e40a5-4c1c-444a-8416-59d32f8faa5c | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | Need deep cleaning for the unit, room (cool spine area) and in front of unit there is still so much material, debris, dust and even some leftover unused materials scattered around there | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628558&prj=626&rqi=TG7b9ohYRsqRqUxlRtNA7vvhdM
YT1MECH-79-001 | 1bf2395e-fca1-4a20-ac4a-873f02209f75 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_F_1 | FFU - Air Scrubber |  |  | Cable Straight Not Straiht | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628531&prj=626&rqi=YHgs8FoYI36fd4jABHY0eSjznK
YT1MECH-36-005 | af55a6e2-cd0e-4c59-8c13-0edda269fabf | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | Branch pipe from CHW pipe to flexible hose need jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628544&prj=626&rqi=lD5CEwzjn5BA3fOMNUz1rA95kQ
YT1MECH-36-004 | 57692001-22cc-4869-86a2-75b952a99701 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | During CxL2B the cable sensor from CA to DH already pulled but need to tidy up and installed properly. Cable test also not perform yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628543&prj=626&rqi=4V68xw7y8dd3HpLEwRhkd87m9h
YT1MECH-42-006 | bf6af7c9-63be-4116-8fb9-7c92c1304ae5 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628574&prj=626&rqi=quTRaNyqWzTtFE3LMGGzym0hVO
YT1MECH-41-006 | bc5e9497-d588-40e1-bf0d-e1a55d576074 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628575&prj=626&rqi=b20PhHjswzOxqXvklUjyIGRjDu
YT1MECH-36-006 | c8f52221-b415-40f6-9273-95bc599283ac | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | Flexible hose needs to tidy up and provide report approval T&T and CTA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628549&prj=626&rqi=f6BHzGYItQol8wPED8dm74uhOU
YT1ELEC-50-003 | 4e8b9804-1ea0-4762-bdb7-e25a86cbd366 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628551&prj=626&rqi=0xuFuOj4RMEerEOPlYHl1deByT
RT1ELEC-169-001 | 00517aed-6ef7-44a9-862d-427e48cf0391 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Controls | equipment | 1PANEL_I/O_Motorized Damper | CP - Control Panel |  |  | equipment name / labelling onsite does not match with name on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628512&prj=626&rqi=8QZNDxHYzDtl8ZnDbDsHsOzP6A
YT1MECH-78-004 | 7d5978a7-7e4f-4501-b98d-a82afe229105 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | Clean the dirt from the FFU unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628307&prj=626&rqi=3PRg4Hh6ZjtaTmPooD1x9KOz6d
YT1MECH-69-004 | 19493552-e361-4b9f-8d32-cb7b96a420d6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | Adjust Door FFU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628309&prj=626&rqi=nGy83QnQLiOklvkUuhYPjNgM0V
GT1ELEC-1-006 | 3cf9e8dd-dda2-4e5e-841c-047d2a125b91 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L3 | Cleaning | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Top of panel found dusty. Please re-clean to minimize dust ingress into panel and busbar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628306&prj=626&rqi=tUJFferYGgS1uE3MPaVciukfHo
RT1ELEC-29-001 | 706a8b7d-4b92-4176-8eae-7a123e4f6c5d | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_G_2 | UPS - Uninterrupted Power Supply |  |  | Please upload following documents: 1. RFIT documents 2. Certificate calibration of Torque Wrench | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628300&prj=626&rqi=17yvePjkcN1TL8vcrvifZeHzVl
YT1ELEC-29-011 | 497ce714-a2f2-4f41-89d3-88cd7204d193 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Please upload Torque Report Earthing Cable (not include on CxL2B earthing cable report) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628402&prj=626&rqi=6HI0MsatpXyesYyb4VWdUD5Lzy
YT1ELEC-30-007 | 391f543b-b3b3-46b9-9b61-36f561991d87 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Please upload Torque Report Earthing Cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628411&prj=626&rqi=T8Nc0BmmNsFGesdy2CTJIXz5MT
YT1MECH-76-004 | 7cefb91d-fc23-432d-81a0-b88af5fc46c0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | Remove Silica From FFU Unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628308&prj=626&rqi=SR6bs0R7uDxj9VFpHC1cq3AhqN
YT1ELEC-31-007 | 7b0caf2c-e16e-42cb-a9d8-31aefbbab5db | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628184&prj=626&rqi=NjNqwTIQLiQ8r9K2gIvW98B7YH
YT1MECH-67-003 | d51be55f-f4ba-42c3-ade8-76b826da559b | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_B_4 | FFU - Air Scrubber |  |  | The FFU door is not closing tightly. Please adjust the door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628165&prj=626&rqi=e5JZaERl4niAdiJlFJeiE0RX3v
YT1ELEC-25-001 | 8d78495a-15fe-4434-aacc-5d3bc0132416 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628182&prj=626&rqi=xS4iyMxjArHGwGdKGacEDu2IEQ
GT1MECH-76-001 | 81edf32a-87ba-4990-b764-4496d55736c4 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | wellyjulian@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | During the Internal CxL3 Pump Performance Test witnessed by CTA, a discrepancy was observed between the flow rate reading displayed on the Flow Meter/SCP Panel and the Pump HMI. (SCP Display: 46 Hz --> 64 L/s and HMI Pump: 46 Hz --> 11.43 L/s) Further investigation is required to verify which reading accurately represents the actual flow rate and to ensure the displayed values are correct and consistent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628111&prj=626&rqi=Pefh8IvtXFQQKXLEBFBmQ3LhsW
YT1ELEC-26-002 | f7f31343-ed16-46b9-a315-f028c4fd1215 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628183&prj=626&rqi=LQ9p7V86j5V5jJn6HmK6lq2nfi
YT1MECH-65-004 | b871278b-e02f-4677-a10c-7a91ead17785 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_B_2 | FFU - Air Scrubber |  |  | The FFU door does not close smoothly. Kindly adjust the door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628163&prj=626&rqi=beFmSXjsq3o9wOqTXSTDzqUtVT
YT1MECH-66-003 | 5cf3ea82-0a1b-4a2a-8105-6b5e2ee0dcd2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_B_3 | FFU - Air Scrubber |  |  | The FFU door does not close smoothly. Kindly adjust the door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628164&prj=626&rqi=msZfDGaVRTc78Qv4HFh8DyitIM
YT1ELEC-32-006 | aef9e48c-cdba-43d9-a499-d302035da1a1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628185&prj=626&rqi=sYIG5kvIc66B4euxcyAImLWZ3n
RT1ELEC-125-010 | 60800ba8-e0c1-4db7-929e-c0164d521113 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | The uploaded drawing of panel is an old version. Please replace it with the latest updated drawing, old version must be unlink/removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627964&prj=626&rqi=Xtg1zat9vit5P7Wh0LLhOfXRxK
GT1MECH-60-004 | bb6be809-752c-41c3-a1ed-408b378c85a5 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | When conduct P2G CRAH, parameter "Waterflow" cannot be simulated (STULZ need to be check and clarify) This issue is for ALL CRAH UNIT | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627986&prj=626&rqi=R3Hb28JITDf0ZvQNpdVdRaoTde
YT1ELEC-166-006 | 19117cbb-df9f-4e6f-998d-fc43a1c7f23a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to attached images | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628171&prj=626&rqi=NzKegh5z6fW17JzFDGiXXiTGx7
YT1ELEC-169-007 | 52f4435b-65e1-47c1-bda8-487097b2e5fe | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628176&prj=626&rqi=rqB4oITudljrMVGfrXfcad2TX9
YT1ELEC-167-001 | 8c4b7984-5b15-4e51-bb53-a629ca6bd2ad | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628174&prj=626&rqi=evS9xgBpTItgVkYv3nBGVtCKrX
YT1ELEC-165-002 | 5275a219-c397-4616-add3-dd7d4347bcb2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628173&prj=626&rqi=Bxx17339FU0GEtRXksR5FtxLUv
RT1ELEC-122-007 | 5e57b66e-c59d-450f-8db6-aac4d2607711 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | The uploaded drawing of panel is an old version. Please replace it with the latest updated drawing, old version must be unlink/removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627961&prj=626&rqi=l4bMak9SYgOnotXTKCUgjFl4b4
RT1ELEC-131-006 | a67895a0-acdd-44c9-9c39-b7d76b46f933 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | The uploaded drawing of panel is an old version. Please replace it with the latest updated drawing, old version must be unlink/removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627967&prj=626&rqi=I6iXQWxm0ERcb03gJ8c9SYEqzZ
YT1ELEC-168-003 | 4361f4d6-01bd-4dc0-b6e5-a58b0d64e9ef | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628175&prj=626&rqi=KAL0dqtjMYWuLWDw9fge4ZuYS5
YT1ELEC-48-004 | a460cb2c-e735-4767-982d-dbc76599a099 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628181&prj=626&rqi=OcxaWDGsTJ3VkE1fCkQ78kBxko
GT1MECH-62-002 | 469ca2d8-6ebe-4f92-b247-f11e48b75414 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | During Air TAB inspection, some of grille section on the unit was loose and cannot remain steady when the airflow CRAH blows. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628033&prj=626&rqi=l22Ya5yziQz6XoVC0lOOufje8U
GT1ELEC-122-001 | c65108da-0b83-4ec4-950d-d2ffd27fadda | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Unused hole must be close | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627971&prj=626&rqi=JfqFzufSsfNhK4NEankOpTjYdS
YT1ELEC-170-002 | e15fe668-1fec-4cfa-9f61-c40a17e5bb15 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628177&prj=626&rqi=t2IMMJucG9Y3T9zVJsvUGC92aM
GT1MECH-60-003 | 669973e7-1278-47c8-be8d-a4d43f1d756c | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | DimasKurniawan@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Graphics Issue | DCOS |  | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | Discrepancy between SICD and actual measurement (SICD = airflow , actual = waterflow) Orise needs to change the parameter and approval. This for all CRAH units | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627984&prj=626&rqi=SwEvSlgTfEvl9UKBSvtCLRTark
YT1ELEC-171-002 | ee39e6f1-89e5-4b29-8255-5411d1b8dd5c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628178&prj=626&rqi=NImhmqP9ZHsAdfMkmsoopDrSlz
RT1ELEC-128-013 | e7651fea-fe96-4f0a-aebc-eadcb50a0879 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | The uploaded drawing of panel is an old version. Please replace it with the latest updated drawing, old version must be unlink/removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627966&prj=626&rqi=S2eRKCisLdR4YdJOfpoDJcAkgV
YT1ELEC-164-006 | 0de9c71b-86be-422d-8ed1-605c84880867 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | White Glove Issue: Please close all White Glove issues listed in this form and attach after-rectification photos as evidence for each item. Please refer to the attached document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628172&prj=626&rqi=itl5UUVsR4C3wRjbL9Tbpgw3Xz
GT1ELEC-10-002 | 324f5c85-8d7c-4b4f-a340-00f730ea1972 | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Based on the MSB Point-to-Graphic (P2G) test results, several DCOS points for breakers QE, QN, Q1-1, Q1-3, Q1-4, Q1-5, and Q1-6 are not available. This issue is applicable to all MSB units. Please refer to the attached picture for details. The unavailable points are as follows: 1. Current N 2. Voltage AN 3. Voltage BN 4. Voltage CN | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627856&prj=626&rqi=8c8lWCxdgucqKcqC2vrGjhTNeX
YT1ELEC-125-005 | b0eca649-9d30-408a-b0a6-d651ac1567b1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Issue White Glove Inspection, please close all issues on WGI form and provide photo evidence for all issues already closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627968&prj=626&rqi=nzYWChVIIg9VpLMztuEaO2Junm
GT1MECH-25-001 | ed6c5cc0-2507-49af-bf12-1c55191cd1c2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | The DS sticker has not been installed. JCI must implement a DS-approved sticker on the chiller's DB panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627850&prj=626&rqi=ypB1ZOt8OvOuBCjOAGF4M9Omo1
GT1MECH-24-002 | a2ba19c0-170b-4a93-8ab6-d7942b2d47ed | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Lesson learned from phase 1) The evaporator leaving temperature setpoint can only be adjusted when the HOA is in Hand Mode. JCI shall implement the software update in Phase 2 to enable remote setpoint control in Auto Mode, then notify CTA for verification onsite. Implement for all chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627853&prj=626&rqi=K11F0dWZsrk8rqruNKVEI7OfO4
GT1MECH-26-001 | 64d379db-52e9-4435-80ca-cf7e823c3793 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | The DS sticker has not been installed. JCI must implement a DS-approved sticker on the chiller's DB panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627851&prj=626&rqi=rP9y9uXJiyP9i6mL2Xz4qE1HBA
GT1MECH-27-001 | 96332586-548b-46bb-9e99-e037395620f0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | The DS sticker has not been installed. JCI must implement a DS-approved sticker on the chiller's DB panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627852&prj=626&rqi=hIYsJH0OoiBEl3YbT4pf3O7CN8
GT1ELEC-11-002 | 18dc6e12-7ec0-4301-8fcf-002bec0ea0b9 | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Based on the MSB Point-to-Graphic (P2G) test results, several DCOS points for breakers QE, QN, Q1-1, Q1-3, Q1-4, Q1-5, and Q1-6 are not available. Please refer to the attached picture for details. The unavailable points are as follows: 1. Current N 2. Voltage AN 3. Voltage BN 4. Voltage CN | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627869&prj=626&rqi=gp0CgpLpB93b6VzddIO3T6YwJP
GT1MECH-24-001 | f963853b-444a-48da-a1eb-be43aea6f9c6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-07-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | The DS sticker has not been installed. JCI must implement a DS-approved sticker on the chiller's DB panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627849&prj=626&rqi=5YZueGOtCVTkJGO5UQPCx4CWFc
RT1ELEC-15-028 | 115c7513-545b-4243-aabc-d7ae2339f052 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Factory Test Data including Calibration certificates not uploaded to FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628021&prj=626&rqi=U7Oy6ejvVJjxsvpTHNW8jh05lo
YT1ELEC-16-009 | c9585653-5494-4fd8-886e-449b5ea483d4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Issue White Glove Inspection, please check the attached images. Make sure issue already closed and please provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627814&prj=626&rqi=CNE8tTxX74NyUCfJ87vACrnI0m
YT1MECH-27-003 | ad02743c-01db-4f22-8171-42d136330c58 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | Cable communication not connected yet to existing unit (VRFOD G_61) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627774&prj=626&rqi=mnXlMduwu3mEPATMhUeMe9wPYc
GT1ELEC-1-005 | cae0276b-2820-4548-ad1d-d21bcfc51520 | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | dickyhermawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS General Issue | DCOS |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Re-assigned to Orise) Need to update latest SICD approved. Based on the RMU Point-to-Graphic (P2G) results, several mandatory DCOS points from the Outgoing RMU MVBCM are not available: See attached picture 1. IED Test Mode 2. Voltage AB 3. Voltage BC 4. Voltage CA 5. Power Factor 6. MW 7. MVA 8. MVAR 9. Frequency | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627772&prj=626&rqi=3SrLqtPcNvSiQvOKO0tFbBwDfl
RT1ELEC-12-011 | 29bb2722-6c53-4a07-9cb4-9bff3c38ba83 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | Factory Test Data including Calibration certificates not yet uploaded to FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628017&prj=626&rqi=LEjXvcYRjyFfOWpHWr7DhOCG38
GT1MECH-16-001 | 1a3cc1a4-eae0-4b5c-900f-7f014a4c953e | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_B_22 | DXID - FCU/DX Indoor Unit |  |  | issue from CxL2B. cable communication not yet connected to existing unit (VRFOD A_21) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627773&prj=626&rqi=eWHhmleZgkE5DVxTRyHApQio9S
YT1MECH-20-001 | 143651ee-bf55-470f-8098-ee9e19a88454 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_B_22 | DXID - FCU/DX Indoor Unit |  |  | Cable communication not yet connected to existing unit (VRFOD A_21) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627771&prj=626&rqi=qCafiOoRmR3EdVE0AvKHITsRO7
YT1ELEC-15-003 | 44bef71d-b5ec-42ad-a14c-8b16671b61eb | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Issue White Glove Inspection, please check the attached images. Make sure issue already closed and please provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627813&prj=626&rqi=xAaeBKNXsBH0beYI1vRp3Yz5C5
YT1ELEC-21-004 | d996998f-66d9-4e0a-824f-a09b029a12ef | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Issue White Gloves Inspection, please check the attached images. Make sure all issues already closed and please submit photo evidence after closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627760&prj=626&rqi=ZTtjUWAFM2UWsGxW4RnUukDjmw
YT1ELEC-27-004 | c4f3fa4f-ab8d-4147-ad11-d53997747557 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | Issue White Glove Inspection, please check the attached images. Make sure issue already closed and please provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627811&prj=626&rqi=thsYPaqoS4ZHNGM8XYtKpWfi01
YT1MECH-26-003 | 3f8c920a-6c13-4c3e-bcbe-bd886da7064a | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | Cable communication not connected yet to existing unit (VRFOD A_21) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627776&prj=626&rqi=JYvFxS7ZgU6hQSYZENEJEVRPyD
GT1MECH-22-001 | 86bf58db-53ef-4e8c-995f-476b10997537 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | issue from CxL2B. Cable communication not connected yet to existing unit (VRFOD A_21) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627778&prj=626&rqi=JAMZzWEk0KzI9b2cn4iJVWc0Nf
YT1ELEC-119-004 | 021635d9-5210-44ee-a176-5f4ad03557a5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Issue White Gloves Inspection, please check the attached images. Make sure all issues already closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627763&prj=626&rqi=mooWbC1ySuCnIVHYI2GQSlfTT4
YT1ELEC-28-001 | c6dfa29f-1850-4b6a-9bd7-a9da83f59fe4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_D_2 | LIBATT - UPS Battery |  |  | Issue White Glove Inspection, please check the attached images. Make sure issue already closed and please provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627812&prj=626&rqi=P0E69GlOR5V61SCQEw5axsWDiU
YT1ELEC-22-004 | 9a030fc6-8b50-4c84-b124-9ec77ea34738 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Issue White Gloves Inspection, please check the attached images. Make sure all issues already closed and please submit photo evidence after closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627770&prj=626&rqi=aLu6SGd7ntkfNPW5kCU78aPedS
RT1ELEC-14-028 | 1d1b014f-f29c-47e1-8741-92b77af26afd | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Factory Test Data including Calibration certificates not uploaded to FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628020&prj=626&rqi=gjBM6V9kTCxCEXE4FABGdL0DXN
RT1ELEC-13-028 | 613372ed-79ac-4798-8745-cf9b6e4e53d8 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Factory Test Data including Calibration certificates not uploaded to FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628018&prj=626&rqi=BSZhwrcIrJ2c8GVaAxU2OTRwVY
YT1ELEC-29-010 | 02b63987-f237-4954-b6dd-3c472953a682 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Issue White Glove Inspection: Please refer to attached image and provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627809&prj=626&rqi=4sb6oHOqLkzcOItm2NQHasyR27
YT1ELEC-30-006 | 45643689-ef4d-4881-88bc-dac1b0e27cb2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Issue White Glove Inspection, please check the attached images. Make sure issue already closed and please provide photo evidence for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627810&prj=626&rqi=OurBRKCc91I6cIjFlWtRW5TVxn
GT1MECH-23-001 | 94749869-142e-4122-abc1-aaff54f92c2f | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | issue from CxL2B. Cable communication not connected yet to existing unit (VRFOD G_61) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627775&prj=626&rqi=y5meJrewhlqlFTKhBLlWiTW7SH
YT1ELEC-122-002 | 6cc38004-9c46-4510-9617-aff4dd07ecb7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-03 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Issue White Gloves Inspection, please check the attached images. Make sure all issues already closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627761&prj=626&rqi=uUaaiUeSXZ773hwrHfNEsLekEy
YT1MECH-25-002 | dbf33136-6a4b-4843-a1a0-19370f19f282 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627505&prj=626&rqi=mLGj9if6VeVeCYucJ7uhZRrKwa
YT1ELEC-20-004 | cb227842-ff5c-4713-adb2-a15aed84559e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Please close issue White Glove Inspection (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627541&prj=626&rqi=6cgSoCnlQYzZsq3c62WccCR6qU
YT1MECH-5-001 | 925be8fc-3c0c-4a98-90ab-0c48f25cc8d8 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of Daily Tack is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627518&prj=626&rqi=apwvP5gVOvY5er7Zr0oJpW4H6w
YT1MECH-26-002 | 2267ec20-4621-407a-b0f3-6f898cf0d1da | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top all of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627508&prj=626&rqi=9rvxRyPIWXh24762H0cJ9PcXwP
GT1ELEC-10-001 | 9bd80f44-923f-4182-a24b-2283578efde9 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | JoshuaPrasatyaGani@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Incoming and outgoing single-core cables to Panels MSB_B and MDSB_B are not installed in trefoil arrangement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627551&prj=626&rqi=dFAj00M70OaBESmkXYEgXMVhoN
YT1MECH-27-002 | dbea278b-1898-4154-a8ba-24ced1c5cdc6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627496&prj=626&rqi=q09vfVZI6uYUok8bznCeae6SWX
YT1MECH-23-002 | bb57f4ba-067d-4561-8b56-ea7e63784d26 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_F_42 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top all of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627507&prj=626&rqi=CysbJnSA5VvclJjpXNUffV5FNL
YT1MECH-4-001 | c35aff9c-4ee1-4a79-b949-d6e0fbd4e038 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning |  | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of Daily Tack is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627521&prj=626&rqi=1NfpbAgpzf0IPFAOWYOwPk7Y2A
RT1ELEC-36-006 | 238aabdb-f5af-4e07-9cff-3785373ce3f3 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Temp. sensor not installed at cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627532&prj=626&rqi=BLazJmRpdH3sa2reKAFiJBW7VC
YT1ELEC-17-009 | 6a26ad6b-25cf-40ec-b50a-60efc395533f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Please close the issue white glove (refer to attached photo): 1. Busbar still dusty 2. Need re-torque & double mark to all bolts 3. Missing bolt (9 pcs) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627537&prj=626&rqi=qROe1RVMFyUeKhD2hqm1AhDL3w
YT1MECH-19-003 | 30ad7fe0-4d7c-4e02-83e8-9d6c2ade7f94 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of Out Door is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627498&prj=626&rqi=Q2lFt1QdCxv7Wt5MqlrPVJrfHi
YT1MECH-22-002 | 5dc36c2a-fe2a-4f38-8592-9d6a0abbcf43 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top all of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627553&prj=626&rqi=ddbUnvtyKZTZFg9MXxpnKPveaK
RT1ELEC-33-005 | 337d540c-c2e4-4dba-99ea-8f54379fb8e6 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | Temp. sensor not installed at cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627533&prj=626&rqi=HgA6HJnzrptybm01jCncQxGeyP
YT1ELEC-18-009 | 37302fbe-19ea-4408-8b7f-2485e5f2728f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Please close issue white glove inspection (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627540&prj=626&rqi=0TZPrS95VMz3oa2ELUogSfGIcs
YT1MECH-24-002 | f7999a09-cee7-49eb-be63-822fd46fdf3d | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_B_41 | DXID - FCU/DX Indoor Unit |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of FCU is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627506&prj=626&rqi=356eJRuqL4XwRVTQmNpxEY7URj
YT1ELEC-13-014 | 9af72608-910c-45f9-8f21-c20c6355be2f | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of all panel is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627514&prj=626&rqi=JLnjx5vlJFnnm0GiWqKJqAXXS8
YT1MECH-2-001 | 9cfcbbda-6bf5-4225-8557-6ce527599703 | JK01-2 | 626 | APAC | Closed | P3 Low CX | MulyaSitanggang@commtechasia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning |  | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | White Glove Issue: 1. Ensure all comment white glove inspection is all rectify 2. Ensure inside, outside and top of Daily Tack is clean 3. Provide evidence report white glove inspection and upload to Facility Grid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627522&prj=626&rqi=Tbmengbx0VNhBxmYPXkUL4wJUd
GT1MECH-68-001 | bb5fa9f2-b0c4-4c3a-ae58-e60bb9c2881a | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627430&prj=626&rqi=QP9StZjKRff6c8PWsy5vY9JsxX
GT1MECH-70-001 | bd65e776-a023-4288-a587-81ad63c229d3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627432&prj=626&rqi=wkxCIU376FZgOMl2mcqn1LpEIU
GT1MECH-59-001 | 9d057899-ae52-46a0-8b0c-67d6f3a99bbd | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627410&prj=626&rqi=VEadnGNFLaTagAoWm5kvmWzfkk
GT1MECH-60-001 | 5532878a-055f-4763-b05b-07bce0fa5438 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | (Issue move to CxL3) External pipe arrow/ direction not installed yet. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627273&prj=626&rqi=rn6f1wiGJh78FJtrXJr9QENL9U
GT1MECH-62-001 | e17f1b31-7791-4a99-bd79-37feed1ac7d6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627417&prj=626&rqi=dmWdP4UNIkeyPU6QIgsd63RYst
GT1MECH-60-002 | 2bab4d0a-64a6-4d71-afce-df46b022c420 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627412&prj=626&rqi=G653qjaetjaLMqGrjqxzutm0QC
GT1MECH-58-001 | feff6d9c-2da3-41dc-8e93-98e765758ca7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627406&prj=626&rqi=KIw5ZTrjTFnpeR8HmH6CazYdbL
GT1MECH-67-001 | a06bb442-dbfa-4c71-88f8-a204aeb40076 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627428&prj=626&rqi=RL6Lp9ec74hj0JWpUcWEgdljEC
GT1MECH-69-001 | 75f57ae5-e37f-4cce-8d3b-2dac8051dff2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_62 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627431&prj=626&rqi=2ITLYX6bK4wLxDvyJHlHUilci6
GT1MECH-65-001 | ead0908e-1971-4555-8190-f1f4a4edcd59 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_D_41 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627425&prj=626&rqi=NToPoEuyMDnR6C6UcQfHAomlpM
GT1MECH-63-001 | adf94cd6-3244-4964-8123-3976983c5f8c | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627418&prj=626&rqi=emyfRpE2489J8UXPNZRq3SYuLR
GT1MECH-66-001 | 35e2aa61-ef87-420d-a16b-ef0da54c87e4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627427&prj=626&rqi=XFbdLf1uxVpgs0yWhKjhGX9KWu
GT1MECH-61-001 | 78ba7809-8ea2-4459-8dc8-cc8ab01060f4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627414&prj=626&rqi=C3u3V1ApxgSb4K7YYVXkuYcQ3A
RT1ELEC-30-001 | 0090b676-05da-4630-ac76-03ad7a0d354c | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_A_2 | LIBATT - UPS Battery |  |  | Please upload following documents: 1. RFIT Report 2. Approved Layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627326&prj=626&rqi=AICHzjNNZKQdfKG7IzOHmLzCOm
GT1MECH-71-001 | de713423-a950-49ab-aee6-6d9744f4d0fc | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627434&prj=626&rqi=AmYRvH2tlLv2vGF4SwY6GU2QQ9
GT1MECH-57-002 | a9157a1b-8068-4c13-9d60-64dbc0be2473 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_21 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627274&prj=626&rqi=575oxarbwXfw98qfFCeUHCSXFU
GT1MECH-56-001 | fb75707a-c3a4-46e2-989f-8895c12326fc | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627405&prj=626&rqi=R6APtE8nX4Aio2EbcQSgWQ6tX5
GT1MECH-64-001 | 3ea45685-0ee9-4e29-a9b8-084af0e5b5d3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-30 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_41 | CRAH - Computer room air handler |  |  | CRAH units are energized using a temporary power source for the purpose of parameter setting and P2G verification. Besides that, GC proposed conducting CxL3 partial testing using a temporary power source. The scope is limited to the following test activities: 1. Alarm and indicator verification. 2. Setpoint verification. 3. Equipment start/stop verification. 4. Fan rotation verification. 5. Equipment control verification. 6. Air & Water TAB Notes: Voltage and current measurements shall be repeated after the equipment is energized with the permanent power source as a mandatory verification requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627424&prj=626&rqi=6j1BeAYInlo7M5Hg3oomkJ5DNF
YT1ELEC-119-005 | 22d94a1a-d272-4f88-90c5-0cf1cdf30596 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Please note that the CxL2B LV Cable Report for 1MDSB_D_2 to 1DB_D_CRITICAL (photo on DB panel side) is still based on a temporary cable installation. Please update the report once the permanent cable has been installed and re-upload the revised report to this checklist. Kindly remove/unlink the previous report that contains the temporary cable installation evidence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627855&prj=626&rqi=OS2fUjRZhoISi6BGQxXnwWcqwf
YT1ELEC-125-004 | eb5ac913-dee6-4da7-b019-84c865c71c7d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Please note that the CxL2B LV Cable Report for 1MDSB_F_2 to 1DB_F_CRITICAL (photo on DB panel side) is still based on a temporary cable installation. Please update the report once the permanent cable has been installed and re-upload the revised report to this checklist. Kindly remove/unlink the previous report that contains the temporary cable installation evidence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627854&prj=626&rqi=uyNmiWejt5ckq5txt6g1tCU9jL
YT1ELEC-22-001 | 837259d2-5b98-41db-92d4-b581c2ca387a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Grounding busbar is not sufficient for all grounding cable terminations. Please extend the busbar to avoid cable stacking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627331&prj=626&rqi=TSFlcrKWsTctwSFvxh9oGNKhxO
YT1ELEC-22-002 | 57b95abc-2086-401e-b268-6e5c79f0ff3f | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627332&prj=626&rqi=780aFtknYbfRoC0csJOTuLQDVg
GT1MECH-57-001 | b4ba81c3-c21b-46f2-99c7-dfa6a255f1ca | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_21 | CRAH - Computer room air handler |  |  | (Issue move to CxL3) External pipe arrow/ direction not installed yet. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627216&prj=626&rqi=eh4bD6MehtNWKkMH2ccNBkgybo
YT1ELEC-22-003 | 507426e0-0b09-4b3a-9651-cf2ab0ebad90 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-29 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627333&prj=626&rqi=U2KfQEPrcU5Yj1nCm1GAn7HEST
YT1ELEC-20-002 | d9102212-9e63-4f39-a0e6-147cdf3f9416 | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | DCOS cable has not been terminated at the UPS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627111&prj=626&rqi=L2ZFyaITyJoFyMeNMypEHWAQDL
GI-029 | 1b0a4780-c4a7-4d28-b440-bced850f1fb5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | The existing water leak cable is trapped between the Li-Batt racks. Based on site walk with Aurecon, the cable must be pulled and re-laid to cover the new Li-Batt racks | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627030&prj=626&rqi=RlzPRbEmDgrbBhSFnGYlhPbVIu
RT1ELEC-153-004 | 05c440e7-a996-4124-9869-d13e5cdefb33 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue EWALL Room D) Minimum 3 threads shall be visible beyond the nut and need to install spring washer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627141&prj=626&rqi=ka5yBOD9B7y6LEfck7LNnfjAwK
RT1ELEC-153-007 | efc9aed4-448b-4fa7-993b-a4ed51f6e3d6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue STS Room D) Need to add flat & belleville/spring washer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627146&prj=626&rqi=MlI0F1HuKTGbTFr1iZLMdynkP6
RT1ELEC-153-005 | c79f17e0-6365-44c0-9d9c-5b331d2d7bdb | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue EWALL Room D) Need to install cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627142&prj=626&rqi=j61YSJIuTS23WV04R1jEm5fK3e
YT1ELEC-16-006 | c99abf85-b352-4382-9a8c-f04adc74984c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627105&prj=626&rqi=TyBHMnEw44YinT4XCjanoSty13
RT1ELEC-152-006 | 3addc60e-e783-4817-bc82-55c664999166 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue Battery Room B) Vinyl cable loose & cable tagging not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627145&prj=626&rqi=i1t2kErkQkFu4TYXc8q0UHaobN
RT1ELEC-153-008 | 5fc3fa65-d0e6-481d-bd50-a463daccc59c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue STS Room D) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627147&prj=626&rqi=Lm9ffZtjc9Y4bgDirGBu3i43nF
GI-025 | 3f3e1fff-06a1-4e38-9990-0677e1ae35c5 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_5 | ERTH - Earthing |  |  | Lev 2. MV Riser 2. Grounding tray size does not accommodate all the grounding cables in the riser, so the cables pile up and cannot be tied up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627025&prj=626&rqi=vU91zn1dnuunub6jVzZcXQfSUF
YT1ELEC-18-006 | 0970e70a-fe66-463e-a775-2337c244da32 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Control cable needs proper dressing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627108&prj=626&rqi=fAuSIrwSmf200hS3dIl3NtA3pJ
YT1ELEC-16-008 | 892ad33a-8d78-42a4-b403-f2b39db7ee24 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Control/Auxiliary cables are not connected and need proper cable dressing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627107&prj=626&rqi=gDIN9g8iFvN4DodPYEY11bv00h
YT1ELEC-18-007 | 5bee0019-290f-44ec-84a9-5866a25081b4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Grounding busbar is not sufficient for all grounding cable terminations. Please extend the busbar to avoid cable stacking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627109&prj=626&rqi=rszmtoUppVjnLImRBFlu3UMLXY
YT1ELEC-20-001 | 2c2b027a-334e-45f8-94b5-4aa0229afc55 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Grounding busbar is not sufficient for all grounding cable terminations. Please extend the busbar to avoid cable stacking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627110&prj=626&rqi=9MFqCR4wFWBgFaptTOVfSmx2I0
RT1ELEC-152-005 | fb20bd6f-3916-4e73-bdd0-ce66f26652c1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue STS Room B) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627144&prj=626&rqi=F49yukQALYOLHuXCuqBStVmQNt
YT1ELEC-16-007 | c809559e-40cd-4300-bd1d-e5ca23b40b5c | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | DCOS cable has not been terminated at the UPS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627106&prj=626&rqi=3rvRVJcfw87JNhvivWTy12x8Kt
YT1ELEC-10-010 | f007f0c0-202c-48ca-9562-880d79d7e139 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Earthing Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627049&prj=626&rqi=loN8S9AtmPrwo3smpp600n05AY
YT1ELEC-20-003 | 67b736ea-c719-44f4-a896-ced2ce647a6f | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627112&prj=626&rqi=scyaeXbsnDCDJgR9YpA5jLBWyt
YT1ELEC-18-008 | e8ea6485-d11e-4178-a6d7-0b1165b2ad14 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627114&prj=626&rqi=BFC0G5IqM05x4IdrMMkTpCfjXr
GI-024 | 3287ec1f-7547-4168-b8e7-d88485299bc4 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | Lev 2. MV Riser 2. Grounding tray size does not accommodate all the grounding cables in the riser, so the cables pile up and cannot be tied up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627022&prj=626&rqi=Johu1CxjZIHGcXvKv6UEZh9CJH
RT1ELEC-153-006 | 84ffb5bf-423a-4645-bc4a-11d7e5e3f7df | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue Battery Room C) Minimum 3 threads shall be visible beyond the nut and need to install spring washer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627143&prj=626&rqi=mPbx9Kbuk62Vf9MwS3XEh4ZTHB
YT1ELEC-13-013 | fb2a1ac1-21a8-4281-a350-5dd79ca0c8a9 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Busduct) Busduct LBSB 3200A 1MSB_F_1 & 1UDP_F_1 clash with sprinkler pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627128&prj=626&rqi=ou0IomWwd3FJiUXyFERONfNXF0
YT1ELEC-19-006 | 955c8265-40f1-4716-b5c9-9efa42299183 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627113&prj=626&rqi=Ty5IextYvYaJPOwlsA43hsx9j8
YT1ELEC-15-001 | 3596ef3c-ed36-4720-a750-5fc26b2fde28 | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | DCOS cable has not been terminated at the UPS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627101&prj=626&rqi=PyJAqdyos1Y9is7jAstkCPLsyZ
GI-028 | 1c62e8c9-a55a-477f-b754-90ffcf4b7429 | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_A_2 | LIBATT - UPS Battery |  |  | The existing water leak cable is trapped between the Li-Batt racks. Based on site walk with Aurecon, the cable must be pulled and re-laid to cover the new Li-Batt racks | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627028&prj=626&rqi=0cY3xpsuekxRYwHWVQUlcrH3TP
YT1ELEC-15-002 | a7ac34cd-8bcc-48f5-9fc9-c22b061ed070 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Control cable between UPS and LIBATTSYS has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627102&prj=626&rqi=9kX2ike6zdxpKbqyyvH9N6TocH
YT1ELEC-47-004 | 018eed02-0297-492b-aafd-4305ef913adb | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Earthing Cable) Cable Tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627050&prj=626&rqi=vfp29xvoVpJIeyZMo4IrgNX2tS
YT1ELEC-16-004 | e23dff46-ac43-49b0-a736-c1180fda9f2b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Minimum 3 threads shall be visible beyond the nut | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627103&prj=626&rqi=hiY5pBE9ONWWTsqLatV6RntFRE
GI-026 | 3ef57bfc-8ec5-45f5-a9bc-895054540834 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | Lev 2. MV Riser 2. Grounding tray size does not accommodate all the grounding cables in the riser, so the cables pile up and cannot be tied up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627026&prj=626&rqi=SaT43Jq6sjdV9PuX2QUKOEsANi
YT1ELEC-16-005 | 425d071d-eb60-4407-bb11-d5a3f7a29ae3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Grounding busbar is not sufficient for all grounding cable terminations. Please extend the busbar to avoid cable stacking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627104&prj=626&rqi=M4GNmnuwtjrnCLCqX47Ah6dKCF
GI-027 | 47b90200-3f81-452e-95f6-e86cfc5445ec | JK01-2 | 626 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-06-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | Lev 2. MV Riser 2. Grounding tray size does not accommodate all the grounding cables in the riser, so the cables pile up and cannot be tied up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627027&prj=626&rqi=hcPuRuidK6fIQzmW2d49wcA2SS
YT1MECH-14-002 | 5cece6ad-8256-479c-98b9-7c610861404c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1EF_D_53 | EF - Exhaust Fan |  |  | (Issue CxL2A LV Cable) Cable over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626843&prj=626&rqi=USKwcnVXvXscAl5bSvSJ5m7FFF
YT1MECH-106-001 | c54d6403-d3e3-4271-9bfb-4e435fd135ca | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | Pipe not connected yet, and also for Cable not yet for Tamper Switch, Solenoid and Flow Switch. Trim set also not done yet. Attach photo once already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626879&prj=626&rqi=Pxd3NDVTOtjvUuWIZvfTXW1O0v
YT1ELEC-21-001 | 14284e6a-3b30-4c88-8443-0b210b05deef | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Please tidy up the control cable conduit installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627043&prj=626&rqi=i1IprNe88vxivebH78JNjXC1Hm
YT1ELEC-117-005 | 012d1785-494d-49a3-b095-cf964bea610b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Incorrect label outgoing (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626842&prj=626&rqi=rjPkNk6HjSAWKaqCiMtatZ6JQu
YT1ELEC-21-002 | b7b3f97d-49df-45e8-a820-8a176257f6ae | JK01-2 | 626 | APAC | Closed | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Please tidy up the DCOS cable installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627045&prj=626&rqi=mMpBm7HHPqsy2FrNk0vRiy8THV
RT1ELEC-52-004 | 66145924-de27-4d9b-b93d-c7b7cc6c7091 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | Minor dents & scratch, need to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626854&prj=626&rqi=ekvApk4xdrX8JE7O35HqqtrCwS
YT1ELEC-125-003 | 25b76de9-13c6-4c51-a263-3a41d2bf21eb | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Incorrect cable termination for grounding (refer to attach photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626881&prj=626&rqi=Cc47ihmGTMnqTHF8WXJXZ6Xw0D
RT1ELEC-52-005 | 5450393d-b012-4156-8ac3-89edbc46577c | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | Need to upload calibration certificate for torque wrench | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626858&prj=626&rqi=YKsUa979ZLhxpdAMDKzPpe8QN3
YT1ELEC-21-003 | 494d3df3-fd76-495a-887b-462378a10eee | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Control cable UPS to LIBATTSYS not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627046&prj=626&rqi=Y89nFkaf0VmcEA279V2MoDiweF
RT1ELEC-56-004 | d7a1fe6d-247f-4e4e-a49f-8f003f7ef293 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | Anchor bolt loose cannot be tightened and not properly for anchor (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626859&prj=626&rqi=hrVSZcqxnBXS5BiqD9rjuewglr
RT1ELEC-20-001 | 7adb6c5b-1d69-4ca4-8828-2c534df92d03 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_A_2 | UPS - Uninterrupted Power Supply |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626853&prj=626&rqi=6xFYzQDCmZkG8Itu2L822dnl0V
GT1ELEC-11-001 | efc2a2fc-1b02-4396-9241-39be7ccb3bd9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626688&prj=626&rqi=2VAeLw7SRwzRx4pHyaa4gOmvmO
RT1ELEC-24-003 | 87f12ebb-dd34-4215-b187-82be9a0ae3ae | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Please protect HMI display to prevent from construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626460&prj=626&rqi=29k8uO3A2fZOPF6UI6YGLGNHTl
RT1ELEC-26-011 | 6eee610b-982c-4867-90c1-b94962adc4ba | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Missing bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626466&prj=626&rqi=gXEDmEQpxHkFFQP6lERl3YeAHZ
RT1ELEC-24-004 | 7e75885d-5908-4a8c-a9ed-3393b9aca465 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Door foam damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626461&prj=626&rqi=jjODaJ4cB1gDLxIRki91vKqbdF
RT1ELEC-24-002 | 97b8d44e-3295-4c22-8506-40605798f3a2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | Minor dents, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626459&prj=626&rqi=dNSAzaOWDct7jjpGml1L0VTlj9
RT1ELEC-26-008 | 628d7d2e-e2f7-4f26-8806-be69851a3942 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Discrepancy between drawing & actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626463&prj=626&rqi=FFtw8XmNLfHYIf4jaHhtLCZjAK
RT1ELEC-21-003 | b296cc16-f0a9-46df-a1b0-ededbb57a7d9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Door foam damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626453&prj=626&rqi=aAF6RSPKlSCvjGOCuTFr475o8h
RT1ELEC-22-007 | 6cdda05f-25e1-4835-839c-10360e3c36f4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Minor scratch & dents, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626458&prj=626&rqi=tCP2bPunwNEz2rCJPRtW0Xxton
RT1ELEC-21-001 | b73c0836-6815-45e1-a8cb-7b9424dcbf56 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Minor dents, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626451&prj=626&rqi=4PuVo4kP9rxCH4njZV7YDKNvEK
RT1ELEC-22-006 | 84554171-de58-4572-bcd3-b3144505d559 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Need to torque verification & mark for rear anchor bolt | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626457&prj=626&rqi=imOnYKr3Di3vjFDtacCyDCRpqG
YT1MECH-18-004 | 17aa6c06-323d-4653-b78f-337715400bce | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | cable tagging not installed yet for cable communication for outdoor to indoor unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626462&prj=626&rqi=2C1jmzDEyWLoal9i1bQ9iY4e5e
GI-023 | af05cf0c-7678-4684-a674-b85df4a18069 | JK01-2 | 626 | APAC | Closed | P3 Low CX | ariagandanegara@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_4.01 | PAV - Pre-Action Valve |  |  | Please rectify and repaint the peeled off pipe coating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626450&prj=626&rqi=7sr0vLqUmu3C5pmcgjFz1nPHOM
RT1ELEC-21-002 | 4af8de57-df91-4249-a08d-28eafd0dfc78 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_1 | UPS - Uninterrupted Power Supply |  |  | Minimum 3 exposed threads required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626452&prj=626&rqi=RcyzNVXgS89ciJIq9LCOwGfFnV
RT1ELEC-26-010 | 16ba8305-9b1d-431c-a834-a6fdeee139be | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Door foam damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626465&prj=626&rqi=jDW68R2gehJ8jJMBV4nI0qw9V1
RT1ELEC-26-009 | 4c015527-98b7-4d89-bf76-87e7d61c9096 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Need torque verification & mark for rear anchor bolt | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626464&prj=626&rqi=WSjeYKFbySMzZNhOi2hmOhw1VI
RT1ELEC-26-012 | bd39f9e8-c2b4-45ad-b90a-60a53846c6c2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | Please protect HMI display to prevent from construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626467&prj=626&rqi=OGBuTF7fEKE74BMNkqb7eQwATe
RT1ELEC-22-005 | a870186e-5366-4120-9483-87e49b64cd16 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | Discrepancy between drawing & actual position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626455&prj=626&rqi=lPsdlMhSUZrHB6TrrLVnJh7Z9u
YT1MECH-43-002 | c73c69d1-5d90-4615-a24a-70bc664f2ddb | JK01-2 | 626 | APAC | Closed | P1 High CX | DimasKurniawan@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor | L2B | Component/Equipment Failure | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | During Tie-in activity for CHW Pipe Cooling Array Level 4th floor, leak was discovered at CHWF mainline pipe. Please provide RCA for this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626357&prj=626&rqi=crjOQUgFC3gLFWFOL3vdIiBZY0
YT1ELEC-16-003 | 44c15a62-a0fa-4edc-b868-e283512e698e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable) Incorrect cable tagging, should be from 1UPS_B_2 to 1LIBATTSYS_B_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626242&prj=626&rqi=2SUV1NLZKCHRBAmniq4dladWM6
YT1DCOS-15-002 | 40e5aba1-48ab-4d63-95c3-a33576fed490 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Controls | equipment | 1DCOS_1_SCP_07 | DCOS - Control Panels |  |  | (Issue CxL2A LV Cable) Cable over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626249&prj=626&rqi=s8tSxAnHn8zZVRcFSFwz3FQaYm
YT1DCOS-12-001 | 46e8aa6a-933a-4200-9569-8e6a88bf7e49 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Controls | equipment | 1DCOS_1_SCP_02 | DCOS - Control Panels |  |  | (Issue CxL2A LV Cable) Cable over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626246&prj=626&rqi=IOoEzF3IheEKkvcadNn4AsSPRS
YT1DCOS-9-001 | be23304e-2dc9-4e7e-9ca4-f0dbbd969aea | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626241&prj=626&rqi=JulACZyNRVv49uIsTAQ6vD7uOA
YT1DCOS-14-001 | 81300962-db7e-492c-859f-d5226a3e8d24 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Controls | equipment | 1DCOS_1_SCP_04 | DCOS - Control Panels |  |  | (Issue CxL2A LV Cable) Cable over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626248&prj=626&rqi=6xHynilAQocrOFXsgYJ1IiZbyo
YT1ELEC-26-001 | 7a96434b-c738-4100-8408-0cf8387f34a5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | (Issue CxL2A LV Cable) Incorrect cable tagging, should be from 1UPS_B_2 to 1LIBATTSYS_B_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626243&prj=626&rqi=FSpmReL75BH0shAR5gcimvzjM2
YT1ELEC-19-005 | 5d4ea5ae-eb4b-4c10-9c5e-1f7acf664a1c | JK01-2 | 626 | APAC | Closed | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | DCOS cable installation is not neatly arranged. Please tidy up and secure all DCOS cabling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626245&prj=626&rqi=AcLrINyhzC38dSI3m7mYgkiEp3
YT1ELEC-116-002 | 374c5070-7d38-4596-9d0a-730e23d5e1c0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | Incorrect breaker label, please follow new breaker outgoing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626244&prj=626&rqi=QOCgeVqPX8ikMGMGM96WLeRfTI
YT1ELEC-117-004 | fcf0a041-6df6-4650-b879-8cf2ff983951 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Incorrect label outgoing breaker, should be: - Q1-3: to 1EF_B_31/32 - Q1-4: to 1EF_B_21 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625790&prj=626&rqi=fKeWFapWii42V6MOT97CaZF9GM
YT1ELEC-17-007 | abcea290-4a02-4d0d-b5d3-e67fd7ea0a3f | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | General Contractor | L2B | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Bolt torque under 3 threads under the nuts & please perform re-torque verification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625635&prj=626&rqi=wdos9F7pZJlvmpQ2IcmDQeNX8h
RT1SEC-15-001 | e3d19569-9d9e-4350-9f73-75dfc74773b8 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Security | equipment | 1CCTV_level_7_DH | CCTV - Closed Circuit Television |  |  | issue CCTV C:07-43 not installed yet because cable tray is not installed yet by GC, the CCTV shall be installed under tray | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625797&prj=626&rqi=36zDZYMWBfTC5kh5tmfINmubMU
YT1ELEC-17-006 | 82f573a7-4575-4a7f-9009-1ef8594ddb21 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Auxiliary and DCOS cables are not properly connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625634&prj=626&rqi=OSarKdzvuZsnznPa7NkUPbOxC7
GT1ELEC-2-004 | 377ea311-3961-4415-8d60-bf1de6898407 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Several point lists included in the approved Point List could not be verified in DCOS during RMU CxL3 P2G testing. LS Electric confirmation and Statement Letter are required. Potential impact to all similar RMU units. Need to update SICD approved and signed by Orise, LS, and GC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625636&prj=626&rqi=l9DDSk5A7ZQ0DntuhaxnUlzBkT
RT1FD-6-001 | 4ca75bef-4bc5-4d5c-ba5e-4a8ce28b3b8f | JK01-2 | 626 | APAC | Closed | P2 Medium CX | ariagandanegara@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Fire Detection | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | 1. Solenoid Cable is not Installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625779&prj=626&rqi=ndsQxKaHpBV40UZMDyqmuEyRaG
RT1FD-6-002 | 3ac8417d-f175-46a7-bccc-c263e33940b1 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | ariagandanegara@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Fire Detection | equipment | 1FS_PASCV_FOH_7.01 | PAV - Pre-Action Valve |  |  | The Pipe is not Installed yet. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625782&prj=626&rqi=a99xA3mDi2KgMpRKjc8TFcflmr
YT1ELEC-17-008 | a3c50110-6c21-4898-924f-3f1b9f3184c9 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Control cable UPS to LIBATTSYS not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627048&prj=626&rqi=K4Jy5asQnK4fRmmZmy4D3y3MrM
YT1MECH-35-001 | 7bdca0ef-f2f8-4780-b5b8-5cde5ae07766 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Labelling / equipment name tag not yet (Issue from L2A) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625581&prj=626&rqi=DK5VM5yGZZgH2G7sOVIzxryN7W
YT1MECH-72-001 | 49e6f0b9-043f-4701-aece-f989bb33f9f3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_D_4 | FFU - Air Scrubber |  |  | (Issue CXL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625331&prj=626&rqi=jNICZ1OUv9BZ1WdMYMTfyKH47K
YT1MECH-70-001 | 7b8247aa-326c-4784-890e-b231b4ea7ddc | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_D_2 | FFU - Air Scrubber |  |  | (Issue CXL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625329&prj=626&rqi=ocoKn8u9Q9BZzNtIZNHbn7JKU0
YT1ELEC-171-001 | e2ffe81f-4710-45df-b774-d85031568d0c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625305&prj=626&rqi=4dKAg97GYc6pA8jFTX8yDD8Gnu
YT1ELEC-52-003 | 521e60ee-717a-4709-9701-af6d56b04db9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable) Remove temporary marker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625315&prj=626&rqi=9aei87uH6goDfcP4CboaGT8CLU
YT1ELEC-52-004 | 1b5a2285-9c9b-4789-a5d2-efe25ee74dbc | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable) Ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625316&prj=626&rqi=KwIXcZEOZS6aJwwml1Bwun4E25
YT1ELEC-168-002 | ba517fdb-3288-4da1-983f-7fe90fe21266 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | (Issue CxL2A LV Cable) Ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625306&prj=626&rqi=J1h0tv0Tc2L2TgD0G52qsH5O20
YT1MECH-73-001 | 5c58f2f1-76bf-4be5-b164-40d07b8b419a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_D_5 | FFU - Air Scrubber |  |  | (Issue CXL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625332&prj=626&rqi=j4wlzrmdS4wyZaZrbS1b9XkuqF
YT1ELEC-168-001 | d3c18758-ca19-4371-90a9-7b4711b054af | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625304&prj=626&rqi=a9HuaaRR34kzqd0v3kBmhlyufA
YT1MECH-74-001 | f449d98f-9f67-4204-87e2-e0f233ed7aae | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_D_1 | FFU - Air Scrubber |  |  | (Issue CXL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625328&prj=626&rqi=cvbvghiSQbJvyNeN1Zsr5Uzcbj
YT1ELEC-53-001 | c140cd43-bf19-4bae-8150-09e49e30b91b | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Cable) Cable insulation damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625317&prj=626&rqi=1FqBBf0vsQ8Zvj5Ynvjal6K3Hg
YT1MECH-71-001 | dc606a78-faa1-4784-b4a8-b1b5be88d548 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_D_3 | FFU - Air Scrubber |  |  | (Issue CXL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625330&prj=626&rqi=DGJ5KNadURugfHsZwqXYRiPJPO
YT1MECH-98-001 | 844bc18f-f67a-479a-b378-c669937de7cf | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Bonding jumper on tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625218&prj=626&rqi=fpAP2w5BxaFYYyKNM5KASozxcE
YT1MECH-89-004 | 93bf7655-812f-4980-9546-615cc86f1a9a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625221&prj=626&rqi=o8xUKiqw7qzblQ1HzNajX2K4mm
YT1MECH-95-001 | db69f2b8-c014-424d-a30e-4d36a33e6f49 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cable tray not finished yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625211&prj=626&rqi=FYrvG2HJPTQ73dKYT5jlive2HS
YT1ELEC-119-002 | a440d5b0-4621-4ff4-bd95-6c182a82d960 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1DB_D_CRITICAL to 1CRAH_D_42) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625212&prj=626&rqi=MDMgYWRw9KN7HJK2ZdSbyzf8vp
YT1MECH-46-001 | 15caf8a9-3954-4688-ba62-3d690234ee44 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_06 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625225&prj=626&rqi=XFBYvasJBQw1DCw6t87eKSJoa1
YT1MECH-47-001 | 5febe84f-c23f-4726-beb6-dbe94d52d7f9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_07 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625226&prj=626&rqi=egmTdagUgPoPntdROnSJr66QgR
YT1MECH-44-001 | 36159f9c-f536-401e-a231-94fb9f988db4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_03 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625223&prj=626&rqi=DA6jXtXqm3ZU3fi3ar1zd7mAjI
YT1ELEC-117-003 | 6339dcd3-887c-4901-a364-f7d0af5beab6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Ensure the gland is properly covered and sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625204&prj=626&rqi=Bw1K4QwqJwo9tiDRWR8FFc7vVS
YT1ELEC-117-002 | 90c0f51e-b5a6-4425-83fb-708b51026860 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625203&prj=626&rqi=GslEfSICLUiVR1l6dHZZ9jUK3t
YT1MECH-40-001 | 3aca236c-3f37-4eac-a6b2-eacf17760240 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_06 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625234&prj=626&rqi=uip5Hih0yxfrefJwxPWuqhEewv
YT1ELEC-125-002 | ea3fa1e5-02cb-4ef3-89c9-519ce174895f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625216&prj=626&rqi=gsLQt6nm1MefkHTq6194k1R2I8
YT1ELEC-117-001 | a9a01669-6605-4ed5-b6a7-2f77369938f4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1DB_B_EWALL to LCP_EF_B_21) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625202&prj=626&rqi=A3CNfD0026HibonWS23ZIL4G9m
YT1MECH-37-001 | eb075b2b-5e80-4e19-90c1-0730181be52b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_02 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625231&prj=626&rqi=GQW9rvVe1CuLVKgUDLSq2UA3aK
YT1MECH-91-002 | 6712459e-0a16-4ff8-9dbb-ab76e29d55d4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625217&prj=626&rqi=GwzRWHfw512EyoT7enqpGQjcoN
YT1MECH-96-002 | ce1c3249-32dd-4f8f-b28a-137992f5317e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | (Issue Cxl2A LV Cable) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625210&prj=626&rqi=bftE71EAYZFsF5eGPJ3X3s8iGA
YT1MECH-45-001 | 7dd4e09d-e8c1-4096-a660-e5dd1587bd80 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_05 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625224&prj=626&rqi=wJsE3cZoEqx17HBM4QZ038dc3g
YT1MECH-96-003 | cb127541-6118-4ece-ae1b-bef7a46d75a2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cable installation is not neat and several cables are over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625220&prj=626&rqi=JyrFIcGvLZzDXURLtIaCH86ucG
YT1MECH-42-002 | 826b2217-2b15-4c1e-a5fc-8fc455253b66 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625237&prj=626&rqi=oJHLcZC9dOOa1U5KzobIACPSAI
YT1ELEC-119-003 | edef6fe9-d8ce-4913-b620-aaaba354d803 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1DB_D_CRITICAL to 1CRAH_D_42) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625213&prj=626&rqi=tGwEOKv5nzzD1mxkKNUtsM1oSh
YT1MECH-99-001 | 4702686d-9582-4d86-9c04-e07f22ad9ba7 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cable installation is not neat and several cables are over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625215&prj=626&rqi=8OPvvNOEGVGyc5BACj1lK6U3y2
YT1MECH-49-001 | dbf4e402-a5c9-4140-985a-f3b5ae013f69 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_11 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625229&prj=626&rqi=wctZuMA1Nz77peipqDgQdAoWn2
YT1MECH-43-001 | 3398a4bd-c0ce-46ca-914c-05c2c3f3cfd4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625222&prj=626&rqi=UvPuRQlrOpGHhQxRmS5LANVhmN
YT1MECH-41-002 | c3254aaf-8b95-4fb0-ad84-6e65040447ab | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625235&prj=626&rqi=gUc6N6PoMX9kG7trFmXh73ZtI4
YT1ELEC-16-002 | c542cb9f-7252-46d7-95d7-7a70826a604e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_B_1 to 1UPS_B_2) Several cable gland caps are damaged (torn) and not properly covering the gland, please ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625208&prj=626&rqi=r1Q39zMmBTo90EBBFmpSWOGgAw
YT1MECH-6-002 | cf0bcb2e-2416-4e7c-aa42-01e04dd7e3ba | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | (Issue CxL2A LV Cable 1DB_B_EWALL to LCP_EF_B_21) Cable over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625199&prj=626&rqi=WvKJmMjIsL6Gl5xuHfWbU4bXob
YT1MECH-6-003 | 58cf1105-840c-4a41-832c-c474bd343db2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | (Issue CxL2A LV Cable 1DB_B_EWALL to LCP_EF_B_21) Cable & conduit needs to install labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625200&prj=626&rqi=UGYKQUfT7PYy4Zfrr163evkzS9
YT1MECH-38-001 | 89e33cf9-30ec-4efc-9096-1f0f3fbffad1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_03 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625232&prj=626&rqi=0WhElVEJvaz4G74sRX7837iuie
YT1MECH-48-001 | 0c9d9621-5c82-4f71-93cf-af329f739ad0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_09 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625228&prj=626&rqi=uS1M1c2DEZsli4tRYHMgXgV2Aw
YT1MECH-97-001 | 6a62babc-0eef-4ebc-b810-3674f9ab0375 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_62 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable) Cable installation is not neat and several cables are over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625219&prj=626&rqi=85MoDXG8UA00YNFnARI9wGp9Sj
YT1MECH-39-001 | 7ac8dfdf-c09c-45dc-8d4e-902da3fc243b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_05 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625233&prj=626&rqi=DKUuEcVsXQMhjb2cdMjpsU7Q1Z
YT1ELEC-16-001 | 145f652e-16a0-4aef-8811-585876fe9dba | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_B_1 to 1UPS_B_2) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625207&prj=626&rqi=99AE7yPN7t1EFiooFF5qRrwvXa
YT1MECH-36-002 | b8e6d659-f0aa-4dd2-a5b1-ae45ebe4e4ef | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625230&prj=626&rqi=dhZuQIagyYrJblSdmWwS8nFCAd
YT1ELEC-126-002 | 346d7b61-2e8b-46f3-a69e-eb0e247383dc | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Discrepancy identified between the breaker protection settings applied in the panel and the latest approved Discrimination Study. Short Time Delay (STD) and Ground Fault Protection settings do not match the approved study (Refer to the attached images) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624922&prj=626&rqi=orAnTd8TQDHL96z6p1mxIOSamk
YT1ELEC-125-001 | 918d21eb-bf0a-4b95-8b0d-c9144cd1b66d | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Discrepancy identified between the breaker protection settings applied in the panel and the latest approved Discrimination Study. Short Time Delay (STD) and Ground Fault Protection settings do not match the approved study (Refer to the attached images) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624913&prj=626&rqi=4vJjhpb613Sz7GdXhvKv9Kt6Zz
GT1SEC-12-001 | 348cd529-d313-4c95-ac1b-3eb5712175b5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor | L3 | Installation not complete | Commissioning |  | Security | equipment | 1ACS_level_6 | ACU _ Access Control |  |  | Door handle not yet installed (D:06-09 E-wall room & D:06-38 Battery room) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625059&prj=626&rqi=4ZmDiTDKZE3IicjXoIY6hljKQM
RT1ELEC-155-005 | 86d23d98-9fdc-46e1-afa0-6f1da74f2bf3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | (Issue EWALL Room F) Incorrect cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624888&prj=626&rqi=kj5mVfO6KJHziumG5zTaTdevX3
YT1ELEC-7-001 | 26b2fa9f-45c2-40ec-8c4f-97762ce956d9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Incorrect vinyl cable color at Panel DB Aux. Vinyl cable color for L1=Black, L2=Brown, L3=Grey, Neutral=Blue, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624879&prj=626&rqi=u8XOBjyv3R19pIEFG2SCHZew7o
YT1ELEC-50-002 | 3e159ba0-1ba6-4626-b19b-4951f77f1dd0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Cable Aux) Cable conduit label not installed. Please provide the label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624862&prj=626&rqi=HswvtTj9fvKp6DyVGY5PU66kwE
RT1ELEC-155-004 | d2b6b082-1d16-45b2-b802-2834182be41a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | (Issue EWALL Room F) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624887&prj=626&rqi=DoGWgeb0XkEHbJSWyTHGcplClO
RT1ELEC-153-002 | 6304e9ca-9568-47ba-9f9d-60d06bff96f5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue EWALL Room C) Cable tag naming does not comply with the project standard. Please correct accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624884&prj=626&rqi=PAVviNkaAafwKJWy3U4lJmg7Vs
YT1ELEC-6-001 | 40af5156-ada7-41ba-b76f-b1ef15a6d1b0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | Incorrect vinyl cable color at Panel DB Aux. Vinyl cable color for L1=Black, L2=Brown, L3=Grey, Neutral=Blue, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624878&prj=626&rqi=S8Bw1wBJHS5oW6NZDO4c2pjyQ0
YT1MECH-18-003 | 422eba04-ab59-4b27-8290-54af586c7b0f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | (Issue CxL2A LV Cable) Missing bonding jumper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624866&prj=626&rqi=NtOnlEnplW445EbiEwykt9M2Rz
RT1ELEC-153-001 | 3a7d695f-2294-46d8-a6fb-fa38bcdf34eb | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue EWALL Room C) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624883&prj=626&rqi=Fz5NKYoagz0Dfjc1F9nG57ZxEr
YT1ELEC-9-002 | a0894989-9017-43cb-b9d8-b63e992db205 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Incorrect vinyl cable color at Panel DB Aux. Vinyl cable color for L1=Black, L2=Brown, L3=Grey, Neutral=Blue, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624876&prj=626&rqi=32bVgyLINBjXrzpFLoSQGplSCy
YT1ELEC-52-001 | 81473c8d-ac2d-4171-9966-c72a2d728cd8 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Cable Aux) Cables are not neatly arranged. Please tidy up and secure all cables properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624859&prj=626&rqi=wIQEv4zRQ4EXRhTjOKIrs39MfW
GT1MECH-80-001 | 1fa37d98-7b6d-4d4e-8ec9-30a94ffbe8cb | JK01-2 | 626 | APAC | Open | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_3.01 (Existing) | PAV - Pre-Action Valve |  |  | Seismic Bracing not yet installed and will be planned to install asap by GC. (This issue for all floor) Ensure that when installing those, there will be not affect piping and support pipe. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624812&prj=626&rqi=ls4E8X3Fjv9oB49UqYio9seuxa
YT1ELEC-9-001 | bf438190-48df-443c-9054-aab1de5adca2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MDSB_D_1 to Panel DB Aux) Incorrect vinyl cable color. Vinyl cable color for L1=Black, L2=Brown, L3=Grey, Neutral=Blue, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624875&prj=626&rqi=wIUWMvxu3GMn7i4RAYn7n4Bd5G
YT1ELEC-52-002 | c4e81cbd-4e04-43ba-8fd4-8baeded220b1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Cable Aux) Need to install label at conduit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624860&prj=626&rqi=fs50LoIkrSItPM7eTJW66vPtCn
YT1ELEC-170-001 | 24c68be6-600d-48b9-837a-fc6826b604db | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | (Issue CxL2A LV Cable 1MDSB_D_2 to 1TOU_D_1) Missing bonding jumper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624873&prj=626&rqi=mf8AXSr9VAXfL0ZXcapuvfgbJ6
RT1ELEC-153-003 | 9074ada2-ca18-4cff-b837-72e8691869ef | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_4 | ERTH - Earthing |  |  | (Issue EWALL Room C) Cable Tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624886&prj=626&rqi=3s1CizrPPJsitqU4ld97GoPpuU
YT1ELEC-8-001 | 72c2cba8-cd88-417c-a9ee-79e71ef3a732 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Incorrect vinyl cable color at Panel DB Aux. Vinyl cable color for L1=Black, L2=Brown, L3=Grey, Neutral=Blue, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624881&prj=626&rqi=7oLAZanpK57nqDwcM00ENpVXZX
YT1ELEC-50-001 | d8f29211-5eee-46e7-9a88-ca028bc914a4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A Cable Aux) Cables are not neatly arranged. Please tidy up and secure all cables properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624861&prj=626&rqi=0auP00WbY4I6mj41Qrxn4luY7p
YT1MECH-31-005 | b90a28c4-9f94-4766-8ffd-60335e1b9f6b | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A Laying cable 1DB_CHWSTR_B_07_CH1 to 1CHWSTR_B_07_CH1) Vinyl need tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624556&prj=626&rqi=CnWtebluGMiK5BE934juEQS2gp
YT1ELEC-166-004 | 391814ce-8944-46e0-9722-ebe4c15b8720 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | [Issue CxL2A 1TOU_B1] Protection neutral not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624500&prj=626&rqi=2qEJkmSc2Ykp48o7CH6bXTflg8
YT1MECH-68-001 | 9e95aaea-22af-4dce-b032-4bdb52f54e42 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_B_5 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_5] Cable over bending, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624512&prj=626&rqi=Jm43tT61tZsVkBwaqbZ15uzYbt
YT1MECH-110-004 | 71a66ae2-8ba9-4a49-8d5e-a0d5a6a322ce | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV CABLE ISOLATOR_1CHWSTR_B_07_CHWP_1 to AHF 1CHWSTR_B_07_CHWP_1) Grounding Cable Scratch until copper wire is visible | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624559&prj=626&rqi=Lkf1WimQUQSjPU3K3E3ROWeFHj
YT1ELEC-166-005 | 185ecae0-28cc-4fe4-aa9f-9b4aaaca64d4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | [Issue CxL2A 1TOU_B1] Vinyl grounding not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624501&prj=626&rqi=sC055CUBxUgKgL7jolysQbbtkj
YT1MECH-87-001 | 1ba347f3-5114-410b-b881-4e33f7e175e6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable ISO 1CRAH_C_22 to 1CRAH_C_22) Vinyl Cable was installed in reversed, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624494&prj=626&rqi=yJpzgsKQNfW108GB1NRJGVmcq3
YT1MECH-19-002 | 1b0e1326-5fe5-42b7-89a8-9a909b215507 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | (Issue CxL2A LV Cable 1MDSB_F_1 to DB 1VRFOD_F_61) Bonding jumper not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624708&prj=626&rqi=3VlQxJm5cWwnfmy9tmFuu8zf5r
YT1MECH-87-002 | e9627e80-abc1-45da-a47c-3a1f7386ce48 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable ISO 1CRAH_C_22 to 1CRAH_C_22 ) tagging cable phase R not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624495&prj=626&rqi=gjDtKK11lwak0pmQp3yvv5Xrl4
YT1MECH-31-004 | 0f909f44-a747-4391-b894-5f7746080b3d | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A Laying cable 1DB_CHWSTR_B_07_CH1 to 1CHWSTR_B_07_CH1) Belleville washer size is larger than the cable lug size. Please replace it with the correct size. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624519&prj=626&rqi=iGlaXb0feZa14ovK1z1fCLZLNK
YT1MECH-64-002 | 9b44a6d3-932a-40d9-b8e0-62775cba2c65 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_B_1 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_1] tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624503&prj=626&rqi=khn7NQhhWtEnWzMbZAJyZtWERH
YT1MECH-30-005 | ab7c2267-16ef-4ff0-900f-66373b99526b | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A Laying cable 1DB_CHWSTR_B_07_CH1 to 1CHWSTR_B_07_CH1) Vinyl cable identification for Phase R and Phase T has been installed incorrectly. Please revise according to the cable tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624558&prj=626&rqi=tYemZb0F843FE90AcIgyXibmv8
YT1MECH-67-001 | 92c1f821-64f5-4626-83b2-688e00dd7632 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_B_4 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_4] Cable over bending, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624510&prj=626&rqi=aiwN20w3R7wADgFMAjQXlEDJUi
YT1ELEC-166-003 | 42673846-a427-4f66-86d7-c5a0aa44816c | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | [Issue CxL2A 1TOU_B1] Cable tagging blurry need rectify (phase N) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624499&prj=626&rqi=jAgBObVwRje8EmyAgbtWYXwQe2
YT1MECH-30-004 | ce8e996a-db52-4f1f-ba7c-da0376e7b036 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A Laying cable 1DB_CHWSTR_D_04_CH1 to 1CHWSTR_D_04_CH1) Vinyl cable need tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624557&prj=626&rqi=idhYUux3rYvLjRnGWpNBcF6wo9
YT1MECH-65-001 | dd36e1a1-83cf-4bba-a46f-eafa00cb9942 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_B_2 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_2] Cable over bending, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624505&prj=626&rqi=uTQhfk5BvLkzt2MJ8hp2pzCMzT
YT1MECH-84-001 | 49525db3-7ebc-462c-865c-5b1fb20eefb5 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable DB_B_Critical to ISO 1CRAH_B_21) Cable scratch until insulation is visible all phase (R,S,T,N,G) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624485&prj=626&rqi=NCTAJOexYDkzQwmCuxDBYQ7J7o
YT1MECH-110-005 | 4b3eb3f0-d38e-4b93-acc5-1f7571b7de3c | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV CABLE ISOLATOR_1CHWSTR_B_07_CHWP_1 to AHF 1CHWSTR_B_07_CHWP_1) Cable end caps rubber need to be properly installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624560&prj=626&rqi=QAcjWNNbzzL8OZugpnIDWrIxvE
YT1ELEC-126-001 | a78caeaa-aeb9-438a-b84d-727acbfef9c0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1MDSB_F_1 to 1DB_F_EWALL) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624703&prj=626&rqi=uhM5Iud4UhpsXWJqCLrnAxzPGO
YT1MECH-68-002 | 7a5ee593-037c-41cf-aa07-02b0c72b4c58 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_B_5 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_5] Tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624513&prj=626&rqi=DGApcncPqUP1j03Gs9aijZ4BwN
YT1MECH-64-001 | 04b2c3db-d7d8-4997-986c-a2642ea49e98 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_B_1 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_1] Cable over bending, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624502&prj=626&rqi=QZLqpHGDHqQ324c5AkyyCsxyGp
YT1MECH-67-002 | cd8bcf21-9ad7-49ca-acef-51574c16e005 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_B_4 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_4] Tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624511&prj=626&rqi=kEs5hGd9M5dVtxw32Gku54lwFl
YT1ELEC-122-001 | 6f3b1a57-24bf-42f3-81cc-bf7270fd9954 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable DB_C_Critical to ISO 1CRAH_C_22) Protection Neutral not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624487&prj=626&rqi=qpUm7zKPAOp9RaqOJBXSUa8bkz
YT1MECH-66-001 | 9f957be7-6080-4512-bc82-0d3c60f90817 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_B_3 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_3] Cable over bending, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624508&prj=626&rqi=ZTya8sI3nJ0WEKtJLzmCIjUc1i
YT1MECH-84-002 | 822d4ee8-d2bf-41f8-8a60-facf99f4a7e0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_21 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable DB_B_Critical to ISO 1CRAH_B_21) Need install cover tray and tagging cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624486&prj=626&rqi=TN9IRWBicNvBGkkBHzNDqKrdOb
YT1MECH-19-001 | 34f4ab85-6d79-46a2-88e4-37d6e00b8c53 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | (Issue CxL2A LV Cable 1MDSB_F_1 to DB 1VRFOD_F_61) 1. Cable lug not yet installed 2. Cable gland not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624705&prj=626&rqi=rBjuJr3ZYxTUA6jvUcCHMg4O2f
YT1MECH-88-002 | 5376f822-5625-4628-83bc-846b6fe7f149 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable DB_C_Critical to ISO 1CRAH_C_41) Cable tagging and cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624488&prj=626&rqi=HNI9vDeAHuXLM14c8kbO2dXbpj
YT1MECH-41-001 | a866b808-307d-4c68-8a55-eeb1dff74bb1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_07 | CA - Cool Array |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1CA_B_7] Grounding cable was incorrectly terminated on the panel body, need rectify it according to the attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624514&prj=626&rqi=QFN7hdhjbP13Uh2aJfB2k0ZsE7
YT1MECH-91-001 | 98100285-2045-471d-82d0-1a66d2be7168 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable ISO to 1CRAH_F_42) Bonding jumper not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624717&prj=626&rqi=YTch4AGPqj7YcAViuwFkd2GosB
YT1MECH-86-001 | 9a2fcae5-709b-41c6-87ba-2273a2bab053 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable ISO 1CRAH_B_22 to 1CRAH_B-22) Cable over bending at phase T, need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624489&prj=626&rqi=ldPSrnES4x1AHZe8M5FYnuOW4X
YT1MECH-65-002 | f96a8f09-c6d6-466d-85f1-8c23173eb680 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_B_2 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_2] Cable lug phase R is broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624506&prj=626&rqi=8evLjQ9t1uJvSz8R3Uik4jUnj7
YT1MECH-93-001 | 4a7ac7b2-d207-41c6-a978-d64fcac184b9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_D_41 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable ISO to 1CRAH_D_41) Label isolator not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624716&prj=626&rqi=cdJ8By958tMX7jNUGcqsoz6rCi
YT1MECH-92-001 | 7de6aa20-8eb1-4288-9575-6b16f3bb9879 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_41 | CRAH - Computer room air handler |  |  | (Issue CxL2A LV Cable DB_B_Critical to ISO 1CRAH_B_41) Labelling panel not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624492&prj=626&rqi=1mMB78P89tTir2DrpFTB3IizWT
YT1MECH-65-003 | 3db3490e-8847-42ce-9120-4dc2fef8744c | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_B_2 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_2] tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624507&prj=626&rqi=hEtSpxoOcEzAHNCdMQ15aA2KUP
YT1MECH-66-002 | b507a7c5-d690-44ab-b570-2d489f00588f | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_B_3 | FFU - Air Scrubber |  |  | [Issue CxL2A Cooling Array Fan 1TOU_B1 to 1FFU_B_3] tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624509&prj=626&rqi=cmlJIJOwTlpB3taDGmbUBIySX9
YT1ELEC-116-001 | 78847511-9846-4673-a04a-0088350c5d3b | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable DB_B_Critical to ISO 1CRAH_B_21) tagging cable not yet installed for Q-2, Q-3, Q-4, Q-5 DB side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624444&prj=626&rqi=C96JErOKG3NoUqUxlL7v1fkWiz
GT1ELEC-2-003 | c463b839-4dad-444b-8647-c9e94b0022c1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Arc flash label on the RMU is still temporary. Please replace it with the permanent label as per the approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624419&prj=626&rqi=oz0IseoayqurvdaqdIotPFfNT3
YT1ELEC-13-011 | 3dd2482c-e8b9-45d9-a9df-f45d64016bf4 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Please re-check the contact resistance test results for ACB Q1. Based on the acceptance criteria (deviation shall not exceed 50% of the lowest measured value), the recorded values exceed the allowable deviation limit. Kindly perform retesting if necessary | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624393&prj=626&rqi=2bavG1OXtUW7yRlZqjijaOZ4El
YT1ELEC-12-015 | 27151a41-61a8-4923-bbce-1d6b3b6e04c4 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Breaker settings in 1MSB_D_1 do not match the latest approved Discrimination Study. Please update the settings accordingly and perform retesting if required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624411&prj=626&rqi=NH6YmvyuQUsSnyu28HWiwM9M4J
YT1ELEC-10-009 | d38810a1-b20a-4495-b979-8208afe27c46 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Breaker Q1-3 protection settings are not in accordance with the latest approved Discrimination Study. Please update all breaker setting values and re-testing to match the approved protection coordination study and resubmit the report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624388&prj=626&rqi=QPd4MGCI9Pv80PSSY2BgUSypv4
GI-020 | 57b0f0e1-eda4-4d5d-be4e-ed5a6f6dcc61 | JK01-2 | 626 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-06-08 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | pressure gauge does not match the unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624424&prj=626&rqi=7GgHCJpy6PcC3GYMBDo9kKA0GT
YT1ELEC-13-012 | 6c057a94-42d3-4d08-a8c8-51e261820cca | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Breaker settings in 1MSB_F_1 do not match the latest approved Discrimination Study. Please update the settings accordingly and perform retesting if required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624395&prj=626&rqi=yBlYLCFnrvFI5QNd26ZfompDB6
GT1ELEC-3-003 | 7ae8cca9-5ff6-4548-94a2-1aa2363f9909 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Arc flash label on the RMU is still temporary. Please replace it with the permanent label as per the approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624420&prj=626&rqi=I7J5XFLS3T5Ay9k4DLQLLhZdjg
GI-021 | b6f39583-25b7-441a-b2a5-7d0abcf1aef9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-06-08 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | pressure gauge does not match the unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624426&prj=626&rqi=k2Z3gs1qX6H0GxUaap7D22VpY8
GI-022 | c870bf9e-ae53-4769-b997-0e02717bc47b | JK01-2 | 626 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-06-08 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | pressure gauge does not match the unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624427&prj=626&rqi=xgSNonfpa3SQAfq39bVzulkFxu
GT1ELEC-1-004 | 75e30b9b-77ae-42e7-acbb-7fe4112f598d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Arc flash label on the RMU is still temporary. Please replace it with the permanent label as per the approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624417&prj=626&rqi=IoYUafkwrMFUV0gDNMnSXOnCec
GT1ELEC-4-003 | ada75057-6de1-40f7-975f-c24076d53388 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L3 | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Arc flash label on the RMU is still temporary. Please replace it with the permanent label as per the approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624421&prj=626&rqi=ygFiK8aI3oVzXT9N1MmXdbEiDu
GI-019 | 254b6ae5-fa65-49c9-a619-e48ece79570a | JK01-2 | 626 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-06-08 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | pressure gauge does not match the unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624422&prj=626&rqi=24uWlGrZnRP8hJN9VXEUJuADs3
YT1ELEC-11-011 | d5e36c81-da05-48a3-a11a-be15ae92c45f | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Breaker settings in 1MSB_C_1 do not match the latest approved Discrimination Study. Please update the settings accordingly and perform retesting if required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624409&prj=626&rqi=L1nWckGGdFVlcdJwGxYAwqmgDA
RT1MECH-34-002 | f0176919-5f9e-44e7-b294-af3449007dab | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-06-06 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | During the Chiller 4 tie-in activity, water leakage was observed from the Buffer Tank. Later found out that the source of the leakage as a torn flange gasket at the venting connection. The issue was promptly rectified by replacing the damaged gasket. Following the rectification, the tie-in activity resumed and was successfully completed in a safe and controlled manner. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624247&prj=626&rqi=Xld4yAklUFMzFclPe1mfYwWIBV
YT1ELEC-17-001 | 1277bea4-12f1-4b88-9fd4-3421362391a7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) This is a DC cable. Cable tagging is incorrect; please replace all "L" and "N" identification with "+" and "-" accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624082&prj=626&rqi=1cDqKAW6sUBKWYdK8mMH6vNbWd
YT1ELEC-27-001 | eaefe634-bee9-4f15-8c5a-f91451a50bd6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) This is a DC cable. Cable tagging is incorrect; please replace all "L" and "N" identification with "+" and "-" accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624100&prj=626&rqi=WBG1kHquYkEcLLgMpRjcQ05StT
YT1ELEC-27-003 | aef3591b-4f48-458c-891c-71541b831089 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) Remove all temporary markings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624119&prj=626&rqi=GI1Y2gajQtnJDNgKy1pTwXppfR
YT1ELEC-17-005 | c382583b-1879-40e6-9924-95189861dd3f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Glanding is not fully covering the cable entry. Ensure proper sealing and full coverage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624087&prj=626&rqi=AdKulYBhNtXMGSAyIuoaipdo8A
YT1ELEC-29-009 | 6fd6a310-4558-432c-bd80-f149f06f723a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Apply correct DC cable identification: Red vinyl for DC+ and Black vinyl for DC- | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624095&prj=626&rqi=VwAXcTwinogQlXMhvPn7EnRBJu
YT1ELEC-29-007 | 0f0f8bcb-66d4-49db-bfe1-e43ab2680761 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) This is a DC cable. Cable tagging is incorrect; please replace all "L" and "N" identification with "+" and "-" accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624091&prj=626&rqi=ltXgIKtUHEVkdbz9n7RcH4k93x
YT1ELEC-29-008 | 20feedaa-b19c-4a44-92d0-1f7ad4f0f582 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624094&prj=626&rqi=h5yF12CLGAUVLmxwQkQ1Ov9zKa
YT1ELEC-27-002 | 55ac70be-768d-46f8-afa0-cab33045279a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) Apply correct DC cable identification: Red vinyl for DC+ and Black vinyl for DC- | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624102&prj=626&rqi=P3kkkyj55sk9rguYgQSEX7TJW5
YT1ELEC-17-002 | 7e09f871-650b-4859-9fbb-1a5d3acac699 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624084&prj=626&rqi=ItzML1qtu2xYxWh3iO5f6EH19l
YT1ELEC-19-002 | cf4130a2-466f-43c6-9d77-493f038a021b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) Flat washer and Belleville washer are missing at cable terminations. Please install as required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624106&prj=626&rqi=H0LLpIciykWP7PQAI7CPZ7YeIZ
YT1ELEC-17-004 | 64255cda-0b0b-4915-88e8-27e674c4087b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Cable tray cover is not installed. Please complete the installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624086&prj=626&rqi=dAK6hWbKaWPPzW97TZMaqrrKE0
YT1ELEC-17-003 | 03308f14-ea18-4c9d-8e75-c8c199dab07d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_C_1 to 1LIBATTSYS_C_1) Apply correct DC cable identification: Red vinyl for DC+ and Black vinyl for DC- | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624085&prj=626&rqi=KyyL9XyAUzi7Xh8Rz2KEuKhXZj
YT1ELEC-19-003 | 612b785f-e624-416a-8068-0c724e23d012 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) Apply correct DC cable identification: Red vinyl for DC+ and Black vinyl for DC- | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624118&prj=626&rqi=c7CQzIGkteQnAxesDIciNjsHou
YT1ELEC-19-001 | 4cd8e71e-46c0-4051-b007-465c989ac400 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) This is a DC cable. Cable tagging is incorrect; please replace all "L" and "N" identification with "+" and "-" accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624105&prj=626&rqi=YncQfTR6wiN7ggI5dr0CDy5MqJ
YT1ELEC-19-004 | 10cc7c9a-7ebe-470a-8762-d60433e2f68d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A Cable 1UPS_D_1 to 1LIBATTSYS_D_1) Washer size is larger than the cable lug. Please replace with the correct washer size | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624120&prj=626&rqi=cTwYlN47wXvlXdViz2EhSW4MBi
YT1MECH-28-006 | 45e73848-f94c-483f-a75e-32f1332c62ff | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Discrepancy noted between the approved MAR and the installed Pressure Gauge (PG). The approved pressure range is specified in kgf/mÂ², while the installed gauge scale is in kPa. Please provide clarification and justification for acceptance. Note: for all Chiller. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623913&prj=626&rqi=18beErjGSJ7QQfSoYsVf3XcgF3
RT1ELEC-160-001 | 3cc92ebc-934e-4dee-b3ba-9757e9828abf | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L6 | DB - Distribution Boards |  |  | Need provide labelling inside panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623918&prj=626&rqi=N6kplq7Ze2qGRcPHfO2CSWDdMv
YT1MECH-28-005 | 68f7fe12-8be7-4d1d-9d34-a31d25b77a9a | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | During the Chiller 2 tie-in activity, leakage was observed at a tee reducer connection that had previously been used for temporary flushing. GC shall inspect and properly tighten all tee reducer connections following flushing activities to ensure system integrity and prevent recurrence of similar issues | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623911&prj=626&rqi=KkSoro7UWOVkcKImb7YRD1gz4I
YT1MECH-107-012 | 66b5b123-e828-46f3-8f80-90b6154c8e46 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_C_2 To ISOLATOR 1CHWSTR_C_02_CHWP_1) Need cleaning inside Iso panel, too many foreign object | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623702&prj=626&rqi=rtkSIrNTYwaJQP2HqeeaRIRsJT
YT1MECH-107-009 | 5c16546a-a526-4529-abc0-6737e862045b | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_C_2 To ISOLATOR 1CHWSTR_C_02_CHWP_1) Please ensure that the grounding and neutral termination positions are in accordance with the design, as on the other isolators the grounding termination is installed on the top side while the neutral termination is installed on the bottom side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623698&prj=626&rqi=UaqhqFOiIBiS6VzD0ooWU9noRJ
YT1MECH-110-003 | 4c2a56e8-fb27-41e7-a278-127d886cd934 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_B_2 To ISOLATOR 1CHWSTR_B_07_CHWP_1) Cable scratch until exposing the copper wire | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623695&prj=626&rqi=2i0n7byGPmqoCZ3UP8ddSXxTel
YT1MECH-107-010 | 6c26d5b9-cb49-4a33-a6f1-293a42e8dffa | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_C_2 To ISOLATOR 1CHWSTR_C_02_CHWP_1) vinyl damage, please rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623700&prj=626&rqi=rbFzC4ApJgx5C2hQXoHHbJiTDZ
GT1ELEC-1-003 | 9420bba0-4946-4439-acbc-75d386816ce2 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | During energization of 1MLTX_B, for power, voltage, and current readings could not be displayed on the RMU panel. Please to investigate and rectify the issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623759&prj=626&rqi=MHm5TL2BFIYBuYIYwV2Vh1Ufev
YT1MECH-110-002 | d8fbb3f2-0f01-44c3-a943-225b1632f7ac | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_B_2 To ISOLATOR 1CHWSTR_B_07_CHWP_1) Need to install ferrule cable connector for termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623690&prj=626&rqi=FnVWl2r8JGkbNpHcxU9VZgGLiU
YT1MECH-107-011 | 43d05221-ace6-4b6a-b55f-00099c0ff802 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_C_2 To ISOLATOR 1CHWSTR_C_02_CHWP_1) Nut broken on the upper neutral side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623701&prj=626&rqi=WlOH9VIS8Xw9O9ErN6P3HV6hek
YT1MECH-107-008 | 33d711f1-6617-48ea-9b8b-dcdf4e6de53a | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_C_2 To ISOLATOR 1CHWSTR_C_02_CHWP_1) Need to install ferrule cable connector for termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623697&prj=626&rqi=rpNOUUeIvn9LFYJdwWcjrW6oXV
YT1ELEC-10-006 | 6f7af570-11af-46e1-803a-c4cdad443272 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cables with insufficient bend radius, cable is over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623594&prj=626&rqi=9vEDuJjEK7BxO25twBeIG2DrWm
RT1ELEC-150-008 | ce94a24e-64f4-4cc9-b359-9972eae44b3d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue CxL2A BD R-Block Lv. 5) Label not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623639&prj=626&rqi=vM9juRwfMojdl1HctZSbsYhAZZ
RT1ELEC-150-007 | 7d6f39df-f524-4a3c-ad7d-9878e1128cc5 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue CxL2A BD R-Block Lv. 5) Incomplete bolts bracket support busduct, please check all bracket support | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623638&prj=626&rqi=vHa0IyAJQK9LkzhhctMjYgdSET
YT1ELEC-12-013 | 5e1fa318-fb1c-40ac-84c5-0c0b85f429c6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623591&prj=626&rqi=CKcECSy9CsUAraMa9InOHMuf4S
YT1ELEC-13-010 | 8045a0d6-8c59-4d5b-bc73-cfa4b96c9340 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623585&prj=626&rqi=KYbXwHfwhMeFJsPaxQyyInU4KO
YT1ELEC-13-009 | 65ed90df-1191-4feb-8081-a3cbee998f9f | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cable termination not yet completed and cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623584&prj=626&rqi=khVervoojrdQOiYHz7pqochsjI
YT1ELEC-12-014 | 00d7ef3b-c443-4e6d-9a00-37322d9a18dc | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Outgoing nameplate should be to "1CHWSTR_D_04_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623592&prj=626&rqi=Lz0PYKU6PyOqRkuiTvHpuTWv77
YT1ELEC-11-010 | c550820f-bc4a-4f21-ab67-af92a2a077b6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Incorrect cable tagging, should be "High Temp / Over Temp" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623593&prj=626&rqi=IJ7x2DpM8vZQef3tVsQgcj6Jqt
YT1ELEC-10-008 | baf966dc-44c1-410b-99fd-9b76e1af8f39 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Incorrect cable tagging, should be "High Temp / Over Temp" and cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623596&prj=626&rqi=KJLy4idDHBlNzcEmK7ihAmxOby
YT1ELEC-11-008 | b1a9b537-0d4b-4a70-81db-c0cf21eb103a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | DS sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623586&prj=626&rqi=n6ZKxVhbVB4zKEE0yxGynLaDyI
YT1ELEC-11-009 | 938d4197-5d20-40a4-bf13-ab17d0d82621 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cable termination not yet completed and cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623587&prj=626&rqi=Thm2v6mCI7Z5CMY6Eq1aIbJEak
YT1ELEC-13-008 | 12097f0e-f63d-488a-8797-97e018afe79e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cables with insufficient bend radius, cable is over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623583&prj=626&rqi=qZ0qTZHZOr3TIg3x8UyXxj3uM4
YT1ELEC-12-011 | aae96c37-ef8f-449b-91da-13b11072089c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Incorrect cable tagging, should be "High Temp / Over Temp" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623589&prj=626&rqi=2UhozU1XmWqNM8N54uKjB1ut41
YT1ELEC-12-012 | 9e8b9943-ed99-4866-a970-9c098517ede5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cable termination not yet completed and cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623590&prj=626&rqi=JLOq0dYGf4X3rTjx2ppB3xg391
YT1ELEC-12-010 | 6e4718c9-c245-408b-b04f-0370449143f1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cables with insufficient bend radius, cable is over-bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623588&prj=626&rqi=k4MmpsjzM11GaJFYQeKCl8OvUg
YT1ELEC-10-007 | 2483d455-d7bf-4e9b-be68-fad1d4e141d5 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A Cable Auxiliary MSB) Cable termination not yet completed and cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623595&prj=626&rqi=cXRjagJl7HCBj0aHqttH6UO0YN
YT1MECH-109-005 | a8d0d9a5-1316-4a42-a00d-37519ae94c30 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_D_2 To ISOLATOR 1CHWSTR_D_04_CHWP_1) Cable insulation is damaged/scratch until exposing the copper conductor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623620&prj=626&rqi=4DFNoZ41Jt5bgM5nkRiUX7lmcN
YT1MECH-108-008 | 297d50c9-0509-43f0-a5ff-ee48938221b5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_F_2 To ISOLATOR 1CHWSTR_F_03_CHWP_1) Nameplate Panel ISO Not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623617&prj=626&rqi=S0q0pdU2PoiXDPrCBbNXLBULiz
RT1ELEC-12-010 | baab52ea-69a6-4ebb-b25a-3ab85368fc8b | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable From 1MSB_B_1 to 1GPC_B) Tagging Cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623606&prj=626&rqi=mPJeNY9TLboInrVmIXUj6TSvAD
YT1MECH-109-006 | dc8c0df6-ab4e-4063-91f8-310a9ef57dc6 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (Issue CxL2A LV Cable 1MDSB_D_2 To ISOLATOR 1CHWSTR_D_04_CHWP_1) Need install Ferrules cable connector | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623635&prj=626&rqi=851wLYzJf00w36q7Y6BMYkgJWj
YT1ELEC-18-005 | d5ec2c79-5320-4e59-b21c-f65c602c3678 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_C_1 to 1UPS_C_2) Cable vinyl not yet installed & missing bolt termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623460&prj=626&rqi=4MwKq6wdzl10qExc5LDVA4VRFk
YT1ELEC-18-004 | 22b42f4a-e70c-49b6-ac5a-b6531493bfbf | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_C_1 to 1UPS_C_2) Cover tray not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623459&prj=626&rqi=9fYUXe9H0b62Rli6iqGszYkLZD
YT1ELEC-119-001 | af5c3972-56bb-4698-93a6-d1af9b82a6b2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1MDSB_D_1 to 1DB_D_CRITICAL) Please ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623456&prj=626&rqi=zmWMAsaFzZOgGw08cn0SjgdLXF
YT1ELEC-18-003 | 78f5c4d3-b45b-42a4-b0bd-5b00b5849845 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_C_1 to 1UPS_C_2) Several cable gland caps area damaged (torn) and not properly covering the gland, please ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623458&prj=626&rqi=3tpbqpHTYOGnG3maRW0WGMQoHn
YT1ELEC-120-001 | 372a676c-8c7e-4e5b-94e9-a4555fdd672a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1MDSB_D_1 to 1DB_D_EWALL) Several cable gland caps area damaged (torn) and not properly covering the gland, please ensure the gland is properly covered & sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623450&prj=626&rqi=sEUzJAsENfKMdYRbT8xSrQLGzn
YT1ELEC-5-009 | b4c9077d-ceca-4492-8993-4a4b9a76d4e8 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Busbar inside MLTX incomer cubicle in MSB panel still dirty and dusty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623442&prj=626&rqi=CXeftBF651rRopydLRpgYkwm8D
YT1ELEC-5-008 | a7e1c7ec-05e7-4093-a3ce-dbf99693210c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Busbar joint between MLTX busduct and MSB not yet torqued and marked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623440&prj=626&rqi=lkcOYkLA7aGcvV3KK2WCehPlYh
YT1ELEC-5-010 | a9c4f503-ef38-4a45-98cb-aa184373c4c4 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Grounding cable from MSB panel to earth bar and from earth bar to SUDB need to be checked to ensure ready for MLTX energization | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623443&prj=626&rqi=YfbrB5OrqVgrgRM9QoHKrkhQu6
YT1ELEC-120-002 | 340c270b-bf67-488e-99d7-6588c5d63411 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-28 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable 1MDSB_D_1 to 1DB_D_EWALL) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623455&prj=626&rqi=iOk7SBV3kTI2S40xMos9MUc5uT
YT1ELEC-10-005 | 33acb8f4-7ad8-4733-b675-78188a97e3d4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_B_1 to Chiller) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623306&prj=626&rqi=Qz8C0Xb8pc2gNs9A3EV43CiSPs
RT1SEC-20-001 | 631f6b70-56a2-4b4e-99a7-2d455ab6cba2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Security | equipment | 1ACS_level_5_DH | ACU _ Access Control |  |  | reader not yet installed, door 05:16 Note: it's because GC's work (flushing pipe), that make the door cannot close so there will also become GC scope to rectify this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623273&prj=626&rqi=njSfbpREdVyTOjKszp5SXzf1DB
YT1MECH-32-002 | 6ad953af-e0ef-44f4-8704-dda2699f5680 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to Chiller) Standardize the cable tagging from "1MSB_C_1 to LBS 1CHWSTR_C_02_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623316&prj=626&rqi=Wz1ttMSaX1urKbQ2mflanBBMjG
YT1MECH-89-003 | 3163b57d-31eb-4d36-9c86-06f2c8db13a4 | JK01-2 | 626 | APAC | Closed | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | DCOS cable has not yet been pulled into the CRAH unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623299&prj=626&rqi=RCm7KNcOX73wS4DQdTlCOXYKxt
YT1ELEC-11-004 | 9db03110-eb52-4838-93f9-3663a80f1757 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Aux power control cable inside MSB panel found over-bent. Please rectify the cable routing/installation Also, GC to clarify the reason why this cable was skipped during CxL2A & CxL2B process | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623300&prj=626&rqi=F51WSwtSW27PQtDcl418gLgPyr
RT1MECH-35-004 | fd9d10cf-76bc-4310-b961-252c7f0345e9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Labelling / equipment name tag not yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623315&prj=626&rqi=aOOiQgBQ2CiwCOAz8BG8FLvCtV
YT1MECH-85-001 | 64ba2019-e0a4-423c-a9c0-10e5a05fe7c9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_21 | CRAH - Computer room air handler |  |  | Incomplete insulation and jacketing observed at several points along the CHW piping | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623302&prj=626&rqi=Rv8uDMGiRzEWJiGYhzNO8y19qK
RT1SEC-20-005 | 4fc9f567-7179-4e12-ba0c-96f248f2f2be | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Security | equipment | 1ACS_level_5_DH | ACU _ Access Control |  |  | door 05:12, 05:17 handle and accessories not installed yet. door 05:11, 05:13 accessories not yet. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623287&prj=626&rqi=YiRawv0L1b3BL7GvDu6K2QnIll
YT1ELEC-10-004 | 216b90ea-d723-4311-9b8d-e5680ae22e65 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_B_1 to Chiller) Standardize the cable tagging from "1MSB_B_1 to LBS 1CHWSTR_B_07_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623303&prj=626&rqi=AvxVSkjSBJ97Qjn2cYMBDUN3Re
RT1SEC-7-001 | edb609d3-a76d-44a3-83ca-f462b55faa45 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Security | equipment | 1ACS_level_2 | ACU _ Access Control |  |  | door 02:19 wall finishing around the pinpad installation require proper finishing, temporary flushing pipe are blocking the door so it cannot close, and also door accessories not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623297&prj=626&rqi=ZCiIFide16GGdxzcVq66K8PcnA
YT1MECH-31-003 | f7a4d646-0d4d-44e8-bb6e-373a3de44b61 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A LV Cable 1MSB_B_1 to Chiller) Standardize the cable tagging from "1MSB_B_1 to LBS 1CHWSTR_B_07_CH_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623308&prj=626&rqi=RG8bdugaN3TT6cxwNCScHxVR9E
RT1SEC-20-002 | 89fc1fe9-3ad7-4014-94f2-64bbfe3c46ab | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Security | equipment | 1ACS_level_5_DH | ACU _ Access Control |  |  | door 05:16 cannot close because of temporary flushing pipe, it causes the reader for this door cannot installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623281&prj=626&rqi=GKXjFjj1AMALMzFeLLhCBegOGQ
YT1ELEC-11-006 | 19c8218a-6638-47d1-880b-f3c2079b3838 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Outgoing nameplate should be "to 1CHWSTR_C_02_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623312&prj=626&rqi=9FrCUD12LQlGA76U1Y8Uxs8GcW
RT1SEC-20-004 | aa3a87c9-2c76-401f-af28-8cfce41bafcb | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Security | equipment | 1ACS_level_5_DH | ACU _ Access Control |  |  | door 05:11 & 05:13 door contact not yet install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623286&prj=626&rqi=6T2Yoz6CwqFV4t4BSgVlmz7UOE
RT1MECH-35-002 | d299e1d8-b897-45f8-bf0f-de19e6533edf | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | anchor bolts need re-torque and re-mark (it still moves when perform torque check) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623310&prj=626&rqi=sL1trYEHKFo8cuputWh8Z07dgW
YT1ELEC-12-009 | 2438580a-5ac3-44a6-b1b9-b759abc96953 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to Chiller) Please remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623319&prj=626&rqi=vkrCivySj1PiaZvTKQGwIke3As
RT1FD-32-002 | 3ffa6822-ff99-457e-9dfa-aabffc5800c0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-6.09 | VES - Vesda |  |  | Pipe affected by paint | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623304&prj=626&rqi=wO258OeaORCUYIGAfmavjn2dda
RT1FD-32-003 | a68753ca-8dd6-4d16-a936-f6c0b61b3f35 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Fire Detection | equipment | ASDSP-6.09 | VES - Vesda |  |  | support pipe misalignment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623305&prj=626&rqi=oEGgbrPejItuVj6xbcqCFRuSBE
YT1MECH-88-001 | 83b93c59-3fc9-45ea-ad49-f356680e6553 | JK01-2 | 626 | APAC | Closed | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | DCOS cable has not yet been pulled into the CRAH unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623298&prj=626&rqi=XRiVDk424rE4am4GFjG7I535rn
YT1ELEC-11-005 | e301662d-4bca-475b-aad0-dd6ddfb9e7ee | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to Chiller) Standardize the cable tagging from "1MSB_C_1 to LBS 1CHWSTR_C_02_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623309&prj=626&rqi=WTMCvuPtTItxFgWkrURhFoaZtP
YT1MECH-30-003 | d4a2838e-e395-450b-beb0-68a244e57733 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to Chiller) Standardize the cable tagging "from 1MSB_D_1 to LBS 1CHWSTR_D_04_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623320&prj=626&rqi=ty2y55AVeoLnIAW10GzW9dnh8R
RT1MECH-35-003 | 3149e98e-b4ea-4773-bf29-bd640001249e | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | manhole and drain pipe not yet insulated and jacketing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623313&prj=626&rqi=UNwscEzvKmOlbw8hMqQ1EF5PQp
YT1ELEC-12-008 | 3197cd12-b83d-4a79-9286-d16ece2e1633 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to Chiller) Standardize the cable tagging "from 1MSB_D_1 to LBS 1CHWSTR_D_04_CH_1" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623318&prj=626&rqi=JKceBI9X5QQHZaHvqeqwEHv6Wa
YT1ELEC-11-007 | 10e0a378-fc54-486d-b8aa-c2a87889690d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to Chiller) Please ensure glanding cap fully properly sealing & cover tray installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623314&prj=626&rqi=vwutS0tLL1QjbCJL3VrNvHMyYW
YT1MECH-96-001 | 8b8e3f9c-251e-49f5-b8cc-2f3eed8f4a24 | JK01-2 | 626 | APAC | Closed | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | DCOS cable has not yet been pulled into the CRAH unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623307&prj=626&rqi=vJQuaqQJmIf616JK7wPvnjK3V3
RT1SEC-20-003 | 3370276b-ad73-478f-9449-a39d29aa1bc4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Security | equipment | 1ACS_level_5_DH | ACU _ Access Control |  |  | door 05:10 not yet install at all | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623284&prj=626&rqi=xEqkjFNhzFUo9WmavSSCstCHLb
RT1MECH-108-008 | 5c677365-cccf-4f7a-af44-fad841032586 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-05-25 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_41 | CRAH - Computer room air handler |  |  | LCD display is damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622964&prj=626&rqi=kENulcXcsU6yeD1L0me9FTvOkt
RT1FD-32-001 | c9d6e5a1-0f6d-46c3-bfca-839af0bf7ebc | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-6.09 | VES - Vesda |  |  | please upload Factory Test Data & Material submittal document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623110&prj=626&rqi=yEsbvNU5NKURS3NSW3XRrq1xjP
GT1ELEC-2-001 | f12b3086-5d1b-48c2-bfb4-837a26e2e2d2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623034&prj=626&rqi=wjyJG1JcLdUrVLnAd2d7afirzi
RT1ELEC-26-006 | c76372b4-7fe7-4263-8c54-82c89441a827 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | [Issue CxL2A Laying Cable 1UPS_D_2 to 1MDSB_D_1] Vinyl need rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623025&prj=626&rqi=kbrpLlz16GiZrSIhJm1yc2C5XP
YT1ELEC-51-002 | 4c2b3c4a-e8fc-4ef3-9677-558ae314d97a | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A Laying Cable 1STSSB_D_2 To 1RPP_DR1_02_05] Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623011&prj=626&rqi=MY5Wt4XKiYUjcXtuisZN9q0VLX
YT1ELEC-166-001 | 1eded69a-4eda-4fbc-bca0-a858176df8b0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | [Issue CxL2A LV Cable 1MDSB_B2 to Cooling Array Fan 1TOU_B1] Need to remove temporary marking cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622984&prj=626&rqi=JZMnQUSrpwVRoGxkNmK1bn7glS
RT1ELEC-52-002 | fe98cc70-14a8-41f1-beac-7bab1ca8a9d9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_1 TO 1RPP_BRI_01_01] Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623003&prj=626&rqi=kCiLcLIHxqiXhv20PoDE2yHEJ1
YT1ELEC-4-005 | fe40afec-1d3d-458a-ba39-b484b1b64535 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | During white glove inspection, equipment body bolts are missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623036&prj=626&rqi=2WOcEgfPG93rEVTvYk0YhCr1Uk
RT1ELEC-22-002 | a666cc35-4a98-42a2-b2b6-1672ff9586ab | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | [issue CxL2A LV Cable 1UPS_B_2 to 1MDSB_B_2] Belleville need to installed in two side | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622969&prj=626&rqi=shh3ePPfleVlAxH9xEVPWrdXFg
YT1ELEC-3-004 | fbe7f98d-74c8-4d72-a1de-15104f3f2a7b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | During white glove inspection, equipment body bolts are missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623037&prj=626&rqi=RvWrOpj2eqD6Tj86sHiYxxLeIs
GT1ELEC-3-002 | 25b38fca-4d12-4f2c-bca0-4222fca86baa | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623032&prj=626&rqi=lJXJ5cG1Qq0gx45V44obbuXwbH
RT1ELEC-26-005 | 73282a13-7c77-4bee-80ca-ec0b7e13b2c7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | [Issue CxL2A Laying Cable 1UPS_D_2 to 1MDSB_D_1] Cable tagging is incorrect, need to rectify revise to: from 1UPS_D_2 to 1MDSB_D_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623023&prj=626&rqi=6dLS14qNRZPydGbbo7VAEfGSnU
YT1ELEC-47-003 | e9b6e2a2-22d3-49b4-b6a1-8239e78fd81d | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_2 TO 1RPP_BRI_02_04] Grounding Vinyl loose, need to add cable ties | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622992&prj=626&rqi=zMXsVf0f6yDVNcSAkg6IGdzTzQ
YT1ELEC-47-002 | cac57278-d136-43b7-bfb9-42c8c3a26d9a | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_2 To 1RPP_BRI_02_01] Grounding has not been fitted with a cable lug and has come loose. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622991&prj=626&rqi=47DaMgfLbc5uxaj3CitmRuKEp6
RT1ELEC-52-001 | 8eccc1f3-83ff-4b33-abae-f319a1b27e25 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_1 To 1RPP_BRI_01_04] Cable Tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623002&prj=626&rqi=8OyXorGO2bAV8gP65UcAsspVUN
YT1ELEC-47-001 | 4d079725-5ad6-442e-a9e9-c646df20a6e9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_2 TO 1RPP_BRI_02_01] Need to remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622988&prj=626&rqi=3dIZ3n41Tb1J56DbuGN8smwwyL
YT1ELEC-51-001 | 185f069d-d341-4e2b-b353-035e08777247 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A Laying Cable 1STSSB_D_2 To 1RPP_DR1_02_05] Cable scratch damage until the insulation is visible. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623009&prj=626&rqi=x84XzOIhRSRbBN8JKUgnHPaBrS
GT1ELEC-2-002 | 7e0723d2-e296-41f2-934b-4155d610bb02 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | BTU of RMU_D energized from temporary power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623035&prj=626&rqi=98ZCR1fv0IOaDBaiazBR0EX4PO
RT1ELEC-22-003 | 2b41fd3a-3523-4834-8efc-2af3d1f86d50 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | [issue CxL2A LV Cable 1UPS_B_2 to 1MDSB_B_2] Need to add cover tray | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622970&prj=626&rqi=2jqk4NOCrdOxfHqt4K5W4zTe9R
RT1ELEC-22-001 | d781f1e3-03be-4423-80aa-953b7e286372 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | [issue CxL2A LV Cable 1UPS_B_2 to 1MDSB_B_2] Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622968&prj=626&rqi=VlJZDZHx2Yr5YqBZCstfGXeTOZ
RT1ELEC-26-007 | 0b82edae-13e5-433f-ad44-73a91f0afade | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | [Issue CxL2A Laying Cable 1UPS_D_2 to 1MDSB_D_1] Need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623026&prj=626&rqi=636Mk5PWAO3cMgdhekZEdLQykZ
RT1ELEC-56-002 | d812f0ad-52a7-47ef-a86c-87a5d659da86 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A Laying Cable 1STSSB_D_1 To 1RPP_DR1_01_05] Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623013&prj=626&rqi=NcG28fGnlJKLcsIH7ddm8kMZEl
RT1ELEC-22-004 | a8b548cc-d111-444c-8c95-2a4a1164874e | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_B_2 | UPS - Uninterrupted Power Supply |  |  | [issue CxL2A LV Cable 1UPS_B_2 to 1MDSB_B_2] 3 Grounding cables are stacked on one busbar. (for All UPS Mech & possible IT) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622971&prj=626&rqi=Et8bq6MYOr45NdUHonQR1PYB0Z
RT1ELEC-52-003 | 3f575107-452c-4455-ae33-1147b5504a0d | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_1 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A LV Cable 1STSSB_B_1 To 1RPP_BRI_01_01] Dressing cable need to tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623004&prj=626&rqi=Qay54lufMeilLNgXuTB0BV3sCj
YT1ELEC-166-002 | c7aa5644-7875-4b15-93b6-b0a88c07d6ad | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | [Issue CxL2A LV Cable 1MDSB_B2 to Cooling Array Fan 1TOU_B1] Need to add belleville/spring washer on both side (Phase N,R,T) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622986&prj=626&rqi=tw55ZRtBVSBlk0wjxl034HYReG
RT1ELEC-56-003 | 9b16d045-c0f7-4fa6-921c-2ade815a0411 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A Laying Cable 1STSSB_D_1 To 1RPP_DR1_01_05] Vinyl need to rectify and cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623014&prj=626&rqi=Rw2bB3oKEFAMidwZ4FMtdLltrG
YT1ELEC-51-003 | e20cc864-31c8-4d8c-abee-2430f457bad8 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | [Issue CxL2A Laying Cable 1STSSB_D_2 To 1RPP_DR1_02_05] Vinyl need to rectify and cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623012&prj=626&rqi=CcarwYKtE8goqILeDIyf7Msc1d
YT1ELEC-18-002 | fe2df746-3fb2-4417-b2f7-62f5fe015a41 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1UPS_C_2 to 1LIBATTSYS_C_2) Cable inside UPS has not been provided with cable tagging, cable termination is not properly installed, and cable vinyl is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622908&prj=626&rqi=DX0yfbDkXcLULeklZhr3qyj8rF
YT1ELEC-30-005 | 4df3a122-0e24-4aa9-bbfc-766df141264a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | (Issue CxL2A LV Cable 1UPS_C_2 to 1LIBATTSYS_C_2) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622910&prj=626&rqi=oJHopWXuEML3HHn93MpSTVz0LP
YT1ELEC-18-001 | 50f377d1-c0c9-4f43-8ecf-3f1d1a31958f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1UPS_C_2 to 1LIBATTSYS_C_2) Incorrect cable tagging, should be "to 1LIBATTSYS_C_2" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622907&prj=626&rqi=Lb2qPE6o5MyxFXKPy6n7vNPYkX
GT1ELEC-1-001 | 35bc4e10-610b-4175-8a62-2239b943c7e7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622895&prj=626&rqi=23DkmsIN8NRliGnXmdGLbs9azz
GT1ELEC-4-002 | 44a4bc79-f2cd-45f2-b20b-de02053add5a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622894&prj=626&rqi=eWj576e4w64YOcZB2XpBgGIbfE
RT1ELEC-15-022 | bb62ca21-243a-4bf9-8f3c-3763b18af2d8 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Equipment tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622900&prj=626&rqi=s22QOKl4yZgtPpeG7EnTWjliEx
RT1ELEC-13-027 | 3832e61b-6079-4bbd-a1bd-42ea0915c52a | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Need remove straps and blocks for shipping (Cleaning) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622767&prj=626&rqi=XFEcgvXqg8AoeRXQUn5IxaRhyq
RT1ELEC-15-023 | 947f2e6a-aa2e-48ca-a3c6-90fc1ce58fd2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Temporary marking need to remove | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622901&prj=626&rqi=7U6VSN2bJ3uYiitU0gF14fcCxj
YT1ELEC-5-007 | 178eb20e-48e6-48df-9db6-9bbe6d7982b9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Incorrect cable tagging external cable to MSB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622792&prj=626&rqi=osjPrCOhU4rAXz6w1O4KgCry9D
RT1ELEC-15-024 | 78431401-859c-43a5-b6c7-86a7d72212a9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Need to add additional base frame as per design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622902&prj=626&rqi=mbKOrTXJ5ZeOWALpYtLx7lU7Sp
RT1ELEC-15-021 | ae0e7020-113d-4595-9f30-0d56ddc22d24 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Generator dirty & dusty. Need deep cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622899&prj=626&rqi=FpFrMx3c0SwL1MHKpeuoFSOBOR
RT1ELEC-15-020 | e2286a9e-b4d6-43fc-9367-cf73129cb69f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Corrosion observed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622898&prj=626&rqi=A0GOdj5iYoimg31Wn6RBjTpoLc
RT1ELEC-15-027 | bad69930-619b-47b2-8db0-ea780a570e08 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Generator cable not yet torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622906&prj=626&rqi=2Yryh92VvFzQmCixJ8FD5kEPU8
RT1ELEC-15-025 | 4351e035-7ca7-4ccc-b037-60acd40d35b9 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | All bolts need to torque & marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622903&prj=626&rqi=KMXQpYRG4hmEvXBG9c8RSNf04R
RT1ELEC-15-026 | 10b12fa6-4da5-458f-98a3-ba7632fbea80 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | Need to install cable tagging & remove temporary marker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622905&prj=626&rqi=0C2TXvCTOddCOHjV83MLhbmcOG
RT1ELEC-13-026 | 73a8a34a-093e-4a54-b9d7-9e5f0d9fcb77 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Need to rectify the corossion pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622766&prj=626&rqi=F1mVk8Bl4s1PnYslrqJFB9kNg9
RT1ELEC-13-025 | 5bbd8db6-2370-4d09-900f-d6f26ef4ddd6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | many scratch on body generator, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622765&prj=626&rqi=eCuAXJqWwia36rdjhaXTmKC7R5
YT1ELEC-169-006 | a84c5b09-9ebc-4eea-8f96-b947b3fd11c7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) Cable tray end sections are open. Please confirm and install end caps where required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622425&prj=626&rqi=VHlyzC7F6CyH8nRY1bnYDhTDmK
YT1MECH-78-003 | 0e52be6a-c2d5-41bc-84b3-26195c9186a9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622450&prj=626&rqi=voHfyYbSsFMal8nXVLGTgzz1RH
YT1MECH-78-002 | df1bd4fb-3ecf-42cb-97dd-e6985baf74dc | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622448&prj=626&rqi=pONZ15OINEE0URUyrhTT7kL2s4
YT1MECH-76-002 | 62e7d2ef-6838-4491-b4f5-e43122117c12 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622445&prj=626&rqi=2Zlkbn745hlQ4Rhsh3XJoEVc84
YT1MECH-53-001 | 697cb13c-8424-4900-a2f6-20cf38e9ba4d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_C_06 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622432&prj=626&rqi=Sux5xrXUyeHjGt6Mba5XE4Z8LA
YT1MECH-69-002 | 859ed022-b179-425d-98a6-6b209ae2f1f7 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622442&prj=626&rqi=uJcTrR8PsN8x5C0NS4pvEGd1ay
YT1MECH-76-003 | b21a3625-3002-4d32-9cde-5976243317bd | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622455&prj=626&rqi=boA0daSlwbPxIxYfevkQo1iKQx
YT1ELEC-169-004 | b0306074-8fee-499d-ad06-5b7e9cec8c24 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) Cover trunking not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622417&prj=626&rqi=uyqLhIKZ1C3Jo7dlA6eeyAmYxZ
YT1ELEC-169-003 | 6b0c0615-3aea-4284-9ed4-4c5465d58eaa | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622416&prj=626&rqi=R5SFqpl9k0IwxJ83Y3jozzuX5i
YT1MECH-77-002 | 3be1e7ac-dba7-480b-a4ac-457ac147849a | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622446&prj=626&rqi=BXSvwPXDTFbjAC1TRRpRzXcPRU
YT1ELEC-169-002 | 6903aa49-314d-462b-99fd-f059c1dc2f35 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) incorrect cable tagging feeder name | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622415&prj=626&rqi=MUBOGdQOpXIlVNgDjUSft1CF0w
YT1ELEC-165-001 | 35b532fa-606d-4b37-9911-fd61b5b66943 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_2 to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622459&prj=626&rqi=91wNteV4b8KQvw5BK94K3tmkXn
YT1ELEC-4-003 | 19f9ec64-aecb-4f6e-b6c4-1961050fa8e9 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | During white glove inspection, flexible busbar was found disconnected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622656&prj=626&rqi=rNJxFFWZjD2uFxbRPqC0hgepd7
YT1ELEC-4-004 | 5270a6e2-6437-4c8a-ac83-4438beab4757 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | During white glove inspection, control cable was found disconnected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622668&prj=626&rqi=eKMlCXdDgfONL0t4jaWPeTkynZ
RT1ELEC-13-024 | f319ef7b-96d9-439e-9520-b053b44cebd0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | Please add labelling cable to GCP Gen_D | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622597&prj=626&rqi=COioJedVvwwwStNBJXM4Yvfe7c
YT1MECH-69-003 | 11aa226d-25d1-479b-8c96-f495ee9a8f8a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622457&prj=626&rqi=fMgJbbxLmfyikgcn4cY5aeigZw
YT1MECH-52-001 | 20a50ccc-d9d3-4707-a91e-df54d839796c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_C_05 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622431&prj=626&rqi=RouiVvOljD0U7DrEi08Y5olCLy
YT1MECH-54-001 | a9fd7a92-5b24-4475-8719-b8fd4af87c68 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_C_07 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622434&prj=626&rqi=66aMwIMrl7IMmKUnLmCWS9HMHj
YT1ELEC-169-005 | 9ecac64f-ea01-4954-9faa-e025d7269f61 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) Bonding jumper not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622419&prj=626&rqi=dFji5zM3166IY8Ux7cLsCzUWN2
YT1MECH-56-001 | a0039ed4-4f7c-4f39-a10a-95a54603a591 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_C_11 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622438&prj=626&rqi=BFu32gKAqmTHkgfLuCuXhG6goR
YT1MECH-75-002 | a6206468-b962-4a81-a88b-b6ae0c43431a | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622444&prj=626&rqi=6d2vhOPueWckQwpTGcSdcl9bOA
YT1MECH-51-001 | 73323114-889d-4cde-b163-19a74c1915d5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CA_C_03 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622430&prj=626&rqi=rhT6ByTvlCceS6l8iezIWILxN1
YT1MECH-50-001 | 97d9ec9c-75bd-43d9-bfbe-6bf0b1e9b8ca | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CA_C_01 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622426&prj=626&rqi=a94gEvpKClXzqXgj26PJGyiJbU
YT1ELEC-169-001 | f2f9f654-48ae-4b61-8f8d-b6219e131823 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to Cooling Aray) Cable tagging not yet installed & please rectify the cable vinyl | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622414&prj=626&rqi=QRGXbgxZcNJVmZzHEIJZaLle6i
YT1MECH-55-001 | 8463f8c9-a01a-49e9-a9a5-70d89ae00b8b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_C_09 | CA - Cool Array |  |  | (Issue CxL2A LV Cable TOU to Cooling Aray) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622437&prj=626&rqi=xSf1FFBtsLoiRLTrAyDaG3Y0b2
YT1MECH-75-003 | 090c6c46-61b0-40af-be54-37e4dd12f829 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622456&prj=626&rqi=QVTLlRNyGQUC6iOfiomTqwrM4t
YT1MECH-77-003 | 435fdbf9-e1a6-4f94-9f8d-fe9b7f7f0560 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | (Issue CxL2A LV Cable 1TOU_C_1 to FFU) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622451&prj=626&rqi=MWTZjr0P5B9BLrQE6hXu2JF4MF
YT1ELEC-4-015 | 097dd0b7-f71a-4b95-81e2-80de4676fb6a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | During RMU energization readiness inspection, several panel bolts were found loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622362&prj=626&rqi=IWHeQLmHAWnn2236yXdtYElmEf
YT1MECH-89-002 | 169e405f-7b66-46db-97f4-19d5909fa4e0 | JK01-2 | 626 | APAC | Closed | P1 High CX | DimasKurniawan@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | \e observed during Cx activity (CRAH_F_41) that the HMI was damaged due to impact during ongoing construction work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622382&prj=626&rqi=hZw4wgMXDemUrQ89pwQ43Py6fg
YT1ELEC-4-013 | 72ab35f3-6216-43aa-9fc4-7070773b4f89 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622275&prj=626&rqi=UjC4NoGvQ67cxiog9w4RXLtNwn
YT1ELEC-1-003 | 62ec957d-4ae9-441d-a236-c4bc52d311ea | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | During site walk for RMU energization readiness, solenoid was found not functioning properly resulting in energization activity unable to proceed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622274&prj=626&rqi=JJEmEiwhUlOPv8XBbBy04CMv43
YT1ELEC-4-014 | 8c620fd5-3847-4a9f-8259-4820faa086ac | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | The panel door lock cannot function properly due to the earthing key not being removable and causing the panel door unable to close normally | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622276&prj=626&rqi=4Wjm0CAqKQwr50lIjFSxMrQhHZ
YT1ELEC-1-005 | 2e4929ad-4f55-4e99-8267-4d35d09f3ec7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | General Contractor | L2B | Missing Components | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Rear panel bolts of the RMU are still missing and not yet installed (around 10-15 pcs) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622361&prj=626&rqi=foFdsObUj7LGBhntzU2w6xGVd3
GT1ELEC-1-002 | 41619295-8f71-45c2-ac81-3a3397aebc9a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | BTU_B Energized using temporary power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622911&prj=626&rqi=DUpYat6PZE5jYy9JHYCCSyrgi8
YT1MECH-89-001 | a5c456b5-b2d1-4030-86ff-27a5f7062fdf | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_41 | CRAH - Computer room air handler |  |  | Need to add water flow direction labeling on the inner pipe of the CRAH unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622378&prj=626&rqi=quTDeFBHlVdLguCYBfGgXuQnPh
YT1ELEC-1-004 | 1e400922-ad7e-4869-b2fd-0fb18ff00007 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Discrimination study sticker not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622277&prj=626&rqi=CqbNg2QEtqi7X1wnBMZQEHz9QQ
RT1ELEC-14-021 | a8522236-e4fd-4d27-aa82-b0fa327c448c | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Please provide shop drawing for inspect dimension panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622257&prj=626&rqi=tnSPDsOQigYu6ZuIsbFkI3TUJ3
RT1ELEC-14-022 | 1f9e5912-09f8-4622-a04d-d02377af0cff | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Need remove straps and blocks for shipping Gen (Cleaning) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622258&prj=626&rqi=V1KGBrkYHOTt2DoIf2ItVaGd8Q
RT1ELEC-14-025 | d1b15e03-4bdb-417a-a171-5720a0929ae0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Please install cover tray grounding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622262&prj=626&rqi=yyVYEjjU3ww0A4Q1BRkp19hBbc
RT1ELEC-14-024 | 8dd42f64-5572-4b13-953f-2d0113552d44 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Spring mounting need rectify, cannot be tightened to the specified torque | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622260&prj=626&rqi=CokimpwZ5xacgRJX5FlRB8dymx
RT1ELEC-14-026 | c9d4fa57-ca18-4143-9374-681f680263d7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Need install jumper grounding tray cable containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622263&prj=626&rqi=D7iy7N07cxvxsui4diL2k2lVcX
YT1ELEC-1-002 | f300124a-5c82-4605-8ca2-8d92f11f06f4 | JK01-2 | 626 | APAC | Closed | P3 Low DCOS | fauzanfikri@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | DCOS conduit pipe damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622156&prj=626&rqi=JFeAZmfkr32QDImgV9pH04P5jE
RT1ELEC-14-019 | b64ed9e2-d2c4-4770-95d3-b41514021381 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Equipment damage (body scratch) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622252&prj=626&rqi=wbIBL2idlPVWF748VuDFPsml73
RT1ELEC-14-020 | 9c3a3fa6-fa58-45f6-9fdd-0bdfa7a69a90 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Need to rectify the corrosion pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622255&prj=626&rqi=4DpRdbJETXqVEFuoXzpBc5rmaX
YT1ELEC-1-001 | f37e215f-b839-4010-9cff-d262295dbebb | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Please update the breaker nameplate numbering to follow the approved nameplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622155&prj=626&rqi=g7R4oh1LyNMvhjihKEfmgBBa0U
GT1ELEC-3-001 | e53e8e3d-f13a-4012-bc8d-7766de78ddb9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | BTU_C energized using temporary power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622159&prj=626&rqi=ytnsuz3luWop7mF1Vij4ZOvraF
RT1ELEC-14-023 | 5fa98d95-43ab-4eac-8ce2-a0346115cb04 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Please add labelling grounding + tidy up heat shrink | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622259&prj=626&rqi=Z3ythnqSDBWDpM38JJDoBgnybV
YT1FD-13-001 | b2ffa55d-ae67-4000-abee-a3f7a61ba2c4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Fire Detection | equipment | ASDSP-3.10 | VES - Vesda |  |  | need to clean and provide proper cover for equipment to minimize debris, dust and also need to repaint pipe which affected by wall painting | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622268&prj=626&rqi=nP71JJagBCWwQ4wHUGhHaF3eYD
GT1ELEC-4-001 | 191046f3-57e8-4d13-92d4-fbb4a5822af2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | General Contractor | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | BTU_F energized using temporary power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622158&prj=626&rqi=TFMmhfkrn7xCf7mqiZHwra2azt
YT1FD-38-001 | 667eb7f2-dbfe-4595-9a73-f9940fb42f8e | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Fire Detection | equipment | ASDSP-7.09 | VES - Vesda |  |  | Please provide more proper labelling name for isolator switch, refer to phase 1 (photo attached) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622267&prj=626&rqi=pdaq4C1MnNUvKhpNJr6TWZxhrG
RT1ELEC-14-027 | 97d9a6ef-0e99-44e4-a9b0-5e9b05fb77f0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Need install vinyl properly and cable ties | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622264&prj=626&rqi=w3qK8gAPZatAX7dnkmim5d8kbR
YT1ELEC-4-011 | 500c0437-78ce-477f-aa0a-eaea413d1704 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Need replace connection grounding system at 1SUDB Side to 1RMU_F_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622102&prj=626&rqi=omAe6E6wez3mTMasO95YyRWXb8
YT1ELEC-4-008 | ffe32b5e-7a33-488e-b75a-92e9d759123c | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Tagging MV Cable incorrect, Revise to: 1SUDB to 1RMU_F_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622099&prj=626&rqi=a3khvpfV7AhoFpW6pe4f3Ziysz
YT1ELEC-4-009 | 868947ec-324e-45c7-b394-fbcc59206e21 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Tagging Grounding incorrect, Revise to: 1RMU_F_1 to EB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622100&prj=626&rqi=IzLKDsCSkNVCnZE2OLflseYtxH
YT1ELEC-2-008 | 448f2cdc-09fa-4469-93a3-d441f28710b4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Please provide the termination point cover at the RMU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622113&prj=626&rqi=JleFUZEc9UkyWnPyS74Wgs0kkv
YT1ELEC-4-010 | 9594700f-77fc-4d09-9adf-0c5beb5eded2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Need install Cover rubber cable gland, because make debris inside panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622101&prj=626&rqi=QMDJaO1x4DrB1mbbq0LPYoujCi
YT1ELEC-3-007 | 626082ae-4bcb-4dc5-a495-01d6579bdee2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Please update the breaker nameplate numbering to follow the approved nameplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622110&prj=626&rqi=WR7zTQRsKYivszYjHIQXMSZb8Q
YT1ELEC-4-007 | fd36fe51-8280-488a-a986-ccdf3344f4fc | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please provide the termination point cover at the RMU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621955&prj=626&rqi=1hXfU7ApqA98xnWSZFK7m1yQ6Y
YT1ELEC-4-006 | 38b39733-265b-481d-b834-65b80d1c3df5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please update the breaker nameplate numbering to follow the approved nameplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621953&prj=626&rqi=G9PyAp2ITcFiAh9AqxpwNxAstW
YT1DCOS-15-001 | 7b70b211-d7b7-4593-ba9d-50e9cab16cbf | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning |  | Controls | equipment | 1DCOS_1_SCP_07 | DCOS - Control Panels |  |  | During the site walk, CTA observed damage to the conduit at the SCP07 panel to sensor, and please add support to the conduit for reinforcement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621956&prj=626&rqi=q4Sat9InG4M7BJMsLgTBulwmGp
RT1ELEC-27-002 | c498eb07-da5d-4f04-9080-2588b36d7c7c | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Drawing inside panel not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621615&prj=626&rqi=7CCkALDmFmhq02nH95y0BVJITw
RT1ELEC-27-006 | 3e72e7d5-1fda-41ab-84f6-fb5849843c61 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Equipment is dirty with dust and foreign object, Cleaning (FOD) is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621634&prj=626&rqi=vt40aNQz5psVwWfFwBQ6GMM9iz
YT1FD-7-001 | d117dc2f-089f-41c9-829c-59c5d8dc3986 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-2.04 | VES - Vesda |  |  | Report CxL2A need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621572&prj=626&rqi=LkaXbunpgWReypxffh8LPUj4bG
RT1ELEC-55-011 | 13c4e025-775c-40a9-a620-0d22334c36ea | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_2 to 1RPP_CR1_02_03) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621593&prj=626&rqi=k6DQx5rf5aNUU6OIO3GO6i3wLb
RT1ELEC-54-007 | 399e15e6-9f3e-45bd-a38b-55315b81ee4e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_1 to 1RPP_CR1_01_05) Remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621587&prj=626&rqi=OZ6P5w9F2tl7NfdjLDgKUhtn8D
RT1ELEC-152-003 | 2a8cc73c-9e74-42d6-ab1c-c4f606b1ea8c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue Tx Room B) Earth bar label not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621344&prj=626&rqi=zTi0Kt3MKeIyFT7ia9jkGxF7Sk
RT1ELEC-152-001 | a3d61b88-6d3d-4304-816e-754b68b14f56 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue Tx Room B) Grounding cable size for the RMU & MLTX is not in accordance with the design. The installed cable is 300 mmÂ², while the approved design requires 240 mmÂ² | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621342&prj=626&rqi=70fWOqpjbAHrn6yUOjWcPPTREv
RT1ELEC-27-001 | 9f749f58-d2c5-4a99-9022-de1f9d9302d5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Any scratch on body panel 1UPS_F_1, need to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621608&prj=626&rqi=PoKYH4coAwXazD4SdTamkO8zOq
RT1ELEC-27-003 | 86c2ab36-5f34-4005-9e71-2e5ae1012851 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621631&prj=626&rqi=676jbGEzGd9WOsE2TgZLiN6bLt
RT1ELEC-152-004 | db771e5a-bc44-4e90-b306-2944f37a448d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue Tx Room B) Please ensure all grounding cable tagging consistent as per standard | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621345&prj=626&rqi=amGl71wwOoiyOkEGSFyQ5GxRPe
YT1FD-12-001 | d7e3c41c-69c5-4f6a-9a54-597f8725fe12 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-2.10 | VES - Vesda |  |  | Report CxL2A need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621583&prj=626&rqi=6hCsZbm4bxUBlUI6M8aX9aFyMu
YT1FD-11-001 | 33c48cf3-1f04-49ac-a339-d03651313b05 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-2.09 | VES - Vesda |  |  | Report CxL2A need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621582&prj=626&rqi=MqeyO0mIGNrmLdpIvwqnQWeadR
RT1ELEC-27-005 | 72c04a70-5d99-46cf-89dd-dcf84917835f | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Add temporary protection to prevent for construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621633&prj=626&rqi=PSuG6oukuNX9UZxx1MyDWQ56q0
RT1ELEC-54-006 | b0362914-5692-4d67-bbd3-b250d99c50b2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_1 to 1RPP_CR1_01_05) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621585&prj=626&rqi=5pr0XX1INcdFflPUgHuL2T2J57
RT1FD-10-001 | 78be6c4f-a63e-446a-91bb-024efa03a301 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-2.08 | VES - Vesda |  |  | upload RFIT doc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621570&prj=626&rqi=z3hh7q0v0e17bpzsc1KhT2ZCta
RT1ELEC-15-019 | e85ee555-f755-47fb-a58e-093dd0e54933 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual breaker rating: - Breaker Q3: 6A actual 16A - Breaker Q4: 6A actual 16A - Breaker Q5: 6A actual 16A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621339&prj=626&rqi=ldaFH3mAjroLciR7JKfYkcuIGp
YT1FD-10-001 | 7f1a70b2-14cf-43c3-8488-7193d4f6bae1 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-2.08 | VES - Vesda |  |  | upload report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621581&prj=626&rqi=pbEVbcH8KLT3LhdqgS5j0ERB47
RT1ELEC-27-004 | b2ae901c-980f-49d0-a940-94e2f82b80ad | JK01-2 | 626 | APAC | Closed | P3 Low CX | kattyrachmawati@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_1 | UPS - Uninterrupted Power Supply |  |  | Nameplate panel not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621632&prj=626&rqi=eIW5BlHhJlp7JW8799JtO4f57S
RT1ELEC-152-002 | 9e7f0b87-c8c5-4312-9ac0-4409c39c50c2 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_2 | ERTH - Earthing |  |  | (Issue Tx Room B) Please follow Equinix standard for cable termination, not yet installed flat washer & spring/belleville washer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621343&prj=626&rqi=oLzlgjyGP3F3HyVVMJt8Nhwbx0
YT1ELEC-2-005 | 4e29741c-07a4-4b22-83d8-ca33079af2f0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable 1RMU_A to 1RMU_D) Need to add cable tagging/label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621090&prj=626&rqi=VABo8RBVGrGJ5AamJwnurbubud
RT1SEC-21-003 | 2eb56269-a967-4593-ad57-4246c174c50d | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Security | equipment | 1ACS_level_7_DH | ACU _ Access Control |  |  | door contact sensor has not been installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621045&prj=626&rqi=3VnjpIpABYH8Cod5i9fdqO28cV
RT1MECH-9-004 | 78c1ae72-c6ac-4f23-b659-a6e8060ce7d9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | issue LCP panel. labelling cable not yet complete | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621049&prj=626&rqi=pM1D1pnHVqBkyICJOGduf7uuaG
RT1FD-16-001 | ab04314d-c182-44a2-bec9-a137e473589a | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-4.03 | VES - Vesda |  |  | need to upload doc: 1. Technical Submittal 2. Factory Test Data 3. RFIT 4. Drawing (already approval) 5. Report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621065&prj=626&rqi=k15mDyZ3JwhiyIdrqgeOaLCHlm
RT1MECH-6-005 | bde7e781-bec3-4220-873d-40433f487358 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | issue LCP panel. labelling cable not yet complete | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621048&prj=626&rqi=FyNR3MoIsawdB0EDJ1cZ0iuIJe
RT1MECH-2-004 | 9c552ba6-ac32-4783-b261-11bbb20f7804 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning |  | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | Fusible link cable issue. attach photo once already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621069&prj=626&rqi=1KEFh53TmE3RwdvTcMr3Pmt43s
RT1SEC-19-002 | 6d4194c9-1f1f-4e7f-9eaa-52a70c0588fd | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Security | equipment | 1ACS_level_4_DH | ACU _ Access Control |  |  | door contact sensor has not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621047&prj=626&rqi=a0D9LfU0B3CxTNb7vXZbK6WDr6
RT1FD-14-001 | 8df66227-a4b1-4537-b91a-0525046ccc29 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-4.01 | VES - Vesda |  |  | need to upload doc: 1. Technical Submittal 2. Factory Test Data 3. RFIT 4. Drawing (already approval) 5. Report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621063&prj=626&rqi=3leMtVfu8h0Ox75N4HgD5wm3MI
RT1SEC-19-001 | 4fed720f-678b-4e37-b60a-5b9da5ea9044 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Security | equipment | 1ACS_level_4_DH | ACU _ Access Control |  |  | issue for CSA GC team; door accessories have not installed yet, such as door handle, door loop, mortise lock, door closer, and even there is one set of complete doors have not been installed yet (one of door at caging door) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621046&prj=626&rqi=p3lGFD9nd0i2beRHrVns6rnS4p
RT1SEC-21-002 | 83e185aa-ec78-435e-b4f9-9d9289036511 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Security | equipment | 1ACS_level_7_DH | ACU _ Access Control |  |  | issue for CSA GC team. a long thread blocking the door so it cannot close properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621044&prj=626&rqi=bkComTw9Ejs9Hf0rTnn4DaO01N
RT1MECH-2-002 | d070a38c-0d75-451b-a627-47f23767b14f | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | need to upload doc: 1. O & M Manuals 2. Shipping & Delivery Receipt (if any) 3. Approved SoO 4. Report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621067&prj=626&rqi=C4BrgeDXZc9W2z8lJcoZFUxn8A
YT1ELEC-2-007 | d3e586e9-12d5-4ad6-ab83-72364d5ba87c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable 1RMU_A to 1RMU_D) Need to add tray/support cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621093&prj=626&rqi=iUcXv5w19fSvgnG5F15vG94drC
RT1MECH-2-005 | 7ccdc2e0-1919-4fed-abac-774856ff0cc4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | Pipe overflow does not install yet. attach photo once already done. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621072&prj=626&rqi=sJbNRvggnm3EBX1gmfkdahu3Eo
RT1SEC-21-001 | 015d0c77-5eaa-4fa7-a77b-204be3f646e5 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Security | equipment | 1ACS_level_7_DH | ACU _ Access Control |  |  | issue for CSA GC team; door accessories have not installed yet, such as door handle, door loop, mortise lock, door closer, and even there is one set of complete doors have not been installed yet (cool spine area) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621043&prj=626&rqi=HnxakVwDBuylIr9jFeSlxGtxLT
RT1MECH-2-003 | 8b8a531d-8976-4841-8efe-bf44279ac0cb | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | Pipes need to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621068&prj=626&rqi=JfHQfMKRvRzh8mj7nTkCmBGRqV
RT1FD-18-001 | 8953d403-19ee-494e-a368-71dc61df9321 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-4.05 | VES - Vesda |  |  | need to upload doc: 1. Technical Submittal 2. Factory Test Data 3. RFIT 4. Drawing (already approval) 5. Report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621066&prj=626&rqi=92Kr2hXFjvIxLTWv9GBQXjbyl8
YT1ELEC-2-006 | 0186f422-90dc-4622-b984-7a7e1baf57a2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable 1RMU_A to 1RMU_D) Cable cleats not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621092&prj=626&rqi=DooVlFUUnH4P6bDopewX3ESy8l
RT1FD-15-001 | e18fdeb1-77fd-4f73-b79f-28fdb2a0499d | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-4.02 | VES - Vesda |  |  | need to upload doc: 1. Technical Submittal 2. Factory Test Data 3. RFIT 4. Drawing (already approval) 5. Report CxL2A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621064&prj=626&rqi=s9z2yAiOGxMQbwogUW441G7ODp
RT1FD-23-001 | a0568d1d-7b5b-4bee-9c3a-863995148590 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-5.01 | VES - Vesda |  |  | Factory Test Data need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621042&prj=626&rqi=2nu12N0yjEyCIc4IBIeqr2Pnu9
RT1MECH-2-006 | 8d8125c4-9f38-4690-9064-649de3ff1e94 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | solenoid cable issue. attach photo once already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621074&prj=626&rqi=1MsCljKXQAVNVxUo6MJjT7wjAI
RT1ELEC-154-001 | cca736b7-eba3-49d0-bffd-148d6aa27075 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_5 | ERTH - Earthing |  |  | (Issue Tx Room C) Conductor still exposed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621031&prj=626&rqi=jh8Mn4fgqJJtWqqdWoOmIhvAf3
RT1ELEC-13-023 | e4d81b00-b06f-48fe-a43a-5e0a1cdbaddf | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Vinyl cable color for Phase S / L2 should be brown, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621030&prj=626&rqi=ZMmNKsRvuqENFtmkyChGLWqggY
RT1ELEC-154-003 | cb64eff0-15f1-4f68-8487-f792ad3aa264 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_5 | ERTH - Earthing |  |  | (Issue Tx Room D) Please follow Equinix standard for cable termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621033&prj=626&rqi=k6CEi3REOKRa82Ef2Z9r6a7Km0
YT1ELEC-11-001 | 76144c1d-326c-4e07-a1d3-f5629e933895 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to 1GEN_C Panel GCP) Need to add belleville or spring washer on the bolt termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621018&prj=626&rqi=9jNZeHCdigba74fV94lmFoXCMv
RT1ELEC-13-021 | c44d6b61-4bee-47c8-ac14-ebf4f90e9894 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Please remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621028&prj=626&rqi=qQIfK1dUrUuCeRMuh5LDzLmNuH
YT1ELEC-12-005 | bc65aa9d-9163-42b4-869b-1fdf701b8013 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Vinyl cable color for Phase S / L2 should be brown, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621025&prj=626&rqi=RicJFlvV4qUNDLeSD2FfopuJXX
YT1ELEC-12-004 | 20e23116-0958-4984-8e97-7696935768f4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Need to add flat washer & spring washer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621024&prj=626&rqi=ZymcJCyW06jTYo1lyW235m2Dtg
YT1ELEC-12-007 | ab1beb8f-0249-407d-b63a-46bc582377d2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Missing bonding jumper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621027&prj=626&rqi=e3WLoRTOvv1s5AdzMThmYAPxfc
YT1ELEC-12-003 | 208c7898-0e79-4df5-b13f-b634d50a83da | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Cable vinyl is not properly covering the termination area between the cable and cable lug | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621023&prj=626&rqi=Blg8EVE9ujguHRH46ug3oVpu4i
YT1ELEC-11-002 | 0a39598d-686f-4465-ba5a-cadc1ee88c19 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to 1GEN_C Panel GCP) Cable vinyl is not properly covering the termination area between the cable and cable lug | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621019&prj=626&rqi=mIKCwYcpScmGdTliwW7EJuudT9
RT1ELEC-14-018 | 0cb8d0ba-c165-410f-872f-33ed333f7641 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to 1GEN_C Panel GCP) Vinyl cable color for Phase S / L2 should be brown, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621021&prj=626&rqi=8Jrxgjk93TGfIjAFE01FpXuT41
RT1ELEC-13-022 | d7d99a49-6d22-4198-ac0f-2c6bb5c52a3a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) Cable vinyl loose & not properly covering the lug | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621029&prj=626&rqi=JL3GqyLSdmuwoplU4BGOea1iP3
YT1ELEC-12-006 | 43776c9d-2f40-48db-990f-91530ea59de7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1GEN_D Panel GCP) 1. Cable tagging not yet installed 2. Glanding cap is torn. Ensure the gland is properly covered and sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621026&prj=626&rqi=m1OOG3oBTHUk1muxUDh7qfj62U
RT1ELEC-154-002 | e7342c4d-53d6-4759-a96e-f9988b32cc38 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_5 | ERTH - Earthing |  |  | (Issue Tx Room C) Please follow Equinix standard for cable termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621032&prj=626&rqi=L8SR4HgH7XtM8zeeNI7z7pMA83
YT1ELEC-11-003 | df879651-1ddb-4288-9731-d8cfd8699219 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_C_1 to 1GEN_C Panel GCP) 1. Cable tagging not yet installed 2. Glanding cap is torn. Ensure the gland is properly covered and sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621020&prj=626&rqi=ntLGcTnr5zfRkabdsGHm9UfDJT
YT1FD-26-003 | a8c09fdb-0069-4a3a-8428-76bca8451b8e | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Fire Detection | equipment | ASDSP-5.04 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620870&prj=626&rqi=G79Nop9X9TuZBPIpA2EKN3z1aP
RT1ELEC-15-017 | 1ead1386-6ac7-466e-b1d1-c4bb65c838e0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620750&prj=626&rqi=P1rM5haa2ePf6N09t58bPzOZPK
RT1ELEC-28-001 | 3667ebb0-498d-4b1a-ab97-d9eee86aebe5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_F_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1MDSB_F_1 to 1UPS_F_2) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620727&prj=626&rqi=0wvPzACUOt8WsNs0ivdpkTizhJ
RT1ELEC-26-004 | c549c4a4-baed-44c5-8eba-bb1033a5425a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1UPS_D_2 to 1MDSB_D_2) Glanding cap is torn. Ensure the gland is properly covered and sealed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620907&prj=626&rqi=UHpeWC0C1WC2nQp62sGXlS08LD
YT1ELEC-48-003 | 2e188796-3482-4865-b07b-30a046761072 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_1 to 1RPP_CR1_01_03) Please add grommets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620918&prj=626&rqi=AuR4V0cua6VbgxQdOfzOuPQwr5
YT1ELEC-13-003 | b5ffff4b-bd88-4604-b16d-dd0ff9a52688 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Cable vinyl broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620737&prj=626&rqi=28mTAaJQG8Aa4s4vTiXEu4OEMV
YT1FD-33-001 | e364f054-b8f8-46d7-92dc-13768736a02f | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Fire Detection | equipment | ASDSP-7.01 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620867&prj=626&rqi=c7JmC6RbDqYL7GXE30p0UhNwK5
YT1FD-28-003 | 8b775ebe-d19a-462d-bc66-77779c09b170 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Fire Detection | equipment | ASDSP-5.07 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620872&prj=626&rqi=AwcIQ3cw05Nc8CBhsluOY4h56X
YT1ELEC-12-002 | 09ca2a8e-2244-4049-b875-b31dc654414e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1MDSB_D_1) Please add grommet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620912&prj=626&rqi=WfbFMDNQaknyWeLQsPIQT2GcHw
YT1FD-25-003 | 0619eb11-9fda-43dd-9c1c-bbb07c65c5a1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-5.03 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620869&prj=626&rqi=SqbT2T5Ig0o6RDFxhaB8eUf2S0
YT1ELEC-12-001 | 3c44b44d-2c71-475c-9405-47c7d400e938 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_D_1 to 1MDSB_D_1) Glanding cap is torn. Ensure the gland is properly covered and sealed & please remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620911&prj=626&rqi=9CT3jdybR2DeC1VrjcVugTFsaw
YT1ELEC-13-004 | c41660a9-298e-46c1-bc4d-aff842f0ce0d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620738&prj=626&rqi=8cSYLdynjJVtkFxpQDh7s8NctY
YT1ELEC-48-001 | bd488f09-3b98-4f7f-a55e-abf9a779c39c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_1 to 1RPP_CR1_01_03) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620916&prj=626&rqi=cyOR8I9MW9nspOG1oKscQMUnLw
RT1ELEC-15-018 | c854709b-3e52-4614-b2f6-52e957867e08 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Vinyl cable color for Phase S / L2 should be brown, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620751&prj=626&rqi=cbgJEXrnFjUUp0BMG2BPu0P4TC
YT1FD-24-002 | 1a2adc3a-ba6c-4b2c-89c1-0304d6a4f470 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Fire Detection | equipment | ASDSP-5.02 | VES - Vesda |  |  | 1. Isolators switch existing but cabling not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620868&prj=626&rqi=vDtDoKspqMhQPdKRN1hMTC1ZiE
RT1ELEC-15-016 | 29d4561f-6355-4546-916c-7db1b7bdb4fb | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Need to add flat & spring washer on the bolt termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620749&prj=626&rqi=VJM5g9wgHivFmHdMRzHuFBhBSs
RT1ELEC-26-003 | 5a787724-1d2d-47a3-aad0-c476ef8b0aa3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1UPS_D_2 to 1MDSB_D_2) Cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620906&prj=626&rqi=haG8CyGBFutsNEQFTlv6slpTc7
YT1ELEC-13-007 | 7cb9d6e5-a3e4-4818-848d-e8a27163c899 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Vinyl cable color for Phase S / L2 should be brown, in accordance with PUIL and IEC 60445 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620747&prj=626&rqi=ftgIgtoLI1ZnEALHrb7fY0dlC6
YT1ELEC-48-002 | 0d737869-8b1b-47b4-8500-d446231239ec | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | (Issue CxL2A LV Cable 1STSSB_C_1 to 1RPP_CR1_01_03) Cable vinyl & cable tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620917&prj=626&rqi=k73avOv29aimjSFlGkXHDTtz8t
YT1FD-27-003 | 9a85cd55-dafb-4381-82da-a5017ab93aaa | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Fire Detection | equipment | ASDSP-5.05 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620871&prj=626&rqi=atXFR3BETrUs2bE5RLiDa9lWW1
RT1ELEC-26-002 | 22f03f9f-1a64-4fb5-a62d-5faa24d944e5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | (Issue CxL2A LV Cable 1UPS_D_2 to 1MDSB_D_2) Temporary marker to be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620905&prj=626&rqi=8nySD3mRfC9RsGys2oimgfISiq
YT1FD-29-003 | 2d179093-8985-400b-a504-bec37cb8f764 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Fire Detection | equipment | ASDSP-5.08 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620874&prj=626&rqi=JueJ0Mq6ZyacA3EzzeFjuvkj5G
YT1ELEC-13-006 | 1d7fdb71-c686-403e-87c4-1782fd9c8fb1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Need to add spring washer on the bolt termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620740&prj=626&rqi=qPfkjrUHa5Mk1wXvXuSv9RTZb0
YT1ELEC-13-002 | 52e361ee-2335-4f4b-a0f7-15803df35b22 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1MDSB_F_1) Tagging cable not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620731&prj=626&rqi=Vhk6h5S8rlcXNs4Ix74tqHapwX
YT1ELEC-13-005 | 4f2f8ded-8ac1-4466-b3ae-643914bb6d31 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1GEN_F GCP Panel) Glanding cap is torn and not properly sealing/covering the gland | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620739&prj=626&rqi=DopQ64Vv2QZpqOR0tevCqEHPQg
YT1FD-34-001 | 937b8aad-ad16-45ea-9cf1-f61b7d46c2b8 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Fire Detection | equipment | ASDSP-7.02 | VES - Vesda |  |  | 1. Isolators switch not installed yet 2. Continuity Cable & IR must be finished before CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620890&prj=626&rqi=MBTKNaj0rlo8ZvvDTQTj18FiOm
YT1ELEC-13-001 | 6ce84aa7-5c18-4db9-b296-461009253eaf | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | (Issue CxL2A LV Cable 1MSB_F_1 to 1MDSB_F_1) Conductor still exposed & cable vinyl loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620728&prj=626&rqi=WxBMTlgHDEB9TwWN6NXfPMNikG
RT1ELEC-12-009 | eb406e7c-75e6-4718-8040-106b891cdbba | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GCP) Discrepancy between drawing & actual panel length | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620658&prj=626&rqi=4SKwDnt3a4MNqsBjje9wH4fLJp
YT1ELEC-162-001 | c8bc7d7a-a2cc-44bd-8c9b-f389897aa240 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1Fuel Leak_L3 | LEAK - Leak Detection |  |  | issue from L2A. permanent equipment labelling issue. attach photo once it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620650&prj=626&rqi=4OiGK7PbNpaR5Pvsxzy72Ax3uE
RT1ELEC-12-006 | aca32ae1-41cd-4d7f-9b47-608d3a69fee5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Panel surface need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620651&prj=626&rqi=tiRbX6ydxLnrOn0kXyYJIpACTG
RT1ELEC-12-005 | 7b139ae3-b017-4833-835b-4d1b20221516 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Dual Battery Charger) Please revise drawing to match with actual condition for panel door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620649&prj=626&rqi=FHLZWMLTkSqffptEinEAh1eAM2
RT1ELEC-12-008 | 33ccd730-293f-44ce-96ff-51feb3c3c867 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing and actual breaker size: - F5: 6A (actual 10A) - F6: 6A (actual 10A) - F7: 6A (actual 16A) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620655&prj=626&rqi=QKLqrisS153uS5lqLJkaxTKBnx
RT1FD-39-001 | a7246cb3-2a18-468e-8700-70b6274d2286 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-7.10 | VES - Vesda |  |  | Installation and Start-up Manual document need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620656&prj=626&rqi=WGuQWefz2uWMWB61IYl0oaI1py
YT1ELEC-128-001 | 72bc0a5a-7bbd-4405-8b0a-711cc3de23f6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1WLEAK_L2 | LEAK - Leak Detection |  |  | issue from L2A. permanent labelling equipment issue. attach photo if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620646&prj=626&rqi=qv1nu8d23qG24FFrwomHOApma9
RT1ELEC-12-007 | 8b75cedb-0b5f-4f12-a8bf-f98aa3cef2a2 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Missing bolt | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620653&prj=626&rqi=asMpSWvbK9XhO0m2sp7EJRRSgS
YT1ELEC-31-006 | ae404760-7050-4612-a7a0-ee75dce21866 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | DC power supply from external AC/DC converter polarity has not been verified yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620397&prj=626&rqi=6bAIM2ZFWF7zFwovsEDizRNpSI
RT1ELEC-155-002 | ca3ddded-0e00-4850-b1fa-6932fe2569a4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | (Issue Tx Room Area) Missing bonding jumper on cable containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620378&prj=626&rqi=nbjDaz8FWCko8xEQXkxtRZ4pn4
RT1ELEC-155-001 | dd9c55af-7e69-4d42-abe7-0428971cf37f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | (Issue Tx Room Area) Please confirm the new grounding cable tagging and ensure all grounding cable tagging is consistent as per standard. Kindly attach the latest grounding cable tagging standard document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620377&prj=626&rqi=FPpHeieym6sGAHxf7O0PwrO1ac
YT1ELEC-31-002 | 06f3eb83-c27f-44de-9f96-e5bb285f1cc5 | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | DCOS control cabling to panel 1LIBATTSYS_F_1 has not yet installed and terminated at Battery cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620392&prj=626&rqi=OHGew7SHJphXl4RUF2unxt6xT9
YT1ELEC-31-004 | 2b3c7817-45e5-438b-b2d6-c26241c7b44c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | External cable to the AC/DC converter has not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620395&prj=626&rqi=tA292xRnW8JLXJqKw8cL4tNEzH
RT1FD-13-001 | ee544415-a52e-411f-ad75-8ff1e1944b4a | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Fire Detection | equipment | ASDSP-3.10 | VES - Vesda |  |  | The equipment nameplate labels for ASDSP and PSU are incorrectly swapped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620479&prj=626&rqi=S8QJervBlDilLsjsltuXZ75CB5
RT1ELEC-155-003 | fbacae00-3631-4b5a-889b-2933413470fa | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Earthing_level_7 | ERTH - Earthing |  |  | (Issue Tx Room Area) Cable termination bolts are not in accordance with Equinix standard. No flat washer at the back side and no Belleville washer before the nut at the front side. If Belleville washer is not available, use spring washer. Please comply with Equinix standard, refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620379&prj=626&rqi=BdTkAUE3ROH11eB04clxmy30ni
YT1ELEC-31-001 | 3a810adc-3f8d-4459-8115-fd5bc81bced8 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | MCCB AUX 1 cable has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620389&prj=626&rqi=G1YASXzSZ4KQw8gLknW999maQ7
RT1ELEC-13-019 | e356921a-a2fd-4170-936c-0945af8cb5ab | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual position. Refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620384&prj=626&rqi=XmBtRK6pdoH8g4WZ7tAsceP1ya
YT1ELEC-31-005 | e90c9ffc-d19f-4692-adfe-938d94f5683c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Communication cable between Module 2 & Module 3 in panel 1LIBATTSYS_F_1 not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620396&prj=626&rqi=KVrKWVPE95hVOXLjbngrue4uQF
YT1ELEC-31-003 | e3bc9e1c-90c9-4b01-9232-c017938e6414 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | UPS temperature sensor has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620394&prj=626&rqi=ggQmDb3xQJ8r3goJPelkNTS1eU
YT1ELEC-32-002 | 500150cb-d466-442b-b6cc-e38122fbd3e3 | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | DCOS control cabling to panel 1LIBATTSYS_F_2 has not yet installed and terminated at Battery cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620399&prj=626&rqi=JDq53qdgJ1XIFvxfTH5kABUKcs
YT1ELEC-32-004 | 18012b2e-a3a3-4cff-a0ff-1f52ecd47dfe | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | External cable to the AC/DC converter has not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620401&prj=626&rqi=bC47ifXMu1fUK3vkgjkO1s84PP
YT1ELEC-32-005 | bc84119a-7a58-432d-97d9-ab8ad4dee7fc | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | DC power supply from external AC/DC converter polarity has not been verified yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620402&prj=626&rqi=bGoT7IWKVdRbxpgxZ0XrsdV9av
RT1ELEC-12-003 | f189d54d-1abe-4eea-9f7b-3de6a2b90d35 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620510&prj=626&rqi=rKVhJAjxNNLNp7Rd7VvQpd1S4j
YT1ELEC-32-003 | 0a8bc644-5aa0-4300-b670-622236d03336 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | UPS temperature sensor has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620400&prj=626&rqi=THkV4dTPYvYOJKkw3tsLxqaPqk
RT1ELEC-12-002 | 7e3d9cb7-95d1-4c9b-86eb-b5c12819db89 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual breaker size: - Q3: drawing 6A (actual 16A) - Q4: drawing 6A (actual 16A) - Q5: drawing 6A (actual 16A) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620509&prj=626&rqi=pLfitvhTjKinueTBgUCEfMUzhD
YT1ELEC-32-001 | 86952746-8433-40e5-96fc-af9dde20beae | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | MCCB AUX 1 cable has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620398&prj=626&rqi=gyhq33QhqFjYZ6phpeaoUCYp1r
RT1ELEC-12-004 | a83c1bde-9ad8-4ddc-8247-a7f9c1fa4c58 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Isolator) Discrepancy between drawing & actual position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620512&prj=626&rqi=NCb3p5wEi7D6nJSLymVtBFTtPy
RT1ELEC-13-020 | 7589cae3-cd12-4621-9624-257920984720 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A - 1GEN_D Panel Battery Isolator) Discrepancy between drawing & actual breaker capacity: - Breaker F3: 25A actual 10A - Breaker F4: 25A actual 10A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620385&prj=626&rqi=Hk3mbuXLIzWIwo9moXPcWL5Enz
RT1ELEC-13-018 | 4e3fb7c1-4cc3-4e79-9cf2-b33db4e1d69c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Missing cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620382&prj=626&rqi=ExhFtQTSlKAqav2OXG91KElHJn
RT1ELEC-149-013 | db0beec0-e5a7-40cc-a899-01b7330ec6d3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1MSB_C_1 to 1UPS_C_1) Busduct support is not aligned / tilted. Please adjust to ensure proper alignment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620380&prj=626&rqi=M7QwTRnOsgtFKuxV7zwZKua0s8
RT1ELEC-13-017 | 92dd9675-d299-4278-8c78-f9bf4b6f0e35 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual breaker capacity: - Breaker Q3: 6A actual 16A - Breaker Q4: 6A actual 16A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620381&prj=626&rqi=4rtKakar32NIDZL0Vt5cWlxP0k
RT1ELEC-54-003 | 6927b749-088d-47af-a42d-013a54912cad | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-03 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Missing bolt on back side panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620202&prj=626&rqi=200sxa7mJQKDNxn77pMydyTXcX
RT1ELEC-54-001 | c4142b23-fbb3-4bfc-ba90-6ffa6b27354c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-03 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Dents & scratches on panel surface observed, need touchup | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620200&prj=626&rqi=WKRkYKu4V74Ts1y8LJdVVtk1EC
RT1ELEC-54-005 | 2ef63a19-807f-4097-91b6-f8adc63867f6 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-05-03 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Discrepancy between drawing & actual position. Refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620204&prj=626&rqi=W2rAzviyeKD8l3Hh12rkp0wb7X
RT1ELEC-54-004 | 1ac9969d-60d7-4cbf-a113-43fb1436584c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Drawing not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620203&prj=626&rqi=DsxMhxuYuR4quLO78leMKsbRXM
RT1ELEC-54-002 | 84b7ce59-36de-48d5-88f2-6a02b4828f61 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-05-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_1 | STSSB - Static Transfer Switchboard |  |  | Please ensure all ACB & HMI are properly protected to prevent construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620201&prj=626&rqi=0hOfjeyVZDatIxV570mXeqvLk9
YT1MECH-108-004 | fec63f27-91eb-40ce-8ce4-036b1c0d77c2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) need to install vynil cable accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619970&prj=626&rqi=txEOj01bgzSBaJXzytyCGSlebi
RT1ELEC-158-004 | 79abaf99-82e9-42e0-a89b-2465bc0aa2de | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L4 | DB - Distribution Boards |  |  | Discrepancy between drawing & actual position for grounding & neutral location inside the panel (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619985&prj=626&rqi=QxUzTzYodlfOuPkMqnS11VCz5H
YT1MECH-109-002 | 890a212e-92c7-45f6-8be2-5cad9b8e3d30 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) need to install vynil cable accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619974&prj=626&rqi=q1XehFRj0K6Z9DBnfZ2UJ2V7RI
RT1ELEC-158-003 | 1c2d4072-f86f-4ae1-bf44-7e98d726845b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L4 | DB - Distribution Boards |  |  | Minor dents need to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619984&prj=626&rqi=1M1erq3XlsH3AUWuLB5O0n9r5r
RT1ELEC-158-002 | db0dac4b-31ee-41ef-b50a-44afc645e0c9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L4 | DB - Distribution Boards |  |  | Each component shall have two labels (terminal and component body). Proper component labelling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619983&prj=626&rqi=BorfMO5Pk8IOWSTCaxx2lLH0LG
YT1MECH-108-005 | 2ea2b6ee-c642-493b-af40-4db154ba8f32 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) provide cable label inside isolator switch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619971&prj=626&rqi=CiaTdjSGyBHPhkpvVVGGi31DHr
YT1MECH-109-001 | d02b80d7-c04c-44ed-a966-c186bb5cf1d2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) Ensure that the cable routing is uniform and consistent for all isolator switches, pay attention to cable neatness, disconnect cable which unused and isolated accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619973&prj=626&rqi=SWMtNwwxzDCIqD0OVloAJh9sqe
YT1MECH-108-007 | f49daccb-54b8-40c7-b33a-12f6495d9ee0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable AHF to Chiller Pump) provide vynil cable and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619979&prj=626&rqi=6v0zGfllzs0uHRLIIBNcLVUyzj
YT1MECH-108-006 | 5266d8e8-ca98-4a19-aeaf-6fccf58c04af | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) Ensure that the cable routing is uniform and consistent for all isolator switches, pay attention to cable neatness, disconnect cable which unused and isolated accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619972&prj=626&rqi=V1YQ9eruYV33ucsY9umMVWBhdC
YT1MECH-107-007 | dca3bc11-dcca-4e12-921d-7bfeb95a5d96 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable AHF to Chiller Pump) provide vynil cable and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619978&prj=626&rqi=2crMSIRlE2eqTwXo8PSG0MWmlG
YT1MECH-110-001 | f9c4313f-1927-4d73-9a28-1513d70289f3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable AHF to Chiller Pump) provide vynil cable and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619981&prj=626&rqi=o4vvigTVret9Yv5WEVsHgfsXvb
RT1ELEC-158-001 | 035ae222-8145-4820-be93-095d2a8f93db | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L4 | DB - Distribution Boards |  |  | Please confirm the correct equipment tagging as per design: 1DB_DALI_L4.1 or 1DB_DALI_L4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619982&prj=626&rqi=lpc2D9rwWQVcjLNBv6lGWUpccQ
YT1MECH-109-003 | cb387980-d5ad-4b0a-9a24-1370e1424a53 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) provide cable labelling inside iso switch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619975&prj=626&rqi=Roaf3cPXmUDY1FnFezANqMkDaH
YT1MECH-109-004 | 60cb5d16-20d9-4837-9c8d-c64f00b16a70 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable AHF to Chiller Pump) provide vynil cable and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619980&prj=626&rqi=bNHRGxrv7fiSzX4XQXMapN0cO5
YT1MECH-11-001 | 4092fc5e-ccab-4930-8289-f6dc817187fe | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1EF_C_54 | EF - Exhaust Fan |  |  | YT tagging status changed, some documents missing 1. Cx Report 2. Ducting visual inspection report 3. Grounding test report 4. O&M | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619827&prj=626&rqi=5oA1rs5FEQv9pYV9LmuWTPIz1V
RT1ELEC-14-016 | a144e714-a3fd-4ca4-a4a4-de2b782e084e | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy breaker size rating on Q3, Q4, Q5. In drawing 6A actual 16A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619836&prj=626&rqi=0fmz1Ttxt8NbFaeZlJnaa7cNO9
RT1ELEC-14-017 | 24fbaf19-71a8-4e67-9060-76aa1ea83538 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Please update drawing to match with actual door component location | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619837&prj=626&rqi=FuwHGOrFrthqHD0x8EGtcA9o2N
RT1ELEC-14-013 | 1948097d-6505-457d-bc74-87da6a48922f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Isolator) Please provide drawing pocket & as built drawing in panel door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619829&prj=626&rqi=2OCIzcIy3i7tmA8eZnyUqwzwZs
YT1MECH-13-001 | 59dc783d-1522-4a42-9834-3b2d55caabfe | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | YT tagging status changed, some documents missing 1. Cx Report 2. Ducting visual inspection report 3. Grounding test report 4. O&M | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619826&prj=626&rqi=g4Xt3jSYJA8l5PHzP4TzuuQZ65
YT1MECH-30-002 | 671009c0-7a85-40df-a520-40ab24b15e35 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | inside the rusty chiller pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619860&prj=626&rqi=FaLdDpiGRp4bEzrQGIGem776Tj
YT1MECH-28-004 | c90af5ac-2102-47e6-8f7b-cad423694856 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | inside the rusty chiller pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619859&prj=626&rqi=brl4l7DpFozAZ8JbJNV8BZupnE
YT1MECH-107-005 | a50004ec-f165-4839-b337-f8738787bd1d | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) need to install labelling inside isolator switch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619845&prj=626&rqi=O13BENiaHkAaLLRmZIwwG3g9OS
YT1MECH-29-001 | 05b632d2-18b8-41ce-a737-1b83c5037e4e | JK01-2 | 626 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | inside the rusty chiller pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619861&prj=626&rqi=GurgZtdWJze4eJiAvLkOEqpKSz
RT1ELEC-14-014 | 1bb9404f-2259-4125-88d8-fe3c707dad33 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Isolator) Please provide protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619830&prj=626&rqi=fW3bm1TA06dUoydWYj8DimZCRt
RT1ELEC-122-006 | 670930d9-6382-4c9f-b426-5432fa36653b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | Cable tubing/tagging faded need to replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619812&prj=626&rqi=6yG0DBnGitXr1ue4slm8n6AMJ9
YT1MECH-107-004 | f4f5fe6d-4785-4df7-93c4-dedc123f800f | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) need to install vynil cable accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619841&prj=626&rqi=F3M2tCKGBBdO6JtqMoUJCfo3yq
YT1MECH-107-006 | d366449e-e91d-4099-ab92-7248cfdb630f | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | (issue cable from isolator switch to Panel AHF) Ensure that the cable routing is uniform and consistent for all isolator switches, pay attention to cable neatness, disconnect cable which unused and isolated accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619847&prj=626&rqi=3Y4PzIW37FB5jX2WFo1T7qN2i8
YT1MECH-30-001 | 95c975e5-3d48-45d0-8836-37e3fbfc4ab6 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | inside the rusty chiller pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619852&prj=626&rqi=cpZavtBVL1PL42CYllV7uEOK6T
YT1MECH-14-001 | 6beb0d03-cbae-49e0-90e1-b3fa96cb5130 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1EF_D_53 | EF - Exhaust Fan |  |  | YT tagging status changed, some documents missing 1. Cx Report 2. Ducting visual inspection report 3. Grounding test report 4. O&M | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619821&prj=626&rqi=N9thEZ8s1nar3M7CaipTfyu7St
YT1MECH-10-001 | 422afa5f-4988-4d6a-ba48-c863b1a67943 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1EF_C_53 | EF - Exhaust Fan |  |  | YT tagging status changed, some documents missing 1. Cx Report 2. Ducting visual inspection report 3. Grounding test report 4. O&M | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619825&prj=626&rqi=411sw0Qo3OxqEShcEwxCjw7tHj
RT1ELEC-14-015 | 78c8774a-60b3-47c5-b8f7-7adaf9f86905 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel DB Aux) Discrepancy between drawing & actual position. Refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619834&prj=626&rqi=sur81hdkGuRNT66I7eb4Sqad3B
YT1MECH-31-002 | 2b8c2ec8-f290-4cf1-8c58-a24127c56a41 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | inside the rusty chiller pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619855&prj=626&rqi=jmVtHzhSeHpb3MaYGUakmni1aQ
RT1ELEC-157-001 | 09208a84-552f-4a36-b81f-6b2cf0ca3fcc | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L3 | DB - Distribution Boards |  |  | Discrepancy between drawing & actual position. Refer to the attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619682&prj=626&rqi=LUMWbpppLzccVVS6sWH3Wx31Jl
YT1ELEC-164-003 | 298249f3-d9e1-4513-b337-144a154695fe | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | (Issue CxL2A LV Cable) Several cable tags are mismatched (should be labeled as CA_B_1 but tagged as CA_B_2). Kindly recheck all and correct accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619666&prj=626&rqi=pZNRF4S4oaQgV21ZJBRYY3lRrq
YT1ELEC-142-001 | 391fdfcc-8024-4bf0-9c49-062b7d2bef98 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_2 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue CxL2A BD 1UDP_B_2 to 1STSSB_B_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619663&prj=626&rqi=ULh7JBqFz56YjsM42IcaHvWUij
RT1ELEC-157-002 | 732fa4f1-a9e8-4411-b88e-6537ad25cb21 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L3 | DB - Distribution Boards |  |  | Each component shall have two labels (terminal & component body). Proper labelling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619685&prj=626&rqi=JUmNAuTYuwEIhdOHtkhXZaUHdm
RT1ELEC-157-003 | 906991f9-cda6-4685-a5f0-b50df234a120 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L3 | DB - Distribution Boards |  |  | Please confirm the correct equipment tagging as per design: 1DB_DALI_L3.1 or 1DB_DALI_L3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619686&prj=626&rqi=jJT7P2CAOKgqUDvrRldyx8DZss
YT1ELEC-164-002 | 5b940219-32e8-474a-b0bf-bc704d1ec865 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | (Issue CxL2A LV Cable) Incorrect cable tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619665&prj=626&rqi=9dj7NTV17BXm42XMvk3q0f0pyW
YT1ELEC-164-001 | e0c927ed-04be-4714-b444-7a126a6cdd42 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | (Issue CxL2A LV Cable) Cable conductor is still exposed. Please ensure proper termination is completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619664&prj=626&rqi=qj2uQW2rIiir3es18l1Ppi39Xj
YT1ELEC-164-004 | a309a973-06ef-4a40-936a-ab8c80f01a00 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | (Issue CxL2A LV Cable) Bolt supports have not been properly tightened & unistrut support is found cut. Please adjust to match other unistrut installations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619667&prj=626&rqi=Q35z9DIff07JC2eDVZO3gQehH0
YT1ELEC-143-002 | 1ace8892-b017-4b60-bff0-861fd409d045 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue CxL2A BD MLTX_D to MSB_D) Sleeve and firestop at wall penetration are not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619558&prj=626&rqi=GggZLyWzmvFMnRGTITh0O2OFhI
YT1MECH-42-001 | aecac9e9-a257-468b-8024-20030642568a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_08 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tray end sections are open. Please confirm and install end caps where required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619670&prj=626&rqi=1WVoa0kM7MOKmuXrmVxbLYrpkh
YT1ELEC-143-003 | 35c862e6-f1cb-45a8-89aa-cedc8b060c02 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue CxL2A BD 1UDP_D_2 to 1STSSB_D_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619560&prj=626&rqi=69Q1LrXEMTTG6k3lPxUc2veVtQ
RT1ELEC-122-004 | d9eea2c5-2f28-4b55-8d95-18be40881a60 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Please remove all temporary markings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619672&prj=626&rqi=Pq2C16SCFJHJEEsmmrKWsEDzv4
YT1ELEC-164-005 | 55669ae3-5d59-4a9e-9e18-5b11030666c0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | (Issue CxL2A LV Cable) Several cable gland caps are damaged (torn) and not properly covering the gland. Replace all damaged gland caps and ensure proper installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619671&prj=626&rqi=Dsnv8MAulip3Ere2PLG70SFYYy
RT1ELEC-122-005 | ca38f938-03c0-4cc9-9722-0233c3086173 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Several cable gland caps are damaged (torn) and not properly covering the gland. Replace all damaged gland caps and ensure proper installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619673&prj=626&rqi=9PM0O3NvRJHw6Lq1N49TVJQl0R
YT1ELEC-143-001 | 60c68e14-d6a4-48f1-bf48-799170194a35 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue from CxL2A BD 1UDP_C_2 to 1STSSB_C_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619542&prj=626&rqi=UFFh6iMP88z8BKBmNWa5lcBGzG
YT1MECH-36-001 | ba234da6-2017-4573-bc97-c91393f01a79 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-27 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CA_B_01 | CA - Cool Array |  |  | (Issue CxL2A LV Cable) Cable tray covers are not yet installed. Please ensure all covers are properly closed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619668&prj=626&rqi=kGNYMtmWCIb7oyG755856YBYif
YT1MECH-17-002 | 4d88e219-609e-4cc7-b1c0-42e5436441e0 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1EF_F_74 | EF - Exhaust Fan |  |  | Provide calibration certificate of test tool used for CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619465&prj=626&rqi=WWa9MxVgSDJomvAwugksG9Rfch
YT1MECH-7-002 | ecd7049e-4fdd-41e4-9bab-65eb749e04e8 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_31 | EF - Exhaust Fan |  |  | Upload calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619459&prj=626&rqi=DmA9cRGMBTUsuxKmPB7B7QaHSK
YT1MECH-8-002 | e69d064d-9cac-4f57-9cd4-0d7166c066f6 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_32 | EF - Exhaust Fan |  |  | Provide calibration certificate of test tools been used in CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619460&prj=626&rqi=k47ridBnwuzjikbjGpVgO6PKNZ
RT1DCOS-15-002 | 955a7781-3b30-4f59-a9d7-f181fd8e88cb | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_1_SCP_07 | DCOS - Control Panels |  |  | Provide MoS CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619477&prj=626&rqi=REpvEtILb45YKtKgdK7l2rfRxh
YT1MECH-8-001 | 6f3e7943-c80f-468f-b8d5-8b3deaaf5fa4 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_32 | EF - Exhaust Fan |  |  | Provide MoS CxL3 doc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619458&prj=626&rqi=BEHz94mbKugUVn9npwLMk9qoZd
RT1DCOS-15-001 | ce6c18d8-95d8-46e9-8cd7-c25806ce62b4 | JK01-2 | 626 | APAC | Closed | P3 Low DCOS | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Controls | equipment | 1DCOS_1_SCP_07 | DCOS - Control Panels |  |  | Please add label for incoming power source | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619475&prj=626&rqi=dApFcbUcZEV4waOfy8QnVruIch
YT1MECH-7-001 | 3cf749ee-8b3e-4b35-8c97-c556dbb1e114 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_31 | EF - Exhaust Fan |  |  | Provide MoS CxL3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619457&prj=626&rqi=uQicic0sm1jWAnAsiH4328NtaG
YT1MECH-17-001 | 8dd18702-3c4a-4733-8a81-ee0a4022cc29 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1EF_F_74 | EF - Exhaust Fan |  |  | Provide MoS CxL3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619464&prj=626&rqi=ktveLdlTEweJl9tLYZmAVEDzGP
YT1MECH-16-001 | 1568db2d-f4da-478a-8b7a-fcc5dd430b6a | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-26 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | Provide calibration certificate of test tools been used for CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619462&prj=626&rqi=SC0qeZ8xerWO0vIhlFLrFNLPjR
YT1ELEC-10-002 | 6909209c-3fd3-47ac-a136-159b38bb20c6 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | MCCB Q1-4 long time trip test result indicates a failure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619281&prj=626&rqi=WyJft7StvcJ4rPND3MCHcNwsTl
YT1ELEC-10-001 | 5fafe1a3-c23d-4879-9141-d35a7148b99a | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Short time protection test for breakers Q1â€“3 was skipped during testing. Kindly perform the required test to verify proper protection functionality | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619280&prj=626&rqi=wzotoSF3vKHSXGQgSAL4ST0QE0
YT1ELEC-10-003 | 1a607b29-2efa-4167-83f6-525ed6002109 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Input/Output PLC verification test has not yet been conducted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619282&prj=626&rqi=kPWIoWdOjhEznUYvAjYOG8LJSI
RT1ELEC-148-003 | f69e594f-df4e-4ebb-8851-092b6f18b7f8 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_2 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1UPS_B_1 to 1UDP_B_2) Laser measurement shows about 15 mm elevation difference (not level). Please adjust to make it straight and level. Refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619292&prj=626&rqi=WwNgxeIohZAhYCiLE6aHOxEk12
RT1ELEC-148-004 | cd51377c-fb7f-4300-8a1f-99e8cdeb2f33 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-23 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_2 | BUST - Bus Duct Temperature Monitoring |  |  | [Issue BD 1UPS_B_1 to 1UDP_B_2] Please clarify with engineering, busduct support location different from the drawing. Confirm if this is approved and safe? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619293&prj=626&rqi=cBi5Req7O7nCUNUNPs3aPUafWw
YT1MECH-111-003 | be427240-ad93-4079-bfcd-a665f0b83ba8 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | JulianJensen@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_2.01 (Existing) | PAV - Pre-Action Valve |  |  | Pressure drop during pipe hydrostatic pressure test (STS Room B & C-Wall B). Refer to the attached image. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619170&prj=626&rqi=m2tvq2cAuK60gibhzn8SRIPaeW
YT1MECH-18-002 | 0974bee2-877c-44ea-9ffc-1e6023b6dd93 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | Provide as built drawing because there was discrepancy between shop drawing and actual layout | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619171&prj=626&rqi=Ht9oCagv4J4TGt9qjFICfFGYrh
GI-018 | 576275dd-6ac1-480b-8b77-ba3b963595ce | JK01-2 | 626 | APAC | Open | P3 Low DCOS | dickyhermawan@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS | [7 empty] | Configuration "Asset Data" is currently in progress by DCOS program Orise. After finish need to verify with CTA Note: - The Maximo asset data from GC has been completed, and Orise has confirmed that the data is complete, except for the ID numbers, which will be provided by the Ops Equinix team. FG GC issue GI-016 (Closed) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619210&prj=626&rqi=dpvd7YhiGNDMX1RRgErlpkb6CA
RT1ELEC-15-012 | dd881299-e5c4-4017-909d-23fc023ca9f9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add clear labels for ammeter and battery to show which one is Battery 1 and Battery 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619050&prj=626&rqi=4aVFbGw7CGhkcQRowkT887LRvC
RT1ELEC-15-010 | bccb0f7f-10ab-4e11-afe8-e85ee5298d15 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Drawing and actual panel are not the same: location of voltage and ammeter is different. Please update the drawing to match actual condition | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619047&prj=626&rqi=HwEVnDYHtU6SyP958fEFdNSds0
RT1ELEC-15-013 | 18fdf9e8-d2e6-4de5-8579-af3ad8ac5554 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add component RSH1 & RSH2 in the drawing component list | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619051&prj=626&rqi=3RECA8YbXS9J2Vjq1wh0stw1wK
RT1ELEC-15-002 | 50ee866c-33fc-4d58-9069-bfbe7ced531c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Rear anchor bolts have not been torque tightened | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619020&prj=626&rqi=J7IxdEzH2WeD9UYjmoDMuwpXZL
RT1FD-3-002 | 554758c6-459f-400a-bfd9-6c00838ebb6f | JK01-2 | 626 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | 1FAS_4 | FP - Fire Panel |  |  | Cable tagging not installed. Refer to the attached image. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618997&prj=626&rqi=bidGiPj6obqN46p3ICuI3Pjqqt
RT1ELEC-15-004 | 5381e2f9-a472-4484-b50d-959971ef31c0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Minor dent found on panel surface, please touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619022&prj=626&rqi=XjaQhjQ6RI3ONjrSA2sG7poOnk
RT1ELEC-15-005 | 33c65cbe-b366-4474-8ec6-b1ea7d60ed83 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Drawing not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619023&prj=626&rqi=RxGBiY1tjbqp9omszfbVttvpAg
RT1FD-3-001 | 2f4ef4e1-74d2-41da-ad6d-5c7521a64110 | JK01-2 | 626 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Fire Detection | equipment | 1FAS_4 | FP - Fire Panel |  |  | Spilled white paint on Fire Alarm and the cable cover pipe. Refer to the attached images. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618994&prj=626&rqi=ErqaxDsmMB8nmutAJEl1iBpFpm
RT1ELEC-15-001 | 5a60b639-5944-48bd-8ee3-a48e11b68c6c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Incorrect generator rating at panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619019&prj=626&rqi=HqWe4QhN87FkqdyV4Ivy0nzWK9
RT1ELEC-15-006 | 66890811-cfeb-45f5-8976-a4793dda8d49 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Incorrect generator rating on the drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619030&prj=626&rqi=6dGQCDFdn39HFnF3MpVxxrS3Ur
RT1ELEC-15-011 | a16834ef-4d90-413a-8b20-094e297cfd37 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add labels above pilot lamps for â€œBattery Charger 1â€ and â€œBattery Charger 2â€ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619049&prj=626&rqi=RAejLFXLpbl5k7fAuZAqXmBBpa
RT1ELEC-15-003 | ff99e471-dcbb-4d02-9d9e-edd2d5ec98fa | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Missing bolt on the panel body | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619021&prj=626&rqi=nZjkWbgTeFh5DJnfQubmD2VMTg
RT1ELEC-15-009 | bace1b26-951d-4e16-9978-25c91c2e7316 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A GPC Panel) Please add temporary protection to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619044&prj=626&rqi=NMlEsINt3rJQ1HPuIixxcbqYtF
RT1ELEC-15-014 | 9b7250cc-ffbc-49eb-b029-f5b1e5042444 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Cable entry/exit location is not in accordance with the approved drawing. As per drawing, cable routing shall be from the bottom of the panel. However, actual installation is from the top of the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619053&prj=626&rqi=BFZA1lIa1OA2IUMLww8DejLJNL
RT1MECH-131-001 | 4b57b031-8675-41eb-b84a-5bc1db250885 | JK01-2 | 626 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_2.01 (Existing) | PAV - Pre-Action Valve |  |  | Pipe has white paint residue. Refer to the attached image. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618991&prj=626&rqi=d9tf2DjvZ4TJGJPw4CyiBe6qQ6
RT1ELEC-15-015 | 13b909fd-d506-4ebe-b5d9-4b1b91fe739e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add temporary protection to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619054&prj=626&rqi=tlk7H4jFjuYWqoEFLGA8yiKnsP
RT1ELEC-15-007 | 656b2fff-2659-4406-b7a4-3bcfb805c382 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Discrepancy between drawing and actual breaker capacity: - Breaker F7: 6A (actual 16A) - Breaker F5: 5A (actual 10A) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619033&prj=626&rqi=d9YTJaC1tmCco8pCiwo8uhOwf3
RT1ELEC-15-008 | 2d0904a2-ef03-4e71-963d-cfd4927ba7b5 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_F | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Based on the RFIT inspection results, a discrepancy was identified between the drawing and the actual panel position (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619036&prj=626&rqi=NShb6Qquxrpg67RywE4L4Fk6G5
YT1ELEC-29-005 | fcca6175-2f0e-4080-bddf-b10cf751079f | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | External cable to the AC/DC converter has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618837&prj=626&rqi=UVNMKScAZN4e9SuGQpO3VGzbsx
RT1ELEC-134-001 | 8d3a89b8-e7ae-4584-bb5b-0c8d490316f4 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1WLEAK_L2 | LEAK - Leak Detection |  |  | need to upload document shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618810&prj=626&rqi=Hj0glqrARtOWXYiWvnUBETBk7G
YT1ELEC-30-003 | ab0b1784-5e9f-4ca3-9b2b-5470d01f6643 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | UPS temperature sensor has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618847&prj=626&rqi=QZOc1OxXfXG7WhV4vaPSfTTPvl
RT1ELEC-168-001 | 909cd3a8-5a15-441f-9b4a-20dc13aa7b25 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1Fuel Leak_L3 | LEAK - Leak Detection |  |  | document related need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618812&prj=626&rqi=SQrDLI1nOnK4zYDTPIBNOGY8sb
YT1ELEC-29-003 | b541bff9-a8bc-4aa1-99eb-3fe8aabd4688 | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | DCOS control cabling to panel 1LIBATTSYS_C_1 has not yet been installed and terminated at Battery Cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618835&prj=626&rqi=A2ZKiGwuGmFdaZhQda68GhzlMh
YT1ELEC-29-002 | 2bf939c3-a5f1-4f68-85f5-38167f044e90 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | MCCB AUX 1 cable has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618834&prj=626&rqi=wZuFw5YFnlPoGpdiP6AvVmLUzj
YT1ELEC-29-004 | 06f07186-a935-4a98-8efd-5d1f02643e2f | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | UPS temperature sensor has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618836&prj=626&rqi=vt46YICWnrQV5LwLZDKvKD8Dpq
YT1ELEC-29-001 | 96d6014c-2d84-46db-8a11-906ca65d6fa3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | There is dust inside the battery rack. Refer to the attached image. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618832&prj=626&rqi=c1CKpRhWRWP0UucDixEwIcDi9Y
YT1ELEC-29-006 | 818c603d-fd93-476b-95a9-8784f34f2693 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Communication cable between Module 2 and Module 3 in panel 1LIBATTSYS_C_1 has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618839&prj=626&rqi=plMGvQkP0hJ4cVMHilURTh2fmz
RT1ELEC-134-002 | 89a186b1-0d4f-4be7-97fd-763531a621d7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1WLEAK_L2 | LEAK - Leak Detection |  |  | permanent equipment labelling issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618811&prj=626&rqi=evhCL6H97OqDX9erQkvHeHp3lU
YT1ELEC-30-001 | b7c73e47-2237-432d-8227-f01940cec4da | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | MCCB AUX 1 cable has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618843&prj=626&rqi=7zhEdUbrVrSLdmnPg60a22cZ44
YT1ELEC-30-002 | e478d269-9180-49ab-96ad-1e96921d419a | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | DCOS control cabling to panel 1LIBATTSYS_C_2 has not yet been installed and terminated at Battery Cabinet 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618845&prj=626&rqi=8WOLreerfLOM4UwGp81Cyj7gIV
RT1ELEC-168-002 | 3da8e371-a210-4833-b7d9-7cd05d3f988e | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1Fuel Leak_L3 | LEAK - Leak Detection |  |  | Permanent equipment nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618813&prj=626&rqi=yI0kYrNjGVHtjplkYQbRBsfjy2
YT1ELEC-30-004 | f541229c-efbf-41cf-b689-075cd69f8510 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-20 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | External cable to the AC/DC converter has not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618848&prj=626&rqi=NHrXwiXjAEJNIGrsTmmEDdOs4g
YT1FD-25-002 | cd3276a3-778c-420c-900d-cc1190be52eb | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-5.03 | VES - Vesda |  |  | issue and document report L2A need to comply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618684&prj=626&rqi=Q1l6zpkfPqi4gMR10HkLWqErF7
YT1MECH-28-003 | f99ca6f4-a7fd-4924-8cdb-e0e7d04136c4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Plastic cover not installed. Refer to the attached image. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618730&prj=626&rqi=H5APs8SMgQra20ypuJfZC1aiyU
RT1ELEC-1-022 | 547fadc8-abbb-4261-836e-c2c2cd2ebe10 | JK01-2 | 626 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (BTU Issue); Missing washers on cover panel. Refer to the attached images. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618709&prj=626&rqi=2nWorLS4gQN1kuThcUy0VGf9jF
RT1MECH-12-002 | f0a248ec-f916-49c2-95a0-cca0ea02cc3a | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1EF_D_41 | EF - Exhaust Fan |  |  | need to upload related document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618703&prj=626&rqi=DodBmXzKDM7NFq8vcZseAOjqT2
YT1FD-24-001 | 24a6bf99-6278-4b52-bf8a-83d18fcf0ebc | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-5.02 | VES - Vesda |  |  | related documents need to upload on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618678&prj=626&rqi=PZuz9uXIqN4Yl3CQt128eIJbyp
YT1MECH-28-002 | 06683636-ce63-4fd2-b34d-d177df93c7ac | JK01-2 | 626 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Paint is not smooth. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618729&prj=626&rqi=xpKptxSorJOBVKJydTiyuJWh6N
RT1FD-25-002 | 8b33aca7-7728-4df1-9ec4-eb4dc89570de | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-5.03 | VES - Vesda |  |  | report L2A need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618682&prj=626&rqi=hVSglQ8DL9kLc3Cg5SsBwq3DSy
YT1FD-29-001 | 2cce88a1-18c2-4109-964a-a5aaea603b29 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-5.08 | VES - Vesda |  |  | L2A issue and report document need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618691&prj=626&rqi=Piq9FKOpDYLvwkWaDpE8iuLirF
RT1MECH-9-003 | 374a1a6b-e1c2-411a-9ee5-5bb1cb052a31 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | provide airflow direction | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618700&prj=626&rqi=EsM1U166uCqAH2SqpCqOskbqfL
RT1MECH-12-001 | d264dbac-b178-495c-9348-07fcdc70220b | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1EF_D_41 | EF - Exhaust Fan |  |  | vibration mounting need to adjust because it's not straight | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618702&prj=626&rqi=I7b6YeMt4kGIE9rCEThBQKfO0W
RT1MECH-9-002 | faf75cb6-64b1-44fc-915f-876d6ff610f7 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | Exhaust Fan ducting not connected yet to the opening wall and Wall Penetration not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618697&prj=626&rqi=Spe1Z4pWigXi10P8VnUtGnnMCc
RT1FD-24-002 | d40a6036-b0cf-4600-9995-ce07462c23cc | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-5.02 | VES - Vesda |  |  | issue and report document L2A need to comply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618680&prj=626&rqi=UHe4C32hOwzB1DIpizFPEErXyk
YT1FD-27-001 | 144ddcb4-734d-40e3-8cde-a58e713d05d5 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-5.05 | VES - Vesda |  |  | document related need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618687&prj=626&rqi=VApZhWsbOMOn4BvmkLimaGXoo9
YT1ELEC-4-002 | 6067a21b-07fc-4b8c-852f-5496d1236ef3 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Control cable signal testing for alarm and trip contacts cannot be performed. GC to confirm the cable routing and termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618718&prj=626&rqi=oq3jXXpc1kbpMZNtToZK9xie4r
YT1ELEC-2-003 | 2ae8c96e-e929-4586-94c0-2c750902e100 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Simulated trip from thermal relay to VCB cannot be performed due to incorrect wiring. GC to rectify the control wiring between MLTX and RMU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618720&prj=626&rqi=3rzbzVYvEWm9lI26jpzOF2kXeJ
YT1ELEC-2-001 | 214b848a-a4db-4bd1-9018-153aadfd0ffe | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Point to point testing for earth cables cannot be performed as the grounding cables have not yet been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618713&prj=626&rqi=bAx0IKt7PUhQm5ikGqWR53RSkM
YT1ELEC-5-006 | c29da558-ad20-445a-a43b-cc5f42f9a221 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Control cable signal testing for alarm and trip contacts cannot be performed. GC to confirm the cable routing and termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618719&prj=626&rqi=ZITPKDjYHSGVQIg5W1ctNZHPWT
YT1FD-28-002 | 9619473b-3a87-417e-9ca9-e5985eaf992c | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-5.07 | VES - Vesda |  |  | L2A issue and report document need to comply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618690&prj=626&rqi=nOWUzfrfe9OqhShHfeM6cunZ9j
YT1FD-27-002 | a5ae2f99-7083-4c31-af26-9a69173bdf54 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-5.05 | VES - Vesda |  |  | L2A reports and issue need to close and comply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618688&prj=626&rqi=WC76oU7Py0BhFi4VdrXWgYOqS9
YT1ELEC-2-002 | 51e4ecb2-18e6-4977-a733-f9a71197db9e | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Control cable signal testing for alarm and trip contacts cannot be carried out. GC to confirm the cable routing and termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618714&prj=626&rqi=WcerjAxtLvBIobRzGRvHXNU8GJ
RT1MECH-12-003 | 69c00765-97c8-4afa-acc3-feca9433136d | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1EF_D_41 | EF - Exhaust Fan |  |  | Exhaust Fan ducting not connected yet to opening and wall penetration not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618704&prj=626&rqi=wdlgRsV3HtCX7ESlFnpzKmf5dy
RT1MECH-9-001 | e48bb19f-ce6a-42c0-a1cb-53814174d662 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1EF_C_41 | EF - Exhaust Fan |  |  | need to upload related documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618696&prj=626&rqi=KYgYQEJ0q39gijuafdndGymvgQ
YT1FD-29-002 | 0e888c81-d5ed-4b09-89f6-27ced6f1a775 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-5.08 | VES - Vesda |  |  | related documents need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618693&prj=626&rqi=bRCAEOSa4tq25hjI9dWahhLXuQ
YT1FD-26-002 | 5cb374a2-4c82-4564-9c16-37ec1e2de31b | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-5.04 | VES - Vesda |  |  | issue and L2A report need to close and comply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618686&prj=626&rqi=WKBStc0nhaNx1dQlpn7jiIAVS0
YT1ELEC-3-003 | b5caafb2-7619-45e1-a7ac-fde556277f06 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Control cable signal testing for alarm and trip contacts cannot be performed. GC to confirm the cable routing and termination | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618717&prj=626&rqi=kVLVtRY14RawUtnvmUDAItT8gN
YT1FD-25-001 | 02044595-55b4-476b-b674-818427d29afa | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-5.03 | VES - Vesda |  |  | related documents need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618683&prj=626&rqi=SwIbo87QTYJqCjzGS2X0PJ4iZK
RT1MECH-12-004 | 8cc35006-7b43-4190-8fcf-75b947eeb282 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1EF_D_41 | EF - Exhaust Fan |  |  | provide airflow direction | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618705&prj=626&rqi=8aJYvH1p7spe2pVDNNWTORbYcb
YT1FD-26-001 | 5a44e685-e519-4396-a9b8-4b0fc7843174 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-5.04 | VES - Vesda |  |  | related documents need to upload on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618685&prj=626&rqi=VJWT5wjsihKUo5sViBbMT9VBoQ
YT1MECH-28-001 | 11711f42-e837-4934-8078-c87f828081af | JK01-2 | 626 | APAC | Closed | P3 Low CX | JulianJensen@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | General Contractor | L2B | Cleaning | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Chiller side panel is dirty. Refer to the attached image | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618728&prj=626&rqi=veSNopFwJp0NDQP1s8tpvHSF8r
YT1FD-28-001 | 2b35f478-ffb5-497d-b653-e04adfd03917 | JK01-2 | 626 | APAC | Closed | Outstanding Paperwork/Documentation | DimasKurniawan@commtechasia.com | 2026-04-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Component/Equipment Failure | Commissioning |  | Fire Detection | equipment | ASDSP-5.07 | VES - Vesda |  |  | related documents need to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618689&prj=626&rqi=cgAzc0kgl0fJTgi1lidUamiWYS
RT1ELEC-13-013 | bde89c19-5f7e-4f41-9b69-f9bcd1542225 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add clear labels for ammeter and battery to show which one is Battery 1 and Battery 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618659&prj=626&rqi=QLDCsAcfCVRxFiSU9xIFC8hXmV
RT1ELEC-159-006 | 05961aba-dc03-4797-a3bd-8c22df650029 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Please confirm the required torque value for the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618633&prj=626&rqi=knpVXEmEw0Uls0QrLpeXPFMpUL
RT1ELEC-13-009 | f30a6b36-0fbf-48d5-9d2c-0066bccd6194 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Length of panel actual 1480mm, please revise drawing panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618655&prj=626&rqi=7FmEVGwqGkoQ1244Lvsq0rQ6B1
RT1ELEC-161-005 | 4864c03e-54d0-4748-a274-e9f10f8bfb18 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Internal panel bolts are still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618622&prj=626&rqi=JLwWXUYKm6O1oUL9cQYmGBkZO8
RT1ELEC-13-010 | d3a02f88-6f61-4d57-8ddf-17fa0d6dd55e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Please provide temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618656&prj=626&rqi=vOOk2tG2LhOB6tPvMmXzFnJbMo
RT1ELEC-161-006 | 5e340a24-5ba2-45c9-af8d-0ed576b6df8a | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Please confirm the required torque value for the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618623&prj=626&rqi=e3pDvY9PqedWq0CHhKtEtkzVey
RT1ELEC-13-005 | 7f4344ff-75f5-4b00-9698-86e3d1fdec99 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Acrylic panel broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618651&prj=626&rqi=qGAUPRVU9E70CY0dMFoJR1MDP8
RT1ELEC-13-002 | 27e525e7-de0b-417d-8ac0-bfb79a044987 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Dirt and dents found on panel surface, please clean and perform touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618648&prj=626&rqi=6vs86oGZRDmhHJgKCP0q5ei72S
RT1ELEC-13-011 | 80a8a5c4-d74b-4a46-8dab-b150b41ab96d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Drawing and actual panel are not the same: location of voltage and ammeter is different. Please update the drawing to match actual condition | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618657&prj=626&rqi=FELZLH28sxIhkMPFUrMWUMclxG
RT1ELEC-13-015 | 4e9d7aaf-2ca8-4c6c-87d0-e665756aad86 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) GC please clarify why the positions of DB Aux panel and Dual Battery Charger panel are swapped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618661&prj=626&rqi=v5Sf0XjIfSc1sQKU2B1rWRRnsL
RT1ELEC-159-003 | d6c94b84-5a8f-4226-9f0d-389e684263df | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Each component shall have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618630&prj=626&rqi=4dbs4Fseyq3XWT7US3fdCC0TSU
RT1ELEC-156-002 | 505db69f-710d-4d83-b569-2583fb8eadf8 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Please confirm the correct equipment tagging as per design: 1DB_DALI_L2.1 or 1DB_DALI_L2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618637&prj=626&rqi=GtYhCZpdCmGjnpq2QUNNaDIrF0
RT1ELEC-161-009 | a64691f0-aa12-4032-9bec-30c2f2512e28 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Please provide temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618626&prj=626&rqi=hWqdGA9RsOiq9g0nA1AR2MqV3z
RT1ELEC-13-006 | 70fa769f-62f1-42c3-8ace-2ffb75916b7c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Incorrect label of capacity generator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618652&prj=626&rqi=8ceyo2r8Xj2AMeV4BFksN0uWRI
RT1ELEC-13-016 | 9d4fc873-b166-4906-b852-e19b60a3a46d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please provide temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618662&prj=626&rqi=iKQgQhOCEWLkqHLlj2caJr6fdc
RT1ELEC-13-008 | 58707752-4ba1-45e3-9cfe-0647ad958280 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Discrepancy between drawing and actual panel position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618654&prj=626&rqi=u8wgofzMVfclbsF5xV1BqwYpXY
RT1ELEC-161-001 | 05c84f40-7c0f-499d-905e-5ed042845e90 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Please upload factory test data document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618618&prj=626&rqi=vqJkFwQSqkthLwXZbsMmSms61Z
RT1ELEC-13-007 | 4a918404-1252-4e91-a531-fe255062ef3a | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Rear anchor bolts have not been torque tightened | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618653&prj=626&rqi=AOHWupB0C9LYzweCN7MnpgfEgw
RT1ELEC-161-008 | b1505a5a-0d43-4dcc-bb81-767b7c7788f6 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | There is a discrepancy between the drawing and the actual installation position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618625&prj=626&rqi=Tr1gLL6I3Ja1y7T37hK3OTPWCW
RT1ELEC-159-002 | 6643f54d-1f3d-4560-bdbd-f00ffd79e33b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Please confirm the correct equipment tagging as per design: 1DB_DALI_L5.1 or 1DB_DALI_L5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618629&prj=626&rqi=hEqxCdRo7B8iucqesMv3FSOMz1
RT1ELEC-13-003 | fe5f5881-1bfb-458b-b8b4-927e2c2db4c8 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Missing bolts on the panel body | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618649&prj=626&rqi=7vhzCY7kFbuUVd6v3FoWf6gSgG
RT1ELEC-161-003 | 53f7a7db-445a-4295-9225-343658b589c4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Each component shall have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618620&prj=626&rqi=VXnlZMlS3IFvRdrf4KZz5Da9iZ
RT1ELEC-13-012 | e9a3f646-2d15-49cb-a5e4-8dc6e35971cd | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add labels above pilot lamps for â€œBattery Charger 1â€ and â€œBattery Charger 2â€ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618658&prj=626&rqi=jbLSnv74RnCQ2cRFyDw3buSQuW
RT1ELEC-159-005 | 7863342f-6182-4ab4-82bc-f6063e1c778b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Internal panel bolts are still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618632&prj=626&rqi=7HkZZjEVH2zg0HPRw5xuLb1Fw4
RT1ELEC-156-006 | c32734fc-3b0a-4800-89a0-266cff12a98a | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Please confirm the required torque value for the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618642&prj=626&rqi=QoOjP23LscR61OhQXBVnGG87bo
RT1ELEC-159-007 | 76dbd05e-ca0a-43e2-9d9e-5604f9c0c35c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Please provide temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618634&prj=626&rqi=yPU01ZgHnvVLHr3dMwRpGPsth2
RT1ELEC-161-002 | 978673f4-37fa-41aa-8905-9e7897928089 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Please confirm the correct equipment tagging as per design: 1DB_DALI_L7.1 or 1DB_DALI_L7 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618619&prj=626&rqi=CUtmFkifWjgArKz9HOPar0WANR
RT1ELEC-156-003 | f0a3e377-1782-4614-93c3-34c53e9d19d2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Each component shall have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618638&prj=626&rqi=4qu5K14bgTzFmEDBY2QVVUhzeQ
RT1ELEC-159-004 | c5321b79-18bd-4b91-a3c8-43295ec05d66 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Grounding cable at panel door still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618631&prj=626&rqi=3k0ifb1FZccJg1HC8wfx6ZM6nT
RT1ELEC-13-014 | 62071c5c-72f2-4925-ad28-df900ee7e72b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add component RSH1 & RSH2 in the drawing component list | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618660&prj=626&rqi=UpZSQblp5zbYOdFbbBCyHrU56j
RT1ELEC-13-004 | 301fe616-d51b-4041-acde-47e4a212418b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Panel requires proper cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618650&prj=626&rqi=sRT3NyFQcjFnitYTiOnk5JiACe
RT1ELEC-156-007 | a156c827-f207-4ac8-ad65-bff33d917ec7 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Please clarify the panel location for 1DB_DALI_L2 in the drawing. The yellow color means Phase P1, not Phase 2. If it should be Phase 2, please update the drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618643&prj=626&rqi=9WcoTFOnDpyI4Wizr9ddXGzZeb
RT1ELEC-156-004 | 7b554834-e75c-4919-b380-16d424f9f696 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Grounding cable at panel door still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618640&prj=626&rqi=hD0J2xWZzHyGTn7CfjT0XzdiEp
RT1ELEC-161-004 | b3fe6ada-232d-4244-90c2-9d92e98134a2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Grounding cable at panel door still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618621&prj=626&rqi=zrTww4llosrGb0VVEPkZoUBMxy
RT1ELEC-156-008 | 872b0802-1c4c-4010-976c-9ad5b41e7c51 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Please provide temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618644&prj=626&rqi=qcLC1H7vj59wispMHl9TabDuKR
RT1ELEC-159-001 | 6cafe43b-5231-4398-8432-64e909681e52 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L5 | DB - Distribution Boards |  |  | Please upload factory test data document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618628&prj=626&rqi=3xYwOPlX0rJSZtMhmRQ62fgrGN
RT1ELEC-156-005 | 62a507ea-e9d9-4821-8529-6003c2dfa3b6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Internal panel bolts are still loose and have not been torqued. Please torque and apply marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618641&prj=626&rqi=5HuK7CqiRCUt79N3NIoLcdgi30
RT1ELEC-156-001 | 6a310eb5-abcb-445f-8424-64aa7e77572e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L2 | DB - Distribution Boards |  |  | Please upload factory test data document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618636&prj=626&rqi=G7sVpWc92elmWKugt7vBISaoRz
RT1ELEC-161-007 | 7f5932d6-32ab-41b0-a57e-e8f3a11da633 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1DB_DALI_L7 | DB - Distribution Boards |  |  | Panel surface is stained. Please clean the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618624&prj=626&rqi=xO4DRXzkeDQEakFs9Ghr0suhI0
RT1MECH-5-002 | c443e4d3-f8d9-4fca-a9b6-e0dec0cc073c | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Need to upload document related to the checklist; SoO, schematic drawing, O&M manuals, etc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618453&prj=626&rqi=ua8nOkqOJMDSO56wlPnu68mVDh
RT1MECH-4-003 | e4f12431-3b9c-4f37-8c02-4eab4d4d57f1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Equipment permanent label and tagging valve issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618447&prj=626&rqi=h7YGSYIa0uDsZs2vnhbIdkDOSx
GI-017 | 1e8de30b-1c50-4a86-bb61-1a5696a719e5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [7 empty] | (Issue CxL2A MV Cable RMU C to F) Sleeve and firestop at wall penetrations have not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618460&prj=626&rqi=2L8YiFnDTbzmhp4C7Jf3ZnKPyl
RT1MECH-5-006 | a62b1ea7-5581-4e28-b059-fb30fdfad248 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Fusible link cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618457&prj=626&rqi=tDVUkJx1lcwkN6aYvltVx6aBy7
RT1ELEC-14-010 | 51ab35c5-5b8e-49be-862d-90286786889b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add clear labels for ammeter and battery to show which one is Battery 1 and Battery 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618371&prj=626&rqi=TysBBGBId0ecmhYIoNmJJGJfO1
RT1MECH-4-002 | 2595e53a-4d0e-43f9-ac35-73689408ae1a | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Need to upload document related to the checklist; SoO, schematic drawing, O&M manuals, etc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618446&prj=626&rqi=W10Jyk09ACifHQGwNKECuUwJxe
RT1MECH-5-004 | d6a6cb62-ee34-48ac-b444-7a130242d4bd | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Pipe overflow has not connected yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618455&prj=626&rqi=zoheumj8aPOllO8IMA0dZUZt9N
RT1MECH-4-008 | c4b7a326-403d-406e-9b3c-54d990067440 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Discrepancy between shop drawing and actual measurement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618452&prj=626&rqi=PipEqdcgQvgLdbn0qHwWWZWqoC
RT1ELEC-14-012 | 788c524a-f638-49a1-b058-df17b13d466e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Minor dents found, please do touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618373&prj=626&rqi=q82F29jdX2Wq9nOgeUdOW8pnO7
RT1MECH-4-007 | 30d502ef-d34a-48e6-a7eb-bc4847152d5e | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Solenoid cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618451&prj=626&rqi=lit9vJVkhnDOCROIKXckHLfGJf
RT1MECH-4-006 | 3d22b116-4943-461f-9efd-40c8862cecab | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Fusible link cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618450&prj=626&rqi=h0fZxqkYOoGSFyoN7Lq185dxlY
RT1ELEC-14-011 | 2656d6fd-ca40-4f9a-b842-8ca578338388 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) GC please clarify why the positions of DB Aux panel and Dual Battery Charger panel are swapped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618372&prj=626&rqi=fOtx3imJrtNXoRW4gwxobd1XV3
RT1ELEC-14-009 | b3d995c3-535e-4283-bf7f-234b1e712012 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Please add labels above pilot lamps for â€œBattery Charger 1â€ and â€œBattery Charger 2â€ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618370&prj=626&rqi=JCcu1iLHK8KT7sTU7ZSvCWKhX5
RT1MECH-4-005 | a4e160f5-fa01-4e2c-8c56-ed888346de23 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Pipework needs to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618449&prj=626&rqi=10Urd8SerNxMqUtsNaodcpt0mf
RT1MECH-5-008 | 0a1454cb-22e7-44b9-b7b4-ae10a609c3a6 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Discrepancy between shop drawing and actual measurement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618459&prj=626&rqi=4Ty53H99YKUuDa5OEthhQ4jGAv
RT1MECH-4-004 | 7b0957db-cd30-4b8e-b986-470af7787cbd | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Pipe overflow has not connected yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618448&prj=626&rqi=QyUNUAIGiDjOsWudFZMtKGrkDi
RT1MECH-5-007 | d97bc3e5-ee1d-4eb6-aaf6-a0980dafd7bb | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Solenoid cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618458&prj=626&rqi=QF9UzIj3s0CzODXEzlRdN7m8P4
RT1ELEC-14-008 | edebc185-29c6-4553-8891-11ddac4e9244 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel Battery Charger) Drawing and actual panel are not the same: location of voltage and ammeter is different. Please update the drawing to match actual condition | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618369&prj=626&rqi=2JoMX1xBmmjJ28kkGVSXhHdvlK
RT1MECH-5-003 | 6c49af30-980f-4a64-8055-679c61db2180 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Equipment permanent label and tagging valve issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618454&prj=626&rqi=zz1jtiHPoMan8qu3o8qxeoIBDf
RT1MECH-5-005 | b32ddeb7-550f-45fc-b91b-b090fe9b80f6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Pipework needs to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618456&prj=626&rqi=b3MX3UUBZWg0PSPwH0vLhgHNm3
RT1ELEC-23-001 | 12cd1b24-38b7-43b2-9e43-44fdbff16449 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Discrepancy between drawing & actual position (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618268&prj=626&rqi=kVUjk9kA52KoMlKc5GrzAZ7hrs
RT1ELEC-148-002 | 5f997655-4fd6-469f-8a8b-ea5725f22d85 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_2 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1UDP_B_2 to 1STSSB_B_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618280&prj=626&rqi=WdTivnZ2RML1yDckTiKcFNi8LZ
RT1MECH-3-008 | 2f0dd9c2-e7e7-4050-b238-6231902a0d21 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | Need to upload document related to the checklist; SoO, schematic drawing, O&M manuals, etc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618361&prj=626&rqi=iVXurhV5DQntrC4s4F4RIiOsj8
RT1ELEC-14-005 | 5a877c9c-a6ee-4c7d-85ea-c53564766196 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Panel is not level based on waterpass checking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618366&prj=626&rqi=Xw2oLfARYNQ74muKLoFaYt2CEt
RT1ELEC-59-007 | fd172262-25eb-41d4-903d-1a2f99ffcca5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Provide temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618226&prj=626&rqi=lsOUReqJjR6caT68ARzr2OszBn
RT1MECH-3-006 | 2ccdb4c5-fcea-40fd-8aa0-c378f76f9359 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | solenoid cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618357&prj=626&rqi=7ynIB3WykpcFXP43mWeIkUmJDV
RT1ELEC-23-004 | 58ee3231-0c12-4034-923c-ccecc45675ee | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Door foam damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618271&prj=626&rqi=yC1KrL7yNMzka2vcY91uDRGd3r
RT1MECH-3-003 | 38b3c27f-e637-46c3-bd59-19d0db052541 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | Pipe overflow has not connected yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618349&prj=626&rqi=lWh7EVWJdC0pVakRiABnNWmKDk
RT1ELEC-14-006 | b31df10f-d9df-4b74-b01a-dbb078ce6814 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Rear anchor bolts have not been torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618367&prj=626&rqi=KCAqjefWRRK0f69qQaqzeHWhoF
RT1ELEC-23-003 | c7a6fc76-8a3a-4669-b347-ffb4c3b679cc | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Please ensure HMI display is properly protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618270&prj=626&rqi=Te9T2HqjBTPomJtE1KrJFqWFv3
RT1MECH-33-001 | cb7f9358-055c-40be-9d71-7d8a66044346 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Dirt Air Separator issue; paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618482&prj=626&rqi=HwCBBiTnUPKnNyTqMNJGWl58hw
RT1ELEC-23-005 | 06b22894-5830-460b-af38-dd13026ae290 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Deep cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618272&prj=626&rqi=YbBl9klgSlU5HIHLbi6TacuJnY
RT1ELEC-59-005 | db8e9638-ec7a-48bc-b1bc-04ac17d6042e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Minor dents & scratches require touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618224&prj=626&rqi=vzsgC7MykqCZ2LyAJ1K4n0StMZ
RT1ELEC-59-003 | a7bc0072-fc12-493f-bb74-54cdb2aa4f77 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Permanent equipment label/tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618222&prj=626&rqi=NNVMqwnCEDk2guybfCSSLrVTcW
RT1ELEC-59-002 | 839494f6-823e-4d32-8f75-cbaf0b0fc021 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Deep cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618221&prj=626&rqi=dhr3eEnqsJRL6R1ToZ3hxfepsz
RT1ELEC-59-004 | 19499c9e-9193-40d9-94e3-18c93edaf100 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Please provide correct GA & SLD drawings for 1STSSB_F_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618223&prj=626&rqi=Lfg9Zv0qEhKXFyZdvXurAZAaON
RT1ELEC-23-002 | 43b0c11c-4bea-41c8-8d0e-909f0262bb05 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_1 | UPS - Uninterrupted Power Supply |  |  | Minor dents require touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618269&prj=626&rqi=TXklakbKhSq1ggOxkhCbh4WQbU
RT1MECH-29-008 | b3309c7c-8bcf-4d1a-8b8e-3da724e43cba | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | DB Panel issue; Cable labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618359&prj=626&rqi=E54OaPeFwUjIKalIvjnXAyELhY
RT1ELEC-59-006 | c9911424-1bab-4fdc-b8f4-1f3420552a83 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Ensure all ACB & HMI are properly protected from construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618225&prj=626&rqi=lVU4mam54EqEnKKgtgaBKNHk9j
RT1MECH-35-001 | cabef85a-f08e-40b2-9e89-90a35d652bca | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | issue from Dirt Separator; paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618318&prj=626&rqi=1NvbshvmT4qh7y4sX3go1spjjT
RT1ELEC-14-004 | c218f58d-f6f2-46c3-82dc-71aa424637f0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Panel requires proper cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618365&prj=626&rqi=MwC9UXC5ovhEsWTLHIXSEoKeI8
RT1ELEC-14-003 | 72019489-65df-4d02-9a94-854deea55415 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Dirt and dents found on panel surface, please clean and perform touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618364&prj=626&rqi=ZyehVmSxk4pxMJHQQ1Epln0CNK
RT1ELEC-14-007 | 19e7af88-bfd7-4c26-9337-ff9696cf95ad | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A Panel GPC) Discrepancy between drawing and actual panel position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618368&prj=626&rqi=PBFXH6jYobPddtsdboZLNF3P4M
RT1MECH-34-001 | 530c9c39-d2cc-487d-861a-6344a8014e74 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Dirt Air Separator issue; need to repaint | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618481&prj=626&rqi=8ejSeeTOe1UffS8Yd60207BR0G
YT1ELEC-4-005 | 6b9a89dd-511b-4d27-bcdc-1170f0137f4a | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Component/Equipment Failure | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Testing of the RMU control box panel could not be performed due to a fault in VCB. LS to clarify and take corrective action to resolve this issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618363&prj=626&rqi=Y3hg5wfuo1MYX4gYgjtwpf8khY
RT1MECH-28-006 | 1141ca19-9bf2-4aad-b367-0aae5a105360 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | DB Panel issue; Cable labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618358&prj=626&rqi=nMUjyNieUh3Yj2U9yqpI3Z2md5
RT1MECH-32-002 | c2a8fcaa-a333-45e2-9a8b-00c985f9643d | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Dirt Air Separator issue; paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618483&prj=626&rqi=PpKKVsAlbKSYSdWSnQ8979Ls11
RT1ELEC-149-011 | 9dab3a20-65ab-42df-993a-129706889c0d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1UDP_C_2 to 1STSSB_C_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618257&prj=626&rqi=XNpLgis7paXeOOMSE77Af28tA2
RT1MECH-3-004 | 4848057c-2501-4453-93d3-415cf9c9a107 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | pipework needs to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618353&prj=626&rqi=vFm7hd1N2Y6eOPYvcmHjDRLLNV
RT1MECH-3-002 | 4bf73984-7260-4d87-9e3d-7ba42fd60254 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | Equipment permanent label and tagging valve issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618347&prj=626&rqi=Ah2PofWhbMJCEGVYLzIRySmLXF
RT1MECH-3-005 | ac3188f9-32ca-4ae2-ad43-69d5a93382aa | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | Fusible link cable issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618354&prj=626&rqi=yWqtr7lEX90do6iKsDEzIuKOmS
RT1ELEC-149-012 | 49430904-6fc2-4057-97ce-c25b9c4288ba | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1UDP_D_2 to 1STSSB_D_1) Wall penetration not yet firestopped | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618259&prj=626&rqi=SHsHmrd2GL4h8cLf8UtSf4Ulya
RT1MECH-3-007 | 19149648-dc0c-46d3-830b-1cc8914a99a6 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | discrepancy between shop drawing and actual measurement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618360&prj=626&rqi=rdKSOQc9ZYTegE13tWE8Yq1Ukv
RT1FD-26-001 | 021bba14-8292-4bbf-836a-235cb5e26cdf | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-5.04 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618190&prj=626&rqi=EQocZUp1DrBqEzkWdzEvnPtdtj
RT1FD-28-001 | 89bac660-1263-410c-9ab5-11f99c0aef9d | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-5.07 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618192&prj=626&rqi=rOCDpfTcAlRg81w0rbANFUwFvU
RT1FD-25-001 | 11469120-19a9-45d5-a67f-64b2771e8f9c | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-5.03 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618187&prj=626&rqi=wofwDJ5QKClQy4wELMQoRHm9ob
RT1FD-24-001 | 290d29cc-d4c4-4fc1-b04e-674efe627d0e | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-5.02 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618189&prj=626&rqi=2edWlSB3QZL4FrON4YjI3V3QIH
RT1FD-8-001 | 3087dba2-8c44-48ae-be91-eaf9a2417a1f | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-2.06 | VES - Vesda |  |  | Upload all related documents to this checklist | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618195&prj=626&rqi=afQsyLRHlSOUrZBxb2TOyPRIaM
RT1ELEC-58-008 | b9a869b6-c7a6-4f2c-8a02-484e2f4154cb | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Ensure all ACS & HMI are properly protected from construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618211&prj=626&rqi=sQzn4oSlo5vLf2EabJcJS52cVP
RT1ELEC-58-003 | 85d04f8c-2736-4818-90b8-5dbf3a5e534e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Please provide correct GA & SLD drawings for 1STSSB_F_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618206&prj=626&rqi=n39FsbvGCgrGDe2QJQG7OwQDBT
RT1FD-31-001 | 8058e1f0-bcb7-4d37-bad9-8aabb7a25096 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-5.10 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618193&prj=626&rqi=VKN3nWseAXGbg8Kd8pIKNPTMil
RT1ELEC-58-007 | c68c7b0f-941c-4dfa-978a-506308bccec2 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Discrepancy between drawing & actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618210&prj=626&rqi=kyC41D2fi9vgJYMJnrssLVhYkF
RT1ELEC-58-009 | 17abd944-9f12-440b-b87b-cec12ec6dd03 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Provide temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618212&prj=626&rqi=p4dyFTL3GrpMmIXn4WUpK9ldcf
RT1ELEC-58-001 | 200bb130-d84a-4e57-beed-38757296eb09 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Please upload calibration certificate of torque wrench | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618204&prj=626&rqi=qxjhrzsT3P7rLPH8mQkgzOHQR2
RT1ELEC-58-004 | c77f60cd-a2c4-430d-a504-471341c8d207 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | ACB has scratches | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618207&prj=626&rqi=TverGGmWKKElb4DeYqjyvlynCC
RT1ELEC-59-001 | f1edff4a-5d75-477c-8cf6-ee6ae8adb9dd | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_2 | STSSB - Static Transfer Switchboard |  |  | Discrepancy between drawing & actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618213&prj=626&rqi=JIapaE2tBvahTR1hsP8pGAnIj9
RT1FD-9-002 | 0ce3a58d-8442-43d2-bf0f-ca8909e18737 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-2.07 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618199&prj=626&rqi=QBsMLCyMul9x7BNYXmiFJyJ8Ar
RT1FD-8-002 | 91d474b6-f3af-49aa-90b4-1a57db9b7b1a | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-2.06 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618197&prj=626&rqi=K8qs6NJDpect5MZtfs7raaDmYb
RT1ELEC-58-005 | b1936f59-9a12-4db6-8b20-31a18beae73f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Deep cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618208&prj=626&rqi=BCvxfcwEeAtCQbSn32IrJRhhk1
RT1ELEC-58-006 | a880eb1d-0ef7-4444-9a56-1ba38c5ec7b7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Minor dents & scratches require touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618209&prj=626&rqi=O7GvzSAUcQXSGmmcCGLmZbkNNl
RT1FD-27-001 | acfbf739-4d79-431a-86e2-416606166fc0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-5.05 | VES - Vesda |  |  | Confirm correct pipe installation routes to approved VESDA drawings. Attach photo on-site if it's already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618191&prj=626&rqi=8y73YuqC4wbDFu8YNTdPelvTFw
RT1FD-9-001 | 72f28cc4-1cfe-4a54-893a-f79f7bce1860 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | ASDSP-2.07 | VES - Vesda |  |  | Upload all related document to this checklist | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618198&prj=626&rqi=dzqA4oPLHxhwBDBwzzOjBsRBsA
GI-016 | ba5285c5-debb-4051-96d6-f8dc795e72b7 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | DCOS graphic configuration for asset data equipment is pending due to missing data from GC and MCE. Please expedite submission of the required Maximo data so the DCOS team can proceed with configuration. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618202&prj=626&rqi=tWVXLFr94UseIEovTWeZGA6xnN
RT1ELEC-58-002 | 5325741b-079c-4820-bfcf-f6c17fcdd4af | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_F_1 | STSSB - Static Transfer Switchboard |  |  | Permanent equipment label/tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618205&prj=626&rqi=xMnQbxaz2P4MR6LTmZyCak7BIq
RT1MECH-98-001 | e89cd0c6-0ea9-4036-b178-dac8e7ddc964 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_F_3 | FFU - Air Scrubber |  |  | nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618039&prj=626&rqi=UXlVtPEKitqwhGhrD4BndUpWqw
RT1MECH-102-001 | b56d4ea1-74c8-44da-8ba2-b9865fa9d181 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_F_5 | FFU - Air Scrubber |  |  | nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618042&prj=626&rqi=R4yJLygTea1YM2sA6HZO52IvrG
YT1MECH-83-001 | 8e5f1937-552b-46ce-b0d7-10b15dd1d078 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_F_5 | FFU - Air Scrubber |  |  | issue from L2A; nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618047&prj=626&rqi=hpMKUpQLPPH46sd7bIVgwAyjGk
YT1MECH-32-001 | 12b93c91-36cd-4fe1-8053-0e76c435a6be | JK01-2 | 626 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | jacketing not proper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618011&prj=626&rqi=JQ4fTgrCDwu2LTXaNPJjhN9kJT
RT1ELEC-149-010 | c9caec02-ad5c-4957-a6fe-84a9a20f5749 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD 1MSD_D_1 to 1UPS_D_1) Please clarify with engineering, the drawing shows 5 busduct supports, but only 4 are installed. Confirm if this is approved and safe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617946&prj=626&rqi=HLp8DFkDzAx31yxwTPEuRxE8zy
YT1MECH-81-001 | 33065fa4-5cbd-4bae-b0dd-48669cc4f506 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_F_3 | FFU - Air Scrubber |  |  | issue from L2A; nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618044&prj=626&rqi=Ro7sKmPFVEIGs3FUyLix5Ef5nN
YT1MECH-82-001 | f1be83d4-3938-4a3c-bc3d-9b8555d36a0b | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_F_4 | FFU - Air Scrubber |  |  | issue from L2A; nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618045&prj=626&rqi=FouiMrgcNg2w1svhtA6pbuv4ya
RT1MECH-96-001 | c67c7290-6818-418f-9def-80cd94b3d9d9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_F_2 | FFU - Air Scrubber |  |  | nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618038&prj=626&rqi=NCvR9i226PLGltHNauyMgfQYEh
RT1MECH-100-001 | 0afea3a2-51cc-401b-a132-3d86f40f8207 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_F_4 | FFU - Air Scrubber |  |  | nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618040&prj=626&rqi=ibxiCcOtswLHE4YEmiEmm90j69
YT1MECH-80-001 | 414be0d5-83e6-4ab5-a916-ef388276f724 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-13 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_F_2 | FFU - Air Scrubber |  |  | issue from L2A; nametag issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618043&prj=626&rqi=3rMezpGBOJetAXSrZCg0DeaDDb
YT1MECH-76-001 | cf67e143-e3d1-4e59-b304-58a3f8ce1e0e | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | issue from L2A; provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617897&prj=626&rqi=hglYmhch6jCIh8N5hTvnCuom0e
YT1MECH-78-001 | 1818c184-7784-4cfe-b657-60691cfedaa6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | issue from L2A; provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617899&prj=626&rqi=AhSJJ4N7GHOscMzoL2XtJYYSi3
RT1ELEC-1-017 | 490d9d9e-9f0c-4786-9991-374b2db9e1c7 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Cable installation not yet completed? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617901&prj=626&rqi=mprBERxZtEVaQcUySrAiTRtToP
RT1ELEC-124-007 | b3eb3505-61c4-4f93-abe7-2f43b6a83312 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Remove temporary marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617891&prj=626&rqi=fpUSFYRQVuWFjPaoZ29UkdgjkT
YT1MECH-69-001 | a9a08e1e-7c2a-4e26-b1c8-295340fb92f8 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | issue from L2A provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617895&prj=626&rqi=NeHZIXyNY3CnyQDZ55Op3xNo5d
YT1MECH-77-001 | 6b5c76ba-003f-4308-86d7-9901a494fd64 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | issue from L2A; provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617898&prj=626&rqi=qgmdvRBGbdYRwn1ffUOB8mvbDa
YT1MECH-75-001 | f5811139-8f9b-4f5a-9a36-948ea8d11881 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | issue from L2A; provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617896&prj=626&rqi=Qb7Ezmbjhw71MXRnpgLCFlaeXT
RT1ELEC-174-001 | 62cbc0b3-7dae-414f-b153-1684e7dfd57c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | Discrepancy between drawing and actual installation. In drawing this for 1TOU_C not 1TOU_D. Please clarify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617915&prj=626&rqi=0BSmeKqfScOeyzScXszJeMgWpv
RT1ELEC-1-016 | 212d08d9-b243-426a-b458-1536a44d6f5d | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Equipment not level/titled, please refer to the attached water pass result photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617900&prj=626&rqi=BpRTjYrzXOFlCuVhetwWdLejkm
RT1ELEC-174-002 | a1340da5-1408-4fd6-a43e-57cd85fcb9ab | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617916&prj=626&rqi=Rcgg9N9Plu7s3dMwwy16qFXdiV
RT1ELEC-176-003 | 5e69682c-a468-4bc0-9a58-986a9e2722a5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Cable tube marker is faded. Replace or re-label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617912&prj=626&rqi=ThgJA28UCzQifAMFgnwhRGCQ2K
RT1ELEC-176-004 | 0b5a385e-ca2e-41a7-b7af-0ba8f0297dc9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Please provide temporary cover to protect form construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617913&prj=626&rqi=9bMFMvuBiBBgJPIWaxQzCTup0w
RT1ELEC-1-020 | c8756426-6969-4c97-855d-87e61291bcca | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Busbar joint between battery not yet torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617904&prj=626&rqi=jFivfCp97hkcPLRCUNfZm0wpTM
RT1ELEC-1-021 | ad391ab4-5e56-4dc1-bb27-85be93ca2851 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Discrepancy between drawing & actual positioning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617905&prj=626&rqi=c3LsMdc5NAhp6HN5WyQk2ddsuV
RT1ELEC-176-001 | 8e692b36-36f6-4325-91e8-8905c05138a3 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Discrepancy between drawing and actual installation. In drawing this for 1TOU_C not 1TOU_D. Please clarify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617910&prj=626&rqi=YfR66iYcN1P785Fa5AjgodEO7u
RT1ELEC-1-019 | 9a0701c4-b118-4b29-acdd-c0ae23dd3ae4 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Incorrect cable connection between batteries (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617903&prj=626&rqi=f12Earl2gb8NRxvolAizDhiWnQ
RT1ELEC-174-004 | 4fac2e42-4e7a-48ac-a13a-4fffd4c6eda6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | Please provide temporary cover to protect form construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617918&prj=626&rqi=RSPIZ8znrYMQl2xol2NnM3tJrM
RT1ELEC-123-007 | 75704981-da80-47e5-bd82-8a2ab72173dc | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Glanding cap at cable gland not properly installed. Reinstall to ensure fully proper sealing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617889&prj=626&rqi=HWiNC0qnRJPQNJrbcESJRWolng
RT1ELEC-124-006 | 7d9d4430-bc58-47df-b015-d68c9e6b0594 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Glanding cap damage/broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617890&prj=626&rqi=FcTMoUy8VULyUgOiRs4CqE4Zcc
RT1ELEC-176-005 | 5d1c7e0f-8718-46ae-9118-1e68d3172a08 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Door gasket panel broken/damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617914&prj=626&rqi=uKJRtTaOGgdeaKulc3Yg2ZegQr
RT1ELEC-174-003 | 5ff4f1f4-de85-4e2e-a650-0c74928234b9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_D_2 | TOU |  |  | Cable tube marker is faded. Replace or re-label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617917&prj=626&rqi=7xT3UdTAuLpY6GtqZNRW5G8saC
RT1ELEC-176-002 | 5aa16fad-df3d-4afe-be3d-5cdcd0c8f2ba | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_D_1 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617911&prj=626&rqi=6K7er1JuIlDEwDF1hiH4k7GpPF
RT1ELEC-123-006 | f34c80b3-fba4-4aeb-be72-af01eca2df61 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Sleeve and firestop at wall opening/penetration not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617888&prj=626&rqi=VrSTqIVLypfMpcq29XcfvtaVio
RT1ELEC-1-018 | 372e3c67-c861-43e6-a384-e8691adbddee | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Battery stopper not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617902&prj=626&rqi=nXwqt3uKvyI9RlTPwvrzRypVbV
YT1MECH-108-002 | 9ca0dd4a-8a55-446b-9a0f-336f5a57c74d | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | Grouting base plate support pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617736&prj=626&rqi=WMPBpVx6cxearys7uvjYyN89RF
YT1ELEC-5-004 | 63bc2395-b025-4ad8-9d4e-30786f3a2f9d | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Earth cable point-to-point continuity cannot be verified as the earth cable has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617660&prj=626&rqi=5OhvehHWEEG3HRlzXAvvSnfYeR
YT1MECH-108-003 | b3f4d89e-5d4c-477e-8da0-306f08a9eecb | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | some parts of the safety valve are rusty, need to replace/touch up, because some other valve seems ok with no rust at all | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617738&prj=626&rqi=4mSrLRezgC6hJm51QOVDRUV3eY
YT1ELEC-3-002 | 2b193831-9bb1-4682-bf1f-71cdf6e4e4fa | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Earth cable point-to-point cannot be verified as the earth cable has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617656&prj=626&rqi=Z1zBgVCghOpKS5audidrl9GyZn
YT1MECH-107-003 | 68c8eb04-8381-4897-9857-471fa079ab73 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | some parts of the safety valve are rusty, need to replace/touch up, because some other valve seems ok with no rust at all | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617772&prj=626&rqi=QJES4ellpdGh83K9SiZyanBRLI
YT1ELEC-5-005 | 7ca8b78a-0c18-4ce8-9b11-6a3c899db290 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Improper grounding cable termination at BTU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617661&prj=626&rqi=TDwPKI7jz58oXCgmOS5xOx1EJG
YT1ELEC-4-001 | f3200b49-0248-46f5-bc52-04532ad8928d | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Earth cable point-to-point continuity cannot be verified as the earth cable has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617659&prj=626&rqi=6e46Vx3rnD0O41hSxw4P5CikN5
YT1MECH-107-002 | bb4cfe60-2f70-40ad-a121-e8ab523980ff | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | Grouting base plate support pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617740&prj=626&rqi=4M0geuU7rBnyJAwoJfr3PkaH9t
YT1MECH-107-001 | af6cdd9a-41ac-4493-9c7c-851503cc8ff6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-09 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWP_1 | CHWP - Chilled water pump |  |  | the bolt appears to have less than 3 thread and there is one bolt with no washer on it | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617739&prj=626&rqi=MPnF5pCyR6SLobV5vFNij5Ez14
YT1MECH-108-001 | f61487f5-f1a6-4153-9a1f-01b8117b4314 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-08 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CHWP_1 | CHWP - Chilled water pump |  |  | some bolts appear to have less than 3 thread | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617619&prj=626&rqi=2LRgYAmoGR483W49DdgmmWhEjG
RT1ELEC-131-005 | d619652b-9f2e-40de-8297-0d2268eb3ed4 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Discrepancy between drawing and actual positioning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617499&prj=626&rqi=KGTHso0TskV1yvH975nkTvYnU5
RT1ELEC-131-001 | c89bca18-8e99-4aea-8945-37b4f94c3538 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breaker, similar to breakers Q1-1 to Q1-5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617494&prj=626&rqi=XPqI3mDWOXk3kVq4pNvqSmQQNR
RT1ELEC-131-003 | c6ed6bb2-cf62-42cf-8a8d-8ae287df5279 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Please add protection to prevent from construction damage, dust & debris also please protect HMI display | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617496&prj=626&rqi=XWrq3dIjDuHHOMEWgdeCJusCj4
RT1ELEC-131-002 | 94b61bf0-30d6-4836-a50f-e9c768ccf051 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (should be 1MDSB_F_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617495&prj=626&rqi=rW8fWy6MLbyKb4DAupEgUvZ9EZ
RT1ELEC-12-001 | bc93057d-d53b-4196-9695-bc5e2b791053 | JK01-2 | 626 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_B | GENL - Generator (LV) |  |  | Panel Isolator, DB Aux any part not tagging, cable not tight and cover acrylic not install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617488&prj=626&rqi=209gdcvtxqhjgDI0O8iPrzic51
RT1MECH-4-001 | 5f51ab93-d163-402b-a3e3-99aef92a12b6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_C | FT - Fuel Tanks |  |  | Fuel day tank not install sight glass, tagging and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617486&prj=626&rqi=rERGBkkWXaAyhVVj9bhpNVEbfG
RT1ELEC-132-003 | 43e33ed8-eb5a-4853-9cf1-828d19e335c7 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Discrepancy between drawing and actual positioning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617506&prj=626&rqi=11CCpAIPaJ1uEGeKVW2uU369lP
RT1ELEC-132-001 | e72f566a-96ce-43cd-92ac-d4bd990f98b3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (should be 1MDSB_F_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617504&prj=626&rqi=ZJg5IW2qNH3sB9dsYj9JFu8mJd
RT1ELEC-132-002 | 9afc8621-9136-4519-ad50-2877c6b45613 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Equipment need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617505&prj=626&rqi=QBl2o9dxx23VfnqB3cGMwyaI3l
RT1ELEC-132-005 | fc57ab5c-e7a1-4cab-ad2d-1c46f7ba351a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617513&prj=626&rqi=ZtuBA9M16X9fl5m4i5DdkVp8PB
RT1MECH-2-001 | 55a37433-b0cf-4531-88ed-e6e4566721dd | JK01-2 | 626 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_B | FT - Fuel Tanks |  |  | Fuel Tank not yet install sight glass, tagging and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617480&prj=626&rqi=DncrSg45RwBGIwT0cvGLADrIUB
RT1ELEC-131-004 | e74b8340-4efe-43c1-892f-b84363fb4b09 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_CRITICAL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_F_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617497&prj=626&rqi=8B1SLrEZTa5Geb6vue7bnz0euY
RT1MECH-3-001 | c7396a78-2d38-4e18-8141-57fc330788f2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_D | FT - Fuel Tanks |  |  | Fuel day tank not yet install sight glass, tagging and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617485&prj=626&rqi=vKuBNb27najWllAoyOIsS0QILS
RT1ELEC-132-004 | d87ecfb4-3cab-4f51-90b5-1680f66d0efa | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-07 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_EWALL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_F_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617511&prj=626&rqi=3n0MTmTJdcJTmW8n1GLZPTToc2
RT1MECH-5-001 | 2c16e722-ad70-434b-9a0c-847bc40019d4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1FDAY_F | FT - Fuel Tanks |  |  | Fuel day tank not install yet sight glass, tagging and labelling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617487&prj=626&rqi=zBDYfV6cTTBnQCRIIaJFKjXoDg
RT1ELEC-14-002 | 2f1e1f25-ff94-4364-ad2c-223f917f9e00 | JK01-2 | 626 | APAC | Closed | P3 Low CX | purnomo.adi@turntown.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | Panel Isolator, DB Aux any part not tagging, cable not tight and cover acrylic not install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617489&prj=626&rqi=UXHr9OTXTrErjtPZaYF1P32WIp
RT1MECH-28-004 | 5ac8a7a6-44c4-4b36-a2c1-83d10246cafc | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Grouting base plate support | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617418&prj=626&rqi=sRXrwQhddqSsGnNB21ZU3IdCaO
RT1ELEC-25-003 | fda89bfa-c77f-473d-9749-906395389e32 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Minor dents require touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617370&prj=626&rqi=WCFceWi7htMgVNTQPSYfwlznp0
RT1ELEC-25-002 | da6f07e1-e4b9-4a3b-90eb-e7bcdc2b221b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Deep cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617369&prj=626&rqi=0TDt57K1GKtEBIM59eB52ChhXI
RT1ELEC-25-004 | 0ab9dcc8-79f5-4cab-98c4-4517601ea0d5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Please ensure HMI display is properly protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617371&prj=626&rqi=8lHQ9qZeTA3aP95TOI8OoYpRV2
RT1MECH-28-003 | b3d96dc7-aca1-4481-a944-d20aa245fd49 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | the bolt appears to have less than 3 thread and there is one bolt with no washer on it | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617410&prj=626&rqi=pDdwJnsbQF6tqKTUjIL2hcYWFL
RT1MECH-29-006 | 775d9636-90f9-45af-9c4e-97817b5d5f49 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | DB Panel anchor bolt seems not straight / tilted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617420&prj=626&rqi=eTZECaJ7OKssDjvkrqKcrzL4ry
RT1ELEC-25-001 | 27f608a7-fb26-4061-85ea-03943b913939 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Latest drawings are not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617368&prj=626&rqi=fhmNa3vs3WKNFhhB3fTELm9ejs
RT1MECH-28-005 | d9c105e0-b286-4ae4-8f17-a1d7cbf89a92 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | some parts of the safety valve are rusty, need to replace/touch up, because some other valve seems ok with no rust at all | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617419&prj=626&rqi=wE3QJuaTfEvTyXBTQAi5Cl2VCK
RT1ELEC-25-005 | 9efb3142-d326-4780-a735-d3ef068bc6f5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_1 | UPS - Uninterrupted Power Supply |  |  | Equipment permanent label/tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617374&prj=626&rqi=Bvyj3f9X9dCl6qzOKBGplbg3So
RT1FD-38-002 | 6df9cee3-8df2-4e8e-8f63-53b135813c63 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-7.09 | VES - Vesda |  |  | provide Cause and Effect Matrix is approved document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617427&prj=626&rqi=fEQxZ8NJnuEQQj5IRXhrT19cAT
RT1MECH-29-007 | 03d4b4f6-4d8c-4c88-ae9b-9c691e6b5537 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | DB panel: there was some scratch inside, need to touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617421&prj=626&rqi=jRonPvJXwSG4bjQZL7Bxy6mzPA
RT1MECH-86-001 | 36f4390e-f331-4dfc-ae23-0076ba4f4f0d | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | provide Approved method statement for L2B static testing upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617309&prj=626&rqi=nb4D7xKY489vgllEeAAbfKw0xE
RT1FD-38-001 | 3767563e-cede-46f8-aa6d-5e7c35062677 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-7.09 | VES - Vesda |  |  | minor scratch and paint damage at pipe vesda | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617304&prj=626&rqi=OSe6ajzuT2cLO8wUalk5YWMI93
RT1MECH-84-001 | 1a401561-9ae6-460c-a9de-7c31a641c35a | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_D_1 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617333&prj=626&rqi=1NwMw3pTAHdEAhIkCjjNCdHNch
RT1MECH-74-001 | 2e50ef7f-0c84-4fda-a740-427ecac8ca6c | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | provided Approved method statement for L2B static testing upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617306&prj=626&rqi=TZJuRIQKA4SN6qKE9H19fEKTnc
RT1MECH-80-001 | eb794c7e-5e7a-4711-82f5-14df3b733f30 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_D_4 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617327&prj=626&rqi=75UMy3NsfxrLFsgBxxaggqJINV
RT1MECH-88-003 | de28aaa4-08c9-41ec-9a23-9ee7ae260cbc | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | provide Approved method statement for L2B static testing upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617314&prj=626&rqi=dgEct5rDzZY8uguP4hCvzB1lBB
RT1MECH-92-001 | 924ac6ae-7c6a-4160-8c8d-4948660cf1d8 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | provide Approved method statement for L2B static testing upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617318&prj=626&rqi=8zbZMN7QUiYWv4QhwAyofqiEx4
RT1MECH-90-002 | cb4d70ff-6799-4ac1-bacf-1c2ef9fca58a | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | Cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617316&prj=626&rqi=CCCrlnJXHGe0UfiWYleij7fRKf
RT1MECH-88-002 | 4d7cf4b7-e00e-4b12-908b-bb1bf3e4f513 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617313&prj=626&rqi=h10VDf31MDCnvR5VQLAERsmfac
RT1MECH-76-001 | 7cd04e9d-ec6a-4039-8b18-ee9606eaf63c | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_D_2 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617321&prj=626&rqi=i84imyAZ1OWCvrfrXogjv4aLSS
RT1MECH-90-003 | e77c9d48-512e-479f-b8cb-4408a15285a5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | Provide permanent equipment label / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617317&prj=626&rqi=szztiIrBacYVWG2pYouLpVgb7k
RT1MECH-90-001 | 2ba9b108-2bd1-4bec-81e8-ca4483a4d7dc | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_4 | FFU - Air Scrubber |  |  | provide Approved method statement for L2B static testing upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617315&prj=626&rqi=iYnG41NcHlnTw7iZIjNQcnbB0a
RT1FD-33-001 | 2d5f9b2b-1ec8-4436-8eb3-719a70177b81 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-7.01 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617305&prj=626&rqi=slWrBTP4OsWPbYj3jEi8K8HCE3
RT1MECH-29-004 | 211a8312-35da-4ecf-b705-595f70e59a83 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Grouting base plate support | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617351&prj=626&rqi=VjSeyFCpKB7BNGdp8q3dbfp9ZH
RT1MECH-29-003 | b212df90-4483-4249-9472-04aaa129f09f | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | some bolts appear to have less than 3 thread | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617350&prj=626&rqi=5XebzlCkMxK5Ne38DEDaJiMCUn
RT1MECH-29-005 | 146c426a-ba6c-4de4-b837-38b875a24c32 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | some parts of the safety valve are rusty, need to replace/touch up, because some other valve seems ok with no rust at all | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617352&prj=626&rqi=Kk7Ez4MH36G5H2DEk3VsqASda0
RT1MECH-92-003 | 8df6596c-d1a8-438e-831b-ff3099651358 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617320&prj=626&rqi=lRJNFGecwvyaWNXhegEAvGxSui
RT1MECH-74-003 | 0aeb30b9-634f-4fca-a7dd-b9c243a063d2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617308&prj=626&rqi=41oiXy8Yo7H5AMDcxK88cQ4BBX
RT1MECH-88-001 | fe156b43-1133-4ee7-9e73-499b5c952075 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_3 | FFU - Air Scrubber |  |  | provide permanent equipment label / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617312&prj=626&rqi=7pLLdH9ikedm8SXPWbFuMLGXWZ
RT1MECH-82-001 | 6c405520-eb40-4c24-baaf-777e023a5004 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_D_5 | FFU - Air Scrubber |  |  | cleaning issue and remove unused material inside equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617331&prj=626&rqi=gq3ububNt1yHp7TC6yEGzfdKnV
RT1MECH-86-003 | 61f6c3fb-2225-46e4-961d-a8b540b6b99f | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617311&prj=626&rqi=hJKyoMJqs1ik5ezsprcXonIKwm
RT1MECH-92-002 | 5ff6fb91-ca3c-4b8d-95c8-08b38c1e98d5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_5 | FFU - Air Scrubber |  |  | Provide equipment permanent label / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617319&prj=626&rqi=GELfceEphajYVXYDCMof6yzxq9
RT1MECH-86-002 | fbb5240c-8cfb-49e0-8547-cff891da32e5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_2 | FFU - Air Scrubber |  |  | provide permanent equipment label / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617310&prj=626&rqi=eztA9Q4wBY7NhVeGrK5MxjABOe
RT1MECH-78-001 | f90f4713-7c7d-400a-8ce1-f8bcf4dcbe83 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_D_3 | FFU - Air Scrubber |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617325&prj=626&rqi=QKLcVW9XFpc7IQRjZr7YnPYGLa
RT1MECH-74-002 | c648c81f-5fcd-4d55-9d68-d66020a186f2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1FFU_C_1 | FFU - Air Scrubber |  |  | provide permanent equipment labels / nametag | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617307&prj=626&rqi=apv7UKZ63oCPgY8ioyihCrg7WL
RT1ELEC-37-007 | 16afad3f-9cec-4b9b-83ef-45875e0ebd0a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Please add temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617130&prj=626&rqi=TdRvNAMB8bACyWoZ7dVnimSvhm
RT1MECH-15-001 | eaa046d7-7d8a-425e-96e2-de9e58848a3a | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_F_61 | EF - Exhaust Fan |  |  | equipment name tag has not been affixed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617120&prj=626&rqi=cewQG73ILAQsO3Z7E2pIlNqtrI
RT1FD-36-001 | 7914a6c7-208d-4296-8f3a-f1a553758b00 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-7.04 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617149&prj=626&rqi=NjHZEHmJf7OURNdzFgh2yGIVLg
RT1FD-35-001 | b14eac3e-a05f-4367-a913-8a3585d705f0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-7.03 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617148&prj=626&rqi=FqicxjkfBY14F4YPoJqRCIPCvJ
RT1MECH-15-003 | 1afda3e8-cc77-4dce-a7a1-33afc08f0fe3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_F_61 | EF - Exhaust Fan |  |  | marking of support installation has not been applied | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617123&prj=626&rqi=EtecrUqxgoISYU14XolfassspU
RT1FD-37-001 | 5f2c1a90-6b58-4408-9ae5-0e5ac9130e44 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-7.05 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617150&prj=626&rqi=lsycml5is3XIBBqK52lNkWv8Ox
RT1ELEC-37-006 | 0f719dd4-92a4-4486-9445-f769efca89e4 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617129&prj=626&rqi=47t0L6eOXqMEITw6bHtwFQlQIT
RT1FD-34-001 | 13b6ea5f-8565-4b5d-b8d6-7ca285a21f89 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-7.02 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617147&prj=626&rqi=yH8apfiH90bIR11bmUqext4odi
RT1MECH-15-002 | c1c5b3ae-ffae-4311-b2ed-bd387b68d478 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_F_61 | EF - Exhaust Fan |  |  | Airflow direction / orientation has not been affixed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617122&prj=626&rqi=z9whoLqA75nRABgTSM6dynTpjg
YT1MECH-114-001 | 75567841-852a-4ae2-a428-dfd9279761f7 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Fuel | equipment | 1LCP_FPUMP_A2 | FT - Fuel Tanks |  |  | Invalid Testing Tools due to expired calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617131&prj=626&rqi=0lEp8hFyMn24JPmFgqilWug4ms
YT1MECH-115-001 | 87a911b3-2753-45cb-aca3-c815ef68e045 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Fuel | equipment | 1LCP_FPUMP_B2 | FT - Fuel Tanks |  |  | Invalid Testing Tools due to expired calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617136&prj=626&rqi=U0IBhHccDRhrRUbDbSdr2EGiIa
RT1FD-30-001 | 3fa74b7a-61e7-4da1-9990-39842d438142 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-5.09 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617146&prj=626&rqi=MSv33oRbbTAPXAtXWNihZYjaKN
RT1FD-29-001 | 21a7ab8d-2a39-47c4-a5d4-b9ebe6e66bbd | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-04-01 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Fire Detection | equipment | ASDSP-5.08 | VES - Vesda |  |  | please provide correct pipe installation routes to approved VESDA drawings, attached photo if it is already done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617145&prj=626&rqi=a79UYLygM8WtUAspKIHABbF7Dd
RT1ELEC-39-002 | 0afb0e7d-7a38-45c3-8542-1c51ad252ff8 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Equipment labelling still temporary. Install permanent labels as per approved scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617013&prj=626&rqi=oSYHl9tg3gZ8bCI2irFW8tGB8n
RT1ELEC-37-003 | 0325dae0-bc9f-4248-b7d1-464630a0ef5a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Equipment labelling still temporary. Install permanent labels as per approved scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617030&prj=626&rqi=Bhl0Hd4KhdtQPJ1CbTcbgFKtMS
RT1ELEC-129-010 | cc0efaac-abb1-4ae3-8126-56a2d7c2e89d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Unused bolt observed at cable gland entry. Remove if not required. Glanding cap also not fully covering | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616955&prj=626&rqi=JCrkdrjnJOIYEAs1M0Y3Y0i7H2
RT1ELEC-129-011 | b2977a11-0d1f-47e7-8093-1af0e3a49639 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable containment penetration not firestopped. Provide firestop | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616956&prj=626&rqi=gFMcY2C3FnPdPbMxBvpfk5ViJq
YT1ELEC-3-001 | 38b46465-098a-4717-8395-739d9a6f2809 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2B | Component/Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | During function test of CxL2B, the alarm signal stayed ON and could not be reset due to incorrect wiring, the same issue also affected fault and trip signals. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617423&prj=626&rqi=MJMCoP2lcLOyeWIkgd351A84oE
RT1ELEC-39-006 | 0ef217a8-fe54-4fd9-9835-85cfe205bb6b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | GC to upload following documents: 1. Certificate calibration of torque wrench 2. Approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617017&prj=626&rqi=myxFPKIwZzCtyWVIwn6aJvufkS
RT1ELEC-39-004 | 93fed936-1b2b-4ba3-877b-34fa125d16f9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Busbar joint marking not consistent. Standardize to red | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617015&prj=626&rqi=aoFcP6osShwHg15YW17JaAnayV
RT1ELEC-39-003 | 89ca2eee-6ee5-459b-b435-fe77f3de6f51 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Anchor bolts too long, torque wrench cannot be applied. Re-torque and re-mark all anchors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617014&prj=626&rqi=UeChxWSRglUtNAnRvdE87zfZCC
RT1ELEC-39-005 | 2a691707-95cc-4b7c-bb8c-baf68ebaf5a0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Please upload Factory Test documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617016&prj=626&rqi=WF90C08VcY7AFaDOhZ4rh08wTx
RT1ELEC-39-001 | 848edbde-8243-4857-ba52-c195f354ef32 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617012&prj=626&rqi=SluFKr9pZKDIgRCQt6SOhkoKx3
RT1ELEC-39-007 | 13181a0b-3430-4033-a5a0-997311fc9591 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_G_2 | LIBATT - UPS Battery |  |  | Please add temporary protection to prevent from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617018&prj=626&rqi=UkXvKYAxvfZMnqIEFamSu6caJY
RT1ELEC-38-001 | cdd1272b-cc33-4c1d-880a-898bcff231bc | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | Please upload factory test documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617020&prj=626&rqi=eKEIrADZ8F7RpwDQKpoZVT7HaN
RT1ELEC-38-003 | b7db2d44-23bd-4ac8-898b-74ad98880af9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | Equipment labelling still temporary. Install permanent labels as per approved scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617023&prj=626&rqi=wTqLxHjtez8WMvDsmIMAcYouHe
RT1ELEC-38-004 | e84754d5-8612-48d8-9a91-5f29087fef90 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | Anchor bolts too long, torque wrench cannot be applied. Re-torque and re-mark all anchors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617024&prj=626&rqi=NXoYb7QxymLdY5YepogMVRe7nY
RT1ELEC-38-002 | 42b9e452-f5a3-40ba-85b2-d0fabc121fa7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | GC to upload following documents: 1. Certificate calibration of torque wrench 2. Approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617021&prj=626&rqi=QYFpl1gtYtwNMyFsV8B85NySDa
RT1ELEC-38-005 | 4d0691fc-0726-45ea-91a9-d06dd9033549 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_2 | LIBATT - UPS Battery |  |  | Busbar joint marking not consistent. Standardize to red | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617025&prj=626&rqi=V2Og1WeW2lpN0VBEatq9C3soCi
RT1ELEC-37-001 | a37a4ff1-08a9-43ab-9810-f9acf5e135e8 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Please upload factory test documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617028&prj=626&rqi=m4Rxg4C2kqfvoEarJUZzG5htvr
RT1ELEC-37-002 | 2e31a019-18f2-4d94-a3a4-1d43d030b97c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | GC to upload following documents: 1. Certificate calibration of torque wrench 2. Approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617029&prj=626&rqi=fxNRdqifW92JuJl4nJVRNNZTiq
RT1ELEC-37-005 | 260f4c7e-52c1-4220-b8cb-987d9bcace24 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Anchor bolts too long, torque wrench cannot be applied. Re-torque and re-mark all anchors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617032&prj=626&rqi=rgPmm7xkqzVGkA9e91Qgthciey
RT1ELEC-37-004 | 2e2e245d-9d52-49a4-8f19-3ffd7d3b2da8 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_F_1 | LIBATT - UPS Battery |  |  | Busbar joint marking not consistent. Standardize to red | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617031&prj=626&rqi=6BvGeUF9Bqhp7SX8O1JjJ97jzS
RT1ELEC-128-010 | 1137bd5f-f518-48d2-b5bd-05d00dff54cd | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable arrangement is not neat. Re-arrange properly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616950&prj=626&rqi=t7X1J2wmGtlwA2td5jFEVWZjSe
RT1ELEC-55-010 | ce389139-1904-4973-a9b8-d4a87bb38ce6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Provide temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616838&prj=626&rqi=5jIr2tYZ0NzWtXNEpdfxOLEDMf
RT1ELEC-128-008 | f0e17789-670d-4d09-b50c-fbfca3449865 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Missing cable tagging for L2, N, and G | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616948&prj=626&rqi=J6mFJ0Jcao8DssTg9X4djI8WPL
RT1ELEC-55-006 | c2911a6f-4eaf-4217-a39d-e0bdad211a21 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Deep cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616832&prj=626&rqi=vb8jBU5IdEeCraYtLqIpyUqPfs
RT1ELEC-129-008 | d1bfa6a9-df1f-4d58-959a-41f54a569a15 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Missing bonding jumper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616953&prj=626&rqi=XP4UvGDIfJV1GpGns7oZISRmXK
RT1ELEC-55-005 | 4afe2435-1be4-4756-b36a-22a58968cd2d | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Busbar joint bolts not yet torqued and torque-marked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616831&prj=626&rqi=G7ydhVoyzAvzowKfl58R2IIznN
RT1ELEC-128-012 | 9a0247b6-7541-4fe9-876e-7cd769ac25bc | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Remove temporary marker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616952&prj=626&rqi=co4VaU9tnp4RcxV5LnUB8kgEZK
RT1ELEC-55-004 | 8a12d2b9-41bf-4aeb-86cf-1b53415ac660 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Control cables appear not connected, please verify and confirm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616830&prj=626&rqi=zln9UTvbvCghZJ8NUYef0m0ViU
RT1ELEC-130-010 | 65cee34b-a469-4ede-9592-fb7d2af43fac | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable insulation (vinyl) is torn. Please replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616945&prj=626&rqi=BuuRTfeoTwcWsn6swIULmY1G1A
RT1ELEC-55-008 | 86eaa272-bd84-46ca-ab04-334c5115aaab | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Vertiv emblem on panel door is loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616835&prj=626&rqi=ZEwNNjI9B9GPL1bkzQme16Fhw6
RT1ELEC-130-009 | 5299cf33-0bb6-4f6f-91ed-8486b841189f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable containment is not properly aligned/levelled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616944&prj=626&rqi=yPkxKszHeeexyeOE3wkAodLRes
RT1ELEC-129-009 | 17e28b87-51bf-49ac-8522-81028aaa1a0f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable tagging not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616954&prj=626&rqi=Yj3GP8JXU7rc8JY0OgMY2Foleg
RT1ELEC-128-011 | 343531f2-2fc7-4341-b950-2af38b9748d1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Cable tagging incorrect and no phase identification (L1, L2, L3). Revise to: from 1MDSB_C_1 to 1DB_C_CRITICAL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616951&prj=626&rqi=j4wwaFJvMOjhJiiPagsTBEiRs1
RT1ELEC-130-011 | f92f69f4-4233-450c-93d5-c1b380221c3a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Incorrect cable tagging. Should be: from 1MDSB_C_1 to 1DB_C_DATA HALL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616946&prj=626&rqi=xyrgOyt9IMl2ZBkNqg3Zhz598A
RT1ELEC-128-009 | 11d8cf0c-e980-4828-ae94-596471576d58 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Glanding cap at cable gland not properly installed; incomplete coverage observed. Reinstall to ensure proper sealing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616949&prj=626&rqi=lP9AV95KGDDyTSQhIBexadqkJ7
RT1ELEC-55-001 | 09519c2a-fc54-436d-b928-1074dac8569c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616826&prj=626&rqi=ZZ5qahsaTbJMz5m3gbRyJ3632H
RT1ELEC-55-003 | 02f9d6b2-5757-4980-9910-d7a5c0a17f6c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Minor dents & scratches require touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616829&prj=626&rqi=PDadbDyCYFuRzeQQ2Ba1If1C9s
RT1ELEC-55-009 | fafe787a-9ddc-477c-af33-60ba2dfd35ac | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Ensure all ACB & HMI are properly protected from construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616836&prj=626&rqi=OEDDyDPuhITpGsNws49ZiN60DM
RT1ELEC-55-002 | 21c5ef7c-a582-4d34-ac80-d165cb82853d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Panel tagging not as per design (should be 1STSSB_C_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616828&prj=626&rqi=6sTDsgKZz2cNkEaelNBNujtQR6
RT1ELEC-55-007 | d2b41587-1ce0-4d00-b29e-a73263c3f3f8 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_C_2 | STSSB - Static Transfer Switchboard |  |  | Please provide correct GA & SLD drawings for 1STSSB_C_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616834&prj=626&rqi=fmutfJ7tu5ucJw5g0hriVZ2OFS
RT1ELEC-130-008 | 85d09a9f-0d23-4d83-b757-b3b78fda862f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-30 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | (Issue CxL2A LV Cable) Improper termination, conductor still exposed. Please rectify cable vinyl | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616943&prj=626&rqi=DqkPvnSL9empbShRevgDBiHDxg
RT1ELEC-36-005 | 5c77a645-02ae-44ce-bde1-ea972cc3cdf8 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | General cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616811&prj=626&rqi=2NyTC0ePE4EFiunmdkvGDjakTl
RT1ELEC-36-002 | f90b74a8-cf39-44a5-8be0-cdd80f2161ca | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616807&prj=626&rqi=P7DKH8gicwRmONSklB1OfwjKj4
RT1ELEC-35-001 | c284d50b-18f2-49d4-8164-51abb7608b60 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Approved layout drawings not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616796&prj=626&rqi=TT3lLVbR4rIXE6UCG4pus6ls5D
RT1ELEC-35-004 | ac5d0db3-9365-49c6-9bb4-89344e9e6b16 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Discrepancy between drawing and actual position (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616801&prj=626&rqi=TctGGUx7HBVlWNa96e3IzuJ7Or
RT1ELEC-36-001 | 76a37e41-02f4-480e-bc0f-90067230093b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Approved layout drawings not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616805&prj=626&rqi=6JMb8nY7gNwrQFRUZpczvJ5vW9
RT1ELEC-36-004 | 13a45b49-1257-4743-9697-1daaa6a8c4be | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Provide temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616810&prj=626&rqi=f7FY888BeOCNYsdd1gK5jx8okH
RT1ELEC-35-002 | 209d56fa-5bb6-49a5-a0d6-04091e74476c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Anchor bolt thread minimum 3 threads exposed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616799&prj=626&rqi=wCb48NBGuhQTKZGyg1meoqPWTL
RT1ELEC-36-003 | bbfecd30-ddc0-4bd6-a865-b32f527531b2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_2 | LIBATT - UPS Battery |  |  | Panel tagging not as per design (should be 1LIBATTSYS_C_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616809&prj=626&rqi=ICkKsfvc5VTs8HvJHBtRSfBOAt
RT1MECH-115-003 | 87e9c12b-90a4-4a94-9033-7e3ad172b8cf | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | please remove unused material / object, and also need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616791&prj=626&rqi=rlZ2ret085MCeER1TZDS93FgAK
RT1ELEC-35-005 | 9eeaa201-2e7d-4364-967b-990daaaa0dd1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Provide temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616802&prj=626&rqi=oYjHeyvjd0QH6YIUzUIs7SeT60
RT1MECH-115-002 | 4323908c-5692-46e5-9d97-26c65c8d8f04 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | cleaning issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616790&prj=626&rqi=CO8keu63X1QVSWgFJWMI86iesI
RT1ELEC-35-006 | 3903e7a5-e13a-4d84-86be-6cb64a5c5612 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | General cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616803&prj=626&rqi=Nrllysk1m2R929KV6Xm0GdQ5mF
RT1MECH-115-001 | cde0bdcb-dcea-4ff7-b8db-9dd18aa7595c | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_D_42 | CRAH - Computer room air handler |  |  | minor scratch has found | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616788&prj=626&rqi=jRIHIxA8uPUh7pV6wXItGvfXOC
RT1ELEC-35-003 | 98adc621-8b16-4449-867a-4b4764c516b5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_C_1 | LIBATT - UPS Battery |  |  | Panel tagging not as per design (should be 1LIBATTSYS_C_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616800&prj=626&rqi=WfdrGO7UHYKVA0LmoexIklwBpv
RT1ELEC-170-006 | 12d1aa1e-47e0-4c49-a05d-a157bb11a75c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Please provide temporary cover to protect from construction damage, dust and debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616669&prj=626&rqi=Mf7ibM5ArNkTcQ56AOQ2B8nLv4
RT1ELEC-170-004 | e2129569-8ae9-4369-848d-1a57e71dbfa3 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | There is a discrepancy between the drawing and the actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616667&prj=626&rqi=2lVXD4NW7uVahx9rCVZ2ld89XG
RT1ELEC-170-002 | 6ea887ef-ce48-409d-ba52-d1718a01b433 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616665&prj=626&rqi=jMwXMs9ZZYbvXfDMDXMvujpuc2
RT1ELEC-171-001 | 48bd70a7-2f45-491c-a009-36aa604b8faf | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616670&prj=626&rqi=vaWz3NgPh0iGzPlrZaj38zmzr1
RT1ELEC-171-003 | 4ff21ba3-9bef-4456-bff2-18c2d3787473 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616672&prj=626&rqi=EUQ3f061T64N5TZUsLz41D35FW
RT1ELEC-170-003 | b6f12640-bae5-42ca-a742-25ada577d4e7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Cable tube marker is faded. Need replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616666&prj=626&rqi=MGNxJ3lASB6mbMoqlpMTINcGFF
RT1ELEC-171-002 | d91014d6-dcea-4e5f-8da8-ce34154c8a76 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | There is a discrepancy between the drawing and the actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616671&prj=626&rqi=xpNLx3yikV6aeT1cnlp3bTTZWe
RT1ELEC-170-001 | 810630ea-0dd7-4158-97da-49fb4749a72f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Approved Technical Submittals / Material approval / Specs not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616664&prj=626&rqi=5ehHzkLd1TINifw4GLiPnVyEN9
RT1ELEC-170-005 | 4405d287-aa3e-423b-8141-b0a0a708f36e | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_1 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616668&prj=626&rqi=kPoFI6EeSAv7RhGbWs71SxMS9T
RT1ELEC-171-004 | 7f76d118-fa4a-4263-9f57-51fcdc861c3f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-26 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_B_2 | TOU |  |  | Please provide temporary cover to protect from construction damage, dust and debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616673&prj=626&rqi=0oO58LglakfOkselygJHunYrYp
RT1ELEC-130-002 | dbc2ee47-2847-49f5-92ca-a48f1b21e92c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | There is a discrepancy between the drawing and the actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616415&prj=626&rqi=1Dmmw8cUQxp8BYslsamP0vxOrv
RT1ELEC-173-005 | cca1cdfb-7c63-491f-afd3-76652dd1f3c2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Please provide temporary cover to protect form construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616478&prj=626&rqi=nXGFmqgNYeGXwvDlBErsd9EmZX
RT1ELEC-173-004 | 36b20d40-22ab-41fc-a7e0-429bee1baa5d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Paint stains on panel surface. Need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616477&prj=626&rqi=asxLd56zxPnOJYX1uYcE0ZG7ti
RT1ELEC-130-006 | 3e6956f9-cd78-45cc-bd6b-1205bdea21c3 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Please confirm torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616423&prj=626&rqi=PChJnHaQkm3rSHu2jR14gNGn4w
RT1ELEC-173-002 | 06fa8ece-6952-42ac-8521-38b209344529 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616475&prj=626&rqi=qLhRPU6cCxNNuL3Holris81oIT
RT1ELEC-173-003 | 8a635376-3f79-424c-89dd-e3990ffba775 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Cable termination is not properly done. Copper conductor is exposed. Please rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616476&prj=626&rqi=QyZmD5GxtQBgfjSsY9LKsNhKkN
RT1ELEC-173-001 | ba93dc15-aeb1-403a-8ca8-359e5c1f5210 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Approved Technical Submittals documents not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616474&prj=626&rqi=TPq2jhg7XjSIePOLGH1ERMxko9
RT1ELEC-173-006 | e67869aa-a485-4e8a-bb84-3b0d7ca65e54 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_1 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616484&prj=626&rqi=p5XPnUh1w06qRQo7HVIyRxFjHN
RT1ELEC-172-004 | 7fe2d5cf-d112-44b4-99d1-8ba45cd3979d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Missing phase separator / barriers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616482&prj=626&rqi=LPuAv9uacbD7R5VrBZMDij65kn
RT1ELEC-175-003 | d34448ec-cb4c-47fb-bf51-d7ebeeb486fe | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Phase separator / barrier is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616520&prj=626&rqi=KdLnxCzzh7BpoPVBximei5bAyl
RT1ELEC-172-003 | dc9c405d-77b9-4a9e-a871-912413149e1c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616481&prj=626&rqi=IKGhnfEe0iTEds0xAYMbCy4xQy
RT1ELEC-172-001 | d7ae71f7-2fbe-4e7a-bcc4-5e6ee9de7892 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Cable tube marker is faded. Please replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616479&prj=626&rqi=aNvVauLMpiuKBpus6zX8OzGOvq
RT1ELEC-130-001 | c12f5c1d-fd4e-4643-b2ec-6acf9f7fa298 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Please upload correct document for 1DB_C_DATA HALL. This documents for 1DB_D_CRITICAL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616342&prj=626&rqi=NzpatX1xc2GB09d3w4RAfDSArh
RT1ELEC-175-002 | 14167d7e-af0a-4e63-bee9-1fdb8bd3f43b | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | TOU F positioning is not shown in the latest approved layout drawing (only TOU A). Revise drawing and include dimensions (mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616519&prj=626&rqi=WywZAaFfyHdCebBFhkIx5VSuiA
RT1ELEC-175-005 | 731cf0b8-179f-4fe8-a1af-32eaf88c3ad9 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616523&prj=626&rqi=cA8i1Pockfc75QwPUDpiFSmfFK
RT1ELEC-130-007 | c1e67f49-3cc7-4505-a800-844c82d6e930 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_C_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616424&prj=626&rqi=OABkrh67g2mA5YtsBYawg11qdp
RT1ELEC-175-001 | 77b2b15c-f979-4557-80b1-fd4687518498 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Please upload following documents: 1. Approved technical submittals documents 2. Factory test data documents 3. GA & Schematic drawing 4. RFIT documents 5. MoS CxL2B documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616518&prj=626&rqi=2J0AT35LcucStLp9Fj9AhwYeSf
YT1ELEC-4-004 | 8acd9b07-2607-4fab-bdcd-c8c0cc540fe3 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2B MV Cable RMU_F to MLTX_F) Tan delta values on phase S increase significantly, indicating possible insulation degradation. Please clarify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616528&prj=626&rqi=NpPU90nZb7kTkTufBFKQ3CHSQx
RT1ELEC-130-004 | 6cabceb4-8779-456f-8a34-6b5901fc36ad | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Panel body is dirty. Need to clean | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616419&prj=626&rqi=YfPDfyQOClZisg7KPjcTciOR4S
RT1ELEC-129-002 | e0a26e6e-2888-49c6-be9d-387a73993672 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (1MDSB_C_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616399&prj=626&rqi=DZsK5G5fVx1wEf6RMcfPMrIM03
RT1ELEC-129-007 | 87d3f015-a7ae-4594-a3fb-070252730bf1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_C_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616407&prj=626&rqi=UFRCuzsANs6O9huTr65qV0g12a
RT1ELEC-130-003 | 16b07965-fe19-4241-be86-e4af6613bc6b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels (feeder) on the acrylic cover above the breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616417&prj=626&rqi=JbIHgflwtkrMYlwaD6A1KR4KrT
RT1ELEC-129-005 | 731a5167-4527-48da-932a-bb1b5aa15a14 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please remove any temporary marker markings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616404&prj=626&rqi=XpqBoh451YCaGkTst1ibFoJwm9
RT1ELEC-129-003 | 889e22b7-32f1-44d6-a1b1-a7ea6d85a8ca | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breaker, similar to breakers Q1-1 to Q1-4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616401&prj=626&rqi=bTWCKowDfSpMx9oniVz3hYm5nn
RT1ELEC-133-004 | 490b90c7-4605-4d5f-bdef-f1fedf12463b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels (feeder) on the acrylic cover above the breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616489&prj=626&rqi=uJulrbvM2gdRDEMzwwdEqRh2uM
RT1ELEC-130-005 | 01d57dd7-f673-49b9-9c9f-bde8bf0924bc | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_DATAHALL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (1MDSB_C_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616422&prj=626&rqi=eZ7Rutk00Do1I1oGyQ6qMoxV6t
RT1ELEC-133-002 | 368268d7-f6b3-49e5-bfff-b0f748d2839a | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | There is a discrepancy between the drawing and the actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616486&prj=626&rqi=ysMSUm1dRtW7HnbS7H5V03RVLA
RT1ELEC-129-001 | 6d3598ed-f13e-4b9f-9d38-81620c278ace | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please upload correct document for 1DB_C_EWALL. This documents for 1DB_D_CRITICAL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616341&prj=626&rqi=aOczhggn6CSgmZfhz0Nox6slR4
RT1ELEC-133-001 | aa24f238-d5ea-422a-88bc-862cc95cdf99 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_F_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616471&prj=626&rqi=DzyPgyiq8jkxdToVDhfCBsVi7N
RT1ELEC-175-004 | 86bb8f86-ad62-414f-9602-6c6afef5e010 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_2 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616522&prj=626&rqi=Vf2I9hfsbv2tsvPtGTXHvOOdWG
RT1ELEC-129-006 | a472474a-f0e8-45af-8388-241925b4c8c7 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | There is a discrepancy between drawing and actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616406&prj=626&rqi=vLA08hTwriwtCIFxJD4YXt6Nm5
RT1ELEC-133-003 | 8e300209-20ec-487e-b742-66672170e319 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (1MDSB_F_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616487&prj=626&rqi=8kUrScjsDYgyt8iN8Mn38CGyeL
RT1ELEC-172-002 | f2a9eed3-ce8f-4240-b474-a42d62511165 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_C_2 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616480&prj=626&rqi=lSyK355YWKdsUhltmE0iPZf9dq
RT1ELEC-177-002 | d83aed2b-7d0b-4351-84c0-f964bec77451 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | TOU F positioning is not shown in the latest approved layout drawing (only TOU A). Revise drawing and include dimensions (mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616508&prj=626&rqi=4Tu77APmoRuwtZPjvBPobNTTae
RT1ELEC-177-005 | 17dcfd33-badc-4ffd-acc3-d71c7537ee34 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616511&prj=626&rqi=7jSExGDokfpdvEZiSfBJmaaebK
RT1ELEC-177-001 | 7d3c1366-33c8-40f0-9c8a-af6002a81732 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | Approved Technical Submittals documents not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616507&prj=626&rqi=FojRqjvcAPDGtjthZLvp5Gl8a0
RT1ELEC-177-004 | ee043035-ec6a-4204-9270-6dc95fab8639 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | Cable vinyl material (neutral) is inconsistent with others. Standardize to match | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616510&prj=626&rqi=KmUGskntDg9opwcp9mkqOM41Yo
RT1ELEC-177-003 | 9292a87c-4f8c-4c8d-81b5-f1a7a05f35aa | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1TOU_F_1 | TOU |  |  | Provide incoming source label below the panel tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616509&prj=626&rqi=M66wRcx83qyvGaCYMXYMhLtQ4g
RT1ELEC-133-007 | aea45b00-a9ee-4ebf-8657-b393a4338878 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Cable tube marker is faded. Need replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616495&prj=626&rqi=ajmVbh1sXD4knhQiq9RDFRP98P
RT1ELEC-133-006 | 971b1c73-9d67-46d1-b41b-293aabd1f591 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Incorrect document uploaded. This for 1DB_D_CRITICAL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616493&prj=626&rqi=37f4sgbjIJDID1Mv089QCK9g8F
RT1ELEC-129-004 | 3fcb2999-172c-4829-bf31-27199695fcd8 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_EWALL | DB - Distribution Boards |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616403&prj=626&rqi=H18BV9KbPG4qUzbfsmdonDHvkR
RT1ELEC-133-005 | a393888e-7fc9-4746-9e36-c2ecc765fd91 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_F_DATAHALL | DB - Distribution Boards |  |  | Please confirm the torque value applied to the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616490&prj=626&rqi=d3ZPcmYjC0NvXPthZiN8yhU0uH
RT1ELEC-128-005 | 86cba36e-cdbc-406f-9215-ccf551237452 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breaker, similar to breakers Q1-1 to Q1-3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616412&prj=626&rqi=9oSpv6O1VHegVzjs3rbnjMgrZk
RT1ELEC-128-003 | 22e2d062-23a6-4655-9e48-95c089299a1a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | There is a discrepancy between the drawing and the actual positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616410&prj=626&rqi=IDs0sBaC3HEeicKFx7en0oZals
RT1ELEC-128-007 | 60a219dc-e22b-4f6d-966a-0a6adb204c0a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Please confirm torque value applied to panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616414&prj=626&rqi=k65ohaPbRNHCOLeVrcU07E3d13
RT1ELEC-128-002 | c5e48ea0-907c-4a92-a821-87998df39299 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Please revise the incoming (source) label of this panel to match the approved drawing/design source (1MDSB_C_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616409&prj=626&rqi=ffSZoCabGd19zy3OacTHoAWUZp
RT1ELEC-128-001 | 9138c6bf-77ea-4898-8a63-fdf1c1d21bae | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Please upload correct document for 1DB_C_CRITICAL. This documents for 1DB_D_CRITICAL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616340&prj=626&rqi=4iFrgVmgWZg0UnDXQKFMY4JccW
RT1ELEC-128-004 | 42aa8449-e4c3-4857-9363-d0229d4d5760 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Please update panel single line diagram with the correct incoming source (1MDSB_C_2) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616411&prj=626&rqi=BsoQnBUFazsmgKzlElPy8hDYMj
RT1ELEC-128-006 | 4892101e-60a4-4aa8-8c1e-4d036fc30a82 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1DB_C_CRITICAL | DB - Distribution Boards |  |  | Equipment need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616413&prj=626&rqi=FwuwLqyaT2NZBRhWK0amDtW020
RT1ELEC-123-005 | ed2db183-ea3b-4c45-896b-fb9ced6449d4 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Please update the drawing to reflect the actual unit positioning based on the RFIT inspection results. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616248&prj=626&rqi=bBX2BPBMWdeTw8vLW0AKOMWEoQ
RT1ELEC-124-005 | 812e440d-fe99-4a90-a140-c6ed215a53a7 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | Please update the drawing to reflect actual unit positioning based on the RFIT inspection results | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616253&prj=626&rqi=1i8TiB6mCYnqeGK7cuymxWLcB2
RT1ELEC-124-001 | ba3c3448-d16f-444a-9d52-2f3f823c21b5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | Please correct the incoming (source) label in accordance with the approved drawing/design (1MDSB_B_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616249&prj=626&rqi=B3NhXC9E8GUhnr5CW7N6Mx6RkS
RT1ELEC-123-001 | 43d4a88c-634a-47bf-b615-c6426e546bbb | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Please correct the incoming (source) label in accordance with the approved drawing/design (1MDSB_B_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616244&prj=626&rqi=U8rioaitRqpyJe2lPlZOSts7GW
RT1ELEC-122-001 | d04e422f-fe58-4449-ae82-9083646e82cd | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | Please update drawing based on RFIT report for positioning unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616238&prj=626&rqi=rKvFM1te13Ct9Dbhq6zg6SmVnp
RT1ELEC-122-003 | 1402cc94-7a60-414f-aa15-7fe6ca6b3131 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breakers, similar to breakers Q1-1 to Q1-5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616243&prj=626&rqi=qLrKhiEbUFzBT0HD3DDr1mQed2
RT1ELEC-122-002 | fea55940-06e6-4a1e-b1ae-75f133a28b7a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_CRITICAL | DB - Distribution Boards |  |  | Please correct the incoming (source) label in accordance with the approved drawing/design (1MDSB_B_1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616240&prj=626&rqi=e6rCUEfMD8367iGpkQYN0K3CCw
RT1ELEC-123-004 | 017e126f-a560-4313-b16d-ebdb95634d04 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breakers, similar to breakers Q1-1 to Q1-4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616247&prj=626&rqi=szrjZ9A1m1bXIRYfnm8zZnrWXe
RT1ELEC-123-003 | c3258801-ba95-40e6-8d08-b4ba69a5acf5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Remove temporary marker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616246&prj=626&rqi=N5fB3Y0bHRmODC11jQXXzpshfo
RT1ELEC-124-004 | 3cca743c-480a-4156-982d-232e0750c395 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | Please add outgoing breaker labels on the acrylic cover above the breakers, similar to breakers Q1-1 to Q1-5 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616252&prj=626&rqi=ASWdFbTGMzlSZYu012c77oG3t1
RT1ELEC-124-002 | 2a2cf7aa-dd37-4073-b1e7-7452070ee15d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | Cable marker is unclear/faded. Please replace with a proper label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616250&prj=626&rqi=A1ILtaiDaWDPkMvdZRb8PRuERe
RT1ELEC-124-003 | 45149e13-c40f-4028-9bcc-170f4fc5cfd0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_DATAHALL | DB - Distribution Boards |  |  | Please clean the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616251&prj=626&rqi=Ew7XR6s8Z55BuxznOebbbe77pQ
RT1ELEC-123-002 | ae0e3ab1-52eb-41b2-80bb-ab0a12c3c407 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_B_EWALL | DB - Distribution Boards |  |  | Please confirm the torque value for the panel bracket bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616245&prj=626&rqi=XypaJ0bACHTvwgx5KSNAj4J8zw
RT1ELEC-53-003 | 4c46b082-05b6-4d13-bc08-9f44b3446e25 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Torque wrench calibration certificate does not match the tool used during inspection. Please upload the correct and valid calibration certificate for the actual torque wrench used | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615856&prj=626&rqi=KkLzQIHHYIr3QPorjLYPW89zdE
RT1ELEC-53-004 | b2cf0da4-c425-4369-96af-65d7e9a83080 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | MoS CxL2A document is still empty and has not been uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615857&prj=626&rqi=hbDx4Y7GesKYSHRdMPCrka9UaB
RT1ELEC-53-001 | 1ac8ee79-f1c2-483e-bd27-8b05ffadc4e2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Factory Test Data document not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615852&prj=626&rqi=HrLdiIUR8GyouLgGMrnR3wIHDo
RT1SEC-12-001 | 4f2ffc30-c2d6-49d8-a3b6-3537bbb08894 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Security | equipment | 1ACS_level_7_General | ACU _ Access Control |  |  | Please upload following documents: 1. Approved technical documents 2. Installation Startup manual documents 3. Inspection checklist 4. Approved shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616228&prj=626&rqi=b8KjndKGNKDCo2DcD073FC6ApN
RT1ELEC-53-006 | 389e1ec4-d3cf-4f4b-ac04-eed728e35185 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Please ensure all ACBs are properly protected to prevent construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615860&prj=626&rqi=way11MofkNWtFNjq9HMMRh7ZLp
RT1SEC-10-002 | eb4c086c-422a-43d2-b00a-6b14d6eb3bc4 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Security | equipment | 1ACS_level_5_General | ACU _ Access Control |  |  | Tx room level 5 is installed with a single reader device instead of a double reader as per approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616227&prj=626&rqi=A7Zdye01xsa8XV54xGILAfjpKy
RT1ELEC-53-007 | 80ed8fa6-6955-408f-a2a6-8020f23cb7a3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Anchor bolts shall have minimum 3 exposed threads | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615861&prj=626&rqi=yZT928hSHu9eZ1vtN3drBH48lv
YT1ELEC-3-006 | 6ad8dc33-8daf-4979-aeac-6d31a44295a5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Please apply cable vinyl for proper insulation and finishing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616234&prj=626&rqi=6QLVWz2gq6B5YwalnvboPUTWTQ
YT1ELEC-3-005 | 6f5c6a55-97a9-4030-889a-e96e0b129546 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Grounding cable is not connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616233&prj=626&rqi=6XxMwaplAvtQ88mEGffSnwJ7F6
RT1ELEC-53-008 | 766e9b2f-3ee8-476d-b7ff-231d0c252a52 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Please confirm busbar join not yet connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616235&prj=626&rqi=tAJhcLdHbNVzOvyehUkm3Zt9dq
RT1ELEC-53-005 | 13994746-9a56-47d2-88c4-c5c053cc3e6f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Minor dents/stains on panel surface observed, need touchup | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615858&prj=626&rqi=YBr0vmepGvjjwxBhV8ZW8E7Jyo
YT1ELEC-3-004 | d6a0ba04-e6e7-4d90-baec-365f8d8622fd | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor | L2B | Torque required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Busbar connections between batteries have not been properly torqued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616232&prj=626&rqi=3Pm8TehO9iXGU2ViRtrrlh7xn7
RT1ELEC-53-002 | 3af62dcc-b41d-494a-87a1-9593981b74fd | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_B_2 | STSSB - Static Transfer Switchboard |  |  | Please upload Installation and Start-up Manual is documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615854&prj=626&rqi=jNSLqXZkcYB3DqAel7Dep0NUwg
RT1SEC-10-001 | 83938e05-a796-4121-a174-a3e62850ca49 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Security | equipment | 1ACS_level_5_General | ACU _ Access Control |  |  | Please upload following documents: 1. Approved technical documents 2. Installation Startup manual documents 3. Inspection checklist 4. Approved shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616224&prj=626&rqi=oFbyKa3epNHKa60catc3i7yZ1q
RT1SEC-9-001 | d7424d34-6170-4dcd-8eb0-f8bfb96f75bb | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Security | equipment | 1ACS_level_4_General | ACU _ Access Control |  |  | Installation does not comply with approved drawing and is positioned too close to the manual call point (MMR B Level 4) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616223&prj=626&rqi=6Vk1ZGlxnn5v6XMaaz6y1NLjBF
YT1ELEC-4-003 | 66e4afe5-d98b-43b1-8edb-135693e9965d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Please confirm the BTU incoming breaker rating. As per approved MoS it is 15A, while the actual installed breaker is 20A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616231&prj=626&rqi=RvfVkDcM1ZmBgmn5mHUDQkuK1u
YT1ELEC-2-004 | 910e6705-c420-47b7-8a26-5f33d225b60b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Please confirm the BTU incoming breaker rating. As per approved MoS: 15A, actual installed breaker is 20A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616230&prj=626&rqi=sZEa4FJAyGTHiBxBRAw8hdnlei
RT1ELEC-56-001 | a1edbad7-8a19-4fa7-bd1d-cd9343535667 | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-03-16 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_1 | STSSB - Static Transfer Switchboard |  |  | STTSB rear back frame anchor bolt not installed. Front panel anchor bolt also not complete | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615755&prj=626&rqi=Np8guKi7hNSm7u8yB2uO5jMTi6
RT1ELEC-26-001 | 44b30f76-ce64-4310-8a0b-c82608c8283c | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-03-16 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_D_2 | UPS - Uninterrupted Power Supply |  |  | UPS Mech D2 rear anchor bolt not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615772&prj=626&rqi=XtCqxn2eVvX6dvHggpBKnrcE2a
RT1ELEC-2-017 | 50bb91ab-d5f1-4973-bf92-7c6ad72b4578 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) The equipment needs FOD | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615750&prj=626&rqi=u4fpPrdp17l3hRIocM2YKl6v6o
RT1ELEC-24-001 | 11cec56e-66c1-4460-8fb0-fa1592a561c6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-03-16 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_C_2 | UPS - Uninterrupted Power Supply |  |  | UPS Mech C2 rear anchor bolt not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615771&prj=626&rqi=JVvkFJ7e3mWYPbVYu1W6nogfF7
YT1ELEC-4-002 | a11486dc-e66e-4f48-82d9-1c54249a8436 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | General Contractor | L2B | Incomplete Connections | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Busbar connection each battery not yet torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615698&prj=626&rqi=d8IzEDKaAfbX0jUOhLHFB8bG18
YT1ELEC-4-001 | e31ee727-38b2-4d7a-9ab4-87f95f779de7 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2B BTU) Grounding cable not yet connected to main earth bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615695&prj=626&rqi=xuJnulyJkUuUp1oX855v3OtTlG
RT1ELEC-2-016 | b57c5fa7-d85b-4f59-a151-2c3c73bebf72 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Minor dent & scratches observed, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615704&prj=626&rqi=Ot1hs85Wl3ohSUH5wQyshao9gm
RT1ELEC-2-015 | 6086b208-1e40-49f3-9eaa-43d44a47cdbb | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-15 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Grounding cable not yet connected to main earth bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615703&prj=626&rqi=gx1cTPJFT513H5putrMjeNyvF9
RT1ELEC-11-012 | b6bf2ae1-cfdd-4419-a807-dc193704ac3c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | (Issue CxL2A MV Cable) MV cable grounding braid not properly installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615671&prj=626&rqi=Qq1ZUbILLGz7l4F7nBpRbB1Sw6
RT1ELEC-4-025 | 2de85fb9-5bad-48f3-8778-f755e4078227 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-13 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable) MV cable grounding braid not properly installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615672&prj=626&rqi=phsqSK8hXdmhykmiZbs5re2AFc
RT1ELEC-1-004 | 3a8d4ce6-a8c6-4aee-8122-5b0445d2324e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Multicore cable schedule not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615392&prj=626&rqi=f5nxesKd4GnIS9FcUtv5tWSvwQ
RT1ELEC-1-007 | 656db4dc-a358-4714-b112-c9317dccb68f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Please upload RFIT report document for positioning unit RMU not MV cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615397&prj=626&rqi=cUpjPgyc9zvWcmkFCYmbVV8odO
RT1ELEC-1-008 | eb69835b-8420-425b-b9d1-2da1cacc1b40 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Dust & debris found inside the equipment need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615398&prj=626&rqi=pnfEsvSIV69W5jq77OpCweAbjV
RT1ELEC-1-013 | 1464f61e-72f1-4b59-aa44-b2f3980a3465 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Sticker found damaged and shall be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615405&prj=626&rqi=TNpTmp8sVvYRCpSerlwLfbKMW0
RT1ELEC-1-010 | f9dd1a71-1b33-41b1-a9ff-fd4b894dc7cf | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Latest GA & schematic drawings not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615402&prj=626&rqi=OQB2DWLssPM2gZHyMEpPWdQbxn
RT1ELEC-1-015 | 73b68c2c-14f0-4cc1-8d06-5b7648f94db1 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Equipment positioning different from latest approved drawing (please refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615407&prj=626&rqi=xlgHgEo3sHuk4hOB7kc0cGKx2o
RT1ELEC-1-009 | af165820-62f6-49fd-8b6a-7a1b6f847936 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Relay protection unit is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615399&prj=626&rqi=9lvDGo8EQ93nXyIpP2A4tVXQrN
RT1ELEC-1-005 | bd379597-2e3e-48f9-a7f7-675c0965e027 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | HV cable design not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615393&prj=626&rqi=SyVLkY99GzKxtvenkZ5homrmOE
RT1ELEC-1-002 | d3535e80-3ddb-4379-b171-555314f49dfb | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Switchgear Installation and Operation manual documents not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615390&prj=626&rqi=LCQFs6ieMfLbmdnkf6ps5mWnuQ
RT1ELEC-1-006 | c626ea27-514d-403e-a7a9-980b5d885cb6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | L2B Static Testing Method statement not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615395&prj=626&rqi=nKAXbg94tozZNJKkiNsHnGI0GA
RT1ELEC-8-004 | e5be6e7b-e95f-4b63-8372-1d1b4f93a9d2 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Equipment positioning different from latest approved drawing (please refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615388&prj=626&rqi=MaOo7s5FuZe23tZwesu4zdxiOn
RT1ELEC-8-003 | d210942a-65ab-4a71-bf7a-629616cc1e19 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Tap changer opening is not covered. Please provide a proper cover for the opening to prevent dust ingress and accidental contact | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615387&prj=626&rqi=RZA1knpGV16dAAClbYMPwLtVgn
RT1ELEC-8-002 | 0764ec86-5a47-48ef-9630-869d09e958c2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Fan cables are not properly dressed. Poor cable arrangement may cause damage or disconnection during maintenance activities. Please tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615386&prj=626&rqi=gHdsalhQVjMiU3vAQaThipql8Q
RT1ELEC-8-001 | dbc973e2-5541-41ea-ad27-361effec74b2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_B | MLTX - Transformer |  |  | Door scratches, need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615385&prj=626&rqi=rsJa05IzlrRpIqCo72KBWdQ3PU
RT1ELEC-1-014 | d18088ca-48fe-4626-909c-90ecc4b7297f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Bolts found rusty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615406&prj=626&rqi=n8LjDZslYTvHdMh63SDibT8Twe
RT1ELEC-1-011 | 9596f028-3ec5-47d1-9c26-0f352939764a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Some components have only one label on the mounting/body, and terminals are not labeled. Each component should have two labels (on the mounting and on the component body) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615403&prj=626&rqi=e8kbtnQnp9gSluQOiHvu9nuGo8
RT1ELEC-1-001 | 9989de70-963f-4724-a6a0-b1712020b959 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | Factory test protocol calibration certificates not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615389&prj=626&rqi=bG54uE9p0nG6dSkW80DP66E6XX
RT1ELEC-1-003 | 2a778aef-2a7f-4ada-abdb-c24f9b08fa6a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_B | RMU - Ring Main Unit |  |  | MV LV Network Discrimination Study documents not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615391&prj=626&rqi=Z7J1nJKsX7IdU0a3yxXCYEZyJ4
YT1ELEC-3-002 | 849e59c7-8261-4d59-87b8-73c440ba5447 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Some of test not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615442&prj=626&rqi=zpEpHkqFFplbcERFXW2pTBenCP
YT1ELEC-2-002 | e029d117-f823-4030-baa0-da607f5ff56a | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Some of test not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615439&prj=626&rqi=SmDicIPi7HjX19VNKEilmY05KJ
YT1ELEC-3-003 | 4b8fd10a-9a0f-451f-9f3e-23d75db35af6 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Invalid Testing Tools due to expired calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615443&prj=626&rqi=KmjXXvxr48xV8OwW8D6T9YUjDb
YT1ELEC-2-003 | 2227f800-ea7b-4a6b-b79c-d4a994c30a49 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Invalid Testing Tools due to expired calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615441&prj=626&rqi=T8tF2E13rb5fp7SoRDD6xTflCM
RT1ELEC-126-007 | 59fea881-e983-4dca-bab3-37a73d21ac91 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Gland plate bolts not properly tightened | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615220&prj=626&rqi=FaJ2cciUKKAoomADZmEIh3JIFr
RT1ELEC-126-002 | 7448142f-817c-464d-8329-868044b90c9b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Please upload material approval/specs documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615215&prj=626&rqi=XnModHbXqzLnbZoq4CSKHgf982
RT1ELEC-126-006 | eff26ade-861e-4434-97ff-4f3ca627eb7d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Dust and debris found inside panel, cleaning required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615219&prj=626&rqi=muUKcj2rlbikhTYhAAcedCDndP
RT1ELEC-126-003 | 0961522d-0eb5-4988-af36-3c42fdd4332c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Equipment positioning not aligned with the latest approved shop drawing (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615216&prj=626&rqi=CsVGjN9aebdj2QmIIg4VIEfgpp
RT1ELEC-125-009 | 40866a91-0085-4356-84fe-51277a3de2c7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Dust and debris found inside panel, cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615213&prj=626&rqi=MnLCJzr1bcTgsxH59sDCvhuHph
RT1ELEC-125-002 | 446040ed-098d-4586-846b-1016333c07df | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Equipment positioning not aligned with the latest approved shop drawing (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615204&prj=626&rqi=xPak2aGGAPvRyvSnYw3nL4286A
RT1ELEC-31-004 | e35f43e9-b184-4652-a01b-b2435766c6d2 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Anchor bolts still loose during torque check. Please check all anchor bolts, re-torque, and apply torque marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615234&prj=626&rqi=akP6I8Ar5hvfyZho4kTUYYpXg0
RT1ELEC-125-003 | 3d5622de-46d8-4aef-8282-7e38409b6492 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Neutral termination bolts found loose, please tighten | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615207&prj=626&rqi=Y2QYRM2tH84pjo6Gb5Mba2nMt4
RT1ELEC-125-005 | f961ef15-fc81-4df9-9ddf-3feb5169c997 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Acrylic bolt missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615209&prj=626&rqi=sbZDvE1QVb7ELkvaW8ednL73Ht
RT1ELEC-31-006 | c9c86984-3e62-4497-b970-db54448bbae0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Anchor bolts must have at least 3 threads | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615236&prj=626&rqi=NLHzW1CTE5p6PN7s1dsm5qYwdw
RT1ELEC-31-003 | f0a22152-78c3-4e23-b711-d7a5edbebee6 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Equipment labelling/tagging still temporary. Permanent labels/tags shall be installed as per the approved labelling scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615233&prj=626&rqi=kZVUQyV3uUHTlzsmPfZFdwQD7x
RT1ELEC-31-002 | 4224de0b-72d4-45ef-aa2b-a7123d507cdb | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Equipment positioning not aligned with the latest approved shop drawing (refer to attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615232&prj=626&rqi=p0Z44i6ugLhkqgBKOGWeXMSX4F
RT1ELEC-125-004 | 2d0e0681-cfbe-46b2-a11f-c4d0fdae9d90 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Confirm cable gland hole quantity and size as per approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615208&prj=626&rqi=jRwAUDZ9YmAMrmHe1jrDSjCSXd
RT1ELEC-31-001 | 14e76f47-5115-4ec4-88bb-2b8caffc1911 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | GC to upload latest approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615225&prj=626&rqi=Z6Nsd7R54gCZAyeXB8VptgDF7Q
RT1ELEC-125-001 | e273baf1-a96f-45a6-bc28-b254dde78967 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Factory Test Data/ Factory QA/QC document not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615201&prj=626&rqi=0gJ7gve47zg0fFVD0ZHLpid8o7
RT1ELEC-125-006 | a4a6d378-41da-4db1-b565-64ff067e1506 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Please rectify cable tube installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615210&prj=626&rqi=Q9yj7ciRM6byhaFU8lsy5UXYtL
RT1ELEC-31-007 | d5fddad9-7435-417c-8fa1-30a46e0b6008 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Unused anchor holes found, please seal/cover all unused holes | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615237&prj=626&rqi=04exLews8z8cWsVmoCW9qkfJSn
RT1ELEC-125-007 | 22418a77-7ecc-43bd-8a5f-98fb64c5682d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Add temporary cover to prevent construction damage, dust, and debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615211&prj=626&rqi=mE8JveJeQXfuaBJk0j0Jyx8iNp
RT1ELEC-31-005 | 328a94ee-5a09-44a8-9ee3-54a1ad271efa | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_B_1 | LIBATT - UPS Battery |  |  | Dust & debris found inside the panel, cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615235&prj=626&rqi=6ucTBFcP4z3gatBnxrPAQbns6M
RT1ELEC-126-008 | ecdebea2-ff0e-49da-94e4-ec60e2937450 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Component/Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Cable over-bent, please correct bending radius | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615221&prj=626&rqi=8SHBrOF8RgzcNMpp1ASVGNk9Vu
RT1ELEC-125-008 | f0bf243d-f615-4803-b53f-1902d4c124d2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_CRITICAL | DB - Distribution Boards |  |  | Provide protection for power meter | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615212&prj=626&rqi=GFYyvOUSmyJUn40XqU6wzMVecR
RT1ELEC-126-004 | 6e62f90f-4153-4f89-b4ac-a58e71cc0176 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Neutral termination bolts found loose, please tighten | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615217&prj=626&rqi=foewvZmjHF3840XBWstwgM8aP3
RT1ELEC-126-005 | 831aef74-268b-49a7-a026-a6ae8a17ce26 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Confirm cable gland hole quantity and size as per approved design | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615218&prj=626&rqi=WK7zoktFvVqEiBIztUFB4GkCGl
RT1ELEC-32-001 | fb7d44e3-6297-4ce2-a03e-b091b89a969e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | GC to upload latest approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615238&prj=626&rqi=YVSciH1h9DLAByzDbkYCMxPXa3
RT1ELEC-32-002 | 004f9fd1-581a-417d-8320-f775fe6263aa | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | Equipment labelling/tagging still temporary. Permanent labels/tags shall be installed as per the approved labelling scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615239&prj=626&rqi=NkaYL8Dd4j6caQVxEWHNKZxSyh
RT1ELEC-32-004 | 97bda84c-4824-4fbe-a4e7-a6663e97033d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | Dust & debris found inside the panel, cleaning required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615241&prj=626&rqi=ADm7q3MrF94ddsBG1UoKOn9INR
RT1ELEC-32-005 | dd24e2df-1b20-4af3-ba52-a0e0ea6a043f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | Installation checklist from Vendor completed (signed off) not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615242&prj=626&rqi=Z2K4H74tO0TGrOBgjphIiLsJaa
RT1ELEC-32-003 | b8f4a74e-ed6b-42fd-86c0-9303057e48bc | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_B_2 | LIBATT - UPS Battery |  |  | Anchor bolts found loose during torque check. Please check all anchor bolts, re-torque, and apply torque marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615240&prj=626&rqi=Cij3vc3wDbPdEc4qwGUPpHNc06
RT1ELEC-126-001 | 6ee5e69d-b69e-49a4-8530-f5048ea47ab5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1DB_D_EWALL | DB - Distribution Boards |  |  | Factory Test Data/ Factory QA/QC document not yet uploaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615214&prj=626&rqi=YYHtwtUwP5ejGvxuvfjJnuphGq
GI-011 | e56d4e89-b002-499a-9f5c-54734c2072c4 | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | dickyhermawan@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Issues SFAT DCOS 25 February â€“ Day 3 as per the Issue List in the Attached Picture for remaining open issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615100&prj=626&rqi=J9vJS7zoSH97GzSEvK6tSVbbIx
RT1ELEC-148-001 | db4c31fc-7429-4d8e-8b86-f5262f4c6af4 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_2 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MSB_B to UDP_B_2) Busduct installation is not level. Please refer to the waterpass photo and the elevation measurements differ at each point as shown in the photos | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615094&prj=626&rqi=8TwuS7zlmdrxydq7BvAzAV8w9q
RT1ELEC-14-001 | c366e9be-50f1-49aa-a34c-123f85ac153c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS |  | Electrical â€“ LV | equipment | 1GEN_C | GENL - Generator (LV) |  |  | (Issue CxL2A DCOS UTP Cable) - Cable installation on GEN_C still not completed (labelling & terminated) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615058&prj=626&rqi=osfp84EbgNUvKTAfykuNIplkIo
GI-009 | 001df17f-f016-4b2c-8eb2-570aa72a392a | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | dickyhermawan@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Issues SFAT DCOS 23 February 2026 â€“ Day 1 as per the Issue List in the Attached Picture for the issues open. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615097&prj=626&rqi=Y4THKaCCkdexlKyGj7BABJmSg2
RT1ELEC-13-001 | 7dcdb647-5dd6-4a37-940a-da9f511eb0be | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS |  | Electrical â€“ LV | equipment | 1GEN_D | GENL - Generator (LV) |  |  | (Issue CxL2A DCOS UTP Cable) - Cable installation on GEN_D still not completed (labelling & terminated) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615062&prj=626&rqi=tsQoVsDbS1NPgSXdlYA6rzgAsz
GI-010 | 56f860ef-057b-4e6f-8bd6-43f054ab04e9 | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | dickyhermawan@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Issues SFAT DCOS 24 February 2026 â€“ Day 2 as per the Issue List in the Attached Picture for the issues open. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615099&prj=626&rqi=ADYAAnET5Ew85wzq3wp2GRtNNP
YT1ELEC-5-002 | a24891a0-6584-4c5d-9c9c-fb4c16c5930a | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Point-to-point verification for control/signal cable cannot be performed as the cable installation is not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615436&prj=626&rqi=GtT0zVFJxjdSI4fKRC6KOtwMVM
YT1ELEC-5-001 | 7e5fe9e3-860d-4d05-8be3-0047afe39e64 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Simulated trip from thermal relay to VCB cannot be performed as the control cable installation is not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615435&prj=626&rqi=rlWekpd7ZLX7kYKGxsaunTzgN5
YT1ELEC-5-003 | cae012d5-54cd-4bc5-b688-391c333cc0a3 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-06 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Auxiliary supply not yet connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615437&prj=626&rqi=666M4Iaqj99Xzlqoi5wtGS354v
RT1ELEC-9-014 | 910241bc-51a2-4869-a994-5e2a427e5ee4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Temporary labels shall be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614756&prj=626&rqi=PX60OvC0Blz4s2tl3DS09RtvxX
RT1ELEC-4-021 | 94159b2e-cc61-4b17-9480-559a58b23848 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Cable lug connections may not be properly torqued? Please verify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614759&prj=626&rqi=7UvhxH41rB3kFrjrSetfeu07F7
RT1ELEC-4-022 | 34caa798-53c4-40a1-bea4-ae1954dc2046 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Battery stopper still not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614760&prj=626&rqi=oyPJOfR7KwW7bl5zlSGJPo8lo5
RT1ELEC-9-015 | 2c21d72d-62a3-4fcb-acd8-6333b3295d60 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Incomplete firestop at all wall openings/penetrations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614757&prj=626&rqi=zXEYOUptOe77Sh14h77p0FiVIA
RT1ELEC-4-023 | 7638ffc7-477b-427e-80b2-cec11479538f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Cable over-bending observed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614761&prj=626&rqi=ALPXg2PAEFjMwemDjTI2Eqaobq
RT1ELEC-4-020 | 35393cb3-a76d-4c5e-be3f-79e2cd47b1be | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Busbar connection between batteries not be properly torqued? Please verify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614758&prj=626&rqi=jW8qE86ntIXfBQkTGaZSvRSnYP
RT1ELEC-10-012 | a1f690a1-aa96-40c7-ace0-618c62c9c813 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Standardize all bonding jumper colors to silver | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614750&prj=626&rqi=TCztdXqphjrquRuX0U1WIKAp9j
RT1ELEC-10-014 | 5f2a88e4-2f59-402f-994e-8dd2c6d4d4ad | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Install bonding jumper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614752&prj=626&rqi=iHAhu3zONnMIeltMsBiwJzlGZv
RT1ELEC-9-012 | 4b1ce734-aaae-4fe7-a13f-502acf85d714 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Clean construction debris on cable containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614754&prj=626&rqi=dQa7Z08SB33h2H1oFstLSCIM9l
RT1ELEC-9-013 | 5f901f4f-75a7-4cb9-baf4-73243aa03ab6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Remove binding wire from cable containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614755&prj=626&rqi=KJfrq93QB3EacUVjDvYAye1qph
RT1ELEC-10-013 | 5fa728d8-acc4-49f9-992d-d6cf8ddf8a11 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | (Issue CxL2A - MV Cable) Incomplete firestopping at all wall openings/penetrations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614751&prj=626&rqi=EffQgKWNnJcbZ9kW05VmuTmLeT
RT1ELEC-4-024 | 6f49e78a-0ff3-48aa-a72a-f5a74a0e0380 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A BTU) Discrepancy between drawing and actual equipment position, refer to attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614762&prj=626&rqi=GJcybut0DlLGdIy8r1h2wiRdiC
RT1ELEC-19-001 | 58c4da40-871f-4940-9701-106ed20cfe6b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Please upload on site (Internal) Torque connection sheet documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614662&prj=626&rqi=dUyQESHldqECX65GBNDMoXYN3K
RT1MECH-16-004 | a471d421-e9f0-4138-b522-6dd696de64f3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | The equipment name tag shall be fabricated from the same material as the name tag used on the other equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614604&prj=626&rqi=byPEUAym79wHb6xaHTd4bsGNAV
RT1ELEC-19-007 | f902c327-d6c1-4e89-9628-c379ac8ec452 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Minor dents need touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614668&prj=626&rqi=scNem0yELCko8Op2dSsZfFMl8f
RT1ELEC-10-011 | e3c1b25a-fdf3-49a0-a97a-7349b0114cb7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | (Issue CxL2A â€“ MV Cable) Grounding braid is not properly installed (joint observed) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614691&prj=626&rqi=nMhF06wGnGs9pZwzSMzvtqOnve
RT1ELEC-19-006 | d9f5c079-b22f-4cdc-884c-e4056419e7fb | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Please ensure the HMI display & all ACBS is properly protected to prevent construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614667&prj=626&rqi=LprlYThlBVAKR9q8icdOSVwo6b
RT1ELEC-19-004 | 8b0dcf62-794e-46a5-b5e0-a49998460b2e | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Based on the RFIT inspection document, there is a discrepancy between the drawing and the actual equipment positioning (refer to the attached photo) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614665&prj=626&rqi=Xb4aF9vvjmcQEcFkBVAmqhxTXV
RT1MECH-17-001 | 33390bb6-9f81-491b-9243-bc393a495169 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_F_74 | EF - Exhaust Fan |  |  | The equipment name tag shall be fabricated from the same material as the name tag used on the other equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614603&prj=626&rqi=7c16O7XevnFOnpx0AVgaAyFDMd
RT1ELEC-19-005 | b4a25dff-91f6-419e-9608-3eed3c3744e4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | There is a discrepancy between the panel drawing and the panel label. The drawing indicates â€œ1CHWSTR_F_05_CH_1â€, while the panel label shows â€œ800A TPN ISOLATOR FOR AIR COOLER CHILLER.â€ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614666&prj=626&rqi=Bcb3MaglCKwcgYVMZheBDHDxur
RT1ELEC-19-002 | 5df2f4c6-8471-4049-a36a-c3bf26c6c879 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | Please upload Discrimination/ Co-ordination Study documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614663&prj=626&rqi=IKJICwxG7k6K6WNuT4BJ9vB3iD
RT1ELEC-19-003 | b01bd463-fdb6-443b-9f27-b4aa10753224 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_F_1 | MSB - Main Input Switchboard |  |  | GC to upload torque wrench calibration certificates for anchor bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614664&prj=626&rqi=qqJ9g75orGp2sVvIpxakojPdlj
RT1MECH-19-002 | 7599e9c3-324a-46c2-8577-44a0e78b4f58 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | Please provide approve shop drawing of the equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483526&prj=626&rqi=5UJTVTW3N6xOFzkRLZG70lnI0Q
RT1MECH-18-003 | 673a2ae4-865f-4fde-a194-da29a7f42e09 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | Please provided approved method statement for this equipment and also method statement for pressure testing/ vacuum testing (if applicable) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483524&prj=626&rqi=hNptz4WBRgOxroyW15toZhPl99
RT1MECH-19-001 | 48313c95-339b-4c0d-a3d2-04e29077af6e | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | The distance between the equipment and the wall does not comply with the approved shop drawing (120 & 390 in drawing, while actual distance is 305 & 665) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483525&prj=626&rqi=SUkpKK1Ww98liBn1AxbyIxbbLn
RT1MECH-19-003 | 0c6b5365-f9a3-4509-8972-72884f543e20 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1VRFOD_F_61 | VRF - Variable Refrigerant Flow System |  |  | Please provide approved method statement for this equipment and also method statement for pressure testing/ vacuum testing (if applicable) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483527&prj=626&rqi=xftQxC3VKTHQUul17Ze2nD9Dr7
RT1MECH-18-001 | 0c8c4d1a-76d9-44e9-bcb0-c1707668bf9a | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | Please provide approve shop drawing of the equipment and floor layout also | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483516&prj=626&rqi=t1qLnYYyWgkWHe3Jo3lHdBawrC
RT1MECH-18-002 | 350368f2-4d5f-4d6c-88a9-ad3a0ddcfbff | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Mechanical â€“Air | equipment | 1VRFOD_D_41 | VRF - Variable Refrigerant Flow System |  |  | Visual inspection observes defect minor scratch on VRFOD body and nameplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483521&prj=626&rqi=tGwbPYyJg4ZTX2bi3GD95or9Kl
RT1ELEC-9-006 | 1311d029-181c-4efd-a0d6-0e33da7d9b03 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Please upload CxL2B MoS document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483411&prj=626&rqi=IIgX1ECyulJ4cVpGqbJYFkTVum
RT1ELEC-9-011 | 73418f01-8eb3-4b4a-8765-096246813c94 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Why is the nameplate tagged as â€œMLTX_Bâ€? Please clarify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483419&prj=626&rqi=McknWlnpJsMyeQZyYisOXUoB6W
RT1ELEC-9-004 | 0820e252-7bee-4b23-9391-7d4b14b72a15 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Please upload Factory Test calibration certificates | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483408&prj=626&rqi=peD4jlssqMO7I4n19Y09pxUSMH
RT1ELEC-9-005 | c04abbb6-068a-42a1-9c2c-2eb8608e4421 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Please upload cable schedule documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483410&prj=626&rqi=jQvChM8ThbFXBHw0u0BEKVstVp
RT1ELEC-9-008 | 15d728b0-c719-48e2-8705-05c6566ef999 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Tap changer opening is not covered. Please provide a proper cover for the opening to prevent dust ingress and accidental contact | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483413&prj=626&rqi=m4ijMgNAurweqKr0HPWUNbXQtc
RT1ELEC-9-010 | bbe6b337-a0cf-4131-90bf-88e8bfa9d9db | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Dust and debris found inside the equipment. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483417&prj=626&rqi=Nzkn5geFLtgce3QDmLZeQ05Nw4
RT1ELEC-9-009 | 00e5efea-2a90-4c08-8f72-7063318844bc | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Temporary labels shall be replaced with permanent labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483416&prj=626&rqi=IxdiNXbQWIMXAZpULJHo8fBryB
RT1ELEC-9-007 | 92e0d713-1569-4b00-a5a2-ae6186f58361 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-03-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Minor dents and scratches were observed on the transformer body and enclosure. Touch-up is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483412&prj=626&rqi=n2Iqnu6C25Eo18318xpooAavsC
RT1MECH-11-001 | bf60539d-ced2-4f39-9efa-eb39fedd2209 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_C_54 | EF - Exhaust Fan |  |  | The equipment nametag shall be made from the same material as the other equipment installed on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221137&prj=626&rqi=EWnN4ZGqeIj7Brmq00hRg9CHvi
RT1MECH-55-001 | a24be696-c060-43d2-81bc-f3f6d5c74928 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_C_09 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221120&prj=626&rqi=uaLpl52oGerLw44fHcaLR4INUt
RT1ELEC-149-009 | e61e4e41-8959-4d4f-ba27-c53c82277006 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MSB_D to UDP_D_2) Busduct above 1UDP_D_2 is not level, adjustment is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212894&prj=626&rqi=hJ46VfZtqxwBaabSMWAvPW5aI0
RT1MECH-14-001 | 952ce96c-6891-45f5-badd-f0213354c81c | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_D_53 | EF - Exhaust Fan |  |  | The equipment nametag shall be made from the same material as the other equipment installed on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221139&prj=626&rqi=tQUGGivm0qJFI3mjrXEnmlQ1Uy
YT1MECH-31-001 | 26d83568-dd3c-4f2b-88f8-f645c64cbfe9 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | During the penetrant test witness conducted on 13 February 2026, approximately 20% of the total number of weld seam were found to be not acceptable. Rectification works were carried out, followed by a re-test; however, the results were still not acceptable. Consequently, another re-test was conducted on 25 February 2026, and the results were found to be acceptable. All test results have also been verified by NDT Level II personnel, pak Wiwid Dwihartanto from KIK. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221132&prj=626&rqi=8gLr1PXR4qsXNDwGeyYspTzevn
RT1MECH-10-001 | 22af31cb-8b69-4288-a57c-76bbf8b3303a | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1EF_C_53 | EF - Exhaust Fan |  |  | The equipment nametag shall be made from the same material as the other equipment installed on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221136&prj=626&rqi=Jjb3uyOzSNBYwsQVC6BlRmCAJ7
RT1MECH-55-002 | 8b3aaf8c-71dd-42d5-bcde-c6298c27ced4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CA_C_09 | CA - Cool Array |  |  | Dust and debris were observed on the equipment and shall be properly cleaned. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221121&prj=626&rqi=W7JW0nxepd8afVrervhQNz8G9k
RT1MECH-13-004 | 6915726e-2511-49b3-a939-ea5a2be26d5a | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | The equipment nametag shall be made from the same material as the other equipment installed on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221138&prj=626&rqi=dbftFAEHVH8Lhg1xjQRS86gky2
RT1DCOS-9-004 | 14dfe095-fbf5-4e47-971c-464489226b3e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | Inside panel is dusty and dirty, cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212855&prj=626&rqi=AgIHFZGNv3yRcUyl2dmftdVgkp
RT1DCOS-10-004 | 4620c2de-c8cf-4f66-94ae-9e7a9792495b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Minor dents on the panel body need to be touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212862&prj=626&rqi=eKumso5iVA2OeDycamIUKS04tl
RT1ELEC-145-002 | 7b0b50a5-db17-4a6f-b571-0d902ddc1d7a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1RPP_1_GW_14 | CP - Control Panel |  |  | Dust & debris found inside the panel, need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199930&prj=626&rqi=zdiFdE1FfBuoLK1uG9pRs0EeFu
RT1ELEC-145-001 | 9676494c-533c-40d2-868f-65acd40ec2ec | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1RPP_1_GW_14 | CP - Control Panel |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199928&prj=626&rqi=VG4BX1DfSzCklYGmm5oVo0mTRd
RT1DCOS-10-005 | 264c94a8-b65d-40cf-a1fe-55ea19ace97c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS |  | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Anchor bolts have not been torqued and marked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212863&prj=626&rqi=d4uPly0ltaTtyrQAwZu3esOpFb
RT1DCOS-10-003 | 9929c33c-d680-477c-bc61-864be596ba9c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Please install temporary cover to protect from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212861&prj=626&rqi=AmSuhqd9tqOQOnbtBYlyMvOkTr
RT1DCOS-10-006 | 60d4fddd-d4c2-440b-9d35-60c6c7342725 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212864&prj=626&rqi=dE5zrkCNVsVPGsRsYM5recnVCv
RT1DCOS-9-002 | 3c7208fd-6cf0-4919-9e58-75f311f0676e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | Based on panel drawing, power supply is tagged as â€œPS 1,â€ but the actual label inside the panel is â€œPS-A.â€ Please update accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212853&prj=626&rqi=0XfF2LMQ0WbF5MUffnzNrpGmpf
RT1DCOS-10-007 | 38458c69-93cb-43f6-9835-2bffa7724bfe | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Based on the panel drawing, the power supply is tagged as â€œPS 1,â€ but the actual label inside the panel is â€œPS-A.â€ Please update accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212865&prj=626&rqi=zqhiuEKy7zLOJkDZEfWFJaQbbs
RT1ELEC-147-003 | f723467d-9f13-4a23-85cf-9adaa179b7ab | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1RPP_1_GW_16 | CP - Control Panel |  |  | Some bolts are rusty and need to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199925&prj=626&rqi=mOx8dsu0fMtP8Ej6IDCmEbrnS1
RT1ELEC-147-002 | 9de44f69-159d-4b83-acb3-9cd38152a791 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS |  | Controls | equipment | 1RPP_1_GW_16 | CP - Control Panel |  |  | Cable gland washer is not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199924&prj=626&rqi=EOydSVz4UfkxAJhvcEaYSrttLD
RT1ELEC-146-001 | 37fb60aa-55ca-4438-b9b4-919e977b7a91 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1RPP_1_GW_15 | CP - Control Panel |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199920&prj=626&rqi=errGcEq5iTaj9Zv3mcvK4v4UX0
RT1DCOS-10-001 | fd59a613-d4de-4172-928e-eccc15b7c814 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Please upload factory test data documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212859&prj=626&rqi=43OSJNmjlazMXOroXCedd4DiCD
RT1ELEC-147-001 | 3a275da8-1e24-4e6d-a33f-328f8d78c799 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1RPP_1_GW_16 | CP - Control Panel |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199923&prj=626&rqi=4GW6tzFKwWWVOOp0XgyTrUMWGN
RT1ELEC-150-005 | b02835ba-6b71-4a77-9293-abb5f1f8a45d | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_D to MSB_D) Busduct installation at Tx Room does not comply with the latest approved drawing. Drawing shows straight routing, actual installation differs (refer to attached photo). Please clarify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212885&prj=626&rqi=lLBfILEl9Pz404pKbmbkJ2R84g
RT1ELEC-150-002 | 8b348390-ac88-4dd9-84d9-af6bc3fd8849 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload approved latest shop drawings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212873&prj=626&rqi=S2Lz6BX27uBwEJ4cM0WRwixOhO
RT1ELEC-150-003 | 7a7faf84-69b5-4e27-84ce-a543719b7b94 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload O&M documents of busduct | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212874&prj=626&rqi=Nz54NbArOyvjGXDxWENrF4B24z
RT1DCOS-10-002 | 3acfef27-ad1f-454f-b1a1-dbe437b73f8a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1DCOS_1_LCP_05 | DCOS - Control Panels |  |  | Please upload MoS CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212860&prj=626&rqi=f4qPu3y79NPiiOcX63VjnhEfuV
RT1ELEC-150-006 | 49f65b41-0dd7-4dfe-a705-04a7bf3ed3e2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_D to MSB_D) Provide temporary protection to prevent construction damage, dust, and debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212886&prj=626&rqi=WuZMls5cPtFvInkYvVwV83ZqQ9
RT1ELEC-2-014 | 187af73e-b2f0-4b9b-8dd7-d72a64518b88 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue DCOS Cable UTP) - Please align the conduit to ensure it is straight and properly aligned (location RMU_D Lv5) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212866&prj=626&rqi=O6Gap6rRGWorh8AvIVEoU3WSbi
RT1ELEC-149-001 | c63e99db-0c05-4d8b-8eb4-293bbce03dbd | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload torque wrench calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212869&prj=626&rqi=Frg8rAznF5nSKv6CCz2UkFhuH1
RT1ELEC-149-004 | 5babb3cd-0228-4916-9732-bb436116955e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload equipment delivery note / material incoming inspection document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212878&prj=626&rqi=h3ihCZtLRxOvcw7I1lsC3iVbRl
RT1ELEC-149-006 | 5f3ea58d-41d3-4698-918a-18b3ed32f1d9 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_D to MSB_D) Elevation discrepancy (refer attached photo): Drawing: 4500mm AFFL, actual: 4444mm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212891&prj=626&rqi=viAlbZFqdw7USVv1lxgcfSfUV4
RT1ELEC-150-001 | ad3e088c-501c-4a42-a847-b93e35b21246 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload calibration certificate for torque wrench | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212872&prj=626&rqi=58KD6ERBnuCm1e9FwESgVVHMfN
RT1ELEC-150-004 | 7fb18e67-900e-4535-a0cf-65897c092391 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_5 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload equipment delivery note / material incoming inspection document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212876&prj=626&rqi=uS12YIGVPfdXJwQcnpoKJSP2hJ
RT1DCOS-9-001 | b7e7803c-902f-456a-aff2-3a4928e56ae6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | Please upload MoS CxL2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212852&prj=626&rqi=SZve6eGVfBFP0UcQw3O0vG7PX1
RT1ELEC-144-002 | c01d60d5-5102-4616-a001-68dca4b76c22 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1RPP_1_GW_13 | CP - Control Panel |  |  | Dust & debris found inside the panel, need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199927&prj=626&rqi=uNqSJkSnlLB2D37o3SLsFjBBTv
RT1DCOS-9-003 | b3cfd90a-e01c-4368-9072-88bbd5f1f1e5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212854&prj=626&rqi=OsXdj11FZRO3XbOYaPG7vHFUMy
RT1DCOS-9-005 | 84d6e04f-e308-44bf-9546-b0fb9e363784 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1DCOS_1_LCP_04 | DCOS - Control Panels |  |  | Please upload factory test data documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212857&prj=626&rqi=klYTgQ9yoiD1HjKT85Z3x9mFKf
RT1ELEC-144-001 | a84baefe-7b1c-4c7a-bcf2-2818e4465e49 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1RPP_1_GW_13 | CP - Control Panel |  |  | Some components have only one label at the terminals, while the component body is not labeled. Each component must have two labels (terminal and component body). Proper component labeling is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199926&prj=626&rqi=B91GGitZ9mdLm0aaOMjB8XjukN
RT1ELEC-149-003 | 6c1b304e-3eb9-414a-ab16-e6c59458a1ac | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload O&M documents of busduct | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212875&prj=626&rqi=mceCXKv0U96d75rPLVZmOgPnHJ
RT1ELEC-149-007 | 7d3ff34a-25b8-4218-957e-dcd345c9e4aa | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_D to MSB_D) Sleeve and firestop at wall penetration are not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212892&prj=626&rqi=RUnXP2MxiDEfNYWyDKMxwERjw8
RT1ELEC-149-005 | c804cb27-9fdc-426c-b5bb-90fd76481275 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_C to MSB_C) Elevation discrepancy (refer attached photo): Drawing: 4200 mm AFFL, actual: 4351 mm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212889&prj=626&rqi=JM68zOheH1NnafG4XqeeeNio42
RT1ELEC-149-002 | aa6d7422-f8aa-4b3f-bb3d-67957c9f8636 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | Please upload approved latest shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212870&prj=626&rqi=5M6X5rlpGNk51b1j28ph7YT38g
RT1ELEC-149-008 | 6517f7fd-89c9-49d6-bd90-259ebe6d22fb | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1Busway_level_4 | BUST - Bus Duct Temperature Monitoring |  |  | (Issue BD MLTX_D to MSB_D) Unistrut support is misaligned/not straight, rectify accordingly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212893&prj=626&rqi=ZsDdL4OSQJ58KYyuk1TKIh2HXg
RT1ELEC-146-002 | 57f95c30-03f8-4276-9bff-92c709e78706 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS |  | Controls | equipment | 1RPP_1_GW_15 | CP - Control Panel |  |  | Cable gland washer is not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199921&prj=626&rqi=Xqu3Igj2NTzFeKmZG3ga66dpwS
RT1MECH-13-002 | 39a9079b-57d5-4639-af7f-ce0bfa59abbb | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | During the inspection of LCP panels D_52 and D_53, the nut at the upper left side of the panel failed the torque test, the nut is keep moving when it get tighten. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199807&prj=626&rqi=GGQXMjCTdjCRHSIW38o2NbHulw
RT1MECH-16-001 | f9cc98bb-d8a5-42f9-9f6b-2ae2f49b200e | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | During the inspection of LCP panels F_73 and F_74, the bolts and nuts located at the upper left side of the panel failed the torque test, not even failed, the anchor bolt is keep moving when it get tighten. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199759&prj=626&rqi=PkUHKMmDSoKunfTjSpubWqAGbh
RT1MECH-13-001 | aa2afb10-efd1-4d57-b4b8-754d9590324f | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | During the inspection of LCP panels D_52 and D_53, there were dirt and dust inside the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199763&prj=626&rqi=pkDwlmjiFlrRQOcA7HvSvQ2u7b
RT1MECH-7-001 | 731f34f8-0607-43df-974b-44a18c26d42c | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_31 | EF - Exhaust Fan |  |  | During inpection of LCP Panel B_31 & B_32, loose bolt and disconnected cable lug was found inside the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199809&prj=626&rqi=FyEZQ9rsGgwj7Sdg35QLI9j3Ds
RT1MECH-13-003 | 6e88e476-4ad3-4ece-9360-c7270343e291 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1EF_D_52 | EF - Exhaust Fan |  |  | During the inspection of LCP Panel D_52 & D_53, loose bolt was found inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199808&prj=626&rqi=iTNOkd5UQsTkUltd0Nkpt6UKzM
RT1MECH-16-003 | 2d8c26ae-bd0b-4b99-b8ac-112eec012ab9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | During the inspection of LCP panels F_73 and F_74, there were dirt, dust, and unused materials inside the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199762&prj=626&rqi=8lRcBpBQvyNQYsfoC0bQO7sC1y
RT1MECH-16-002 | 43291ae3-1d26-452d-b083-2306bf17b875 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-23 04:00:00.000 +0400 | General Contractor | L2A | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_F_73 | EF - Exhaust Fan |  |  | During the inspection of LCP panels F_73 and F_74, A cable lug was found disconnected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199760&prj=626&rqi=DixKk34G75wy0t58iylgJEs8cm
YT1MECH-57-001 | 230f5c7a-961a-4c91-bf4e-0ac792cef46b | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-22 04:00:00.000 +0400 | General Contractor | L2B | Component/Equipment Failure | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | During the hydrostatic test of the CHW pipe in the cool spine area at 10-11 Feb 26, a pressure drop of 0.6 bar was observed over a 24-hour period, exceeding the 0.5 bar acceptance criteria. Consequently, a re-hydrotest was conducted on the CHW pipe the next day, and the result for the second test is within the acceptance criteria. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199744&prj=626&rqi=Cns5S04Gkjy0rragxr2S2gQ4XJ
RT1ELEC-4-019 | 0d0877c8-5a2e-4a4f-84e9-ef77dfa8106b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) Cable containment alignment is not straight as per approved drawing (at Level 6) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199701&prj=626&rqi=b0TEwCearUHLCOM5dOZA3HnE9o
RT1ELEC-3-022 | 05e6a0f7-0720-4988-a7a7-7293c996d9b7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) Grounding braid has not been connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199695&prj=626&rqi=Vu4amElG5TUrtr4VIEfstoGBS5
RT1ELEC-4-016 | d71d1371-0a9e-4b1f-83c6-6fc752a587c5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) Sleeve and firestop at wall penetrations have not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199698&prj=626&rqi=BX6gGPwt0XBKvGN2E4hR4jREFi
RT1MECH-30-002 | aa45b5a5-098a-41d5-96a6-63063e0d1abd | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Findings of scratches were observed at several locations on the equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199654&prj=626&rqi=Z26CxoLANGkC7touZgiZc4kUfP
RT1ELEC-4-017 | 1e5e0168-3a1c-4d11-89c8-780d56a70ae1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) Bonding jumpers at several cable ladder joints have not been installed. Please re-check all cable ladder joint connections | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199699&prj=626&rqi=FBYHgKnQAJcYzYkP9d9Vp8bdqp
RT1ELEC-4-018 | a8ea4024-07b7-43fc-9ae9-4dd864b2cfe9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) MV cable grounding braid looks not properly installed, with too many joints observed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199700&prj=626&rqi=Tykd3McQonrX7jUZsuAyStBStm
RT1ELEC-3-023 | 53eea84b-88a0-4ef3-99bd-b190292ecaf3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue CxL2A MV Cable RMU C to F) Cable skirt installation not yet completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199696&prj=626&rqi=pJLOWOt4dzGsUaXK39Xb0KYY08
RT1MECH-29-002 | 65d07d5e-bd94-441f-a94d-da06a5deca8c | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-20 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Findings of damage, scratches, and dents were observed at several locations on the equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199653&prj=626&rqi=cz70gm7LGXd3VkGB3hxH8HoiUZ
RT1MECH-28-002 | 0fbbc58f-df44-4576-8c0f-6938a9f93a76 | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-16 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199250&prj=626&rqi=a4FDfRDhdnsM4gdb6f1jY8SEvY
RT1ELEC-142-002 | a085b543-a4ac-4417-ad11-a00d2899740a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1RPP_1_GW_05 | CP - Control Panel |  |  | There is dust and debris inside the panel. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199209&prj=626&rqi=kbZwdTg3mIHDtvwYqpQq6oEa8C
RT1ELEC-34-001 | 6a9a30c1-5586-4d60-a0be-5418ef7f8673 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_D_2 | LIBATT - UPS Battery |  |  | Please upload battery cabinet (inc circuit breaker) factory data document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199202&prj=626&rqi=umY4ocRlpui7Do7sW8hII8rMvl
RT1ELEC-34-003 | bb7f3347-2147-4e44-a34a-515cb4fc85ee | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_D_2 | LIBATT - UPS Battery |  |  | Please upload battery busbar join connection report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199204&prj=626&rqi=zXSyQ8mZnytP0mzfan4CGWYuSW
RT1ELEC-33-002 | d59bad56-e24c-4ca4-b98a-d9abb17c0a7f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | GC to upload the latest approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199197&prj=626&rqi=5SCeuXtjcj5F5oRvEUaAPscnot
RT1ELEC-33-001 | 2436c513-383c-47c0-8cf4-580f751436bf | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | Please upload battery cabinet (inc circuit breaker) Factory Data document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199196&prj=626&rqi=xPEXAz3T8N2tXea4C0LeYjMgMX
RT1ELEC-143-001 | f2184cc5-b029-4932-93b0-272586507c3c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS |  | Controls | equipment | 1RPP_1_GW_06 | CP - Control Panel |  |  | All unused holes must be properly covered to keep the enclosure fully closed and protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199210&prj=626&rqi=RFmLUCWjuLUM5uoFfHq5j7zFhE
RT1ELEC-142-001 | 1f3caf87-1f39-4e69-8507-8e1d1dc4d189 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS Installation not complete | DCOS |  | Controls | equipment | 1RPP_1_GW_05 | CP - Control Panel |  |  | All unused holes must be properly covered to keep the enclosure fully closed and protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199207&prj=626&rqi=4pcvKYGqDMjEBGFM5HKGTxoGmJ
RT1ELEC-33-004 | 431b1fcf-4da9-4e26-9b45-2ed5fb9a88ed | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | Equipment labeling/tagging is still using temporary. Permanent labels/tags shall be installed in accordance with the approved labeling scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199200&prj=626&rqi=BhRjHdLKypYhK2q6Umu8rUwHJz
RT1ELEC-34-002 | 7ca488c9-bfcc-4c34-a836-6737ad920fff | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_D_2 | LIBATT - UPS Battery |  |  | GC to upload the latest approved layout drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199203&prj=626&rqi=5AeHPPKvGbAUREkyhlSc4b8UVA
RT1ELEC-33-003 | cbe6a016-61e3-409f-8a05-1708c808e698 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_D_1 | LIBATT - UPS Battery |  |  | Please upload battery busbar join connection report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199198&prj=626&rqi=LXnE0ezEv0HXGgWpQO6121WkGw
RT1ELEC-34-004 | ae83cc9e-8b41-418e-8637-33118a157250 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1LIBATTSYS_D_2 | LIBATT - UPS Battery |  |  | Equipment labelling/tagging is still using temporary. Permanent labels/tags shall be installed in accordance with the approved labeling scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199205&prj=626&rqi=oRIJ6S8k7hTw98qqmkBmod4thy
RT1ELEC-143-002 | 56e05f4f-a49a-4c5d-803c-9c0ff9a147c9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | DCOS General Issue | DCOS |  | Controls | equipment | 1RPP_1_GW_06 | CP - Control Panel |  |  | There is dust and debris inside the panel. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199211&prj=626&rqi=7uEG4bMkVbxXQPsKLt1aLvJ3A9
RT1ELEC-57-004 | 120047da-9711-4b10-aabd-9519ad6c04f9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Minor dents, need touch-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198990&prj=626&rqi=upAB2NQOnSKFXfB1UQ9lOVK8kA
RT1ELEC-57-008 | 6868df6a-cb59-4393-80fe-81f783f06a18 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Busbar joint bolts have not been torqued & torque-marked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198997&prj=626&rqi=HG3aN1omHRq4UccYI9norUDVlW
RT1ELEC-4-010 | 0aead64f-db45-4c55-b7b3-26425af089dd | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Terminal blocks require sticker/labeling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198909&prj=626&rqi=bZjHkt1srKDOKhNlJtZlXzPbvX
RT1ELEC-4-008 | 3a368ad7-016c-45ff-9e50-9e530076296e | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Gaps observed between cubicles, need to rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198907&prj=626&rqi=Ix0wcU80hfH8PICZKT02KxmZZV
RT1ELEC-4-009 | c718fe6a-5682-4e2f-b35a-438ca65fe51e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Scratches on the door body, touch-up repair is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198908&prj=626&rqi=7veH70Do0KgOFGyVeofbA6niFH
RT1ELEC-4-011 | b860e7fd-6fc3-4a8f-87e0-6b73785a97e5 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Anchor bolt torque could not be verified during inspection due to excessive bolt length, torque wrench head could not be applied | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198910&prj=626&rqi=u7Xgc9k9sFIrsB8TCEkANYD5xZ
RT1ELEC-57-001 | 7c2a8b8e-728b-452d-8d65-ed5ee670e1a4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Please upload calibration certificates tools | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198984&prj=626&rqi=F5ue0trI4QP9KoUXQtxwNpQTyb
RT1ELEC-4-005 | 17b16c03-839a-46a9-9ed6-2cb51cc4beb6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please upload HV cable design documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198903&prj=626&rqi=OOxDL1Wz0HsLGdHIPgf1v2n6dP
RT1ELEC-4-015 | 676740a6-9b02-4fa1-941b-5a13612c7933 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Relay protection unit is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198914&prj=626&rqi=ykMSxQe0k1qfEIrDBTdBDBf9sv
RT1ELEC-57-007 | 0db223dc-5de9-447c-8c7b-e4d239395c7c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Dust and dirt observed inside the panel, cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198996&prj=626&rqi=No9XIdgMKOxwc0Xlyv4Jb00eAw
RT1ELEC-4-014 | ee004d06-1b95-4bd9-9bdd-6edfd094001a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Permanent equipment tagging/nameplate not yet install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198913&prj=626&rqi=8qmo2MeFIDC5cTWi4mULYGA5gz
RT1ELEC-57-009 | 0a84f8b2-0996-47b4-98c4-6ad4e1863f55 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Control cables appear not connected, please verify and confirm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198998&prj=626&rqi=afI1yJavg68qgm4ZpMXZkcdkxQ
RT1ELEC-4-006 | a2199e35-4c71-4790-8913-e7654ddb0bad | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Panel is not level (tilted) refer to the attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198904&prj=626&rqi=25ohefS9wQTRIz6c2zmejD3CKr
RT1ELEC-57-002 | 6966e6c9-873c-436a-9a2a-2e8972044700 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Please upload Installation and Start-up Manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198988&prj=626&rqi=uoIJXRRgN32EkGvNVrGQwdT6II
RT1ELEC-57-006 | f952c890-ef04-4280-8670-b6118d4a60f1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Drawing not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198994&prj=626&rqi=kOLKhiFYjqVioJND1U4tiPvje9
RT1ELEC-4-013 | ccd89aae-4046-43f5-8380-a8de1b34b282 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Verification of the circuit breaker serial number could not be carried out. The MCE vendor is required to provide clear photographs of the circuit breaker serial number for verification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198912&prj=626&rqi=RxQ7Nf4tN54Sg8iR7xyrNKguca
RT1ELEC-57-003 | 3cfb4e03-8cfc-4377-8c52-8820bd2f6ac5 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Equipment positioning does not comply with the latest approved drawing: - Right side to wall: drawing 1425 mm, actual 1440 mm - Rear side to wall: drawing 483 mm, actual 575 mm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198989&prj=626&rqi=psNW80iqLXJJFJexzJaKtuO50h
RT1ELEC-57-005 | 2d2d9700-a03b-41b7-9f84-f107198ade91 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1STSSB_D_2 | STSSB - Static Transfer Switchboard |  |  | Need to install temporary cover to protect equipment from construction damage, dust & debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198991&prj=626&rqi=oBf3TT2fUNppfIkdAwPamaNCoB
RT1ELEC-4-012 | 9f997823-82f7-405a-a93d-daf518058cc5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Drawings are not available inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198911&prj=626&rqi=Ylq7IeNMdKJctaefzH7cIl7oiT
RT1ELEC-4-004 | 926ac9f3-771a-4466-bccf-cd14dbba18a0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please upload cable schedule documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198902&prj=626&rqi=Qzd5ndsQJyaAxSAZR5rJYrW1Qn
RT1ELEC-4-007 | 72d0ef54-68e2-413e-817e-0d22ca4187f6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Equipment is dusty and requires cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198906&prj=626&rqi=qnXDO3ERYT9P5H98HinD40kxIi
RT1ELEC-4-001 | 501d2f63-1d82-49de-8d79-302a5299fcc9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please upload factory test protocol calibration certificates | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198899&prj=626&rqi=RV87RuSjxriBn8dctvRzVbj12q
RT1MECH-31-002 | 55e356d3-83c5-442f-aa40-6aff9ca2cf0c | JK01-2 | 626 | APAC | Closed | P3 Low CX | DimasKurniawan@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | Visual inspection observes defect minor scratch on chiller body and nameplate unit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198884&prj=626&rqi=zZGoCpUG41DMzdmaNuzaDbnwME
RT1ELEC-10-006 | 99c96d83-a90c-4a7d-94bb-54be130b6990 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Minor dents observed, touch-up repair is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198890&prj=626&rqi=6LsFM2s0ysTCEfwtJYHYYA1QkA
RT1ELEC-10-004 | d8041fee-db5f-4822-9bc2-06c4270f2c9c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Some components have only one label on the mounting or body, and terminal labels are missing. Each component shall have two labels (on the mounting and on the component body). Terminal labeling is mandatory | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198886&prj=626&rqi=PDGUOCpinW9hePzfDBlRDtRqOn
RT1ELEC-10-009 | 5d99afc0-cba5-4732-b8d3-400b52f3b01c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Cleaning is required, excessive dust observed on the transformer, and cable tie and plastic debris found inside the enclosure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198893&prj=626&rqi=aV8aZBCQi0YeVw2uAoQAIpqDrH
RT1ELEC-10-007 | 707bb7ee-f352-4012-864b-f5e1a394cc56 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Control cables appear not connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198891&prj=626&rqi=VVgQ7FVJmyqAXbghcJGTTn3nC3
RT1ELEC-10-008 | cc37156c-7f0f-41ff-8290-d83b4949cb29 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Bolts were found loose during torque check, clarify the required torque value and re-torque with proper torque marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198892&prj=626&rqi=RUKgnSC78OxsFd24zx5DcBesoT
RT1ELEC-10-003 | 06ea9e91-9050-44d6-a72e-5fc8692648bb | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Need to provide "danger" sticker/label on the transformer body | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198866&prj=626&rqi=7nkbOYVX42iGICv3qt03i2bkpF
RT1ELEC-10-010 | 5f064ae6-8572-4e7f-8f2f-fe08d1c70356 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Please upload cable schedule & L2B MoS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198894&prj=626&rqi=jGeRCf1kKkUfHwjc3hlKpOBlTp
RT1ELEC-10-002 | 52991aa5-e33b-4419-bc15-6295ed4997c1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Please upload cable schedule documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198863&prj=626&rqi=74TY7gdcoVLyWlRBYYIvf1RnUy
RT1ELEC-10-005 | 5c6514b8-01b7-4b8e-9ffe-fa2b40dd27ac | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Fan cables are not properly dressed. Poor cable arrangement may cause damage or disconnection during maintenance activities. Please tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198889&prj=626&rqi=NVMRbHJXyF1GQMDdZEp3V78ZsW
RT1ELEC-4-002 | 8113018f-f41d-4b2a-a4f9-380a52656726 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please upload Installation and Operation manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198900&prj=626&rqi=VTdvbhqj6O87PG6QF4q3mYBy7t
RT1ELEC-4-003 | 0abfcc2b-c1a9-41e8-b24d-07a2a64678cf | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Please upload MV Discrimination Study | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198901&prj=626&rqi=bNHbiZ0OZ2P8xhGAOZgTMiHpw4
RT1ELEC-17-004 | 9600bdff-5484-43de-9152-f1c3c17bfb38 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Provide protection to the ACB to prevent construction damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198622&prj=626&rqi=UP3h7Dvdn55elW5n2gP4YuQABv
YT1MECH-25-001 | 11128491-4ba5-4d51-8617-b15268ff754a | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198680&prj=626&rqi=uHufwVxjUezfc5Ji7iGZH8v9XI
YT1MECH-22-001 | 50d38421-7bd6-4d42-ba93-b06bacc2ccdd | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_41 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198674&prj=626&rqi=tbxBP1H6wQqRgVr9b5t8nwnNJu
RT1MECH-52-003 | 22fe31be-5f56-49ab-ae32-3a6c789e2fe1 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_C_05 | CA - Cool Array |  |  | The unit support is misaligned. Rectify the alignment and remove any unused bolts if not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198668&prj=626&rqi=5TZzGaXtTcQmTYjFU18KobERjY
RT1ELEC-17-006 | 5fae2d48-2fd1-4400-b30b-d05d5d748936 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Remove marker pen markings on the busbar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198624&prj=626&rqi=7JQyETYYWXMt0t647PQQKD392t
RT1ELEC-17-003 | c1e6d363-ecc0-432e-9615-87ab2ba16b19 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Temporary labels shall be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198621&prj=626&rqi=9PWNHMJfXd5fHslJF0MEcSP1OX
RT1ELEC-17-001 | a9e5f3b5-c90a-45e9-bd8f-addc22ba87e6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Please upload on site (Internal) torque connection sheet document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198619&prj=626&rqi=pbEAzBhtcKLrN0Fd8lS1m6W5yy
RT1ELEC-17-005 | 8729df35-b793-45a5-bc77-028c731b657b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Anchor bolts were found loose during testing, re-torque and apply torque marking to all anchor bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198623&prj=626&rqi=zX8816F37H0k00Q6SE3tpJyHCj
YT1MECH-23-001 | 4688f305-69b4-457e-b947-3cd7f43237c1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_F_42 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198677&prj=626&rqi=cuOmB56V63Q03s14Mo7SjaUEgr
RT1MECH-52-002 | e6b6bf9a-b83d-444d-954c-79a2c672d181 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1CA_C_05 | CA - Cool Array |  |  | Please upload approved method statement for flushing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198667&prj=626&rqi=mnWfSWrmmju4KBE5aDcY13Diod
YT1MECH-24-001 | 8d48e012-40fc-4a7c-91fa-936a77549bdb | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_B_41 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198675&prj=626&rqi=hPGUe5jZ67iEyppAEvLuRyenwg
YT1MECH-26-001 | 44d82827-6549-45ed-842c-301ea649486a | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198679&prj=626&rqi=v0jctuxKTePOr9RUzQLIQsSdtm
YT1MECH-27-001 | 98a828f7-24cc-405e-bedb-16fcc824b8c5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | wellyjulian@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2B | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | (Issue from CxL2A) Permanent equipment Tagging not installed yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198678&prj=626&rqi=f264zUNKZXn3f8Sdku0IhFMQUS
RT1ELEC-17-002 | 5c3d0e33-5771-4339-9a68-2770aeca3296 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Minor dents on the panel body shall be repaired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198620&prj=626&rqi=F8HEnwx2yNv4PIhjCxDKifHDCU
RT1ELEC-17-007 | 204d523e-21c4-462f-abe0-0f4f9646c099 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C_1 | MSB - Main Input Switchboard |  |  | Equipment cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198625&prj=626&rqi=tEbapvwOqTia8t6g14zkBWD0oP
RT1MECH-114-006 | 6615f1a6-fc5a-4b7a-a24e-69f2ce99e8d0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Body-to-baseframe connection bolts are missing and must be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198334&prj=626&rqi=LSAwx4PyjJSu5SZqBRee7Ci98A
RT1MECH-114-001 | 9cf0cf29-15de-49e2-9a60-bc754b75a855 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Air openings are left open. Temporary covers shall be provided to prevent dust and foreign object ingress | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198326&prj=626&rqi=WkZYd2xyYPy2DZGHOI5aXFgw9V
RT1MECH-114-002 | 6dd545ff-9351-4ca0-bcca-7aed14b9fbe2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Stains on the equipment body shall be cleaned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198327&prj=626&rqi=1dTatx7bhi1KBhPIi7g3rmVuOo
RT1MECH-114-003 | 7688d68f-80fe-4e66-8632-b4e85c678c10 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Internal equipment is dirty with excessive dust, cleaning is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198329&prj=626&rqi=fKwb1rDRsjq6dv5r7hKcoAhU5j
RT1MECH-114-007 | a9845060-723e-418b-a72a-5bd0fe01fb8b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Damaged insulation at the chilled water outlet shall be repaired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198335&prj=626&rqi=xCRZG8m2aBzX09k1ZbnEfQCBwW
RT1MECH-114-004 | f6ba9592-24d3-465f-b581-e724072ecd82 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Left-side access door cannot be fully opened due to obstruction by the STSSB panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198330&prj=626&rqi=5uV20w3CloLpEmTnjt1iMEhDlZ
RT1MECH-114-005 | e5c2b0b4-6061-4ee3-aa5f-fb30019c11b0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_42 | CRAH - Computer room air handler |  |  | Fan cables shall be properly dressed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198331&prj=626&rqi=IISb54kZZsGeYeX0hgVQ9fvaDK
RT1MECH-29-001 | 8fb53a41-2480-4ea0-8322-c6ff75a57e02 | JK01-2 | 626 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_F_03_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198298&prj=626&rqi=MiTF9Mtiq9rFP8m3hSuT7aOdTB
RT1ELEC-18-006 | 34eac576-e1f1-4a20-bdce-4769f32d9b7d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Marker markings on the busbar shall be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198313&prj=626&rqi=oTRZgDENBnNqvBiFfk3Hu8m9Ae
RT1MECH-32-001 | b83b1e69-82a8-41d9-bd0c-e995db8cbf03 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | IwanS.Kurniawan@turntown.com | 2026-02-03 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CHWBT_1 | CHWBT - Chilled water buffer tank |  |  | Buffer Tank _C Jacket insulation broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198295&prj=626&rqi=j3Yz2NdUbqqsL06e3YIxEXGWzD
RT1ELEC-18-004 | 5c230737-1070-42d1-be7d-db93df820b5a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Fuse labels shall be replaced with new labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198311&prj=626&rqi=jOmMxQz6DUY93eFHHHeFHHG46W
RT1MECH-30-001 | faddeff0-771e-4666-a2b2-d130d3f8742b | JK01-2 | 626 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_D_04_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198299&prj=626&rqi=H8HL74jzlUzQH4whs0ZyeU0VWr
RT1ELEC-18-003 | 7c12faa3-4eb5-408c-bba0-787b5222a389 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Temporary labels shall be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198310&prj=626&rqi=YKRdLjGrBZChjkc5XIpN082JWa
RT1MECH-28-001 | 899789ea-389e-4097-b518-9cee8a86eb80 | JK01-2 | 626 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_C_02_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | paint broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198297&prj=626&rqi=m7fZrYxIXBDi3Q7fPPvw5fqAqT
RT1ELEC-18-007 | ee18f1e0-f314-49ed-aeb6-0ee09f850167 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Phase separator / barrier between phases is missing and must be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198314&prj=626&rqi=6TcpdsPYj0EsHY1Vf8sdFkw8wj
RT1MECH-31-001 | 76325dd5-bbb1-4c36-8faf-019916a78dce | JK01-2 | 626 | APAC | Closed | P3 Low CX | IwanS.Kurniawan@turntown.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWSTR_B_07_CH_1 | WCC - Chiller â€“ Water Cooled |  |  | paint damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198300&prj=626&rqi=pUTglmujV843O1XJ1i7SEL8fsg
RT1MECH-135-002 | d3d190da-3d8f-41cd-a058-a1b187dbd4e7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1LCP_FPUMP_B2 | FT - Fuel Tanks |  |  | The device tagging label inside panel is different from the approved drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198292&prj=626&rqi=h65u5cK6tnf45mHRPSReH8U0Dl
RT1MECH-134-001 | 7ce2cdf1-392e-4d0d-9df7-efac93b483a3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Fuel | equipment | 1LCP_FPUMP_A2 | FT - Fuel Tanks |  |  | The device tagging label inside panel is different from the approved drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198293&prj=626&rqi=8xE4p6gHHcMOa1jDAK7IQA5ZCO
RT1MECH-135-001 | 73a46cfc-d759-439b-a6e4-f5e330e134bb | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Fuel | equipment | 1LCP_FPUMP_B2 | FT - Fuel Tanks |  |  | LCP_FPUMP_B2 Panel Installation not level | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198291&prj=626&rqi=044BJfuzXtDCi3edtj4XIMspO7
RT1ELEC-18-005 | 3f12f6f1-1421-49ee-81dd-0b4f9c209732 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Equipment is dirty with dust and foreign materials. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198312&prj=626&rqi=q23L8dCcUJCF9W08vx35OaT610
RT1ELEC-18-002 | 025e0a6e-2d3f-4927-8539-43705e864f2d | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Equipment positioning does not comply with the latest approved drawing (photo attached): - Left side to wall: drawing 1598 mm, actual 1629 mm - Rear to wall: drawing 244 mm, actual 235 mm - Front clearance to 1STSSB_D_2: drawing 1478 mm, actual 1580 mm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198309&prj=626&rqi=pMWzSHB2vUA9LjRv3roj8eEBjk
RT1ELEC-3-021 | 6b0d48b7-499f-4902-a1b5-0c346da0d1a9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Design correction needed | Design |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | BTU battery panel need to add battery stopper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198167&prj=626&rqi=mX0veEvTFJZE3ZFYJly15pznWo
RT1ELEC-10-001 | c801ce74-9467-466a-ac77-8061785eeaf7 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_C | MLTX - Transformer |  |  | Maintenance doors facing wall, need to relocate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198159&prj=626&rqi=YH7pwLeMrbF2OZ283AgnCTgQeY
RT1ELEC-3-020 | dbd01fa6-e334-4889-8b3a-32bfd8ac1eb9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Design correction needed | Design |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | BTU panels are at risk of water splashes from the louvers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198165&prj=626&rqi=ypWy3DMeOT5m62tXmGLXDXkLQr
RT1ELEC-2-013 | 9881ed32-104b-4e15-8472-74d7d7da9633 | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | BTU panel HMI display loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198175&prj=626&rqi=KrDfiDN6iMIKXMH1DAuAvxSxik
RT1ELEC-9-001 | 5354ee34-5dc7-42c8-800d-1e35015b1a22 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Maintenance doors facing wall, need to relocate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198160&prj=626&rqi=laCOzRromobrUMduA0JfduwFXo
YT1ELEC-2-001 | 7edcae4d-3464-4200-ae5d-79a045edc64f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | (Issue from CxL2A) - Permanent equipment labels were not installed. Equipment tagging with the correct language and approved colour scheme is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198170&prj=626&rqi=Hp5lpBntVZp71Tn1zAW45PkY86
RT1ELEC-2-011 | 04f8e172-399e-4d9c-96b8-effdc5e89ab7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Design correction needed | Design |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | BTU panels are at risk of water splashes from the louvers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198173&prj=626&rqi=oDPkwd5ukDAWNsPgSA2xMfxCNR
YT1MECH-6-001 | 72d12120-bdd7-4507-8932-a905a9f9ba64 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-02 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | (Issue from CxL2A) - Please provide permanent equipment labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198171&prj=626&rqi=VrruT5YApsHM6vTs8k6mFkFAZz
RT1ELEC-3-019 | 8a15cc53-f69f-4c44-b96c-8295e186f331 | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | BTU_C HMI display loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198164&prj=626&rqi=G5AdkLwVIXMNglUDaq6sXuh7Rc
RT1ELEC-9-002 | d65bde20-9add-4ec4-b84b-e54f299374ec | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | Missing door hinge | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198161&prj=626&rqi=oRopaAXUrUP3QyDFKWhUytZBlC
RT1ELEC-2-012 | dfbc8dd8-a644-446c-aecc-6e2f43a06c70 | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | BTU battery connection not complete. need add battery stopper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198174&prj=626&rqi=eF1wHiCK3ig4KZnvGCrpxB9ks8
YT1ELEC-3-001 | 3fce39d7-da51-4423-869f-feaa32345105 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | (Issue from CxL2A) - Permanent equipment labels/tagging have not been installed (Main Tagging Equipment) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198172&prj=626&rqi=Q3d6fr3bfXDwvrbis2Sr4cTBxm
RT1ELEC-18-001 | 2b16ccb2-0a6c-4501-8a1c-f0aa5689049c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D_1 | MSB - Main Input Switchboard |  |  | Please upload calibration certificates for factory test | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198126&prj=626&rqi=zfdE9DQITw8YHEne6GhtLYeaA9
RT1ELEC-9-003 | d168490e-422c-42ba-ac7a-fa7db85e45d9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_D | MLTX - Transformer |  |  | the door cannot be closed properly. scratches on the door frame | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198162&prj=626&rqi=aL5gduMFnOAYqUEzFSp5BGvhSf
RT1ELEC-3-018 | 2bc1e288-6fd9-4421-8ee8-c41f0b1b8fe9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | 1BTU_C all battery connection not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198163&prj=626&rqi=0bEQnSNoAc6BVIe80ShrKoM9n5
RT1ELEC-11-002 | e4908ac0-85d0-4a60-9c22-5d75b32a1e42 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Side access door installation MLTX enclosure (for maintenance access) differs with the approved drawing. GC/MCE shall clarify. Incorrect installation or missing access door will result in no proper maintenance access. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198101&prj=626&rqi=cESuUqIkN39KNGtkfi7joF8Hnz
GI-008 | 52a58b34-bb68-4f60-af97-a70c2f3f7c9d | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | MLTX_F - Incorrect Enclosure Maintenance Door Direction | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198084&prj=626&rqi=xdNB4yANvZP31Czk52nMlbPoY8
RT1ELEC-11-003 | 2daddd6b-8999-4b6e-9709-732a6798f41d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Vibrations pads has not been torque-tightened and torque marking is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198102&prj=626&rqi=tB0TI6J01jr5aAYhDZQBvSjCR9
RT1ELEC-11-011 | 895ccd1a-0c01-465b-86e6-46953899b15c | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Please upload cable schedule documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198111&prj=626&rqi=Yt8LwraHgcWhHnP1P1mxq669DS
RT1ELEC-11-006 | 504bb825-9b88-4b38-a977-0f64ddb5eb09 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Need to provide "danger" sticker/label on the transformer body. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198105&prj=626&rqi=I3Go59vDlaas1TmI4UZIznsFRU
RT1ELEC-11-007 | 348e8457-c9af-4b9c-b2bb-a05a28a9b661 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Fan cables are not properly dressed. Poor cable arrangement may cause damage or disconnection during maintenance activities. Please tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198106&prj=626&rqi=7HusfGQdfRKozBFaIMVeZcz1I9
RT1ELEC-11-005 | fd8f652b-c4f1-4099-bb8e-29ecbb42775a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Some components have only one label on the mounting or body, and terminal labels are missing. Each component shall have two labels (on the mounting and on the component body). Terminal labeling is mandatory | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198104&prj=626&rqi=BUs5ZMpKhWQvg88tWHIw4txEb0
RT1ELEC-11-008 | 8928fc03-52a6-417f-9da7-f11a2fd0ca8b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Scratches and dents are observed on the equipment. Touch-up work is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198107&prj=626&rqi=7SpKIzD5bnX1X83zmkkHFUMZwa
RT1ELEC-11-009 | 149ddf4a-0e99-47e4-9917-d9bb2ebd9d89 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Permanent equipment tagging is not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198108&prj=626&rqi=RqraYWE7Ect8c0dUiLnBULm5w5
RT1ELEC-11-010 | fd6699ca-880f-471b-8629-88926aad9cda | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Anchor bolt size does not comply with approved LS specification (required M12, installed M16) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198109&prj=626&rqi=lEBIXQXh4cIAoeLZXBUF9JDwJ6
RT1ELEC-11-001 | 1cd1038a-53e1-40de-a4ca-1eca6265f006 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Please upload following document: 1. Approved factory test calibration certificates 2. CxL2B Method Statement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198086&prj=626&rqi=8VrV1cWVFzKkeaYeX50zpWA2ih
RT1ELEC-11-004 | a0086f06-eacd-4823-8710-b7446e11e536 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MLTX_F | MLTX - Transformer |  |  | Need to be cleaning & touch up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198103&prj=626&rqi=xZTX7nb6idqt74thbPxL7d2Jnc
RT1ELEC-3-016 | 851cf7e2-3154-40e1-9005-42d5f2b1f443 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-28 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Bonding jumper on cable ladder not installed, please re-check all jointing cable ladder | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197869&prj=626&rqi=bCMFD5AhPVQpXFde2bnHQzQtXx
YT1MECH-111-001 | 4af9c48b-ea06-48cc-841c-e3dbc869c893 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_2.01 (Existing) | PAV - Pre-Action Valve |  |  | Seismic bracing not yet installed (drawing not yet approved) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197847&prj=626&rqi=B35HhWdbadwA2NmXhSjIGmQgdW
RT1ELEC-3-017 | 073bca26-297c-4c9f-8c4b-9fddf21d64ae | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-28 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Sleeve and firestop at wall opening/penetration not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197874&prj=626&rqi=7LBJGDo6YQO2BXCxvsw1OeJLHa
YT1MECH-111-002 | 93ab4e40-d5ce-4825-9257-b403f50f78b7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-28 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1FS_PASCV_FOH_2.01 (Existing) | PAV - Pre-Action Valve |  |  | At cool spine area level 2, sprinkler pipe BOP elevation differs from the latest approved drawing: 5300 mm (drawing) vs 5100 mm (actual) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197848&prj=626&rqi=bvRO32GOKWVseJkMEN3sBfbMcl
GI-004 | 59585240-11e0-4983-9380-33eafc99a7af | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-01-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Design correction needed | Design |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | BTU panels are potentially exposed to water splashes from the louvers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197642&prj=626&rqi=M0ch2tdBOZ4RsyjrpyLlRiTAz6
GI-002 | bcb491b7-39b7-4d4d-94f0-66c5121170d8 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | Dicky.Sukmana@turntown.com | 2026-01-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | RMU_F MV2 missing PQM | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197636&prj=626&rqi=xt8dBkDGnZQnILRTf4X5XoNrQB
GI-003 | 80d97991-9a3f-4ece-bac1-c755e0cdf5bd | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-01-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | Battery cable termination not proper | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197637&prj=626&rqi=vlo2R6Kw2YCWv82nJm8aMWsiml
GI-005 | 8caeed82-e951-408b-97b5-a6012a0581e2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | Dicky.Sukmana@turntown.com | 2026-01-26 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_F | RMU - Ring Main Unit |  |  | BTU panel position is not the same as in shop drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197643&prj=626&rqi=dls69DVV4L1cWTTjuPWprOgK8M
RT1MECH-119-003 | 5f6ab609-6964-474b-b751-9aa31ab773ce | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | Please cut cable ties and tidy up the cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197317&prj=626&rqi=CJbOtDoeLGI284Ih265YIJtBFA
RT1SEC-3-002 | 12e1c90a-2c53-470a-983f-e85828a06cf1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Security | equipment | 1CCTV_level_4_General | CCTV - Closed Circuit Television |  |  | Why is the uploaded inspection report for CCTV Level 7? This checklist is for Level 4. Please replace it with the correct report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197299&prj=626&rqi=MPVunEtaOUnp9ga0KqIH7TLHV4
RT1MECH-118-004 | ac6d8952-9155-47a8-9ca2-e0f1f0fcd6ad | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Equipment labels/tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197309&prj=626&rqi=BbtfCmvA6vrbE8LaEI5pWKOIib
RT1MECH-119-002 | 662c7459-7e49-4089-938f-e5fd05c5ffb1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | Equipment is dirty with dust and foreign objects. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197315&prj=626&rqi=dQTgdPosXZPSGPqLFgVE68OOEU
RT1MECH-119-004 | 401e4bd0-1328-4545-98f6-15f6e98a97a7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | Equipment labels/tagging not yet installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197318&prj=626&rqi=d9TIsADhmLOFqEmjoTFWr4JMwe
RT1MECH-118-001 | a1e0143f-b6ce-4bc8-9c4e-04ba7fe0c60f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197301&prj=626&rqi=XepAqixJo6VW696JzkmMfpWDos
RT1MECH-118-002 | 31723255-370d-49f2-9d34-39795fb9f723 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Physical dents identified on the equipment body | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197304&prj=626&rqi=0o3sEPOL2DLX7T9flq8OglKQT6
RT1SEC-4-001 | 6486acc2-3369-4cee-be8e-b47f59226262 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Security | equipment | 1CCTV_level_5_General | CCTV - Closed Circuit Television |  |  | Please upload calibration certificates | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197300&prj=626&rqi=P4aS2W6rHPdI8ngFopU1fRb73D
RT1MECH-118-006 | 3f8fe407-15cb-4c09-a397-26cbf27f7f5f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Equipment is dirty with dust and foreign objects. Cleaning is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197311&prj=626&rqi=nwSrrMSh4yjnJBPuiDqgvq97mc
RT1SEC-3-001 | 536668fa-8052-4309-b389-d7bf1a60c228 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Security | equipment | 1CCTV_level_4_General | CCTV - Closed Circuit Television |  |  | Please upload calibration certificates | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197298&prj=626&rqi=KYqfmMByvVF8Hi78rxM7URZQAN
RT1MECH-119-001 | 47b197c0-27e5-42d9-bf87-b30b0efc3138 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_61 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197314&prj=626&rqi=UUgMmESrsviLUL2QvE5x4OQvTq
RT1MECH-118-005 | 5ac18414-0c68-4a91-8454-71e93ca5f159 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Please cut and tidy up the cable ties | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197310&prj=626&rqi=QLIdodLsyKKPt386Gcg8A75zPK
RT1MECH-118-003 | 9165ed0a-27b2-40b2-abf8-a3603c600af5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_62 | CRAH - Computer room air handler |  |  | Please install the proper covers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197307&prj=626&rqi=BaEiRldM4uYifK0OWJyNh2l2gI
RT1MECH-111-005 | 53ccb8d0-8b1e-4b05-b953-5fdc59a7c873 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Anchor bolt markings are unclear and require re-marking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197182&prj=626&rqi=dG4dBRDs32mcgEhZuMIB7q53oj
RT1MECH-107-001 | 23b0e9a2-03e2-48ab-9e7b-0f06147d009b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Please upload General Arrangement and schematics drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197164&prj=626&rqi=xbSNvOFuY1eTguuIXzFa6lzAVn
RT1MECH-107-003 | 7ffdb14a-feee-49f3-912f-3e95d678b663 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | FAT report serial number does not match the serial number of the installed unit (FAT Doc: 001156011000007928 / Installed: 001156011000007967) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197166&prj=626&rqi=nvd4alcxCuJfgezUenZ9jVQ9U7
RT1MECH-107-002 | 2ccc5e05-0513-43de-a7f2-970de6756fc3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197165&prj=626&rqi=TBaEgyo7OsFp4ru4vFEFNwpFLx
RT1MECH-111-007 | 4f2715ba-d648-46af-9733-e927954dadfe | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Control cables are messy and need to be properly arranged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197184&prj=626&rqi=yesokLABRf9tZjP0eB2F2o6Qx5
RT1MECH-107-008 | b4d92406-54c2-43b5-bdb9-49cf3d0dc4ad | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Update the layout drawing for 1CRAH_C_22 based on the actual site condition. Ref JK1-2-M130-02-IFC-DWG - MECHANICAL EQUIPMENT PLAN L2 - FITOUT | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197171&prj=626&rqi=lBbncahBzocepQYx2w0PTAHXoG
RT1MECH-106-002 | f9eea3d3-1289-49f3-a51f-4957429db79d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Please upload General Arrangement and schematics drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197150&prj=626&rqi=qqwtDD1a6VS8M7hyeuWLUSXPJ1
RT1MECH-106-003 | 0100de70-9111-4dd8-a0da-2e4a21cdc13d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Component/Equipment Failure | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197151&prj=626&rqi=uyvmLF2pnw5mzURCbA2DYQhDlO
RT1MECH-107-007 | 91b181df-6cb8-493d-b7fa-2960150d1b54 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Equipment is very dirty with dust and foreign objects. Cleaning (FOD) is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197170&prj=626&rqi=RDxk19vugFGoUKiKRrUgk5xmpc
RT1MECH-111-003 | 42cad7e6-e862-4071-8506-09fb9445b1b9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Equipment position does not match the latest approved drawing. Rear: 290mm in drawing (actual 300 mm), side: 190 mm in drawing (actual 100 mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197180&prj=626&rqi=BCyiFTzCaeGeNESBkd7ZgrvyyF
RT1MECH-106-009 | b646ad5c-1ee0-4096-8fd5-eb810fc13427 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Equipment needs a temporary cover to protect it from dust and foreign objects | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197162&prj=626&rqi=9Vct8SePv5YzKE9LM83ma4Nzji
RT1MECH-106-006 | 97e17c72-2239-475e-9ae8-b65dad469030 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Internal chilled water outlet insulation is damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197159&prj=626&rqi=qw3A26qsL8rzRLTyLIRjuocEbO
RT1MECH-106-004 | 5391c7d4-21e6-4dbd-8226-d7fc264c5f63 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Equipment is very dirty with dust and foreign objects. Cleaning (FOD) is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197155&prj=626&rqi=QBDACdIp10ikU6c45sEcgs5xwg
RT1MECH-106-005 | 6a8ed059-2796-40ce-a10a-0bd3ffc8e6b8 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | nameplate / equipment tag is not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197157&prj=626&rqi=9uZjGwJm8KOoTo7E77tm6N5wpJ
RT1MECH-106-001 | 4e25f789-a3d4-4484-a039-2fbdaf7c7f46 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | FAT report serial number does not match the serial number of the installed unit (FAT Doc: 001156011000007967 / Installed: 001156011000007928) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197147&prj=626&rqi=yaz7PLIH8u33I05E0QYZqHlzw5
RT1MECH-106-008 | 0933edc5-663b-497d-b833-9bcd404943e1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Chilled water inlet and outlet pipes are open and need to be covered to prevent foreign objects from entering | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197161&prj=626&rqi=cUugo8eWBkAZ7DugFsRnIN9S3W
RT1MECH-106-007 | fbaadffc-eafe-4750-97b3-8b603d53ad5a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_B_22 | CRAH - Computer room air handler |  |  | Control cables are messy and need to be properly arranged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197160&prj=626&rqi=WORsrT8upHBwVIaLPKmHT7JstZ
RT1MECH-111-001 | f6ae2d13-bb57-432c-94ec-0f7c21d6778a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Please upload General Arrangement and schematics drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197173&prj=626&rqi=b7aXTwufIBgSdZCRvAASk7bXRd
RT1MECH-107-005 | c54031c2-e1be-43cd-83d6-8ba3394e3a6b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Nameplate / equipment tag is not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197168&prj=626&rqi=PGDpaTi3SuGty8gVNO2ECtzsoo
RT1MECH-111-006 | 89fe366c-7454-4ff6-a335-9d66e757c58d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Chilled water inlet and outlet pipes are open and need to be covered to prevent foreign objects from entering | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197183&prj=626&rqi=bZKiLdS3njMKel3R2MVPoTo2gA
RT1MECH-111-004 | 6260f756-00ea-434a-879b-d1946581c34a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Equipment is very dirty with dust and foreign objects. Cleaning (FOD) is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197181&prj=626&rqi=kR0qtTGpd2iftEq9eRyzvlsM81
RT1MECH-107-004 | 4d03e566-ff31-4acd-9e83-6cfb8dc2f941 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Cable arrangement is not neat and needs tidying up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197167&prj=626&rqi=Ezv2J0ol8FgqxJaTTiySPxxGNf
RT1MECH-111-008 | fbae5e53-a650-4f38-9689-fb6fc9449f40 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Nameplate / equipment tag is not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197186&prj=626&rqi=i6SjYTJWQbWaXaeecRekHK8TuJ
RT1MECH-111-009 | 63cd5ba7-5fee-42cc-b821-7386eecf1162 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Equipment needs a temporary cover to protect it from dust and foreign objects | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197187&prj=626&rqi=uUZ41k836E6JGQadzyA9BTp5OT
RT1MECH-111-002 | 34b95aa9-314a-44be-8738-521502eb7a40 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_42 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197174&prj=626&rqi=yh4BMOgZJfP8u2o5bUghoJSfFJ
RT1MECH-107-006 | 6fa8e4b8-6a43-43a8-b614-6b4af7432304 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_22 | CRAH - Computer room air handler |  |  | Internal chilled water outlet insulation is damaged | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197169&prj=626&rqi=8bLqilyQqG7L3wzPQAr51VEuMV
RT1MECH-110-002 | 729cea56-4d23-440d-b898-ba66082ac953 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Air openings are still open and must be covered with a temporary protective cover to prevent dust and foreign objects from entering the equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196964&prj=626&rqi=x2wYnnm4cc2g5G9nqJgKkfjzun
RT1MECH-110-009 | 0e4b0a3e-bf92-4579-b993-3d95eac50230 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Component/Equipment Failure | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Connection loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197010&prj=626&rqi=9pCwNw3GLyrAdEHfNheNkcV6fN
RT1MECH-110-005 | 02a7c9ff-4313-4677-b934-9609ab04728f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Permanent equipment labels / tagging have not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196967&prj=626&rqi=bRMOEsw2c3ANgHxvYv1dvGCrWe
RT1MECH-110-007 | 1751ad6f-633a-42a7-b076-af0e72c21ed2 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Equipment positioning does not comply with the latest approved drawing. The required clearance from the wall is 715 mm as per drawing (actual 820 mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196970&prj=626&rqi=qz5q16hlq8f9DacY06LMcFZhWO
RT1MECH-110-003 | ccd9c1bb-5642-4472-966e-0f854d6d1b18 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Dents / scratches were observed on the equipment body and doors during inspection. Please refer to the attached photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196965&prj=626&rqi=5SWnnPR282p24BS8aeOhEZPYio
RT1MECH-110-006 | a960ea83-6e38-4dab-88b9-1258f90557ac | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Please re-mark all anchor bolts and body-to-baseframe bolts, as the existing markings are not visible or have not been applied | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196968&prj=626&rqi=RvzG5IgFAyNtKAa0lEULlW2fSN
RT1MECH-110-001 | 22971e48-e276-4076-8229-7ebd33cb710f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Please upload Operation & Manual document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196962&prj=626&rqi=qfdDguN6iRJHfiiKkDii9kjGTA
GI-006 | e903f6de-8df0-4306-98fb-c513a21dd739 | JK01-2 | 626 | APAC | Closed | P2 Medium DCOS | dickyhermawan@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Issues SFAT DCOS 13 Jan 2026 â€“ Day 1 as per the Issue List in the Attached Picture. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197979&prj=626&rqi=dBPcShj2UhsF1oTSuV7o7KJbUF
RT1MECH-110-008 | 730ed7ff-cdae-4f70-89c9-a102ce8d348d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Component/Equipment Failure | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Disposable filter found damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196971&prj=626&rqi=IcyD11qhjlSxZY8nO6XGGKVqrF
RT1MECH-110-004 | cf811447-9bd3-447e-bec6-25c05e7fa4f9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_42 | CRAH - Computer room air handler |  |  | Significant dust and debris were found inside the equipment. Please perform FOD cleaning. Refer to the attached photos | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196966&prj=626&rqi=9XYeGzNXQT9XxwYIakVGUsVX3H
RT1ELEC-3-013 | df6cf29c-3c60-4f3b-b8f8-6120ca8d5bea | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Verification of the circuit breaker serial number could not be carried out due to obstruction by MV cables under ongoing construction. The MCE vendor is required to provide clear photographs of the circuit breaker serial number for verification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196731&prj=626&rqi=JPd6YNPxWJOTkr0vTp2o7d6gcm
RT1ELEC-16-007 | f888fef1-63e2-4b7b-8af2-4c562aae8209 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Equipment found dusty and dirty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196739&prj=626&rqi=SOtDTjBLyeoot2Q6kSqKsZzJy8
RT1ELEC-3-012 | ef18660f-1001-4d77-ac4a-641d969305f8 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Component/Equipment Failure | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Cable insulation is not properly covering | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196730&prj=626&rqi=1Jz3IaF4SHa9ZteUHOeXGV1g0q
RT1ELEC-16-005 | 9b34cf99-722d-43b0-81c4-399f4d87b7e4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Cable marker/labels are faded and unreadable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196737&prj=626&rqi=0qOJCdHtDcLddLrBOTapFU0sW4
RT1MECH-6-001 | 533d1a3f-d6e9-4acc-b5f3-8138fa40deed | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | Please upload Technical Submittals documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196755&prj=626&rqi=n0vpDeBMYgvVi3vyzFynvpLLIR
RT1ELEC-3-010 | 037a408a-5322-4450-a98e-afc03947d3df | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Some components have only one label on the mounting/body, and the terminals are not labeled. Each component should have two labels (on the mounting and on the component body). Terminal labels are required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196728&prj=626&rqi=0cWcnQxZ9c1Mo9nHbDKYOnUtOV
RT1ELEC-16-010 | 4d18942d-4154-4981-9f7f-0d718b689ebe | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Please upload document related to inspection/checklist from Vendor completed (signed off) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196742&prj=626&rqi=bgziJdj4NEKOwCRgHXYpT5MhqM
RT1ELEC-16-002 | c14b2d75-37e2-497b-8ef1-f3d3214dc914 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Defects, scratches, and dents were found on the panel body and door during visual inspection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196734&prj=626&rqi=KPcO0HCsJNwMIl8smoWl2dSYbv
RT1MECH-6-004 | cf90dc21-472c-4490-af5d-2bff3978afc3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | Number of spring mountings installed does not match the approved drawing (actual: 2, drawing: 4) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196766&prj=626&rqi=qBbFZVi1S7MFmYNsQseI3aD4M2
RT1ELEC-16-003 | 435582ed-d50d-40bc-ad6b-2ea09bfef5da | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Several phase stickers/labels were observed missing or detached. Replacement is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196735&prj=626&rqi=593Toz7309AWUVJLCys6OsGY7Z
RT1ELEC-16-009 | 3fdbb2a9-6ee6-4adb-a712-a4130836bc9b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Component/Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Please upload on-site torque wrench calibration certificate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196741&prj=626&rqi=6d5kz8tjXF9uupCHxD9c5hNZqW
RT1ELEC-16-006 | 6a4fd00b-e1bb-4021-bf7b-9cb85d858918 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Several ACBs are not provided with protection, which may lead to scratches or damage during construction. Please provide proper protection for the ACBs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196738&prj=626&rqi=Br6SwdgUN9Py6UDgYJJ2kPcplb
RT1ELEC-16-004 | 4d43d337-7b9f-4824-be09-91586cce8f70 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Loose cable found disconnected from the terminal | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196736&prj=626&rqi=DvjWRB0xpuFCAXxogJFl4y6f6l
RT1MECH-6-002 | 61618271-51bf-4764-8d20-744cd16588b2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | Please upload Approved Engineering Sequences of Operation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196756&prj=626&rqi=UMtU7miqwQNuLs3kZiMtVsyP5y
RT1ELEC-3-014 | aaea3a94-a56e-49da-9f57-ad270106f105 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Please provide a temporary cover to avoid debris or foreign objects entering the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196732&prj=626&rqi=a31WbB8KQ76w5l3FmNFqAxzkOY
RT1ELEC-3-009 | 80af3504-2271-4df1-a20d-d37e9667f4b7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Construction is incomplete. Cable termination has not been done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196727&prj=626&rqi=kWI8e9z8MPi04rSBjY9OOo7b0O
RT1MECH-6-003 | 233d3363-5c91-42e3-9c8f-83f53cce441f | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1EF_B_21 | EF - Exhaust Fan |  |  | Please provide permanent equipment labels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196757&prj=626&rqi=zxte06u0VMhsHI5uwJbJ6GotcU
RT1ELEC-3-015 | c8618a28-a022-4d5c-8baa-bca364232e6d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Cable arrangement in the cable duct is too crowded, so it cannot fit the cables properly. Please tidy up and reorganize the cables | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196754&prj=626&rqi=Q3IA7vPqTMExmyVTj2ehVISBlT
RT1ELEC-3-011 | d7ce818e-31c2-46da-a6dc-60e2c9cf1aa9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | The earth switch has no status indication. Status indication needs to be provided, and an attention/similar label should be installed above the inspection window | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196729&prj=626&rqi=9xpWFZlnYxgBUaouUSDxZXDA7Y
RT1ELEC-3-007 | 905b4727-0c34-49a4-ab60-e222313ddf12 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | No drawing pocket and latest approved drawings were not found inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196725&prj=626&rqi=Rf8xqm8qA0pklg61vn1PZ7V6al
RT1ELEC-16-008 | 72505622-1ae3-47a3-b787-6d3fae84288e | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Please upload on site (Internal) Torque connection sheet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196740&prj=626&rqi=H9kxfyImfSfMHTPkeyN0xoQl5H
RT1ELEC-16-001 | e55d0a7f-60d0-4bce-a92d-beb1e6c2f3f6 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B_1 | MSB - Main Input Switchboard |  |  | Panel position does not match the latest approved drawing. Rear: 235mm in drawing (actual 250mm, side: 1450 mm in drawing vs (actual 1410 mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196733&prj=626&rqi=SRJWGCCwyiQshSN5YDwa9RHQhr
RT1ELEC-3-008 | b038132b-0863-44bb-9fc5-728d45d10f52 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Permanent equipment labels/tagging have not been installed (Main Tagging Equipment) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196726&prj=626&rqi=9tgMmmPzco9xMTpN4QyqmLs94R
RT1ELEC-3-006 | 5a4e66a9-d9fa-465a-bdba-34015f5dafd3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Visual inspection found defects, scratches, and dents on the panel body/door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196697&prj=626&rqi=fn7jkeay3Pu3mRqHFEwRalTypv
RT1ELEC-3-002 | e13e7e33-0fab-45fb-9f50-f73beefda2e7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Please upload HV cable design documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196691&prj=626&rqi=tfZ9eGC1uAuDVitcTTtQNosOmN
RT1ELEC-3-005 | a433b48d-c3fd-46a2-9938-3c88dde14f8b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Door has scratches caused by interference with the panel body | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196695&prj=626&rqi=OBVwkm69JC70Q2a5ILo1BTpa5a
RT1ELEC-3-001 | b9e4b4a6-6832-447b-b110-56cc6b972297 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Please upload cable schedule documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196690&prj=626&rqi=6Gn7GHhlkPQcfnJeejKyUSxkzf
RT1ELEC-3-003 | 79d124f1-079d-4470-8205-90927db522a4 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Panel is not properly leveled during installation, panel found not level (tilted) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196692&prj=626&rqi=bnxjsH52Fr4kvOnUi5OaMZJNLM
RT1ELEC-3-004 | 87c37733-9f6a-4507-90ff-15ab830990fd | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-01-11 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_C | RMU - Ring Main Unit |  |  | Panel position does not match the latest approved drawing. Rear: 100 mm in drawing (actual 115 mm, side: 100 mm in drawing (actual 210 mm) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196694&prj=626&rqi=gLwTjhaVlPrwjnvUM0PzGZeDth
RT1MECH-45-004 | 8cd1a4f3-1ca2-437f-8c3e-60c593fd9d96 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_05 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196547&prj=626&rqi=qwt2l6PK6lJJOI80GwjxSKtjPF
RT1MECH-49-003 | 90edabda-3c28-452c-a2b9-a7a742fff518 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_11 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196551&prj=626&rqi=uAl8LVmh3dnhTv3spHqNmZuoRP
RT1MECH-46-003 | 459694fc-5362-4a50-8e08-d8bf7fd573cf | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_06 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196548&prj=626&rqi=1bTiQCKkF1r3NB7rTvxfIYUza2
RT1MECH-25-003 | fe608654-7f86-4d10-947e-7249fce9a538 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Installation not correct | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | FCU positioning does not comply with the latest approved drawings. For BOU, the drawing indicates 3500 mm (actual 3450 mm), and the wall-to-unit is specified as 450 mm (actual 550 mm). Alignment with the approved drawings is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196545&prj=626&rqi=WfIyaDYg5mT4aQqZCAMUXj0CS5
RT1MECH-48-004 | b74fa729-9146-45d8-8349-6ee27c66504d | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_09 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196550&prj=626&rqi=h2qhukioZgzeF4qOPiNHwjyLaP
RT1MECH-43-005 | 0f4008c5-08b1-4906-8f5f-672a94222537 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Torque verification of the unit anchor bolts at the corner positions could not be carried out due to limited access, as the torque wrench could not be properly applied. Confirmation of anchor bolt torque compliance with the specified criteria is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196539&prj=626&rqi=KuxhqXvImXF3XQJ3NXWFWlOtNS
RT1MECH-47-003 | b59202a6-d055-4809-8dec-3309a6a5daf9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_07 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196549&prj=626&rqi=ImqX0GEqsTGkwFu0VMPMijJwbx
RT1MECH-44-004 | ad903724-09a3-4b54-a1f9-f55504f1e915 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor | L2A | Torque required | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_03 | CA - Cool Array |  |  | Anchor bolt torque could not be checked at the corner positions due to limited access, as the torque wrench could not fit properly. Confirmation that the anchor bolt torque meets the specified requirements is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196546&prj=626&rqi=dxB2e0VlaI2GudZzgcNjKGizSt
RT1MECH-116-001 | f43d3e04-2a4a-492c-b848-d83c42189a98 | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | Tagging equipment ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196450&prj=626&rqi=CkX5TKgEaolhtY4O5e3JPeI51R
RT1MECH-116-002 | 17640162-1634-463c-b1fd-8b962d4da690 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | Air opening not sealed yet to prevent debriss | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196451&prj=626&rqi=Pjzso5S6yg2unlLoPAPPDiTF2n
RT1MECH-116-003 | 3ca3976b-b8f2-47ad-89d4-2a441a1018dc | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_F_61 | CRAH - Computer room air handler |  |  | Internal panel need to FoD and cleaning inside the CRAH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196452&prj=626&rqi=qsYpbIMhRd1Haz1YN9zP6jCVwN
RT1MECH-25-001 | b28276d1-f9b6-4465-929c-7d814aee47fd | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | Missing document upload: - MoS - Material approval - QA QC report factory - Drawing installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196469&prj=626&rqi=xRBIathhnMmtF7dKq7RSSW0gaw
RT1MECH-48-002 | f1a75644-59f0-4364-9d66-2d463b0a46f9 | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_09 | CA - Cool Array |  |  | Equipment tagging ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196435&prj=626&rqi=190D4c17pkergHeRRbgN8hRAz3
RT1MECH-45-002 | b42b8a09-2a24-462d-94ac-2e5359ed8940 | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_05 | CA - Cool Array |  |  | Equipment tagging ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196428&prj=626&rqi=vYBVNAifxOIIihIZnqa4xwIfxg
RT1MECH-27-001 | ef902380-3f77-4479-a507-371dafb95f4d | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | Missing document upload: - MoS - Material approval - QA QC report factory - Drawing installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196458&prj=626&rqi=gK5LUvYVQ0GW9cRC5h204EXFwd
RT1MECH-45-003 | 43f01bfe-e56b-43ee-a0e6-eeaef542d2c7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_05 | CA - Cool Array |  |  | Cable sensors need to FoD, tidy up and suggest adding spiral cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196429&prj=626&rqi=ygzME24e8Zqw0vIfBI2368y93n
RT1ELEC-2-003 | d1035ce7-21ba-4274-9fee-87fc45da82b7 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Gland plates are not installed on the RMU panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196449&prj=626&rqi=LzqZVslPwR899oU8gcTbucBkAA
RT1MECH-26-002 | f12e311a-c0de-4d9c-9d6e-6ac6d1b36bd0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | Equipment tagging ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196466&prj=626&rqi=07cf82QKKXhQfsvT1iBypx5dfA
RT1MECH-45-001 | 739ee671-ee7a-4bfa-ae53-7acef15fef3e | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_05 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196427&prj=626&rqi=7dwu91RhEWZ3Go8pcs9j911lzN
RT1MECH-43-001 | 4b34d168-b96d-4fe1-92c5-a1aa5fb22a4a | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196420&prj=626&rqi=MQh2gWMUtRHn06IULGI9jo1i52
RT1MECH-44-003 | a816ff80-3e2e-41ae-b5cb-e5aeb0301781 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_03 | CA - Cool Array |  |  | Bolt torque under 3 threads under the nuts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196426&prj=626&rqi=VFySqfOvZ0QUE7fYF8KWXuhlJD
RT1MECH-43-002 | e0fa5681-d5e0-40cd-9667-8d8d6360720f | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Tagging ID equipment not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196421&prj=626&rqi=7wwEbnthRH77r5hbCajUQa59ju
RT1ELEC-2-005 | d59c38cc-1973-4bc7-819f-c4a7c2e85190 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Latest GA and schematic drawings were not available within the panel. Drawings to be provided and installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196464&prj=626&rqi=Hm2rKUXJCS2fGq1B5kJW8xGG5l
RT1MECH-49-002 | a90c5f38-4fd2-42b3-83ae-aa78b581bef2 | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_11 | CA - Cool Array |  |  | Tagging equipment ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196438&prj=626&rqi=p9Jzmjj1SDoBHyHSiyGkDJgud0
RT1ELEC-2-002 | 15200893-8049-4d97-8cef-3d31f5f3254a | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Please upload HV cable design is document | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196448&prj=626&rqi=B3Kx73LEhy11IMylNumi2d9Olj
RT1MECH-117-001 | bdd55265-9851-44c2-802f-520ef390cb1c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_62 | CRAH - Computer room air handler |  |  | Air opening not sealed yet onsite to prevent debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196455&prj=626&rqi=jPWbpe0dscGCn2tIuIsRbFMp0y
RT1MECH-27-003 | 1d1295ef-a93c-4cc8-b41c-97031c3f58c5 | JK01-2 | 626 | APAC | Closed | P1 High CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | Positioning FCU have discrepancy between drawing and the actual onsite. Please refer to drawing attached, GC need to provide the clarification. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196461&prj=626&rqi=7OnmsvCK7YlbQti8PDBSvtGU6B
RT1MECH-48-001 | a3afc91c-d0be-45c9-8141-181afa8d8f1c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_09 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196434&prj=626&rqi=3sFEeSwqrpsqlfJJ9zFFhPMmPK
RT1MECH-48-003 | 16772cf5-67b3-4b73-8ade-7e38e01c00a7 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_09 | CA - Cool Array |  |  | Installation for 1CA_D_09 is not level. Please refer photo attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196436&prj=626&rqi=rSbeR2sxsYMDUOeZPSy4hPuWO9
RT1ELEC-2-004 | f162394b-e963-4901-89b8-7b4a50236b46 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Cleaning | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Surface scratches, stains, and paint marks were observed on the panel door and enclosure body. Rectification is required to meet project quality requirements | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196462&prj=626&rqi=CiAsCgoGimI3dUIdFSGGsTDY5w
RT1ELEC-2-009 | e6eeec59-1973-4563-8357-a8629742d9b1 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Verification of the circuit breaker serial number could not be carried out due to obstruction by MV cables under ongoing construction. The MCE vendor is required to provide clear photographs of the circuit breaker serial number for verification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196475&prj=626&rqi=qBsDLGhTwnt1B450Ml7Ui3hdCH
RT1MECH-47-001 | 68136e33-b33e-450e-98cd-4624c67b8171 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_07 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196432&prj=626&rqi=XmYgnbQmBJyIU3OCbbtuQmLiOb
RT1ELEC-2-008 | b29a2d4d-347e-4f7b-87b0-4ba46b4319dd | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Permanent equipment labels were not installed. Equipment tagging with the correct language and approved colour scheme is required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196473&prj=626&rqi=GS2lQzqilJJPqDbwYve8DkkukP
RT1MECH-46-002 | 2a4e1fde-0307-4ad0-9aa9-a6c6cff61617 | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_06 | CA - Cool Array |  |  | Equipment ID tagging not yet installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196431&prj=626&rqi=sFLDBINvDHDB1kVd5l13GE3gVC
RT1MECH-26-003 | c964070c-49e8-4c24-94b7-641c92b30b1c | JK01-2 | 626 | APAC | Closed | P1 High CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | Positioning FCU have discrepancy between drawing and the actual onsite. Please refer to drawing attached, GC need to provide the clarification. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196468&prj=626&rqi=tWnFNjhDXSQzz4KR0mq8qQTe88
RT1ELEC-2-010 | 22b9ed23-4bd5-41b7-9bb1-101114b3ca95 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Exposed copper conductor observed at control cable termination. Ferrule is missing or incorrectly crimped. Re-termination with correct ferrule required to ensure no bare copper is visible | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196476&prj=626&rqi=0TDsZq5VPN7bDsPmP5uRvkvPol
RT1ELEC-2-001 | 631bebaa-831f-43e8-bd62-f2acd36c703b | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | Please attach CxL2B testing methode | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196447&prj=626&rqi=Abgkqgzkom5fvvtsg8upizB4r7
RT1ELEC-2-007 | 11426c32-886c-4dc8-9a86-a1b3bb1c8a23 | JK01-2 | 626 | APAC | Closed | P3 Low CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Cleaning | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | The equipment was found in a dirty condition. Please provide temporary cover to protect from debris | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196472&prj=626&rqi=nMT0GwstHKarXTBWu3yUn38pG6
RT1ELEC-2-006 | 010290d3-8869-4570-abf4-977bdd9a4288 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | fauzanfikri@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_D | RMU - Ring Main Unit |  |  | The switchgear tool board was not secured to the wall and was found placed on the floor. Proper installation and securing to the wall are required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196467&prj=626&rqi=Sfywma8B9PPJMToGcTF5jm3s1T
RT1MECH-49-001 | 6d0c15dc-c160-4b1c-a7a9-bff72113c8e3 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_11 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196437&prj=626&rqi=Uq7mPLg45sCSdiHrS2MM7Gfb4P
RT1MECH-43-003 | 3ced91de-d1ad-4d6b-9121-0761ee691ebe | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | bolt torque under 3 threats behind the nuts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196422&prj=626&rqi=XXwyWqSLIkrDn9istMf8eSErgG
RT1MECH-44-002 | 1e36abe8-398b-4090-810c-c31101606997 | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_03 | CA - Cool Array |  |  | Equipment tagging ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196425&prj=626&rqi=Pc89TNZlD9sK148mbW4c2jbK0g
RT1MECH-117-003 | 9e9fb7b4-4abb-4f89-9a22-d40e3491d375 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_62 | CRAH - Computer room air handler |  |  | Need to FoD and cleaning inside the CRAH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196457&prj=626&rqi=rwjq0I2rR4fQH5xbPupdoQjpgS
RT1MECH-26-001 | 8ff102f5-6e9b-4c43-aa25-09af30e265b3 | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_F_61 | DXID - FCU/DX Indoor Unit |  |  | Missing document upload: - MoS - Material approval - QA QC report factory - Drawing installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196465&prj=626&rqi=DkfoVVC2ooPG92MmXFdLtdd1Bu
RT1MECH-43-004 | 9af1819e-073f-4e67-b89d-dd630d8e85bb | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_01 | CA - Cool Array |  |  | Sensor cable needs to tidy up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196423&prj=626&rqi=6CGOMpOdet34pNLpv6CTiAjQwV
RT1MECH-44-001 | 2ab757ac-3e05-4884-a052-16be6e76db09 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_03 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196424&prj=626&rqi=cPqlQFUh4skFy084XxKZqF3MzT
RT1MECH-27-002 | 5e2ffb74-3e32-41ac-8996-e9db2eaf82f5 | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_62 | DXID - FCU/DX Indoor Unit |  |  | Equipment tagging ID not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196459&prj=626&rqi=VZ7bnvrVHxvupHwfuoa99Mz5gm
RT1MECH-47-002 | fd28bc86-957d-4ea9-844d-7bbe19a0d75b | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_07 | CA - Cool Array |  |  | Equipment tagging not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196433&prj=626&rqi=qKYVssnISy0n75dvkWJT4jXM36
RT1MECH-46-001 | 17d02f67-e5d3-4f49-8ccd-f5c8e2fee25c | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_D_06 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196430&prj=626&rqi=Jqoa6fuEvdGYEwwmTqORlqMYBW
RT1MECH-117-002 | 16422e38-e2b0-43fd-bb6d-0f0cd7dfdda6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_C_62 | CRAH - Computer room air handler |  |  | Equipment ID tagging not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196456&prj=626&rqi=WrlSFFlpUqt4IPVYv0VqXNebKW
RT1MECH-25-002 | 168d3307-c199-4f73-99bb-a25669e1d6dc | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_D_41 | DXID - FCU/DX Indoor Unit |  |  | equipment tagging not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196470&prj=626&rqi=AKZUFem4PhrCVkXMbfaZM1jcx2
RT1MECH-60-001 | 00531488-03b4-4719-87fb-2b06c6cbba5a | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196328&prj=626&rqi=xy09sgTZcqVB6iUbrcq1dgaHKG
RT1MECH-58-001 | ba733ecf-495c-4510-bf19-5f126b869a9c | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196326&prj=626&rqi=QPWdBjp0ad2dqDbDLdKAGJKdFo
RT1MECH-61-001 | ceed1f91-f33a-4d66-bb4c-5600c6ff9503 | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196329&prj=626&rqi=JZHIHjJZj4wCwYjF4xJTLZkXKe
RT1MECH-63-002 | 590779fc-df30-483e-8b1e-9cc33eb60ca1 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_11 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196338&prj=626&rqi=G1EYzrpO5ORYjKvUfcv8DfTYBB
RT1MECH-59-001 | e53fd04a-196a-40be-b663-39314b089c8f | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196327&prj=626&rqi=Fka5o6tSEJMC2qcJVsuOrmuSdg
RT1MECH-61-002 | 21618233-838b-4986-a3f4-b125040b4dcb | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_07 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196336&prj=626&rqi=bl0zj28WeXwDcGvDIxQrLj0GE8
RT1MECH-58-002 | 60213dfa-5429-49aa-b6cc-f97176442b95 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_03 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196333&prj=626&rqi=YyPVsHccO3pHMfnFJgJUPYzFhS
RT1MECH-63-001 | c8f2dc9a-5c27-46be-8366-920813d4057d | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_11 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196331&prj=626&rqi=F7BiEZnaJnh7SdcW8qDj9Cq4nb
RT1MECH-62-001 | 0df42deb-fb5c-4e6d-8aa8-cda5fd7b21e0 | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196330&prj=626&rqi=WoCvv1TE0wpaqH7VC3XtSxy55g
RT1MECH-57-002 | eaa683e4-3f4f-4ff9-8336-9cd2587330bb | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196332&prj=626&rqi=OxOvOmfDQ4uWkurQmODqfmz7UX
RT1MECH-59-002 | 6408c380-dcd7-431c-9934-584764a0e053 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_05 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196334&prj=626&rqi=1BS3ZOU7yINFxYYhX6lPXgVCHj
RT1MECH-62-002 | 7d49605e-9020-4a4e-bdd6-4086304a5f19 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_09 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196337&prj=626&rqi=CR2Pa1nrQS7XFy2y6bdnVwKJLm
RT1MECH-57-001 | 142fa3b6-9314-4e62-b05f-7463ee2ea1d6 | JK01-2 | 626 | APAC | Closed | P3 Low CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_01 | CA - Cool Array |  |  | The tagging equipment is not installed yet onsite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196325&prj=626&rqi=wHfbrv2TtWtcyVUMZ9peTWMgG6
RT1MECH-60-002 | a8b6168a-695e-4042-915b-f494a71724f1 | JK01-2 | 626 | APAC | Closed | P2 Medium CX | dickyhermawan@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor | L2A | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1CA_F_06 | CA - Cool Array |  |  | The remote temperature and DP sensors have not been installed onsite yet because the installation location at the data hall is not ready due to ongoing construction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196335&prj=626&rqi=r6oj897VFdhOzh4cYPbVPsUlFM
RT1MECH-621-001 | 60e4d449-a004-488e-a41f-c70a9f46a21b | KL02-1/2 | 647 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | MCP-1EF-M1-09 | MCP - Mech Control Panel |  |  | MCP-1EF-M1-09 Labeling Incorrect | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631733&prj=647&rqi=HaL5BLDnbReNT3pGASxAxLmz9X
RT1MECH-620-001 | df6780d8-167c-4386-8ceb-7e6f36573b8c | KL02-1/2 | 647 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | MCP-1EF-M1-08 | MCP - Mech Control Panel |  |  | MCP-1EF-M1-08 Labeling incorrect | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631732&prj=647&rqi=plAUzbwiS21EdLnMAz9ZJ2rlD7
GI-044 | 35fcb9b7-d32b-4f9f-8480-894aa4b68250 | KL02-1/2 | 647 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-07-05 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1EF_M1_08 | EF - Exhaust Fan |  |  | 1EF_M1_08 The equipment tag does not attach as per approved naming convention | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627973&prj=647&rqi=xedFsynCrZM5SPrGMXmobs19u1
RT1MECH-618-001 | d8cc04f3-dd50-48a9-b661-c746289afb00 | KL02-1/2 | 647 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-07-05 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1EF_M1_09 | EF - Exhaust Fan |  |  | 1EF_M1_09 The equipment tag does not attach as per approved naming convention | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627972&prj=647&rqi=lOIBDU4IeFdedfffgNyO6AVcGg
GI-040 | 8f4e55ef-1b12-4a29-8fab-19bd5d56f297 | KL02-1/2 | 647 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | [FWT] Fuel PLC Bench - Fuel return valve open status should be to the lower fuel level Fbulk, but the return valve maintains to bulk tank 2; status remain until the following Fbulk detect high high level, following return valve faulty and fire mode; | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626840&prj=647&rqi=Dubd2BsCt4rkJgZVbWsEAK82Wy
GI-041 | e2025aa1-6925-4bf3-8003-11fdaac62500 | KL02-1/2 | 647 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | [7 empty] | [FWT] Fuel PLC Bench - SOO mention the bulk tank 1 is lead signal is pump 2, lag signal is pump 2 and lead is pump 1; reversely bulk tank 2 is lead signal is pump 1, lag signal is pump 1 and lead is pump 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626841&prj=647&rqi=6m8QPPp4mHvwWAGXVCaLygFSo4
GI-038 | 71b48bbe-1b89-4f7d-a608-8c2924869c4a | KL02-1/2 | 647 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | [7 empty] | [FWT] Fuel PLC bench - No password protection & user selection for setpoint page and ATG setpoint modification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626838&prj=647&rqi=2nhZKtbG9fyHgwBzpFkfPnWaIg
GI-039 | b5c55e0b-dab4-4792-9217-546668ef8831 | KL02-1/2 | 647 | APAC | Open | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Incomplete Connections | Commissioning | [7 empty] | [FWT] Fuel PLC Bench - Modulating valve trigger failed to close after failed to open trigger | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626839&prj=647&rqi=0stTjWWcrKF29gy9s6Duqgzip8
GI-034 | 1109b288-e501-4507-b849-887ea871aa75 | KL02-1/2 | 647 | APAC | Closed | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | [7 empty] | [FWT] Fuel PLC bench -1FP_M1_2, 1FP_M1_3, 1FP_HMI_1 and 1FP_HMI_2 tagging is block by the outer door panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626653&prj=647&rqi=FIikNl25RcrPxxswSnibyWZ2WU
RT1MECH-766-002 | 3d7729be-d086-414d-97a4-a82969f4b7e7 | KL02-1/2 | 647 | APAC | Open | P2 Medium CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not complete | Commissioning |  | Fuel | equipment | 1FP_A_LCP_1 | FCP - Fuel Control Panel |  |  | [FWT} Fuel PLC bench -Fiber optic media converter is not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626652&prj=647&rqi=rjdBYB0tYNEQhvMhA0ZfUMpmDY
RT1MECH-766-001 | 21df2425-4737-4cfb-84eb-52f0e61e3a53 | KL02-1/2 | 647 | APAC | Open | P2 Medium CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning |  | Fuel | equipment | 1FP_A_LCP_1 | FCP - Fuel Control Panel |  |  | [FWT] Fuel PLC Bench -Setpoint of the voltage relay as default -Pump overload setting as default | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626654&prj=647&rqi=CiNzYcVwpPxVkc2vRbvRri8TxB
RT1MECH-772-001 | aea3af35-01ab-4eff-adfb-d8614ea9a420 | KL02-1/2 | 647 | APAC | Open | P2 Medium CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Incomplete Connections | Commissioning |  | Fuel | equipment | 1FP_HMI_1 | FCP - Fuel Control Panel |  |  | [FWT] Fuel PLC Bench - HMI setpoint is not sync between HMI 1 and HMI 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626656&prj=647&rqi=pfBCt2tovdvo7QnQuXCPJe6tUL
GI-032 | 73acc397-9223-480e-a981-4e90cf1f1ba2 | KL02-1/2 | 647 | APAC | Open | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation not issued/ Required | Commissioning | [7 empty] | [FWT] Fuel PLC Bench -Terminal block quantity and tagging different with approval construction drawing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626648&prj=647&rqi=KCcuuxRrBU2drn2nWV2uHFSINY
GI-036 | 4f930e9f-10af-4fec-99bc-f9ae2574e40d | KL02-1/2 | 647 | APAC | Open | P3 Low CX | KaiJetSim@commtechasia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning | [7 empty] | [FWT] Fuel PLC Bench - To standardize the equipment labelling at the HMI page, with approval naming convention | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626655&prj=647&rqi=ARkLtim8LMv9P1EaEPEcDrCi5J
GI-030 | 6a56fc4d-0d5b-4dae-8699-6996c576ab99 | KL02-1/2 | 647 | APAC | Open | P3 Low CX | geoffreytan@commtechasia.com | 2026-05-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [7 empty] | [FWT] 1RPP_XX_01_XX - Update the wiring drawing of the MCMS module, to indicate network cable position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623429&prj=647&rqi=hJWJI9bhKl7S7OV8yUfMRh1ogj
GI-029 | 0725daef-cc7f-48ba-a142-614c3c1a1a7e | KL02-1/2 | 647 | APAC | Open | P3 Low CX | geoffreytan@commtechasia.com | 2026-05-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [7 empty] | [FWT] 1RPP_XX_01_XX 1. Name label of equipment missing 2. Spare Breaker label missing 3. MCMS Card label, too add identifier labels to the MCMS cards | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623428&prj=647&rqi=073nYFtymfdXJPRDkjh1maU8YQ
GI-028 | ba85417a-9bdd-42cb-b96b-0e13dbc69222 | KL02-1/2 | 647 | APAC | Closed | P2 Medium CX | geoffreytan@commtechasia.com | 2026-05-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1LBSB_1 | LBSB - Loadbank Switchboard |  |  | [FWT] Bolt connections, bolt threads come out less than 3 threads above the nuts. To comply with Equinix Commissioning Playbook 6. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623425&prj=647&rqi=dEKVeEWXJoyMrc9Zuynu1lJ7g0
GI-010 | d029474f-a658-4f51-b7f8-3d0f1918d90b | KL02-1/2 | 647 | APAC | Closed | P3 Low CX | geoffreytan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Cleaning | Commissioning | [7 empty] | (FWT) Surface Rust to be cleaned off Equipment S/N: 50612A68708365 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616931&prj=647&rqi=MAnpC0MRLc6gXVeSW63XRv2yvQ
GI-011 | 70f27b45-8af1-42c4-b714-bf2bfb4a6a6d | KL02-1/2 | 647 | APAC | Open | P3 Low CX | geoffreytan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning | [7 empty] | (FWT) VSD Panel incoming breaker setting for LSIG to be provided by JCI. Equipment S/N: 50612A68708365 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616932&prj=647&rqi=UKZQu1OI8QynZcLwrYcMpgc0JK
GI-009 | 4bc49852-4746-4495-aef2-d4dc49259c03 | KL02-1/2 | 647 | APAC | Open | P3 Low CX | geoffreytan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [7 empty] | (FWT) To install missing labelling for cables within control panel. Equipment S/N: 50612A68708365 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616930&prj=647&rqi=bKBIEt39qQnNFZh4TwXjgsoafD
GI-007 | 6f98e1c7-2e2a-48a4-8613-9cd3ec8fb2cb | KL02-1/2 | 647 | APAC | Open | P3 Low CX | geoffreytan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [7 empty] | (FWT) To install cover for emergency-stop button at chiller control panel. Equipment S/N: 50612A68708365 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616927&prj=647&rqi=X4qxCSdWQFpKJuFS2HFHTLDHKq
GI-008 | ccc0b929-fcfd-44e8-acc1-0e1e65d76671 | KL02-1/2 | 647 | APAC | Closed | P3 Low CX | geoffreytan@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [7 empty] | (FWT) Chiller tagging nameplate to be installed. Equipment S/N: 50612A68708365 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616929&prj=647&rqi=jmkJjEzwObmV4Hqia7TFJkstpq
GI-006 | 4cd7e105-3047-4b21-ad8c-ec61c6df4d9a | KL02-1/2 | 647 | APAC | Open | P3 Low CX | fazandrayusfiandika@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS | [7 empty] | (FWT) DCOS test was conducted based on the pending signed off SICD by the DCOS SI. Observed changes and additions to DCOS point mapping as follows: - Output Breaker 1 Status (CB3A): Modbus address changed from 607 â†’ 609. - Output Breaker 1 Status (CB3B): Point to be removed. - Equipment Over Temperature Warning: To be added (address range 686â€“702). - SCR 1 Shorted: To be added (address range 839â€“847). - SCR 2 Shorted: To be added (address range 873â€“881). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197981&prj=647&rqi=amG1wICx1Ebw7dU6AiszbU9eXQ
YT1MECH-6-001 | bd9fb040-a5dc-4aec-81cd-52495e5a003e | LD06 | 675 | N-EMEA | Ready for Verification | P3 Low CX | andrew.sharp@implexcritical.com | 2026-08-06 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning |  | Mechanical â€“ Water | equipment | TCS/SFN - 01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | Confirm TSC/SFN pipework has been flushed in accordance with the Equinix TCS/SFN Cleaning and Flushing Requirements and all documentation including test equipment calibration certificates are uploaded, reviewed and CxA approved on the Equinix document platform | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632577&prj=675&rqi=cHVum8C7ng9FEJdVWEeQYWmHVX
GT1MECH-11-001 | a18b4fa7-db22-4e46-9db4-246ba5a9c05f | LD06 | 675 | N-EMEA | Open | P3 Low CX | andrew.sharp@implexcritical.com | 2026-08-06 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning |  | Mechanical â€“ Water | equipment | TCS/SFN - 01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | Confirm (if applicable) any EoR/EQX approved as-built drawings have been uploaded to Equinix document control platform. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632614&prj=675&rqi=WzPNVzB1xF5mHqjF68hQGIIaPw
RT1MECH-6-002 | e899203d-f637-4c48-a27f-1935f02a3677 | LD06 | 675 | N-EMEA | Closed | P3 Low CX | andrew.sharp@implexcritical.com | 2026-07-08 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | TCS/SFN - 01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | It is recommended that protective caps/covers are fitted to the stems of the PICVs to protect against any potential damage. This comment is applicable to all the TCS/SFN PICVs and the Primary CHW PICVs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628520&prj=675&rqi=l7TZOAY50rw8L3T3k31FT85ASY
RT1MECH-6-001 | ffb4e81b-4606-4d51-8108-ad780822cdbc | LD06 | 675 | N-EMEA | Closed | P3 Low CX | andrew.sharp@implexcritical.com | 2026-06-18 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“ Water | equipment | TCS/SFN - 01 | TCS/SFN - Technology Cooling System/Secondary Fluid Network |  |  | Confirm the EoR/EQX approved DCOS points list has been uploaded to Equinix document control platform. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626206&prj=675&rqi=qoez1qQqRtFzvE99bHkdtJgK4m
GI-017 | 8ce3578c-5b6c-42f8-b4fb-1d2a738b7933 | LD07.2-P1 | 617 | N-EMEA | Closed | P1 High CX | eosman@global-cxm.com | 2026-04-29 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning | [7 empty] | UPS-13 Module 4 keeps dropping load during 4 hour heat run. Testing cancelled. Schneider and Socomec investigating | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620004&prj=617&rqi=iCJ1iRalXDd3dFmbYDJuEIIVVW
GI-015 | a6db1d42-6946-4f95-8592-eb15c4c37806 | LD07.2-P1 | 617 | N-EMEA | Closed | P3 Low CX | eosman@global-cxm.com | 2026-04-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning | [7 empty] | LV-13 Micrologic Damaged to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618350&prj=617&rqi=bhmG8sAZSrtIm8cI5LrFSMFemT
GI-014 | d806e3ec-2064-498c-93d7-fdfe3f960a02 | LD07.2-P1 | 617 | N-EMEA | Closed | P3 Low CX | eosman@global-cxm.com | 2026-03-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning | [7 empty] | PPR's for LD7.2 P2 - Armstrong FAT not including DCOS works carried out due to limitations of equipment being available. To be captured as on site witnessing when available | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616257&prj=617&rqi=pb3idii5IiY6fDQx3KmxdGR4qq
GI-012 | 89318b11-c482-4883-a569-c756a1a71928 | LD07.2-P1 | 617 | N-EMEA | Closed | P2 Medium CX | eosman@global-cxm.com | 2026-02-19 04:00:00.000 +0400 | Equinix Commissioning Manager |  | Component/Equipment Failure | Commissioning | [7 empty] | PT100 Sensor on TX-16-D Failed, 6x Replacements have been ordered, Request to replace all PT100 as a preventative measure from Equinix | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199662&prj=617&rqi=0bswgMhvZPtudKyjan68oAv3lW
RT1ELEC-1-001 | e403a738-a547-4f9b-8287-e0c2a156685a | LD07.2-P2 | 687 | N-EMEA | Open | P3 Low CX | eosman@global-cxm.com | 2026-08-10 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ MV | equipment | GEN-8-01 | GENM - Generator |  |  | LV/ELC Cable entrance box has been left detached and inside the unit to allow steel works to be erected with out hindrance (LOR) to fix in place when they complete their steel gantries. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633013&prj=687&rqi=NeeDKuaANh2XBFEQj0HQwpc8CX
GI-004 | 845c72b2-55c3-4fa8-b11d-1ddbe4e37ed4 | LD07.2-P2 | 687 | N-EMEA | Closed | P3 Low CX | jhancill@global-cxm.com | 2026-07-28 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning | [7 empty] | All chillers waiting on shrouding to be installed in front of L1-L3 cables inside panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631146&prj=687&rqi=8RXIxZgJmbaTRKMq5nfMtl4Spa
GI-003 | bb31b76d-e57c-4e05-b08b-31a4f5803d47 | LD07.2-P2 | 687 | N-EMEA | Open | P3 Low CX | jhancill@global-cxm.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | All new AACC's missing asset ID's | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624337&prj=687&rqi=1jq3wMWdI33nZjod16yBfA71by
GI-002 | 63d82508-6a82-45c9-8404-1125c144b840 | LD07.2-P2 | 687 | N-EMEA | Closed | P3 Low CX | eosman@global-cxm.com | 2026-05-28 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning | [7 empty] | PPR's for LD7.2 P2 - Armstrong FAT not including DCOS works carried out due to limitations of equipment being available. To be captured as on site witnessing when available | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623352&prj=687&rqi=blGdA2CtKT5VC2znDlpI7oZvVy
GI-149 | 3cac6124-e5cb-4703-bff3-3e70b50f0a13 | LD09-P2 | 308 | N-EMEA | Closed | P2 Medium DCOS | Alen.Francis@eu.equinix.com | 2026-01-29 04:00:00.000 +0400 | Facility Manager |  | DCOS Comms Issue/ Fault | Commissioning | [7 empty] | GDC Requires the folowing Items to be clear of Alarms so they are Resilient. These Items are customer impacting. LD9.PG2_CRAC_12A_01 LD9.PG2_CRAC_12A_02 LD9.PG2_CRAC_12B_01 LD9.PG2_CRAC_12B_02 LD9.PG2_CRAC_12C_01 LD9.PG2_CRAC_12C_02 LD9.PG2_CRAC_12D_01 LD9.PG2_CRAC_12D_02 LD9.PG2_CS_2_3 LD9.PG2_CTA_2_3 LD9.PG2_CTB_2_3 LD9.PG2_UPA_12M | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197891&prj=308&rqi=uZbOgFfv7P87Sw9snnkcXwhxL3
GI-148 | 1a9c3232-dc5e-441e-8611-b51be437ffe0 | LD09-P2 | 308 | N-EMEA | Closed | P3 Low DCOS | Alen.Francis@eu.equinix.com | 2026-01-29 04:00:00.000 +0400 | Facility Manager |  | DCOS General Issue | DCOS | [7 empty] | GDC Item outstanding in DCIM LD9.PG2.RMU_M_RMU_L2_BSM: measure_active_power SUDB-2 Utility Incomer Power factor GSB3 Gen Incomer Frequency GSB4 Gen Incomer Frequency GSB5 Gen Incomer Active Power GSB5 Gen Incomer Frequency GSB6 Gen Incomer Frequency Issue: These Points cannot be proven at the moment as there is no load on the MV equipment. Can this be proven once load is availble | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197885&prj=308&rqi=a2QbXfcAL9pDCOL2llF2I2hH9k
YT1ELEC-677-001 | 36d0e790-ccf0-4e99-9f30-0a7cfbe6b7cd | LD14-1 | 646 | N-EMEA | Open | P3 Low CX | jknight@global-cxm.com | 2026-09-01 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1HEAT_R1_411 | AH - Air Heater |  |  | Earth on heater frame comes off TX earth bar. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636284&prj=646&rqi=BVyf891efCALtzngzIgel5FotE
GI-069 | 56f6de86-ceb0-4f8d-b6ac-2215b3d3de1b | LD14-1 | 646 | N-EMEA | Closed | P2 Medium CX | jknight@global-cxm.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1EB_PUR1_1 | ERTH - Earthing |  |  | Single link earth bar fitted. Earth bar does not match drawing or spec and main earths are doubled up on one stud. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635550&prj=646&rqi=CWgHupkYZGt3sYCgRY68qbuDHj
GI-068 | 7835d523-fb40-48e5-b372-6029c57e7628 | LD14-1 | 646 | N-EMEA | Open | P3 Low CX | jknight@global-cxm.com | 2026-08-19 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1EBPPR-M1_8 | ERTH - Earthing |  |  | Two studs on the earth bar have snapped off inside the nut. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634375&prj=646&rqi=sw4i2mZRI3LOJg9JvZMk43bGtU
RT1FD-104-002 | 68f6fd06-586a-437f-8c09-22582798b436 | LD14-1 | 646 | N-EMEA | Open | P3 Low CX | abadat@global-cxm.com | 2026-08-06 04:00:00.000 +0400 | VER - Vertiv | L2A | Installation not correct | Commissioning |  | Fire Detection | equipment | LD14_FAP_06_01 | FP - Fire Panel |  |  | The FAP door cannot be opened and closed properly. The interfaces below are installed too close to the FAP. There should be a spacer in between the interfaces and the FAP in order to allow the door to open/close as intended. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632711&prj=646&rqi=ebl7OBDJL1aOiF3H8NyKnUKbKT
RT1FD-104-001 | 2d90198a-ab24-4f7e-adb6-15daa44a3ff3 | LD14-1 | 646 | N-EMEA | Open | P3 Low CX | abadat@global-cxm.com | 2026-08-06 04:00:00.000 +0400 | VER - Vertiv | L2A | Labelling | Commissioning |  | Fire Detection | equipment | LD14_FAP_06_01 | FP - Fire Panel |  |  | No identifying label attached. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632710&prj=646&rqi=jedOEoeNGBPRGdL2VFATzAUpz5
YT1ELEC-718-001 | 9cc4a218-6e9f-421a-87d0-eedcf363b55a | LD14-1 | 646 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-07-16 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1EBLV_M1 | ERTH - Earthing |  |  | Cable References to be Confirmed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629822&prj=646&rqi=RX4bVkcyu6fUaSJZljy5EO7BYR
GI-053 | 72dfd4e3-064b-4ee4-a094-167f261a7240 | LD14-1 | 646 | N-EMEA | Open | P3 Low CX | jknight@global-cxm.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1MVTB_R1_HMI | HMI - HMI Panel |  |  | Cable ID missing from earth. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628602&prj=646&rqi=gGoiEeUTT30Txev91Cf7SrndFw
RT1ELEC-729-001 | f48eccf5-6214-4538-9b0e-7a39e0b5ff06 | LD14-1 | 646 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-07-02 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1EBPPR-M1_6 | ERTH - Earthing |  |  | asset ID not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627710&prj=646&rqi=HkGLqdoccYeCuC0KbvpI07KOeZ
RT1ELEC-730-001 | bd2c6e19-058f-4e7f-a0e7-e7355ff2572a | LD14-1 | 646 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-07-02 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1EBPPR-M1_7 | ERTH - Earthing |  |  | asset ID not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627715&prj=646&rqi=ZvmKj17Wwa1RokZ3ZcCJXx54Q5
RT1ELEC-731-001 | 2d572e16-c906-439f-a7e5-f68eb3a6b89b | LD14-1 | 646 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-07-02 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1EBPPR-M1_8 | ERTH - Earthing |  |  | asset ID not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627716&prj=646&rqi=ou79csl4wpiaeB4tXdKlLcokKW
RT1ELEC-682-001 | fbf24e02-5131-4f02-849f-83585eb8463c | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-07-01 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1HEAT_R1_411 | AH - Air Heater |  |  | Permanent labels not attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627575&prj=646&rqi=XTOU3jQrHmublUx5vLdZ100kKl
GI-040 | 2d519c3e-d27a-4069-b13e-3a7561929da5 | LD14-1 | 646 | N-EMEA | Closed | P2 Medium CX | ganderson@global-cxm.com | 2026-06-17 04:00:00.000 +0400 | General Contractor |  | Installation Damage | Commissioning | [7 empty] | Critical MeWall - UPS Switch Room M1 - water ingress took place in switch room M1 due to the removal of the Roxtec blocks. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625666&prj=646&rqi=UA7bhCR6IzgqnhIrwXfYh1Lar3
RT1MECH-688-001 | a71efea7-ac29-42b9-9c80-a9ddd1ab0d84 | LD14-1 | 646 | N-EMEA | Open | P3 Low CX | gharbottle@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1WT_M1R1_FLT_04 | WT - Water treatment |  |  | Missing permanent asset label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624836&prj=646&rqi=JVytQSAWG7dX4DsZJ18vlgTP0T
RT1MECH-687-001 | 97880c50-50dd-4808-9dfb-1b680fe10912 | LD14-1 | 646 | N-EMEA | Open | P3 Low CX | gharbottle@global-cxm.com | 2026-06-10 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1WT_M1R1_FLT_03 | WT - Water treatment |  |  | Missing permanent asset label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624835&prj=646&rqi=U4yhBfavmXwNu1T6DVLkOF5V2C
GI-032 | ba71f7da-1ddd-423e-ba70-338b2335b8d8 | LD14-1 | 646 | N-EMEA | Open | P3 Low CX | jknight@global-cxm.com | 2026-05-14 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MEB_A | ERTH - Earthing |  |  | Asset labels missing for earth bar. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621958&prj=646&rqi=KjhYpiiw6kqH45drq3DqkggNPU
RT1MECH-593-001 | 67ec8d01-ec67-41be-b5f8-f5a9639d6f20 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-05-04 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_H_410 | DXID - FCU/DX Indoor Unit |  | FXHQ100AVEB8 | No asset identification label present on installed FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620374&prj=646&rqi=jf1ExmKMdJEfZvXFP3ylFKnfhg
RT1MECH-586-001 | b1c4ac14-51cc-4a6e-b5a8-1225c4af9dd2 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-05-04 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_312 | DXID - FCU/DX Indoor Unit |  | FXHQ100AVEB8 | No asset identification label present on installed FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620375&prj=646&rqi=BnABu8MqH6bXorBLUPnq2sPLpx
RT1ELEC-79-001 | 857db1d3-241c-4cd4-a401-7042d8364985 | LD14-1 | 646 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-04-30 04:00:00.000 +0400 | SCH - Schneider Electric | L2A | Installation Damage | Commissioning |  | Electrical â€“ MV | equipment | 1MVTB_C_HMI | HMI - HMI Panel |  |  | HMI selector key set (supplied as a pair) includes one bent key. The second key remains in good condition | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620096&prj=646&rqi=h3HwpHdwlU39s7OghzERiWLl3y
RT1ELEC-76-001 | 4a9baa65-7a11-46f7-974c-5ff3c5dcc134 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-30 04:00:00.000 +0400 | SCH - Schneider Electric | L2A | Installation Damage | Commissioning |  | Electrical â€“ MV | equipment | 1MVTB_M1_HMI | HMI - HMI Panel |  |  | Key snapped within generator selector switch barrel on HMI | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620114&prj=646&rqi=nrIWkfV6ES9YK8O9L8Exx3OtKx
RT1ELEC-75-002 | bcdb68c0-8ece-4cd0-b148-2eee08a24d16 | LD14-1 | 646 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-04-30 04:00:00.000 +0400 | SCH - Schneider Electric | L2A | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1MVTB_R1_HMI | HMI - HMI Panel |  |  | Two identification labels missing within HMI panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620113&prj=646&rqi=y4wPVfZiP0Lnx2FKJ6R96tIlTW
RT1ELEC-75-001 | c956ac61-3911-463e-9cbd-0b5289282fe2 | LD14-1 | 646 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-04-30 04:00:00.000 +0400 | SCH - Schneider Electric | L2A | Installation Damage | Commissioning |  | Electrical â€“ MV | equipment | 1MVTB_R1_HMI | HMI - HMI Panel |  |  | Damaged keys for the HMI selector | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620112&prj=646&rqi=NtCo99l3yz0ztuidlx0f44qNxZ
RT1MECH-662-001 | ee68fdf1-133b-4568-aa2d-6a75ab971fed | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_A_205 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618036&prj=646&rqi=Eno18jhgqJWMysNlXd8xzV9nCT
RT1MECH-660-001 | 06bea186-0272-42c7-b470-dcdc8d465b10 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_A_211 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618050&prj=646&rqi=qLjDgNLuGbX7QrQgoy8htbw2Ht
RT1MECH-307-002 | 321131ed-73ab-4b4c-b3df-58bfbb233978 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_H_410 | DXID - FCU/DX Indoor Unit |  | FXHQ100AVEB8 | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618073&prj=646&rqi=pj8syBZ2vNVRpWXI0fi57wGEcz
RT1MECH-307-001 | d770ead7-ea4c-458c-9ff0-e7225431a68b | LD14-1 | 646 | N-EMEA | Closed | P2 Medium CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Installation Damage | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_H_410 | DXID - FCU/DX Indoor Unit |  | FXHQ100AVEB8 | During RT inspection, FCU casing damage was noted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618070&prj=646&rqi=aH71oOVHLrl0F7IXSMVNQcp8Uy
RT1MECH-673-001 | 0cbb84bb-0ad6-4f47-8ea4-3f3c75453dec | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_A_412 | DXID - FCU/DX Indoor Unit |  |  | Install correct asset ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617976&prj=646&rqi=excYgsqt5spIbkpzApJMPW6fOT
RT1MECH-672-001 | a4a2eae0-a30e-4309-adde-f09737e0dcec | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_411 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617970&prj=646&rqi=6K7f59DYLlMjdwcUGqZhdBuWbb
RT1MECH-661-001 | 0c133c6a-f23b-454d-95a1-446a412e1d7f | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_H_212 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618051&prj=646&rqi=xBmfYT6wqRoUMFhXUqgpY7TJOO
RT1MECH-655-001 | c2ce4ed8-6b55-472e-b7c8-80427a6a3f93 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_M1_111 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618054&prj=646&rqi=Z9Oygiu3X4YaaPjEy8KyupbZdx
RT1MECH-663-001 | c446f852-6972-4531-884a-cfcfaf6121f5 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_H_206 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618037&prj=646&rqi=f0PINsrhKBOEbXiQwGtjSeadk7
RT1MECH-656-001 | 9928be51-799d-47da-81a1-c7155f804215 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_H_112 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617563&prj=646&rqi=plCJS3up71HJaNmWinzKnPcDIo
RT1MECH-650-001 | c66116db-fc78-4ca5-a012-c3ca727a33ec | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_M1_011 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617565&prj=646&rqi=FuE21881GqdEvqKRJtt3dIzXLJ
RT1MECH-649-001 | a46f8197-12be-4485-b0f8-0bd46f832648 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_M1R1_010 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617568&prj=646&rqi=eUdK59ORfDgscNqp0wv8EKEK3L
RT1MECH-654-001 | e61726f5-65d7-431a-a9e4-82262bb46f3c | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-08 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_M1R1_110 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617567&prj=646&rqi=GBQhdC0w4xLp9YmjK0R31zQ94Q
RT1MECH-665-001 | 707dd93a-edd8-4151-8e14-92ed42b1c4f7 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-07 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_H_311 | DXID - FCU/DX Indoor Unit |  |  | No asset Id on fcu | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617509&prj=646&rqi=ux7qb8Wdjz0fV0oLkXG3eIeg1N
RT1MECH-664-001 | e4a5e87e-4346-4507-8883-ae2c38b6aef4 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-04-07 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_A_310 | DXID - FCU/DX Indoor Unit |  |  | No permanent asset identification label installed on FCU | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617493&prj=646&rqi=tBkiR1axc50s5mF0Gaoxx4iJ9n
RT1MECH-658-001 | c2989251-eee0-4592-91bb-894b864e2d43 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-27 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_114 | DXID - FCU/DX Indoor Unit |  |  | FCU installed without permanent equipment/asset identification label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616708&prj=646&rqi=cpuR6wJwvSuTppfYKymcgTbqPL
RT1MECH-651-001 | 52bb7fd9-19fa-40b4-8d78-aa744d9cff98 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-27 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_H_012 | DXID - FCU/DX Indoor Unit |  |  | FCU installed without permanent equipment/asset identification label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616711&prj=646&rqi=EUPurFWHZxI8iCEi4e2dHkckXo
RT1MECH-653-001 | 3a0ec0f6-bf83-4cda-9022-1b3a00f2f0b6 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-27 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_014 | DXID - FCU/DX Indoor Unit |  |  | FCU installed without permanent equipment/asset identification label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616710&prj=646&rqi=QlejFZZANanZ08BJF0sQZtzZXN
RT1MECH-667-001 | a10372e9-24e2-4a9f-907f-7b4d879ad905 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_R1_302 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615952&prj=646&rqi=Bwga2JC9itetOLGRoqlC2aOwxf
RT1MECH-670-001 | fe4cb541-aa1f-4296-bc52-418662fec03a | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_H_305 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615942&prj=646&rqi=vg8RKdLAeQm8Nd1OGyu6KPHYmA
RT1MECH-669-001 | 47a290ea-5f11-43c3-91b0-08ea0158552f | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_A_304 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615947&prj=646&rqi=G9ur8KNbJfBgZGlh5pqdDT8ja2
RT1MECH-668-001 | 07c2a96d-0af3-4103-9ad0-10180250f31c | LD14-1 | 646 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_M1R1_303 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615949&prj=646&rqi=P84r3dCEk7I55GoM9Q3PhH1buu
RT1MECH-671-001 | 02da3810-04ef-4954-81e1-f1495402f95e | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_C_306 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615948&prj=646&rqi=CJKDSBhgms4y1td8IQbWTNnWiP
RT1MECH-674-001 | 0dfdb6d4-7f57-4a00-ab60-a51dcec56663 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-16 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_R1_401 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615800&prj=646&rqi=HXAJSm7Yub4jl3nvqZpjwcpArP
RT1MECH-675-001 | 4c76d781-b4ae-4f31-9668-eb51dc6527d2 | LD14-1 | 646 | N-EMEA | Open | P3 Low CX | lali@global-cxm.com | 2026-03-16 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_B_402 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615810&prj=646&rqi=QopxNGlMZWgdqjltRCcVWDgzSR
RT1MECH-676-001 | 4a67cee5-8f00-4f9c-abc9-f487f7fb6395 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | lali@global-cxm.com | 2026-03-16 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1FCU_H_403 | DXID - FCU/DX Indoor Unit |  |  | Verify permanent equipment labels affixed, proper label type and colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615816&prj=646&rqi=qCLNu41PVik5iSm9OL7M9vK3C4
GI-029 | 5a6133be-2c02-4137-8e28-4df1fd7bba2d | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General FWT/FAT Issue | Level 1 FWT | [7 empty] | BAC Cooling Tower - during the FAT it was noted that the internal wire mesh to support the internal insulation of the upper chamber is not fitted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198784&prj=646&rqi=t8vUGfeNfXP76mHUPGaTmNnI1V
GI-030 | d95017f5-7bc8-4631-8b8c-0aa0bfa57219 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General FWT/FAT Issue | Level 1 FWT | [7 empty] | BAC Cooling Tower - It was noted during the FAT that there was slight misalignment of the plates used for locking/securing of the access doors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198795&prj=646&rqi=EPgZYpz7X5L03boEaEpGlNPQza
GI-027 | 24bc03d9-f418-4049-8ff6-047f0dbdbfbd | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General FWT/FAT Issue | Level 1 FWT | [7 empty] | BAC Cooling Tower - during the FAT inspection it was found that there is sharp edging on the stainless steel profile strips on the external corners of the unit that require dressing or chamfering. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198780&prj=646&rqi=NG0LdHE3uiyoOlIud9op8ALo5O
GI-031 | 27e11036-7b73-44e8-aec1-a10484aaa902 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General FWT/FAT Issue | Level 1 FWT | [7 empty] | BAC Cooling Tower - During the visual inspection of the unit at the FAT it was noted that there is a slight weep between two mating surfaces of the basin module and the lower chamber wall. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198796&prj=646&rqi=TTKGr9BRWm0hZS0lkSIMhahsIG
GI-026 | ab80558d-9543-4214-99fe-0dbf0a9cdc28 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General FWT/FAT Issue | Level 1 FWT | [7 empty] | During the BAC FAT for the cooling tower it was noted that earthing points/lugs were not fitted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198768&prj=646&rqi=GcMRkgI6v5ZwDWxRh7Ku4t2VWE
GI-019 | 09226a2d-4e2d-4bd7-9dff-72c352ba5f70 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-02-02 04:00:00.000 +0400 | REH - Rehlko Gens |  | Missing Components | Commissioning | [7 empty] | Generators - Selective Catalytic Reducers: The SCR units were delivered to site without protective covers fitted to the exhaust outlet flanges. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198198&prj=646&rqi=RzDScjgheyDJGrgRa0Ra4yvmRQ
GI-018 | e183ad4a-d26d-43a4-a9ab-3f88fe68d722 | LD14-1 | 646 | N-EMEA | Closed | P2 Medium CX | ganderson@global-cxm.com | 2026-01-26 04:00:00.000 +0400 | VER - Vertiv Electrical |  | General FWT/FAT Issue | Level 1 FWT | [7 empty] | Critical MeWall E-house - Transformer has been supplied without anti-vibration pads. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197574&prj=646&rqi=pikYRSzp4A6PMZOrxrkr0lSSHt
GI-016 | e9e3a8c1-e099-428a-bb56-2ddc1563ab6e | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-01-22 04:00:00.000 +0400 | SCH - Schneider Electric |  | General FWT/FAT Issue | Level 1 FWT | [7 empty] | SUDB E-house A - protective conduit to be fitted to DX unit external condensers' piping/cabling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197513&prj=646&rqi=HVjHA7RaHNGrQvALtAyummrN88
GI-017 | 033339e2-913a-4d38-bdda-8390be725fe2 | LD14-1 | 646 | N-EMEA | Closed | P3 Low CX | ganderson@global-cxm.com | 2026-01-22 04:00:00.000 +0400 | SCH - Schneider Electric |  | General FWT/FAT Issue | Level 1 FWT | [7 empty] | SUDB E-house B - protective conduit to be fitted to DX unit external condensers' piping/cabling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197514&prj=646&rqi=0YqiVtgsFr7cn43ZM9vcPanjtJ
RT1MECH-319-001 | 743ae7c4-dc61-443b-a16f-e121fc198974 | LD14.2 | 686 | N-EMEA | Closed | P3 Low CX | gharbottle@global-cxm.com | 2026-06-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1VRFOD_R1_15 | VRF - Variable Refrigerant Flow System |  |  | Missing permanent asst label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625064&prj=686&rqi=0iJvsf3mZ8R20f10g4eoHQfKNp
RT1MECH-321-001 | 7d6896cc-c0fe-42bf-aff1-1dc3c64cd2e8 | LD14.2 | 686 | N-EMEA | Closed | P3 Low CX | gharbottle@global-cxm.com | 2026-06-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1VRFOD_M2_17 | VRF - Variable Refrigerant Flow System |  |  | Missing permanent asset label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625068&prj=686&rqi=TUCdfEhykHF4vceYRIEmZLTIND
RT1MECH-320-001 | d52b8483-cfe8-4686-97a9-c0dcce1b0f96 | LD14.2 | 686 | N-EMEA | Closed | P3 Low CX | gharbottle@global-cxm.com | 2026-06-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1VRFOD_M1_16 | VRF - Variable Refrigerant Flow System |  |  | Missing permanent asset label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625066&prj=686&rqi=Yh1r0sjALhdUpP49qUKXc4cto4
GI-053 | ff854119-8f51-43a9-bd80-26772e5c94a2 | LS02-1 | 455 | S-EMEA | Closed | P3 Low DCOS | Alen.Francis@eu.equinix.com | 2026-01-29 04:00:00.000 +0400 | Equinix Ops |  | Design correction needed | Design | [7 empty] | GDC Requires the following to be actioned. Due to Low Load in the building and multiple assets in a alarm local Ops needed to open up alarm bands to stop the large amount of alarms coming through to the EOC Please when load is availble can they be put back to the commissioned settings as per smartsheet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197892&prj=455&rqi=ZIyiDtxMH3nmSLnG3RxZltn5ag
YT1ELEC-192-002 | 986cc4cd-1aa6-10ac-4deb-abc24afb80aa | LS02-2 | 674 | S-EMEA | Open | P3 Low CX | radek.kmak.ext@bureauveritas.com | 2026-09-18 04:00:00.000 +0400 | SCH - Schneider Electric | L2B | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1SUDB_02 Feeder Q3 (Feeder to RMU_C Q1) | SUDB - Secondary Utility Distribution Board |  |  | Verify permanent equipment labels affixed, contract specific label colour scheme RMU C Feeder | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638686&prj=674&rqi=BK06xbYDLfPG0rEsWa7tDP9gRW
YT1ELEC-192-001 | 1e0aeb64-b411-2f5c-1aca-0a50ada9213e | LS02-2 | 674 | S-EMEA | Open | P2 Medium CX | radek.kmak.ext@bureauveritas.com | 2026-09-18 04:00:00.000 +0400 | SCH - Schneider Electric | L2B | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1SUDB_02 Feeder Q3 (Feeder to RMU_C Q1) | SUDB - Secondary Utility Distribution Board |  |  | Verify protection relays are programmed with service settings as per coordination / discrimination study Relay needs reconfiguration | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638685&prj=674&rqi=orJvWknlmJLTrstipBNvurd2kk
YT1ELEC-191-002 | 08d22ba5-52fb-4ca9-96bc-a9de9e137a84 | LS02-2 | 674 | S-EMEA | Open | P2 Medium CX | radek.kmak.ext@bureauveritas.com | 2026-09-15 04:00:00.000 +0400 | General Contractor | L2B | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1SUDB_01 Feeder Q2 (Feeder to RMU_E) | SUDB - Secondary Utility Distribution Board |  |  | Poor containment installation, bent containment, missing and damaged covers. Missing firestopping | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638070&prj=674&rqi=h9fVqKPCrAwQ8GG85MvXhZgv9g
YT1ELEC-191-001 | 8a7985e7-e1a3-4463-b5fb-0eb21be51d30 | LS02-2 | 674 | S-EMEA | Open | P3 Low CX | radek.kmak.ext@bureauveritas.com | 2026-09-14 04:00:00.000 +0400 | SCH - Schneider Electric | L2B | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1SUDB_01 Feeder Q2 (Feeder to RMU_E) | SUDB - Secondary Utility Distribution Board |  |  | Verify permanent equipment labels affixed, contract specific label colour scheme | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637946&prj=674&rqi=8PcLB5evGDJKnhFV2Mt11VKXHY
GT1ELEC-123-002 | 2232c815-f554-45fa-9c28-5525180ff776 | LS02-2 | 674 | S-EMEA | Open | P3 Low CX | radek.kmak.ext@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L3 | Documentation not issued/ Required | Commissioning |  | Electrical â€“ MV | equipment | 1SUDB_02 Feeder Q4 (Bypass from SUDB_01) | SUDB - Secondary Utility Distribution Board |  |  | Confirm Live test results (SAT) uploaded to Asite | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636720&prj=674&rqi=nZ5967nIvrP1vwItIfFcp96Khj
GI-010 | e5cce807-bc21-4bb7-a6b2-d1ab5f8a4a5d | LS02-2 | 674 | S-EMEA | Closed | P2 Medium CX | gabriel.matiasarnal@bureauveritas.com | 2026-08-05 04:00:00.000 +0400 | General Contractor |  | General Design Issue | Design |  |  | equipment type |  |  |  |  | As per Site Specification for Earthing, LS021-QUA-XX-XX-RP-E-ERTH-8001-Earthing. "Separate protective earth networks shall be provided for low voltage and medium voltage of metallic enclosures of electrical panels and equipment" and "Protective grounding system, consisting of the grounding lines and the corresponding grounding electrodes that directly connect to ground the conductive parts of the installation elements not normally subjected to electrical voltage, but which could be put under voltage by faults or accidental contacts, in order to protect people against contacts with dangerous voltages." Under that definition the Container Housing the Generator should have a grounding connected to the BTP Gen and the cable schedule doesnt reflect this. Please confirm if Generator Container needs a Grounding Bound | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632247&prj=674&rqi=qfsiA2KjN6uaHqIhypRUOXGvE6
GI-011 | b7c41a58-31cb-4ab8-bcd2-194b2ae34ad2 | LS02-2 | 674 | S-EMEA | Closed | P2 Medium CX | gabriel.matiasarnal@bureauveritas.com | 2026-08-05 04:00:00.000 +0400 | General Contractor |  | General Design Issue | Design | [7 empty] | As per Site Specification for Earthing, LS021-QUA-XX-XX-RP-E-ERTH-8001-Earthing. "Separate protective earth networks shall be provided for low voltage and medium voltage of metallic enclosures of electrical panels and equipment" and "Protective grounding system, consisting of the grounding lines and the corresponding grounding electrodes that directly connect to ground the conductive parts of the installation elements not normally subjected to electrical voltage, but which could be put under voltage by faults or accidental contacts, in order to protect people against contacts with dangerous voltages." Under that definition the Metal Frame holding the chiller should have a grounding connected to the BTP Roof 2 and the cable schedule doesnt reflect this. Please confirm if Chiller Metal Frame needs a Grounding Bound | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632270&prj=674&rqi=hAvcVbLo6CgwcmeARi2JBrMfVM
GI-008 | 8b0a4913-b3d5-4754-9fa0-8067451db08c | LS02-2 | 674 | S-EMEA | Closed | P2 Medium CX | lars.dietrich@bureauveritas.com | 2026-07-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Position of Fuel-Kill-Valve. The blow fuse is located in the Air-Intake right next to the FDAY of the Generator Container. See drawings attached. In event of fire, which occurs usually at the Motor these fuses will not trigger as permanently cooled by the Inlet Air. Please review design and explain how the system should operate in event of fire. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630861&prj=674&rqi=1pXxUhIPF6icz6YZ6RXCLFIUQb
GI-009 | 3cc650e5-8fdc-4c83-9ed8-96289541cb92 | LS02-2 | 674 | S-EMEA | Closed | P2 Medium CX | lars.dietrich@bureauveritas.com | 2026-07-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | No Drip-Trays under ACC on the Roof. there are no drip trays installed underneath ACC`s. Trane uses POE oil in DX cycle and Glycol N in FC cycle. Both are prohibited to enter rainwater drains or sewer. Please provide the plan to prevent the Glycol and POE oil to enter rainwater drain in event of leak. Even oil separator in rainwater drain ,might still allow the POE to enter and pollute nearby river as POE is made of Acid and Alcohol. Getting in touch with water, it splits up in itÂ´s origin substances and might not be captured by oil separator. Please explain how to prevent substances used in ACC to enter rainwater drainage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630867&prj=674&rqi=6V0PzVnDMWqEvHl8v4NjcjKdxz
GI-007 | eacae5d6-ff49-457b-9363-79d3fd6e9913 | LS02-2 | 674 | S-EMEA | Open | P3 Low CX | gabriel.matiasarnal@bureauveritas.com | 2026-07-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation not issued/ Required | Commissioning | [7 empty] | LVSB C1/D1/E1 Aux Switchboard generator Technical submitall and drawings not matching installation Your installation and O&M manual (LS021-STE-GT-B1-OM-E-GENL-7063-Switchboard Panel â€“ SWAUX01 O&M Manual-AB01-Phase 2) has only one socket X1.1 However on TN and Drawings on doc holder it has two more sockets, please remove it from TN and reupload new version on ASITE, place correct drawings on panels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630555&prj=674&rqi=nbSeESyBhgkIWnvMeOAO4faCGQ
GI-005 | c56acda0-3780-42d8-a51e-6448c619c26e | LS02-2 | 674 | S-EMEA | Closed | P2 Medium CX | gabriel.matiasarnal@bureauveritas.com | 2026-07-17 04:00:00.000 +0400 | SOC - Socomec |  | Torque required | Commissioning | [7 empty] | On STS Q30 Connection without washer and less than one thread out If its a design constraint because of space please confirm that installation is ok | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629880&prj=674&rqi=6BOq1x9SDVzrotWzHe3uqk3KNt
GI-006 | e18fcb2d-4d49-4a4f-9827-93f94bb09b3a | LS02-2 | 674 | S-EMEA | Closed | P2 Medium CX | gabriel.matiasarnal@bureauveritas.com | 2026-07-17 04:00:00.000 +0400 | SOC - Socomec |  | Missing Components | Commissioning | [7 empty] | Internal Busbar connection missing a washer Confirm if bolt and nut wont be affected by vibration when loaded without a washer installed or if STS busbars need extra washers to be installed (Torque mark on the other side, missing the double torque mark but a different issue was created for it) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629881&prj=674&rqi=XylvSrkfCwRMYjplunppcOOw7R
GI-004 | 1265c909-6fb7-460a-abb7-2056b8fc54bf | LS02-2 | 674 | S-EMEA | Closed | P3 Low CX | gabriel.matiasarnal@bureauveritas.com | 2026-07-16 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning | [7 empty] | Following RPPs missing permanent labels and arc flash label: 1RPP_CR_1_6 1RPP_CR_2_3 1RPP_CR_2_6 1RPP_DR_1_1 1RPP_DR_1_2 1RPP_DR_1_4 1RPP_DR_1_5 1RPP_DR_1_8 1RPP_DR_2_1 1RPP_DR_2_2 1RPP_DR_2_4 1RPP_DR_2_5 1RPP_DR_2_8 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629609&prj=674&rqi=wHTXNwNuoH7pJBf0eirmuRPRa3
GI-002 | 0297c165-46d7-4327-9f28-f961d06d2f4b | LS02-2 | 674 | S-EMEA | Open | P3 Low CX | gabriel.matiasarnal@bureauveritas.com | 2026-07-09 04:00:00.000 +0400 | General Contractor - Commissioning |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | Generators missing docs on holder | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628546&prj=674&rqi=CYiGc1etbCpZph2vg63zUssTWK
RT1ELEC-176-002 | b14298e1-9988-4c2b-f640-6a2991fe7ed3 | LS02-2 | 674 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-30 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1LVSB_C_2 | LVSB - Low Voltage Switchboard |  |  | loose earthing cable termination Carry out full visual inspection of panel and confirm no defects, scratches, dents, abnormalities | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627322&prj=674&rqi=02RS3DYaJFASJe5y9r8jrKrimt
RT1ELEC-142-002 | a9c0373e-ae65-8e32-cc82-e6a1085f270e | LS02-2 | 674 | S-EMEA | Open | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-25 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation Damage | Commissioning |  | Electrical â€“ MV | equipment | 1SUDB_02 Feeder Q4 (Bypass from SUDB_01) | SUDB - Secondary Utility Distribution Board |  |  | Multiple dents and scratches Confirm SUDB delivery visual Inspection/checklist is complete with defects noted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626907&prj=674&rqi=60iAnRmiv28pqK6WThELgxTRmc
RT1ELEC-142-003 | f087104a-eec4-5f96-f517-b55b17eb972f | LS02-2 | 674 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-25 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Torque required | Commissioning |  | Electrical â€“ MV | equipment | 1SUDB_02 Feeder Q4 (Bypass from SUDB_01) | SUDB - Secondary Utility Distribution Board |  |  | qa4 earth termination missing torque marks. Broken torque marked. Tightness of bolted electrical connections by calibrated torque-wrench method in accordance with manufacturerâ€™s published data. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626908&prj=674&rqi=3uf2EYDSvH1Q5nVdItpoj6pvas
GT1ELEC-123-001 | dbec31ef-2f7b-a02f-fb99-bc43b2c43d6f | LS02-2 | 674 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-25 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | DCOS Graphics Issue | DCOS |  | Electrical â€“ MV | equipment | 1SUDB_02 Feeder Q4 (Bypass from SUDB_01) | SUDB - Secondary Utility Distribution Board |  |  | Live circuits not having right colour. grey instead of white. Please check upstream to downstream. Refer to attached screen shots. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626880&prj=674&rqi=knmnmSE8fmlk03eklgTH2eC5yQ
RT1ELEC-142-001 | 735d10fe-4736-92c0-cdfa-c1a836cbfe80 | LS02-2 | 674 | S-EMEA | Closed | P2 Medium CX | ismail.kose@bureauveritas.com | 2026-06-25 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1SUDB_02 Feeder Q4 (Bypass from SUDB_01) | SUDB - Secondary Utility Distribution Board |  |  | SUDB_02/Q2: Visual copper spots at ct control cable. BX13 - 9 Earth cable csh200 -S2pe Carry out full visual inspection of switchboard and confirm no defects, scratches, dents, abnormalities | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626906&prj=674&rqi=f13888Hxi9MWlcEWvRWMkDhPlN
RT1ELEC-178-002 | 61afa48b-9cae-e368-2050-e36adbc000c5 | LS02-2 | 674 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1LVSB_C_4 | LVSB - Low Voltage Switchboard |  |  | Verify Installation of equipment is complete in final location and as per Manufacturers Spec. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624971&prj=674&rqi=NeQsh9XYTPVMOEqtcoWQj8YeTf
RT1ELEC-178-003 | 27a0b3bf-62b0-5236-2d35-e10759ee3e37 | LS02-2 | 674 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1LVSB_C_4 | LVSB - Low Voltage Switchboard |  |  | main power supply should be torque marked after being torqued with a certified torque wrench. source: Verify Internal bolted electrical connections tightened by calibrated torque-wrench method in accordance with manufacturerâ€™s published data. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624972&prj=674&rqi=4GjKY5DoAwEXx3MmAtQO37AKPJ
RT1ELEC-186-002 | 1a6fae13-133c-31a6-c670-d5b412f4c48b | LS02-2 | 674 | S-EMEA | Closed | P3 Low CX | ismail.kose@bureauveritas.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1LVSB_R_11 | LVSB - Low Voltage Switchboard |  |  | door hinges support/locking mechanism broken Carry out full visual inspection of panel and confirm no defects, scratches, dents, abnormalities | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624973&prj=674&rqi=aZKkSTK7kNhea4FDvfjG0UWs3E
GI-001 | 7a43606c-c333-4e54-88aa-0e898693c4b6 | LS02-2 | 674 | S-EMEA | Closed | P2 Medium CX | serdar.tuccaroglu@bureauveritas.com | 2026-05-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation not issued/ Required | Commissioning | [7 empty] | 75 L2A checklists have been scheduled to be completed by 22/05/2026 while only 41 are signed off, 24 are awaiting documentation and 5 are in progress: Actual vs Planned L2A Commissioning Ratio is 55%. GC Project Cx schedule is not accurate and not aligned with the FG timeline monitor. GC 2WLA is not accurate and not aligned with the FG timeline monitor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622956&prj=674&rqi=lfGFHs36XEs42f8aqDoC7cWQkY
RT1ELEC-179-001 | 4f668fd5-c2b5-4947-beb4-5a64e1079459 | LS02-2 | 674 | S-EMEA | Closed | P3 Low CX | andrew.mercer@bureauveritas.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LVSB_C_5 | LVSB - Low Voltage Switchboard |  |  | Technical submittal is provided only in Portuguese. As per Playbook 6.1 Section 1.2.1.1., all commissioning documentation through Cx levels 0 to 6 is mandatory to be written in English, local language can supplement the English language documents based on region specific requirements. Where a discrepancy between English and local language arises in a document, the English language form takes precedence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622467&prj=674&rqi=AnfoiNYzRhiqkD4SohU8ufC9cm
RT1ELEC-186-001 | fc7a8619-ce9e-4f20-a6b2-aa6ee530afda | LS02-2 | 674 | S-EMEA | Closed | P3 Low CX | andrew.mercer@bureauveritas.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LVSB_R_11 | LVSB - Low Voltage Switchboard |  |  | Technical submittal is provided only in Portuguese. As per Playbook 6.1 Section 1.2.1.1., all commissioning documentation through Cx levels 0 to 6 is mandatory to be written in English, local language can supplement the English language documents based on region specific requirements. Where a discrepancy between English and local language arises in a document, the English language form takes precedence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622474&prj=674&rqi=FCQQ5oal6NMPOY1V8fDHVbMwfw
RT1ELEC-177-001 | 57609a64-6b0d-4a9e-bc8a-6791e1b9e85e | LS02-2 | 674 | S-EMEA | Closed | P3 Low CX | andrew.mercer@bureauveritas.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LVSB_C_3 | LVSB - Low Voltage Switchboard |  |  | Technical submittal is provided only in Portuguese. As per Playbook 6.1 Section 1.2.1.1., all commissioning documentation through Cx levels 0 to 6 is mandatory to be written in English, local language can supplement the English language documents based on region specific requirements. Where a discrepancy between English and local language arises in a document, the English language form takes precedence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622462&prj=674&rqi=hR4Af5TijlQO66NgD2UhfQQucH
RT1ELEC-178-001 | a2ba5fb2-a2f5-4c7d-ac2f-c9aa7d40dfa6 | LS02-2 | 674 | S-EMEA | Closed | P3 Low CX | andrew.mercer@bureauveritas.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LVSB_C_4 | LVSB - Low Voltage Switchboard |  |  | Technical submittal is provided only in Portuguese. As per Playbook 6.1 Section 1.2.1.1., all commissioning documentation through Cx levels 0 to 6 is mandatory to be written in English, local language can supplement the English language documents based on region specific requirements. Where a discrepancy between English and local language arises in a document, the English language form takes precedence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622475&prj=674&rqi=LURzDcDVpD7qlnIrR7TePJGi2H
RT1ELEC-176-001 | e43d5bc4-fb07-4e9b-80ca-8a10e2471b1a | LS02-2 | 674 | S-EMEA | Closed | P3 Low CX | andrew.mercer@bureauveritas.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1LVSB_C_2 | LVSB - Low Voltage Switchboard |  |  | Technical submittal is provided only in Portuguese. As per Playbook 6.1 Section 1.2.1.1., all commissioning documentation through Cx levels 0 to 6 is mandatory to be written in English, local language can supplement the English language documents based on region specific requirements. Where a discrepancy between English and local language arises in a document, the English language form takes precedence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622418&prj=674&rqi=4TBeNcTdoaInY4d8Sjf42X8sHG
GI-002 | 966bc4e7-b052-4d31-b53f-f5263daefd3a | MA05-P1 | 645 | N-EMEA | Open | P2 Medium CX | nrae@global-cxm.com | 2026-09-16 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning | [7 empty] | Large nick/slice noticed on HV cable on 1-MLTX-G. Cable ID tag 1-CBL-ML-TX-G 3X1C 120mm2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638444&prj=645&rqi=xygRXn2dlZpAX8mtYGnaMzblzJ
RT1MECH-57-001 | f680a4bc-96f5-4ded-846f-292c6eab5853 | MA05-P1 | 645 | N-EMEA | Closed | P3 Low CX | nrae@global-cxm.com | 2026-06-08 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1-CH-E-1 | ACC - Chiller â€“ Air Cooled |  |  | Carry out visual inspection of Equipment and confirm no defects, scratches, dents and any other damage. Bent fins on the chiller coil, minor damage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624406&prj=645&rqi=wfMUgk5OmTAWQ3N5PF0DZEEyM6
RT1MECH-58-001 | 44a37619-bcd3-4903-bc5c-25fda1b3890b | MA05-P1 | 645 | N-EMEA | Closed | P3 Low CX | nrae@global-cxm.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1-CH-G-1 | ACC - Chiller â€“ Air Cooled |  |  | Anti vibe mounts are not installed correctly. Vendor has supplied the wrong anti vibe mounts. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624467&prj=645&rqi=nMyyP5Cwoda3rJr0MKtGJ35QZa
RT1MECH-57-003 | 01e12f2a-bbb9-41ad-8473-c2a9476b38a2 | MA05-P1 | 645 | N-EMEA | Closed | P3 Low CX | nrae@global-cxm.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1-CH-E-1 | ACC - Chiller â€“ Air Cooled |  |  | Permanent equipment labels to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624453&prj=645&rqi=VEh8jsTDztfHg1YLwjVBi4K79f
RT1MECH-57-002 | ee48e0bd-54f8-48f1-bf5a-537f1473ca51 | MA05-P1 | 645 | N-EMEA | Closed | P3 Low CX | nrae@global-cxm.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1-CH-E-1 | ACC - Chiller â€“ Air Cooled |  |  | Verify Anti-Vibration mounts are correctly fitted and adjusted Anti vibe mounts still to be installed in 4 locations. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624441&prj=645&rqi=afOK5QHBvkXOJi4jKaFSZkEMaN
WREPORT-23-001 | f1db59b5-f9e2-439c-b9bb-1920ab7f6dd5 | MA05-P1 | 645 | N-EMEA | Closed | P2 Medium CX | tkhan@global-cxm.com | 2026-04-15 04:00:00.000 +0400 | Equinix Ops | DELIVERABLES | Design correction needed | Design |  | Multi-Discipline | system | Weekly Report |  |  |  | Approval time for new CR to change the timer values of MSB-T11 and Chiller's restart time was around 5 weeks | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619503&prj=645&rqi=dnaFGIZDZCYomjscYgvznjKfzs | https://equinix.facilitygrid.co.uk/x/project/645/system/13103
RT1ELEC-36-001 | def5e2a8-d199-44f6-856c-89d423a91407 | MA05-P1 | 645 | N-EMEA | Closed | P3 Low CX | asaville@global-cxm.com | 2026-03-17 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1-MSB-E | MSB - Main Input Switchboard |  |  | Permanent labelling to be installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615820&prj=645&rqi=jHqBzRQ5IYHvi4sOMGOK556giW
GI-2677 | 8c311f7d-783e-4fde-968c-9fe53800fcde | MB03-1 | 227 | APAC | Closed | P3 Low CX | KunalKavathankar@commtechasia.com | 2026-02-06 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Alarm maintenance mode and alarm shelve duration not demonstrated Asset tab datasheet and weblink was not demonstrated Applicable for all assets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198685&prj=227&rqi=S03LTqglEar866AKgC0lBBozaS
GI-2676 | 097dff9d-84b1-470b-a4e1-12c2568a4638 | MB03-1 | 227 | APAC | Closed | P3 Low CX | sganeshmahadik@ap.equinix.com | 2026-02-02 04:00:00.000 +0400 | Facility Manager |  | DCIM Maximo Issue | DCIM | [7 empty] | Maximos not available to integrate with DCIM, BCM and Battery Monitoring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198095&prj=227&rqi=jRq94fGh9lSNubbZZACwcWR0y7
GT1MECH-175-003 | cdb67a9e-d630-4067-ae90-6acd347dd8c4 | MD05-1 | 396 | S-EMEA | Open | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-08-05 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | An alarm has been triggered on fire pump No. 2 due to a low engine coolant temperature. The pumpâ€™s temperature sensor is not measuring correctly and will need to be replaced. This does not affect the pumpâ€™s functionality. Once the issue has been resolved, the supervisory alarm associated with that pump should be activated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632284&prj=396&rqi=OpPb0eMZSGfaOeORng958J8RlO
GI-102 | 1f3de397-5d39-479d-8864-8f27b3c0b7cc | MD05-1 | 396 | S-EMEA | Closed | P2 Medium CX | arkaitz.santos@eu.equinix.com | 2026-08-04 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning | [7 empty] | Vesda fault alarm active sine August 1st. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632134&prj=396&rqi=lJdvotg0FIfacpwYcYHAJbIxbD
DCOSL5-1-003 | fb7200a5-a53c-45db-b9dd-1e51ad0c7eed | MD05-1 | 396 | S-EMEA | Closed | P3 Low CX | arkaitz.santos@eu.equinix.com | 2026-07-14 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  | Controls | system | DCOS |  |  |  | PV_1 and PV_2 communication lost every few minutes and during night time. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629180&prj=396&rqi=A0uPEs3oLrgQKdxnP4lLYoFKwb | https://equinix.facilitygrid.co.uk/x/project/396/system/14475
DCOSL5-1-002 | bfad8917-4461-437d-819e-3c039a1c7dd7 | MD05-1 | 396 | S-EMEA | Closed | P2 Medium DCOS | arkaitz.santos@eu.equinix.com | 2026-07-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Template Issue | DCOS |  | Controls | system | DCOS |  |  |  | Need to clean the around 50 assets with warnings at DCOS IDE. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629124&prj=396&rqi=SnQ24UHzsjfmKXfMDy4bGtWJnn | https://equinix.facilitygrid.co.uk/x/project/396/system/14475
DCOSL5-1-001 | c84dadca-723b-4efd-900e-3765769020be | MD05-1 | 396 | S-EMEA | Closed | P2 Medium DCOS | arkaitz.santos@eu.equinix.com | 2026-07-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | Clear the around 13000 alarms generated each day at DCOS Aveva system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628600&prj=396&rqi=ekirLxDMFebJxTSvtsKPSsPNzM | https://equinix.facilitygrid.co.uk/x/project/396/system/14475
GI-100 | 79a90ecd-08f6-4512-8c68-fd40c83bf5b1 | MD05-1 | 396 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-07-08 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | Rotor lock alarms are being generated intermittently on low load running 2 happened over the weekend of 03/07-05/07 on WCC A & B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628296&prj=396&rqi=vxLVAzvezIvhKMr4GXi1cvD378
GI-096 | fdf8016b-68dd-45bb-b518-3ac23d1f6a4f | MD05-1 | 396 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | WCC A & R are failing to restart automatically during transfer to gens in IST | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627300&prj=396&rqi=zizX8osQgXGH02tItG1jBHR9Rg
GT1MECH-310-001 | 80749aa8-9003-4e5b-942c-ac41e281d04d | MD05-1 | 396 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-06-26 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  | Fuel | equipment | 1FPCP_B_01 | FPCP (Fuel Pump Control Panel) |  |  | During the IST tests conducted today, it was verified that the fuel system loses redundancy in pump system B during transitions from facility to the generator set. An alarm appears on the Fuel Distribution Loop 2 controller for B, and the pumps B go into alarm. System in A is available and working. The system must be reset from the control panel at fuel pump B. The fuel system has operated correctly during all tests, but redundancy for system B is lost until it is manually reset from the INPRO PLC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627148&prj=396&rqi=H5lStzku9Vp6VrC2748rOqg6R8
GI-095 | 1cf110d4-fda0-4291-aabe-c758291eabc5 | MD05-1 | 396 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-06-26 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | During IST during Test 3 hall SLAs we're breached for 10 minutes due to slow restart of WCCs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627075&prj=396&rqi=3lsS9he3m5VJT7HA3VOnCU4sUs
GI-094 | 64a501d1-d2c0-4631-bb87-0078c287f2bb | MD05-1 | 396 | S-EMEA | Closed | P3 Low DCOS | liam.piervulivo@hdrinc.com | 2026-06-24 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Configuration | DCOS |  |  | equipment type |  |  |  |  | WCC compressor suction/ discharge pressures do not make sense Revise MODBUS addresses with vendor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626686&prj=396&rqi=XHfXnjxAQYvRMRITyD7yzc2pCJ
GI-092 | 6b9bfc9e-6d02-4c66-bd29-63081d290ece | MD05-1 | 396 | S-EMEA | Closed | Outstanding Paperwork/Documentation | liam.piervulivo@hdrinc.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS General Issue | DCOS | [7 empty] | SOO testing docs outstadning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626673&prj=396&rqi=kSe6GYkSdW5D3TOLMOAwGXeM2Y
SOR-17-001 | b4e36145-068f-4b32-af51-077a37fac275 | MD05-1 | 396 | S-EMEA | Closed | P3 Low CX | jason.beachill@hdrinc.com | 2026-06-15 04:00:00.000 +0400 | DCOS - Equinix |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | Equipo Ref DCOS Ref Facility Grid Bomba 1Âº DAC 1CHWSTR_X_X_CWP_1 1CHWSTR_X_CWP_02 Bomba 1Âº Condensor 1CHWSTR_X_X_CWP_2 1CHWSTR_X_CWP_01 Bomba 2Âº Instalacion 1CHWSTR_X_X_CHWP_1 1CHWSTR_X_CWP_03 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625290&prj=396&rqi=a0xA3b87qEJJcUGkSQIaTWh5s0
GI-090 | 1d8b44da-eae8-4db3-b726-6e3ad026d1f3 | MD05-1 | 396 | S-EMEA | Closed | P3 Low CX | liam.piervulivo@hdrinc.com | 2026-06-15 04:00:00.000 +0400 | Equinix Commissioning Manager |  | Installation Not Correct | Commissioning | [7 empty] | WCC B & R loading to be repeated with glycol in primary circuit | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625278&prj=396&rqi=3SKIfnehkLpwhf8gNDnhd02P6P
FPT-410-001 | 37f9c372-afa6-4f2a-980a-99b1ae9c1336 | MD05-1 | 396 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  | HVAC | system | CHW System |  |  |  | CWST A TT-13 is reading a degree higher than logical, this temp did not drop to TT-08 value when buffer tank is in recharge mode Instrument calibration needs to be checked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625299&prj=396&rqi=oDd56mfGIbA3LGxVL2v127hjVp | https://equinix.facilitygrid.co.uk/x/project/396/system/13433
GI-089 | 9d93d169-35d6-4393-a624-cc98b21bb3cf | MD05-1 | 396 | S-EMEA | Closed | P2 Medium DCOS | liam.piervulivo@hdrinc.com | 2026-06-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Comms Issue/Fault | DCOS | [7 empty] | Loss of DAC run status lost when outlet temps increased past 38 deg C Run status lost due to deviation from SP, as raising SP to 25 deg C resulted in return of run status | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624787&prj=396&rqi=WMA36LtkB7A6DQz5nNfWYvIzLq
FPT-397-001 | c1280204-62e5-41e2-af4f-8382fa166074 | MD05-1 | 396 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-06-09 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Correct | Commissioning |  | Fuel | equipment | 1FPCP_A_01 | FPCP (Fuel Pump Control Panel) |  |  | During the fire valve simulation in GEN R , it was found that the lever could not be lowered fully as it interfered with a manual valve, and the system was unable to shut off the fuel supply. The pipework must be modified to prevent any contact. This applies to generators A, B and R. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624483&prj=396&rqi=zeksxMzmtFDaavJnekIl7Ua52o
GI-086 | cd8aac1a-c279-40c4-95dd-608b0cf1931c | MD05-1 | 396 | S-EMEA | Closed | Outstanding Paperwork/Documentation | liam.piervulivo@hdrinc.com | 2026-06-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Design Correction Needed | Design | [7 empty] | SOO not inline with onsite programming as changes have been made SOO needs top be uploaded and approved | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624382&prj=396&rqi=voSBGjrlOFafoKoHPZ60QwpsXO
GI-087 | 36aa95d6-2f55-4f5f-95d0-9c489ba6b8a1 | MD05-1 | 396 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-06-09 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning | [7 empty] | DAC supply temps are very oscillatory when SP is above OAT, particularly when difference is more than 10 deg C | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624384&prj=396&rqi=bmV0NKLG44uyX3RXtlRjdWIpZv
GI-085 | 9afc95b0-280f-473e-a287-514066a2c6b9 | MD05-1 | 396 | S-EMEA | Open | P3 Low CX | liam.piervulivo@hdrinc.com | 2026-06-09 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | DAC sending fault signals for less than a second when on and running, this are not considered real failures | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624381&prj=396&rqi=qyKYfFGnLjNKwglHDPwCWMwIIv
GT1MECH-309-002 | 263314d6-ae55-4a88-a8a1-2762e695ffbb | MD05-1 | 396 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning |  | Fuel | equipment | 1FPCP_A_01 | FPCP (Fuel Pump Control Panel) |  |  | Minor changes have been made to the wiring in the two PLC panels in both Room A and Room B. The diagrams must be updated, and the new cables installed in both the panels and the diagrams must be identified. Furthermore, it must be checked that there are no discrepancies between the panels and the diagrams. Check relay K17 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623637&prj=396&rqi=CWkqvF9jlx0mIuPhYXu4NXKaV7
GT1MECH-309-001 | ca01bac0-6087-4f92-9689-657fd52b6466 | MD05-1 | 396 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  | Fuel | equipment | 1FPCP_A_01 | FPCP (Fuel Pump Control Panel) |  |  | The differential pressure switch on the fuel filter is not working properly. Inpro will supply a replacement, and its correct operation must be checked. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623633&prj=396&rqi=i5Qtp1hTg9bg9nYIqC5fvOFUoH
GI-080 | 5607cb6a-c77d-4aab-9230-ec42a639e755 | MD05-1 | 396 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-05-07 04:00:00.000 +0400 | VER - Vertiv Electrical |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | Cool array HOTSPOT functionality not working in DH 1.3 or DH 1.4, to be checked prior to L4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620663&prj=396&rqi=vvb4jCVGgDeIqmu52NkRacSSBw
GI-077 | fd54a73f-6554-4676-9924-900096683528 | MD05-1 | 396 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-05-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation Not Correct | Commissioning |  |  | equipment type |  |  |  |  | Confirmation on what signal type & range is required for PICV valves feedback (V or mA, 0-10V, 2-10V, 4-20mA, 0-20mA) In PPR 1,2 & 3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620511&prj=396&rqi=jIunBTWT5L8zgUAH3LmKdBzQ2Z
GI-079 | 68e9a82a-ac08-4614-b707-a9ef04b93cc0 | MD05-1 | 396 | S-EMEA | Closed | P1 High CX | liam.piervulivo@hdrinc.com | 2026-05-06 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Correct | Commissioning |  |  | equipment type |  |  |  |  | design flow rates are not being achieved on condenser or primary circuits, affecting WCC, DAC and heat exchanger performance Potentially linked to foaming or gas entrained witnessed in water samples | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620515&prj=396&rqi=oHVrgwcBcng1Ln6YpUBFHJIAuO
GI-078 | da237b6b-760c-4346-ac1c-ae62582c7755 | MD05-1 | 396 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-05-06 04:00:00.000 +0400 | ARM -Armstrong |  | General Design issue | Design |  |  | equipment type |  |  |  |  | Flow switches to be set up with pump min speed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620513&prj=396&rqi=0S2AewZxzE0GMFZfl5LsdlYWoB
GI-064 | b3b2ae49-9983-4599-826b-ad41a673dfbb | MD05-1 | 396 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-04-27 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | Temperature control of condenser water inlet is not fine enough and causing issues with WCChttps://equinix.facilitygrid.co.uk/inquire/?action=eiss&trf=1&PID=619505&prj=396# | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619505&prj=396&rqi=xHbXT8mG4fztfCU7DCbqgBkTue
GI-063 | c4aea048-dff0-4c0a-846c-d434213f45a0 | MD05-1 | 396 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-04-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | Primary/ condenser loop flowrates cannot be consistently read and appear lowerthan design when read at orifice plate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619504&prj=396&rqi=IUiRov3iCuv4iCbP1lief6mDWB
GT1MECH-175-002 | 422002aa-ce1f-49f7-add9-c9e6ecf231c5 | MD05-1 | 396 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-04-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning |  | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | The water liquid cooling system for the fire pumps discharges directly onto the exterior of the building, creating small pools of water. We request that the discharge point be situated near a drainage point. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617019&prj=396&rqi=Jo1B7R4yJXCwss19TdfvXTajNQ
GT1MECH-175-001 | ebe0a730-4ee2-4705-a096-7fb8c4a48f21 | MD05-1 | 396 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-04-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | During the internal test of the the pumps verifying the curve and consumption was noted that the jockey pump starts at 8 bar and stops at 8,5 bar with a delay more or less of 2 seconds. As a result of the delay, the pressure in the pipe rises to 13 bar. Please verify the way to improve the settings in order to avoid high pressure in the piping system during the jockey functionality. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617008&prj=396&rqi=fQ2cgGHKbPUe61rZl5DzbRGOzh
GI-061 | b192e526-dd6a-49f4-96e9-54036bcf0354 | MD05-1 | 396 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-03-18 04:00:00.000 +0400 | ARM -Armstrong |  | Design Correction Needed | Design |  |  | equipment type |  |  |  |  | DPT 01&02 range is too high and causing issues with measurement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615971&prj=396&rqi=miyTDeOuKDK20F5CdEobJNpN23
GI-060 | 6f974a48-a390-4cc9-9e4b-04f9c3b17a81 | MD05-1 | 396 | S-EMEA | Closed | P3 Low CX | luis.newman@hdrinc.com | 2026-03-09 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning | [7 empty] | Blanking panels in Ewall B are not properly fixed down and with a small amount of airflow from the CRAHs the panel is being pushed back and swaying back and forward | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615115&prj=396&rqi=eWJTUfkxl8GQinHlADggQxeHe2
GI-058 | ecbcdf16-54d2-4b66-b8fe-ef9b5eebb7cb | MD05-1 | 396 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-03-04 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | Condenser flow status point monitored by DCOS is looking at a lack of alarm for condenser flow, this is generating a flow status when everything is off (chillers & pumps) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614682&prj=396&rqi=4bARZLntj6GzorYCPREDLG7QkG
GI-059 | b5505312-8cd6-4938-9810-f41601d5b3d9 | MD05-1 | 396 | S-EMEA | Closed | P2 Medium DCOS | liam.piervulivo@hdrinc.com | 2026-03-04 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Design Correction Needed | Design |  |  | equipment type |  |  |  |  | Ready to run point not used in sequencer logic as per CHW SOO sFAT | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614683&prj=396&rqi=94Fz91lNdHDbdnvhlGTHD73zu6
GI-057 | ed16bead-c0f7-4e94-b80c-5bd802b31fec | MD05-1 | 396 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-03-04 04:00:00.000 +0400 | AER - Aermec |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | Ready to run signal logic sent to DCOS logic needs to be changed so that chiller is always either in fault or ready to run. One is the inverse of the other | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614681&prj=396&rqi=nqBBLuA2a6dKtt6OiyxjuE9ZFf
YT1MECH-327-001 | 18ebb488-6c44-4f23-ba04-4de84a5e00ce | MD05-1 | 396 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-02-19 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning |  | Fuel | equipment | 1FPCP_A_01 | FPCP (Fuel Pump Control Panel) |  |  | Inside the pump rooms, the cable containment system needs to be repaired. The DP copper piping also needs to be repaired, and outside, the valves and pipes need to be painted and checked. At a minimum, the valves, flanges and pipes need to be repainted, cleaned and oxidation to be repaired. To be fixed the cable installed in the bulk tanks (improve the fixation, cables with the correct radios, and to be cleaned). This applies to FPCP_A01, FPCP_B01, and Fuel Pumps in A and B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199527&prj=396&rqi=QGrnx9PIpLQRFUyw7ipABKofbj
YT1MECH-189-004 | 710b900e-be81-4f4f-9b4e-4c045266239a | MD05-1 | 396 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-02-18 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | In one of the pump fuel tanks It is observed a leak in the tank. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199458&prj=396&rqi=kL5rhwtitrmlG1N26Y8eJODXTm
GI-054 | c8230603-4b57-4cd6-b286-221c5db84ff0 | MD05-1 | 396 | S-EMEA | Closed | P2 Medium CX | luis.newman@hdrinc.com | 2026-02-11 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning | [7 empty] | Water detected in Ewall B, in front of MDSB_B1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199028&prj=396&rqi=WOp8WNtFP9wziYDUwSaX5RcgPK
GI-051 | 882dbdf7-2027-4eb2-ae3c-40becad6bae3 | MD05-1 | 396 | S-EMEA | Closed | P3 Low CX | liam.piervulivo@hdrinc.com | 2026-02-09 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning |  |  | equipment type |  |  |  |  | Lagging and cladding to be replaced where it's been removed to install DAC temp sesnors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198787&prj=396&rqi=PeFFiCrvqXs9L9TjXbq4FSKKAa
GI-053 | a0e4c355-9247-4ef5-9c5a-db7195f35f2d | MD05-1 | 396 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-02-09 04:00:00.000 +0400 | ARM -Armstrong |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | PPR/ PCR control valves are not actuating correctly as per DCOS signal. Suspect loose 4-20mA connection instead actuator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198789&prj=396&rqi=R66gzAZnff7BefGmCNG0K1cLcW
YT1MECH-189-003 | e96d2683-fd7f-4391-80f5-d0435163d65c | MD05-1 | 396 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-01-30 04:00:00.000 +0400 | General Contractor - Commissioning |  | Incomplete Connections | Commissioning |  | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | To be verified the leaks in the refrigerant pipe of the pumps | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198005&prj=396&rqi=d4wMrCKSkHYTE00e8sdN7dJ2Da
GI-050 | 3e0f1b1f-1113-4a88-8ca0-fe370e3984e8 | MD05-1 | 396 | S-EMEA | Closed | P2 Medium DCOS | liam.piervulivo@hdrinc.com | 2026-01-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Installation Not Complete | DCOS |  |  | equipment type |  |  |  |  | Hard wired cable to control DAC SP not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198017&prj=396&rqi=KJPl2t1wzzVrmn90A18zzUZbOm
YT1MECH-189-002 | c68323ad-f681-4a91-bf77-7b2eab88ceb6 | MD05-1 | 396 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-01-29 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning |  | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | To be include a water protection in the ventilation pipe out of the fire pump room | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197861&prj=396&rqi=XCBy8YqcGWVoYuhuvqJC4lYLj1
YT1MECH-189-001 | 6778559e-2cad-4336-838f-cecc0188cda4 | MD05-1 | 396 | S-EMEA | Closed | P3 Low CX | Mario.CaveroPerez@hdrinc.com | 2026-01-28 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Damage | Commissioning |  | Fire Suppression | equipment | 1SP_B_01 | SP - Sprinkler Pump |  | FGBS 150-125-315 UL/FM | To be repaired the protection element from the pump 1SP_B_01. Also pending to be connected the bonding-earthing cables in 2 pipes | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197782&prj=396&rqi=sXHF2D5BYVwdEbkvGOZdSk2haD
GI-049 | 31731d42-65b7-4a60-a894-7b7bc9cb6823 | MD05-1 | 396 | S-EMEA | Closed | P2 Medium CX | liam.piervulivo@hdrinc.com | 2026-01-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | Indoor Fan Coil units in battery rooms and NER rooms are not working in heating mode This is causing these rooms to be outside the acceptable temperature range | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196963&prj=396&rqi=gnEmP1QoJBeWoZyltHj6p4Za4E
GI-274 | 4d4065be-5240-4188-8c53-4f3fa69a8f9a | MI01-3 | 500 | AMER | Open | P2 Medium DCOS | sdetardo@equinix.com | 2026-07-15 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | please see Sensor 1 for CRAH 5_25 is in alarm at 81.4 degrees. This sensor does not appear in the floor layout of the colo. Please review all CRAH sensors on the graphics and that alarming is feeding through | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629426&prj=500&rqi=1dGpjdyz4NMFRo5V01t1MxbvBL
GI-275 | 5d50e4d3-1fd7-4aca-852a-2ee09c88fb73 | MI01-3 | 500 | AMER | Closed | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-07-15 04:00:00.000 +0400 | General Contractor |  | Documentation Not issued/ Required | Commissioning | [7 empty] | Panel Drawings missing in BCM enclosure - west COLO | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629431&prj=500&rqi=PvBIDtlFa65Dn288qYMl7GL4o5
GI-132 | 3c58d47e-b001-4ee0-88a7-dc983d943ba7 | MI01-EOL | 611 | AMER | Open | P3 Low CX | sdetardo@equinix.com | 2026-08-26 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [7 empty] | Installation incomplete - hose for Fire System Nitrogen device - see photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635390&prj=611&rqi=Pgma7UvRqUhhlEWZeJhZ5qZAK9
GI-131 | 4b2a9da8-d728-4505-a041-90c3f21be7a3 | MI01-EOL | 611 | AMER | Open | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-08-24 04:00:00.000 +0400 | Controls Contractor |  | Documentation not issued/Required | Commissioning | [7 empty] | Equinix TES/Controls has not received the IP Address or Password list for the delivered equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634931&prj=611&rqi=8FdVp3p3Ip1SURduspimbOnAd1
GI-130 | 12a23fc8-451a-4d70-b223-ba949af399c5 | MI01-EOL | 611 | AMER | Open | P2 Medium CX | sdetardo@equinix.com | 2026-08-20 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design | [7 empty] | Generator breakers do not have kirk keys. In the event voltage is present from the mobile temp gen - it is possible to backfeed the fixed generator. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634383&prj=611&rqi=na45eaPxjEWaqaGQeLF0e7PQpC
GI-129 | e94a8e56-fad4-4959-ab19-28b488c30a04 | MI01-EOL | 611 | AMER | Open | P2 Medium CX | sdetardo@equinix.com | 2026-08-18 04:00:00.000 +0400 | Design Professional |  | Installation not complete | Commissioning | [7 empty] | Mobile Generator / Rollup Tap Box remote start is inoperable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634134&prj=611&rqi=yaNCqX2JU8chhofKeeXrqJGXlP
GI-127 | 1a03a597-6a2d-432c-a456-e8c6386e5d56 | MI01-EOL | 611 | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-07-17 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | update graphics to show new sources of chillers and pumps | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629890&prj=611&rqi=p2GD7eTIHnbh0O63ss1XDfa3xO
GI-118 | 3c3e3ccf-dcf0-4d49-8905-18d25c9b4641 | MI01-EOL | 611 | AMER | Closed | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | PLC inside daytank controller not labelled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629788&prj=611&rqi=RULyDzV1OoNHk3ais1bBBqiYEU
GI-122 | 59146b64-5e0e-4da8-bed9-ac4dd1f04779 | MI01-EOL | 611 | AMER | Closed | P1 High CX | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Commissioning Issue | Commissioning | [7 empty] | Free hanging wires with ends using tape inside the MSB K | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629792&prj=611&rqi=1SHNCxJQZFAaYZU7U5X0YQmg3p
GI-121 | f44c05da-aca3-41c5-9c1f-1c23c6f85945 | MI01-EOL | 611 | AMER | Closed | P2 Medium CX | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Inside K Block HMI - ethernet cable too long, not labeled, and pulling weight on the Power Connection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629791&prj=611&rqi=MJIx9KHrYOFgLEEX9qxZaTT8ZB
GI-120 | c65a97c8-951d-4b1e-bfb9-97e4597534a9 | MI01-EOL | 611 | AMER | Closed | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | TGW and associated ethernet inside day tank controller not labeled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629790&prj=611&rqi=hGlfODAp6pD3xiJX4aTySPV0RB
GI-119 | a9bdab94-4100-4871-abe4-7c3424fb20e7 | MI01-EOL | 611 | AMER | Closed | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Ethernet to both MSB K + MSB L PLC's not labeled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629789&prj=611&rqi=hKYtPvTLL4F8m31k7uNRmGyhcs
GI-124 | 09135520-7962-4400-bf81-bcff56ae2b55 | MI01-EOL | 611 | AMER | Closed | Outstanding Paperwork/Documentation | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | fuel controller - uplink is labelled with the name of the panel, not the upstream switch + port. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629795&prj=611&rqi=ABzZ2x5GbwNexYKbw09V79CEkY
GI-123 | 63a61cc3-e2c4-4833-8bb5-5aab3f882f35 | MI01-EOL | 611 | AMER | Open | P2 Medium CX | sdetardo@equinix.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Commissioning Issue | Commissioning | [7 empty] | loose cabling, open raceway, and ethernets using couplers - not home runs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629794&prj=611&rqi=OfTDmAQhlhvF9Q7ZawkDzuua4h
GI-117 | 84a65536-66c6-4c63-a640-1830100615f7 | MI01-EOL | 611 | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-07-14 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | When navigating - Floor Layout - > Electrical Room -> 2nd Floor -> West Electrical Room There are items in data loss, and a large daytank in the wrong place. See attached screenshot | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629233&prj=611&rqi=HRmjf1Hn2fumhbZYB7ax1f3K59
GI-116 | c50f2384-af59-40d1-9226-79bf129a7498 | MI01-EOL | 611 | AMER | Closed | P3 Low CX | lily.perrette@veolia.com | 2026-07-09 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [7 empty] | MV-3 relay getting com alarm, and PHS can't bing it, PHS has been able to bing it but stop communicating , can see PQM, | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628598&prj=611&rqi=SWHsgL54S4XF6EWnQm65rPBpNC
GI-115 | 43cbd525-1cc7-43f8-bb2b-7a6dc2d75b88 | MI01-EOL | 611 | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-07-08 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [7 empty] | Maintenance mode is not syncing between Aveva assets and SmartView assets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628442&prj=611&rqi=nmqpXs6fiymxP1RpPRM1o3QomA
GI-113 | 0b39f0b9-0869-4331-bd9e-116af7e8371b | MI01-EOL | 611 | AMER | Closed | P1 High CX | sdetardo@equinix.com | 2026-07-08 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | [7 empty] | MSB Main Switchgear compartment has high noise and is vibrating the enclosure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628439&prj=611&rqi=D1p4L98VWb6BGavxGBAZ0ExInZ
GI-114 | 32bfa306-0cb7-4e15-bc29-09e4f23bd78c | MI01-EOL | 611 | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-07-08 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Duplicate entries for MSB PQMs exist in SmartView. Please review all SmartView assets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628441&prj=611&rqi=jNNpPEOX3YbZl0PtHaTbmy0xao
GI-112 | 40bd9a3e-644e-4707-90d2-1fd998b604ec | MI01-EOL | 611 | AMER | Closed | P1 High CX | sdetardo@equinix.com | 2026-07-01 04:00:00.000 +0400 | VER - Vertiv |  | Commissioning Issue | Commissioning | [7 empty] | On K2 UPS HMI - The IOB Breaker is labeled MIB. All other UPS's are correct | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627594&prj=611&rqi=mJwutZ1uSB2yPEDk22RpELEdlj
GI-111 | 6281c137-5b2c-4b4b-a7fb-71c9ca4846cf | MI01-EOL | 611 | AMER | Open | P2 Medium CX | sdetardo@equinix.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment failure | Commissioning | [7 empty] | All battery strings have certain batteries in WARNING and 1 now Critical. K1: 2 Warning K2: 1 Critical ; 6 Warning L1: 11 Warning L2: 6 Warning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627592&prj=611&rqi=MDQP3ZtjQIQMahMqA35U1cJJtP
GI-108 | a1653aba-4bb1-4a3e-b278-5e78ba0b42e8 | MI01-EOL | 611 | AMER | Closed | P2 Medium CX | sdetardo@equinix.com | 2026-06-18 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | [7 empty] | Permanent Labels on breakers on SCC-R are missing for feeds down to 2nd floor UDP R's | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625904&prj=611&rqi=8hzZCY2OYVq94doHqlMrLKVGtd
GI-106 | abafac82-fc01-41fc-ab1c-3e93182a48ca | MI01-EOL | 611 | AMER | Closed | P2 Medium CX | sdetardo@equinix.com | 2026-06-18 04:00:00.000 +0400 | Controls Contractor |  | Labelling | Commissioning | [7 empty] | CAT6's are not labeled inside Control Panel CP-2W-01, in addition PLC does not have an IP address or identifying NAME | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625896&prj=611&rqi=5REfv97HOHF2aVMr1iMqVYfEH9
GI-109 | 5ec00712-3cfa-45f0-b6e7-1be37347d879 | MI01-EOL | 611 | AMER | Closed | P1 High CX | sdetardo@equinix.com | 2026-06-18 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | UPS Faceplate has Battery Remaining Time in "Seconds" -- value given "22" - is actually minutes - see screenshot | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625911&prj=611&rqi=8bQVCL40LGxmex4MQukVfUBGOt
GI-105 | e2804dd1-49ab-418d-a76d-ae7e5b90d4b8 | MI01-EOL | 611 | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-06-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [7 empty] | Controls cabinet "CP-2W-01" is missing schematics inside the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625895&prj=611&rqi=aIhCtgW29sNtRa3N4ArQWUDPcq
GI-107 | 4e7f0dab-410d-4f43-9afe-c49cc553d239 | MI01-EOL | 611 | AMER | Closed | P2 Medium CX | sdetardo@equinix.com | 2026-06-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [7 empty] | WING Wireless extender is not permanently installed in any type of enclosure. Device is exposed to high heat and conditions of engine room. Wires are hanging . Unit appears to be still in "testing phase" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625897&prj=611&rqi=JQDoTlmAs4lHMQjgU9azHIRCXE
GI-104 | 13930014-bb5d-490c-9d6f-b8799adb0c60 | MI01-EOL | 611 | AMER | Closed | P2 Medium CX | sdetardo@equinix.com | 2026-06-17 04:00:00.000 +0400 | Electrical Contractor |  | Component/Equipment failure | Commissioning | [7 empty] | Perimeter Receptacles along the exterior colo wall (ex outside colo 255) have no power (northwest side) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625763&prj=611&rqi=quIs65cEIgtD8ktFq5CK9nivLV
GI-103 | 78c0d54c-7d27-46fc-8b15-ef693562199e | MI01-EOL | 611 | AMER | Closed | P1 High CX | sdetardo@equinix.com | 2026-06-17 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment failure | Commissioning | [7 empty] | 3 of 4 crahs in the electrical room did not restart after a utility hit. The units were stuck in "Remote OFF" Power cycle of the 480v switch reset the hmi and the units restarted. It was addl discovered that the internal UPS is not holding on these 2 units as the controls should have stayed on when the 480v was killed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625738&prj=611&rqi=SW5Gk41J746cfkbTHyCWeYdefO
GI-101 | a92d4020-9aac-47c0-b227-02d56939b57e | MI01-EOL | 611 | AMER | Closed | P3 Low CX | dustin.haugh@veolia.com | 2026-06-12 04:00:00.000 +0400 | CMM - Cummins |  | Commissioning Issue | Commissioning | [7 empty] | Generator D glycol leak from union pictured | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625096&prj=611&rqi=MA0Ji9k03KcFjfLYRaLcL6YNCp
GI-099 | 8affa0c0-723e-4c71-8536-a980d11d9c7d | MI01-EOL | 611 | AMER | Closed | P1 High DCOS | sdetardo@equinix.com | 2026-06-11 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [7 empty] | PUE calc and popup do not take into account new blocks K + L | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625041&prj=611&rqi=UoXShDR2WXKP0wE0cJD5G0Lq37
GI-097 | 12c91236-584e-481d-a76e-377cd6d80171 | MI01-EOL | 611 | AMER | Closed | P3 Low CX | klemmens@equinix.com | 2026-06-10 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [7 empty] | BTUs connects to the network directly and then bringing in the point for general alarm via OPC. BUT screen disables when that is implemented. Please have this issue fixed with SE. We need to see the display. Assigned to Veolia for redirection of issue by DM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624789&prj=611&rqi=3ZPaG5l9kJRUr2qt7Chu0PfMMU
GI-096 | 9dd51390-fdc4-4495-81d8-4dc47909747a | MI01-EOL | 611 | AMER | Closed | P2 Medium DCOS | sdetardo@equinix.com | 2026-06-09 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | We are missing a Power Overview screen that covers the K + L electrical equipment -SD 6/11 - reviewed screen - MSB-K and STS KR2 are listed twice, please review | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624582&prj=611&rqi=q1M7Mck3ZlVprvi5eJUwLQFsfl
GI-095 | a653f390-30e2-4629-852f-34f38b7b8f38 | MI01-EOL | 611 | AMER | Closed | P3 Low DCOS | sdetardo@equinix.com | 2026-06-08 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | On floor layout view for 2nd floor SE - the cage on/off button does not turn off cage backgrounds from background. Addl - cage layout has heavier line width and does not match other floor quadrants | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624342&prj=611&rqi=QydhKqNr5LFcjYi7t2dZZXwolv
GI-086 | 8cebd824-9c68-d0e9-e1f6-64ccb6aa8123 | MI01-EOL | 611 | AMER | Closed | P3 Low DCOS | samet.ozdemir@veolia.com | 2026-06-05 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment failure | Commissioning | [7 empty] | Leak detection was added in the generator room but cannot be tested due to single use ropes being installed. PHS to provide new rope since current one was wetted or supply new reusable rope if avalible. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624145&prj=611&rqi=YW4CbMocsJXRNbgw8qkFDRWfnf
GI-084 | bcfe50c7-6a1a-4b2f-b15e-a5f5c473d2c2 | MI01-EOL | 611 | AMER | Closed | P3 Low DCOS | samet.ozdemir@veolia.com | 2026-06-05 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | Ensure equipment on the electrical floor layout matches the same locations as the drawings. See attached snippet for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624140&prj=611&rqi=Siq5msyfJO2DMR10dHQLma6VAo
GI-087 | 8466cbcb-25da-b30f-f7f0-2cec61f787a2 | MI01-EOL | 611 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-06-05 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not complete | Commissioning | [7 empty] | Provide buckets for all chain valves in the generator and electrical rooms where needed. see attached photos and reference photo of bucket. Also relocate valve tags to the bottom of the chains for visibility. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624148&prj=611&rqi=qGeqNkajgIJZFtzhRYG4Wze36P
GI-091 | 085c642a-715d-42f7-b746-9ed2a8b3cdc7 | MI01-EOL | 611 | AMER | Closed | P2 Medium DCOS | samet.ozdemir@veolia.com | 2026-06-05 04:00:00.000 +0400 | Owner's Representative |  | Design correction needed | Design | [7 empty] | Installed ASCO solenoid valves on the fuel oil day tanks are not in compliance with the Equinix EBCS-1 standard in that the valve does not have limit switches or aux contacts providing positional feedback. The solenoid valves are also fail close valves because they need 24V to open. Conversations were held with Equinix project team on potentially replacing these valves. Equinix to provide direction. See attached photos for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624177&prj=611&rqi=r64fKZnFLShRgdYNNfMok3WSmv
GI-083 | 8fff143c-4014-48f6-b681-f6236d88b950 | MI01-EOL | 611 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-04 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning | [7 empty] | 2UDP L1: orange wire labeled Phase A&B not landed on breaker PDU 21-25 /2E10. Unsure of leadâ€™s purpose, but it is dead ended inside the cabinet.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624134&prj=611&rqi=0NoTIP1r01Bu17mZgU3QwkV4ma
GI-061 | 990f579a-9c23-4d92-b3b3-0bff732eaf28 | MI01-EOL | 611 | AMER | Closed | P3 Low DCOS | samet.ozdemir@veolia.com | 2026-06-03 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | Objects on the BMS floor layout need to match the equipment location in the field. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623788&prj=611&rqi=bA3O9PG5nf0rGad18iy3QwWjZD
GI-063 | 2196ac3e-ea3a-4a64-8f14-bff99aca2d6f | MI01-EOL | 611 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-03 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [7 empty] | UDP-All equipment panel grounds not installed in various cabinets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623798&prj=611&rqi=XEUsYrt2vp7mE28F5OwBduO1hX
GI-062 | 9e625bc7-967a-4da8-bc76-05ecbeea0261 | MI01-EOL | 611 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-03 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation Damage | Commissioning | [7 empty] | UDP-L-2 doors are misaligned preventing closure. Some doors are bent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623791&prj=611&rqi=HeiQASNSiXsq6vTHlLUvakNuf5
GI-052 | 412c01ad-b963-4e83-aa30-da2b4078c97b | MI01-EOL | 611 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-05-28 04:00:00.000 +0400 | CMM - Cummins |  | Component/Equipment failure | Commissioning |  |  | equipment type |  |  |  |  | (All Glycol Pumps) L4 Pump overloads consistently trip when set to 11A. After review of pump amps rating, overloads have been set to 16A. To be retested and verified | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623401&prj=611&rqi=A7Sxy2pg15IUyH1FVCQYtuqVix
GI-049 | f6592acd-fa79-4d6e-8d28-9babdcf2f280 | MI01-EOL | 611 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Incorrect Settings | Commissioning |  |  | equipment type |  |  |  |  | (Vertiv CRAHs) L4 CHWV fails closed instead of failing last/open. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623337&prj=611&rqi=4OPqW9sRGuBhL8LikAvhGzJPVC
GT1ELEC-2-001 | 938edf77-0e51-4abf-89df-fa2705a0e50d | MI01-EOL | 611 | AMER | Closed | P3 Low CX | darren.thurber@veolia.com | 2026-05-27 04:00:00.000 +0400 | SCH - Schneider MV | L3 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 2BTU-1 | BTU - Battery Tripping unit |  | SCH - Schneider | BTU - Verify metering is accurate. Provide points list for metering and alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623228&prj=611&rqi=c8PcHjeKzXcBHEq5lWylq7qZEM
GI-041 | 5296237d-7821-4701-87a1-7c1a65fc3c2f | MI01-EOL | 611 | AMER | Closed | P1 High DCOS | alec.dughi@veolia.com | 2026-05-15 04:00:00.000 +0400 | General Contractor |  | Component/Equipment failure | Commissioning |  |  | equipment type |  |  |  |  | (BOTH Gen Day Tanks) L4 Float level sensors give slightly inconsistent values between each other and between different trials. When float sensor is physically moved to top/bottom extremes of travel, signal received varies, and is not exactly 4-20mA (more like ~5 - 18mA) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622001&prj=611&rqi=IWehm4W1N5TyfdM7PqGorWI05Z
GI-039 | be00b7d9-ecba-46b3-9686-a4c6692d51c8 | MI01-EOL | 611 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-05-15 04:00:00.000 +0400 | CMM - Cummins |  | Design not as specified | Design |  |  | equipment type |  |  |  |  | (BOTH Gen Glycol Pump Skids) L4 When pump skid is called on, the selector will randomize between pump 1 and 2 to equalize lifetime wear. If a running pump fails, the other pump will be called on as a backup. Per Equinix design, this behavior needs to be modified such that pump 1 is the default, and only if it fails will pump 2 turn on. Cummins was directed from pump skid vendor to modify the wiring to the pump selector to conform to Equinix's SOO. The new wiring will default to pump 1, but will not call another pump on when pump 1 fails. Original wiring was left as is, Cummins is awaiting further direction from the vendor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621996&prj=611&rqi=Hg7OZRPtkvkHJH7UbDIKB2hp7q
GI-038 | 443ede3a-6271-4645-a4c7-b67f28df09b3 | MI01-EOL | 611 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-05-14 04:00:00.000 +0400 | General Contractor |  | Component/Equipment failure | Commissioning |  |  | equipment type |  |  |  |  | (Gen fuel pump system) L4 Fuel is back-siphoning from each day tank to belly tank on the first floor. The fuel is suspected to be leaking through the solenoid valves FCV-01 and FCV-02, through lag pump piping and pressure relief valve, back into the belly tank. The pressure relief valves at the pumps were tightened from 0psi to ~80psi. This slowed down the siphoning issue but it still persists. Next step is to add check valves to the supply lines to prevent this backflow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621914&prj=611&rqi=FV0O1eEFoMWHm5UBtnAqP0uczD
GI-037 | 364f908f-c6af-4787-871c-ce496d42a1c0 | MI01-EOL | 611 | AMER | Closed | P3 Low DCOS | samet.ozdemir@veolia.com | 2026-05-11 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | The command / status of the day tank solenoid valves in the Aveva graphic did not match the faceplate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621127&prj=611&rqi=trrzyzC4yBvLH0k6Sdfnxwavgm
GI-034 | 73d78517-89b6-4d38-9ddb-b5cda1774086 | MI01-EOL | 611 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | Provide permanent labels for all energized mechanical equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621015&prj=611&rqi=igWTo24IDM79sJLzlNqG0DGHsB
GI-036 | b909cab1-6acc-4f3c-b57b-ba25ae97b522 | MI01-EOL | 611 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-05-08 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [7 empty] | B phase power feeder serving the day tank PLC was found to be loose. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621017&prj=611&rqi=y21GHByoJLkEjzR5XLVi4AhwtC
GI-030 | ebead893-c713-4d0d-a933-6b1b3360bc5b | MI01-EOL | 611 | AMER | Closed | P3 Low DCOS | alec.dughi@veolia.com | 2026-05-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | (DAY TANKS) L4 Day tank names are switched in BMS. "02240T00_2FDAYK_RAS_LT" should read "02240T00_2FDAYL_RAS_LT" and vice versa. No asset to link to, leaving as a general DCOS issue #fuel pump system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620566&prj=611&rqi=Olcg7OPXHZqurSUOATdI5FeSe8
GI-029 | ebed18b2-eb60-46fc-9584-24365b2aa2ee | MI01-EOL | 611 | AMER | Closed | P2 Medium CX | samet.ozdemir@veolia.com | 2026-05-06 04:00:00.000 +0400 | Electrical Contractor |  | Installation not complete | Commissioning | [7 empty] | 2nd floor day tank fuel oil pumps were found to be spinning the wrong way. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620565&prj=611&rqi=319TvOgBz07xNAmU3WbUHO9cUe
GI-031 | 8c5ca7c6-ebd1-45fc-96a7-b82130cc15d2 | MI01-EOL | 611 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-05-06 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | When the fuel oil pumps were in operation the pump CTs indicated the pump was not running. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620570&prj=611&rqi=7ufcYfWcT8ZvqUHxFqCtsuOOpH
GI-028 | 7647a9c4-d24c-4dc5-93b5-e4f394287b16 | MI01-EOL | 611 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-04-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [7 empty] | Battery cabinet L-1 is missing jumper between battery cells.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620089&prj=611&rqi=DMRmSZYBIXGp4o2ezuFBgYa7NM
GI-027 | bb921931-201b-4a15-9ae1-65c31c972b38 | MI01-EOL | 611 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-04-23 04:00:00.000 +0400 | VER - Vertiv |  | Installation Damage | Commissioning | [7 empty] | UPS K1 broken connector.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619219&prj=611&rqi=7qRwNrilCnHu0JDuXZHUeI1VEu
GI-025 | 0eeaf64e-843c-48bc-9c30-96e747f78b7e | MI01-EOL | 611 | AMER | Closed | P1 High CX | chase.negich@veolia.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment failure | Commissioning | [7 empty] | Kirk key R32 broken off in RMU K.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618855&prj=611&rqi=BBMLg9zrKhSVwkl18Qo9mktFsz
GI-023 | eb079b60-3b72-4b88-a32d-995ac982bfb9 | MI01-EOL | 611 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-09 04:00:00.000 +0400 | Mechanical Contractor |  | Documentation not issued/Required | Commissioning | [7 empty] | Provide pressure test results for generator coolant piping (glycol loop) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617675&prj=611&rqi=EM8m4E7R2jUQibzgoTULC90wrH
GI-022 | 29fb4ee0-1ceb-4d04-823f-0ad9dcd99294 | MI01-EOL | 611 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-09 04:00:00.000 +0400 | Mechanical Contractor |  | Documentation not issued/Required | Commissioning | [7 empty] | Provide pressure test results for chilled water piping | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617665&prj=611&rqi=YsHX7xBsfXLo3HfI3bo6gNn3p3
GI-019 | 71c95333-0f71-45b9-a199-7b47f77447a8 | MI01-EOL | 611 | AMER | Closed | P3 Low CX | francis.callan@veolia.com | 2026-03-25 04:00:00.000 +0400 | Mechanical Contractor |  | Installation Damage | Commissioning | [7 empty] | Duct work inside battery room K has been damaged such that it causes safety concerns with the support able to fall. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616449&prj=611&rqi=vklQ5xrkv62D9uwgAOm17xh6YF
GI-010 | e3c6dd54-47dc-4d6a-859a-4aee8fe504f2 | MI01-EOL | 611 | AMER | Closed | P2 Medium CX | klemmens@equinix.com | 2026-02-26 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Missing Components | Commissioning | [7 empty] | CW181 should come with 40-50ft Leak detection rope per the standard MCE. Please confirm this will be delivered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352242&prj=611&rqi=5PybLkFNeldLiC58rVnIR0bQiD
GI-004 | 54692fe1-988a-47bf-9597-caf11898d470 | MI01-EOL | 611 | AMER | Closed | P1 High CX | jonas.wudkwych@veolia.com | 2026-02-18 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation Damage | Commissioning | [7 empty] | Mismatched hardware on Schneider 400A breakers There are 3 different bolts that were used across these breakers stamped O1RL, SKS, and UH. All these bolts have different lengths. This might be causing some of the issues with stripping the threads. The common hardware configurations I noted are as follows: O1RL bolts are the most common and have 2 square washers and a Belleville washer. SKS bolts are longer and have 2 square washers, a Belleville washer, and a lock washer. UH bolts only have 1 square washer and a Belleville washer The Schneider documentation I found calls out M10 x 25 bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199485&prj=611&rqi=maDgMMRYj7oPbxt5NsWeyRKDga
GI-001 | 019836e3-e309-4a7d-a1a1-372b5170d682 | MI01-EOL | 611 | AMER | Closed | P1 High CX | lily.perrette@veolia.com | 2026-01-26 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Component/Equipment failure | Commissioning | [7 empty] | MSB Sections not lining up - Electrician have run into issues with bus work with connecting sections, bus work is not lining up. We verified the sections are lined up in order and with correct MSB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197597&prj=611&rqi=NVrilqIy1bQxZfaRboqcxdi8wd
GI-006 | d5d70b08-087e-4b82-b931-4c98e43b89ae | ML05-P1 | 619 | S-EMEA | Closed | P3 Low CX | stefb@straightlineconsulting.co.uk | 2026-05-08 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1-UDP-C-1 | UDP - UPS Output Switchboard |  |  | ELECTRICAL LV; Whilst investigating an excessive issue on the MLTX in this power string for an unrelated Issue, it was observed that excessive heat was detected on the Load Bank ACB Cubicle of the UDP. Whilst, at time of writing, this Asset is L4 Blue Tag Signed-Off, it may need to be taken back to a previous status, and defective parts replaced/ retested. The excessive heat has led to distortion of the internal PVC arc-flash separation. Clamps of the fixed part of the ACB appear to be not all identical and, during the load tests undertaken after reclosing the ACB and external panels, temperatures exceeding 80Â° were detected on breaker metallic parts. Also refer to attached EoR email. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620964&prj=619&rqi=TKtNcXBz0ej8XClr2WKVNfraxx
GI-005 | 8e7cbe41-c824-47eb-b9ed-ab3579f73478 | ML05-P1 | 619 | S-EMEA | Closed | P1 High CX | stefb@straightlineconsulting.co.uk | 2026-05-07 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1-MSB-C-1 | MSB - Main Input Switchboard |  |  | ELECTRICAL; LV. This Issue was originally raised against the Tx, but further tests on 07/05/26 have revealed that the E & I LV Busbar from the TX to the MSB is causing the problem. Refer to attached documents. The buzzing noise is being caused by the installation, clamping and torquing of the busbar connections onto the Tx secondary side. Previously raised Issue wording; Following completion of the TX L4 Blue Tag, and during 4 hour load burns on the final MV Cables 1-CBL-MV-014 and 015 (test dates 27/04/26 & 28/04/26:, the Tx started to make a noticeable buzzing sound once under circa 80% load; 2.0 MW. Casing inspections and thermal scans have revealed no issues, but the noise continues, for most of the time, when the Tx is under load. Thermal scans revealed low temperatures of 30-45 Degrees Centigrade; temperatures of no concern. SGB have requested that acoustic scans be conducted. 08/05/2026; RESPONSE ADDED; This Issue cannot be Closed as, following tests on 07/05/2026, a new Issue can be raised for E & I Vertiv responsibility, with further detail added. 29/06/2026; RESPONSE ADDED; Testing carried out and witnessed on 26/06/2026 confirmed that origin of issue was discovered and rectified, observed for 2 hour load test at 2MW - no buzzing sound observed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620940&prj=619&rqi=JhAArCtTClJoDazoBFdcyEiloW
BT1ELEC-5-001 | 05067220-ce93-4e23-a2ac-a1d6a25ced96 | ML05-P1 | 619 | S-EMEA | Closed | P2 Medium CX | garyf@straightlineconsulting.co.uk | 2026-04-16 04:00:00.000 +0400 | General Contractor - Commissioning | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1-UDP-C-2 | UDP - UPS Output Switchboard |  |  | Electrical Communication failure with CB C1 feed from 1-MSB-C-1, this is a loss of communication that has happened post-L3 DCOS screenshots and appears to be a failure of the IFE module or the communication module itself. Closed 06-05-2026 With attached Screenshots 23-1 & 23-2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618522&prj=619&rqi=Q5ziXLUX61ipinT2OxCYcMkzdL
BT1ELEC-5-002 | 017abfd8-67f1-4c42-aafb-ce0cbd9a8658 | ML05-P1 | 619 | S-EMEA | Closed | P3 Low CX | garyf@straightlineconsulting.co.uk | 2026-03-25 04:00:00.000 +0400 | General Contractor - Commissioning | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1-UDP-C-2 | UDP - UPS Output Switchboard |  |  | ELECTRICAL 26/03/2026 Whilst completing DCOS screenshots for 1-UPS-C-2 Blue Tag, it was noted that the following CB's are not reporting correct data from the trip unit â€¢ 1-UDP-C-2 - LOADBANK CB (see attached image) â€¢ 1-UDP-C-2 SUPPLY FROM 1-UPS-C-2 CB (see attached image) 27/03/2026 On review of SE DCOS response to this issue, it has been reassigned to E+I for corrective works. 30/06/2026 Schneider / E+I engineer attended site to make correction to power sign wave direction settings using EcoStructure software on 1-UDP-C-2 - LOADBANK CB - works complete on this breaker, report and screenshots attached in responses. Breaker 1-UDP-C-2 SUPPLY FROM 1-UPS-C-2 CB - issue still not resolved, breaker not communicating with software. E+I to issue report and recommendations (replace breaker / replace module) 07/07/2026 issue with breaker 1-UDP-C-2 SUPPLY FROM 1-UPS-C-2 CB has been identified by Vertiv. Replacement Micrologic module recommended and scheduled for installation with verification of correct data being reported. Clear close-out scope of works identified and arranged. Issue priority to be down graded to P3 Low, issue will be closed following the remedial works and associated CX report. 17/07/2026 Schneider / E+I engineer attended site to replace breaker micrologic module (NSX630N 5.3E Micrologic) and confirm connectivity to communications, make correction to power sign wave direction settings using EcoStructure software on 1-UDP-C-2 - SUPPLY FROM 1-UPS-C-2 CB - works complete on this breaker, report and screenshots attached in responses / documents. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616499&prj=619&rqi=Xq4LoBsCe66y2cRace2iVEpIms
BT1ELEC-1-001 | 577c0178-f2a9-4bdd-8340-5061da455c19 | ML05-P1 | 619 | S-EMEA | Closed | P1 High CX | garyf@straightlineconsulting.co.uk | 2026-03-18 04:00:00.000 +0400 | General Contractor - Commissioning | L4 | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1-UPS-C-1 | UPS - Uninterrupted Power Supply |  |  | Electrical Date: 19/03/2026 Whilst completing the blue tag testing of 1-MSB-C-1, test 2 of the E+I test script requires a mains failure from RMU-C. 1-MSB-C-1 PLC then completes a transfer from Utilities supply to Generator supply (test completed at 2MW via building Load Bank). Once supplied by 1-GEN-C-1, the UPS exhibited voltage fluctuations (see attached images), which caused the rectifier to shut down and the UPS to reject the load. This test was repeated at a reduced load, and the same occurrence was observed; see the attached images of the Voltage relay in MSB-C-1, indicating both over- and under-voltage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616019&prj=619&rqi=A6XUsGwDVtHJoxstTuqJuU1eXc
GI-004 | d2ec3be9-f2be-4a1c-9e56-e6cd92009a1b | ML05-P1 | 619 | S-EMEA | Closed | P3 Low CX | stefb@straightlineconsulting.co.uk | 2026-02-05 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1-RMU-C | RMU - Ring Main Unit |  |  | ELECTRICAL; When replacing the Microswitch components in Loop 2 cubicle, a small fixing screw was not fitted as it was not to hand. Refer to attached, marked photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198683&prj=619&rqi=lwnhrb5uiOodGM1z1jqDUNJZKv
GI-002 | f40a6ffc-73aa-4819-945e-dd8d8149d099 | ML05-P1 | 619 | S-EMEA | Closed | P1 High CX | stefb@straightlineconsulting.co.uk | 2026-01-19 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning |  | Electrical â€“ MV | equipment | 1-RMU-C | RMU - Ring Main Unit |  |  | ELECTRICAL; On Tx Feeder Cubicle 3, the mechanical mechanism which operates the microswitch broke during operation, and requires urgent replacement. At present, with the circuit breaker Closed, the microswitch is sending an Open signal. With this being a major safety Issue, the RMU has been shut down and isolated. Temporary remedial works are to remove the corresponding component from Cubicle 2 and fit into Cubicle 3, whilst awaiting new replacement parts. This is to be undertaken ASAP. The defective component is to be removed and sent to SE MV R&D Department for urgent analysis and RCA. 10/02/2026; Updated RCA now attached, so this issue can now be Closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197149&prj=619&rqi=Yr3xgoizrC0qLQ4gMiYrFLUJuD
YT1MECH-27-001 | 762c263b-1afd-4ca4-8ecf-7efa1d436bf9 | ML05-P1 | 619 | S-EMEA | Closed | P3 Low CX | stefb@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1-CRAH-C-18 | CRAH - Computer Room Air Handler (CHW) |  |  | Mechanical; During the 5 bar pressure test on 13/01/2026, a very slight weep was discovered on one of the welded joints. Note that this pipework was installed some years ago in Phase 1. 15/01/2026; Pressure test re-conducted, witnessed and passed. Issue Closed. Refer to Observation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196854&prj=619&rqi=wzt5Wvxjwzu1ZicadYP2SckuTl
GI-001 | 417270b9-9653-4c7a-a366-37330f875bad | ML05-P1 | 619 | S-EMEA | Closed | P3 Low CX | garyf@straightlineconsulting.co.uk | 2026-01-08 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1-UPS-C-1 | UPS - Uninterrupted Power Supply |  |  | There are a number of paint work defects identified on 1-UPS-C-1, see attached images as examples that were identified 16/101/2025 The paint work defects will be addressed by VERTIV once the L4 Blue Tag commissioning has been completed and this issue will be closed. 26/01/2026; Repairs inspected and Accepted; Issue Closed. Very Well Done. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196631&prj=619&rqi=3IdjZwCV8n3TL7pnCYhWLqFAhi
WGR-1-001 | 420b7524-c24e-4da0-b864-80ca15acc9e5 | ML05-P1 | 619 | S-EMEA | Closed | P2 Medium CX | garyf@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | DELIVERABLES | Commissioning Issue | Commissioning |  | Multi-Discipline | equipment | Room 114 - UPS Room | Room Readiness |  |  | Fire stopping of 1 No. Earth Cable leaving the UPS switch room to go to the Battery Room. 12/02/2026; Accepted and Closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196490&prj=619&rqi=CilPFLNUKcghLtvrgbQ2H8iCgt
WGR-1-003 | 4852f1fb-43e6-4a89-a41f-60b2c8585c00 | ML05-P1 | 619 | S-EMEA | Closed | P3 Low CX | garyf@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | DELIVERABLES | Commissioning Issue | Commissioning |  | Multi-Discipline | equipment | Room 114 - UPS Room | Room Readiness |  |  | Fire stopping of 1 No. Earth cable leaving the UPS switch room (underneath raised access flooring to the right of the earth bar) is to be completed. 12/02/2026; Accepted and Closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196552&prj=619&rqi=XhEOa8ZYLfvaMmHZlCcXQTgSXo
YT1ELEC-32-002 | 37f73983-1b60-4096-a9c6-f95e227a2688 | ML05-P1 | 619 | S-EMEA | Closed | P2 Medium CX | stefb@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1-MSB-C-1 | MSB - Main Input Switchboard |  |  | ELECTRICAL; There is an earth connection that has not been terminated underneath the MLTX, which is connected to the MSB earth bar. Vertiv/ E & I to address and Close ASAP. This Issue was originally raised against the MLTX L2B Yellow Tag (issue #11), but as Issues cannot be transferred to other Asset's once raised, we could only Close it, and create this new Issue on the MSB, 12-01-2026 UPDATE; Earth cable removed, so Issue can now be Closed. Refer to photos attached to Response. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196559&prj=619&rqi=SaYWs6sXjpt0xOZ8KFDGehExQE
WGR-1-002 | 30174e53-c60e-4859-b2f0-7d69ba7433ce | ML05-P1 | 619 | S-EMEA | Closed | P3 Low CX | garyf@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Commissioning | DELIVERABLES | Commissioning Issue | Commissioning |  | Multi-Discipline | equipment | Room 114 - UPS Room | Room Readiness |  |  | ELECTRICAL; MV & LV Schematics have not been positioned within the switchroom | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196493&prj=619&rqi=hQyUpgZaYQLBtye9pLqZeEacH5
DCIML4-2-001 | 21bcb98f-ef7a-4067-b160-6ee749b21e77 | MT01-3 | 622 | AMER | Closed | P3 Low CX | Jonathan.Calotes@jll.com | 2026-08-31 04:00:00.000 +0400 | DCOS - Equinix | L4 | Commissioning Issue | Commissioning |  | Integrated Automation | system | DCIM |  |  |  | EQX working on Modbus license for MT1-03 for JLL access | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636135&prj=622&rqi=Xbc50ghCpjbJp8lMTjacf000kB | https://equinix.facilitygrid.co.uk/x/project/622/system/12546
GI-003 | c7072787-d5c9-43dc-a0e3-8a47e808edcd | MT01-3 | 622 | AMER | Closed | P3 Low CX | piotr.sosniak@jll.com | 2026-08-24 04:00:00.000 +0400 | Mechanical Contractor |  | Documentation not issued/ Required | Commissioning |  | Mechanical â€“ Water | system | Chilled Water |  |  |  | Provide TAB Plan for chilled water and air systems. Include Flow meter calibration, pump curves, DP initial settings, DP final settings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634932&prj=622&rqi=WmaWh88uXyuYtFsVaBhxgeAuPN | https://equinix.facilitygrid.co.uk/x/project/622/system/14872
GI-002 | 3a70cd6b-40aa-4de3-a85b-f879f2798a47 | MT01-3 | 622 | AMER | Closed | P2 Medium CX | Nathan.fu@jll.com | 2026-07-15 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not complete | Commissioning | [7 empty] | The chilled water pump vibration was still observed during the test on July 15, 2026, even with the new VFD settings implemented. The field testing team believes the vibration appears to be from the fluid flow in and out of the pump rather than from the pump motor. The Smardt team has reported this issue to Armstrong and Kolostat, and both parties will follow up and investigate accordingly. Updated to July 17, 2026 (JLL): Armstrong technician is suspecting an issue with the coupling between the motor and pump shafts. He's requesting replacements and should be back on site to install them., Smardt will work with Armstrong next week to plan this. Smardt is hoping to get them to address this issue first thing when the site is operational again in a couple of weeks. From their experience with Armstrong, replacing the coupling is fairly quick | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629423&prj=622&rqi=LmOZax2eYZ6AqthoqV9tCrbtFc
GI-001 | 04977420-59cc-4fbe-a4c4-58ef817ec1cd | MT01-3 | 622 | AMER | Closed | Outstanding Paperwork/Documentation | amirreza.barekatain@jll.com | 2026-06-29 04:00:00.000 +0400 | Electrical Contractor |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | - Missing certificate of calibration of phase rotation >> OK | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627289&prj=622&rqi=DamGyl0uoQgOeGsu3eCHPcS6w9
DCIML2B-1-001 | 89e66022-1eef-45da-aabe-c803b155de37 | MT01-3 | 622 | AMER | Closed | P3 Low CX | roozer.samuvel@jll.com | 2026-06-23 04:00:00.000 +0400 | General Contractor | L2B | DCOS Design Issue | DCOS |  | Integrated Automation | system | DCIM |  |  |  | During the SFAT brief, it was identified that the alarm banner around the chiller graphics is missing from the BMS manager interface. This may be due to the site operating on older Aveva standards that do not include this alarm banner functionality as part of the standard configuration. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626571&prj=622&rqi=De8AlDfzs0SFXRdl4ju0g5k784 | https://equinix.facilitygrid.co.uk/x/project/622/system/12546
RT1ELEC-44-002 | 908fd7c5-8be0-45c9-93be-549ddcd62cd2 | MT01-3 | 622 | AMER | Closed | P3 Low CX | amirreza.barekatain@jll.com | 2026-02-08 04:00:00.000 +0400 | Engineer | L2A | Design correction needed | Design |  |  | equipment type |  |  |  |  | missing some cable specifications on cable schedule E720. BA1-C56 -- E602.6; PDUA1-1-1 BA1-C57 -- E602.6; PDUA1-1-1 BA1-C68 -- E602.6; PDUA1-1-3 BA1-C84 -- E602.6; PDUA1-2-1 BA1-C89 -- E602.6; PDUA1-2-2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198758&prj=622&rqi=oaqS557oOG3E6YIMYXrlFVvvzx
GI-075 | 3f717c0d-2318-47c9-929d-349567b30a13 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller â€“ cable management under chiller and to compressors needs tidying up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637090&prj=643&rqi=OeHRLCHttMhVXsqppybltuiGs1
GI-083 | 63280561-85eb-402e-b299-fc31a72bf2b3 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Tags missing for equipment (please reference latest approved P&ID) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637099&prj=643&rqi=0Pkg1ckrDEWc9UtMRNmWGu8inM
GI-082 | 094813fa-cbdf-49ec-a994-08c4cb99e6b1 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Tags missing for valves | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637098&prj=643&rqi=OqRgmYGgRIUnpzgsa4ijFYfJYV
GI-085 | 902d2550-10ee-4469-a011-32698ddd2cf0 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ The approved size of the external Uniâ€‘Strut supporting the AC unit is longer than the specified dimensions; an asâ€‘built diagram must be sent to Mercury Design to verify there are no clashes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637101&prj=643&rqi=IJnG1nzmIncryjJ9c1NI1ILnSS
GI-086 | 904070cf-8801-4505-9d54-bf4ca3dc3ef6 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ PPU dimensions must be laserâ€‘verified and Hamzah must supply evidence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637102&prj=643&rqi=G7d3sbuE6vrwnUImTi6KC1lnWX
GI-087 | c4d12bd6-74e0-42ca-9758-3afe0ac5a09b | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Nozzleâ€¯4 external flanges are 30â€¯mm higher than the 3090 actual dimensions; Armstrongâ€™s asâ€‘built drawing must be sent to the MER team. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637103&prj=643&rqi=qzpNLuRoTETsaw25Orghe029bM
GI-094 | 9b6b875f-0e39-471f-8fc8-bfded6f0d5d2 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Torque required | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Torque reports and any calibration certificates for all flanges, bellows, etc., must be supplied. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637113&prj=643&rqi=TuvhLG0aORdg16cDTuPObq85Rv
GI-095 | 8f124b43-68b9-4a2b-9475-1ad3f2ad9afe | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Labelling | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Both HVAC fans must be labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637114&prj=643&rqi=rt94ff7VTHQaz3DxZlK5IlWwsD
GI-096 | 9a8688a3-7b8f-4b62-9dfc-8d4fc4213b68 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Confirmation regarding the proper operation of the check valve is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637115&prj=643&rqi=g156bf1TqZtpgDexS7KyJyxo9L
GI-097 | 5a13faf3-ef7d-43be-9b2d-0b4e7d65c63b | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Leak detection was not installed at the time of FWT. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637117&prj=643&rqi=EeznsosyycMnTgDPuaXHMFBk0i
GI-098 | b93808dd-a5e7-4587-abd4-4c7bb6a77c25 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ The floor is not painted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637119&prj=643&rqi=ruggnpJE4TqrQaTDuOVNGHYgL1
GI-099 | 4fdc9d98-0e85-484b-960d-78af94fc5b1e | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation Damage | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Plinth painting is damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637120&prj=643&rqi=sWvKDMpSbqBPWp9bJOs8nE1cq3
GI-100 | 49e47016-c962-4754-a820-705dbd13ff7b | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ A drip tray must be installed below the portable valve and above the panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637121&prj=643&rqi=aDFAhgRzInmcPCZFEmq4OJnzEO
GI-101 | 99307952-36f6-41c0-b1c9-97f604434f9e | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Valves after the sockets must be installed for each 3/3 flow meter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637122&prj=643&rqi=wrAMIoDBg6XyrHlivCYZ8PuAaw
GI-102 | 05652d57-c3da-4163-8e56-1b8a04e10afe | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ The pneumatic test report must be accompanied by a markedâ€‘up schematic clearly indicating the tested sections. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637123&prj=643&rqi=hRq0ID0g4fcgCAlC4vlRivINNj
GI-103 | bb2930c6-49b1-4e04-8b5e-1e4645412067 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Support clamps for the two vertical copper discharge lines from the safety valves are required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637124&prj=643&rqi=EIQ7FDKpswQZh3vmA1IkyCZROn
GI-104 | f225d34d-ea99-4d37-b5dc-26623c835383 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ The chillerâ€™s cable runs are leaning against copper pipe; ensure these are correctly secured and not touching any pipework. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637125&prj=643&rqi=EDLl8QPH1lxRlxAm7ZRmtLDNRy
GI-105 | e6297a91-27d0-414f-91ba-39187966c6da | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Verification throughout FWT P&ID was an old revision â€“ please reâ€‘upload the latest revision for review | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637126&prj=643&rqi=Yj9aZNX4UNW0uUrayMw7iwYIZu
GI-072 | e3d7a8ff-aef0-4cb1-b385-0492de243aff | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller â€“ cannot verify fuses F3, F4â€¯&â€¯F6, F7â€¯&â€¯F1 as no sizes on schematic | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637084&prj=643&rqi=bRiUX1uFSAHueSTbsxciz0fTff
GI-073 | 815d1609-8f6a-4c15-a456-e63b40c8fe44 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ No way to secondary injection settings on breakers on both switchboards and chiller (this can be verified at L2B onsite) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637085&prj=643&rqi=pWQ4D8t3aITtUhspX168BIH0Tw
GI-074 | 6d1ce631-11b9-43be-8eff-02067ffc37ac | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller â€“ temperature sensors have been packed with silicone | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637089&prj=643&rqi=I3tbmC7pEAWidT9O6zqrI4Mt4x
GI-084 | 636191b5-a644-477a-a99d-4c78f70a7065 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Tags missing for instrumentation (please reference latest approved P&ID) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637100&prj=643&rqi=JRFssEll6lmY0t4bv3NJ1TICwf
GI-076 | d4b13c43-43a8-4c1c-8aa1-0610de15b272 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller â€“ cable stuffing glands not tight (under chiller and compressors) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637091&prj=643&rqi=lO3dTbmOH3Fo7TVMMK3Qf56H5i
GI-077 | af59460e-d251-4685-94a5-88a88a00a0dc | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Schematics to be installed on wall (P&ID, both switchboards) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637092&prj=643&rqi=Dr0dOKubsZ1xdpxJ7J04LNDqtR
GI-078 | 16825e4b-fcac-49ac-a6d0-ecffa0a3f46f | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Modbus module on all VFD to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637094&prj=643&rqi=HxdNjotX8sTsQDOpwf9NF56uuA
GI-079 | 6162aaaa-3b09-40c0-ae52-f038ef5b282e | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ All fuses in chiller and electrical panels to have a small key installed on the inside door explaining their size and purpose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637095&prj=643&rqi=YBa9js0itiTwBlsXzUjDmSvfXo
GI-080 | cfe15e7e-e854-4091-8544-bfcfd99e7176 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ PCRSBâ€‘Fâ€‘1 primary injection results missing for chiller supply breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637096&prj=643&rqi=cqAuv30nEyWUPUyJeeWeR4YDMw
GI-081 | caf02b2d-348d-433b-88d7-bb7b4600afbc | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ PCRSBâ€‘Fâ€‘1 aux and section D3 missing on schematic | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637097&prj=643&rqi=FSYKisGAWHkkJhtyyII6uT82yg
GI-088 | 4932c417-ec88-483b-8839-1ee51b364024 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Nozzleâ€¯1 andâ€¯2 flanges show 500â€¯mm but actual measurement is 550â€¯mm; Armstrongâ€™s asâ€‘built documentation must be sent to Mercury Design. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637104&prj=643&rqi=9enE3Rmyuaj37ia8vecXE3rcSX
GI-106 | 52935394-b9bd-4f16-9516-e7caabb70d21 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Insulation to be installed on incoming portable water connection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637127&prj=643&rqi=Oi8viZMiuqMEOg8cqs3p9jRgXu
GI-107 | b0dc1941-b6e7-4302-adec-38d555c37539 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Pipework to be capped prior to shipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637128&prj=643&rqi=J6DBhthgwQkwveWkIsHnJKeuzB
GI-108 | b91da40f-d4e3-4d71-a950-439950618a32 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Condensate pipework to be completed prior to shipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637129&prj=643&rqi=mBnGJD822f60Yu4vkvNuT4m3QC
GI-109 | bc09bccc-ff05-4218-bf13-69fd208cc69e | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 :Chiller - pipe insulation to be replaced | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637130&prj=643&rqi=DxXdDoXzGqFDv4LxHmzTxRfVs4
GI-110 | 958244ed-390a-4f1f-89e2-bbf47164e697 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Cleaning | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 : Chiller and all container requires a final clean prior to shipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637133&prj=643&rqi=EGhGRAWEBPzHnDEItXHK56LGHy
GI-111 | 4defa19a-9039-489d-b7b7-5ccfd3f4b3c0 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Labelling | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 Tags and labels missing for pipework (glycol) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637134&prj=643&rqi=z2oqpj3sy2NX9YA1KyF3VMcMbl
GI-112 | 64922474-cb68-42d7-88fe-62a6f91b04a6 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Labelling | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Tags and labels missing for pipework (flow direction) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637135&prj=643&rqi=gkl7AReRR8Fs7Tfm0jE55vlUtt
GI-089 | 65909393-7f5d-4f5b-bd2d-613900cb9916 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Nozzleâ€¯3 andâ€¯4 flanges show 750â€¯mm but actual measurement is 761â€¯mm; Armstrongâ€™s asâ€‘built documentation must be sent to Mercury Design. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637107&prj=643&rqi=QEjHDVzY97B3vqH9X58S9ZuHEi
GI-092 | acd9c2d1-f205-43d6-9cbd-8299ac75f1ad | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller lifting eyes must be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637110&prj=643&rqi=hr7Dg5GHSKtmhc4aqltXD1ahqs
GI-093 | c0398aa1-0c35-4fec-9da6-aa621bb8b30c | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Technical data sheet for bellows must be sent and reviewed against installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637111&prj=643&rqi=IsI9HuRddP3ZWT9tQn4LmQjcJc
GI-090 | 5f05992e-fdc6-426c-90bb-2d78ce067738 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Installation Damage | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Both vessel lagging must be repaired. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637108&prj=643&rqi=kNflLRxPk6X6GrBj4OM4dFqkb8
GI-091 | bf8197f1-0538-4d3a-b40f-68f7adc78a41 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-07 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ All NDT and test reports for the chillerâ€™s refrigerant system must be sent by Aermec. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637109&prj=643&rqi=AdNjxaMi2f6iQ2lGFe06Fhv0T3
GI-069 | 387050c9-d035-4880-8969-d1be10b1a6de | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ 1DCOSâ€‘RIOâ€‘05 no torque markings on the frame bolts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637080&prj=643&rqi=ecBoVGeRs8iB6LD54CEwBusOZL
GI-059 | 129c7ed4-98fe-4e31-a60f-ae01ebdc61d4 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Grommet trip protection missing from tray work | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637068&prj=643&rqi=fv9uBimnIKFxBc1yNSQBbIcYXz
GI-062 | 06987d37-c3b9-4acf-8247-e377b41c540a | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Earth bar to be colourâ€‘coded Green and Yellow | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637071&prj=643&rqi=dLz1Dco2z30mMqYQjCTRo4ZFGv
GI-068 | 40ecce70-eeb4-4ccb-adf1-96b9d11a75a5 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ No entry for DCOS cable in UPCRSBâ€‘Fâ€‘10 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637079&prj=643&rqi=DBLi3UPAmHeyy2YmFQOx8E9EDO
GI-065 | fcac7554-62a9-4f49-b4ba-b49dbc59e4a8 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Paint damage on heatâ€‘exchanger frame | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637076&prj=643&rqi=222uuDHnOF57VwsVy1tZqumxKH
GI-067 | b17f2c3c-4fbb-4a2a-be4f-774ce06b2c03 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ No Roxtec transit frame installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637078&prj=643&rqi=nQbFHa0kP8KRKFbZnsKONdNnEv
GI-063 | 814e3f27-f866-44f0-99ae-4e2fc14b0b72 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Earth straps to be installed on all flanges | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637072&prj=643&rqi=Spaehm0EyQeQtq6gVAeAFzwhFC
GI-060 | 25ab3d85-0008-41bd-9c36-e3221620e046 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Cable bone tags missing from 1PCRSB_F_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637069&prj=643&rqi=88UCLKjNEBLasvCygkIAEP5a6W
GI-064 | 5dcf8eed-7117-4843-8c25-5b24c782d83b | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Gland plates to be earthed on pump isolators | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637075&prj=643&rqi=45D18UYIffxOvFXynVBGCgcJG3
GI-061 | fc43cdb7-ac94-4e55-a854-eca560732055 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ 1PCRSB_F_1 400â€¯V labels to be changed to 415â€¯V | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637070&prj=643&rqi=sJTZYy75kixB6TlUxkt0GnArGN
GI-057 | eb9fd5e2-745d-4d6c-806a-db98fa1c870d | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Pump isolators â€“ missing internal shrouds to ensure IP2X protection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637062&prj=643&rqi=zfdQzOGus6HqnwraSlYSfnTzGm
GI-058 | f4766c28-1e44-4e85-9b52-fb0185128d59 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Pump isolators â€“ 400â€¯V labels to be changed to 415â€¯V | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637067&prj=643&rqi=nw2B53ZqnI68vb031p6ySrlUAr
GI-066 | 81f349d9-e56c-4873-8ea9-345bbc0828b2 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | AER - Aermec |  | Missing Components | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ UPCRSBâ€‘Fâ€‘10 metal tieâ€‘wraps inside panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637077&prj=643&rqi=v3gTbhIXoZIAhRfmWuG6nk9Dj3
GI-071 | 7b75788c-1dc8-476a-9e22-6439a75891fb | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ External louvre not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637082&prj=643&rqi=gCWic3UnpPNy9IxCJQnrG5NjcA
GI-070 | 3d920093-a212-4af8-a8d2-bc9f55ca6c6a | MU04-3 | 643 | N-EMEA | Open | P1 High CX | mahmoud.kheira@bureauveritas.com | 2026-09-06 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller â€“ incoming cable not connected to earth | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637081&prj=643&rqi=TqdhipP62Vg8g1xpCZ017j4JFm
GI-049 | f1f5a1e8-a94f-40d5-8780-92a84d691a81 | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ There is bund installed within area protecting electrical equipment from any liquid exposure during leak incident. Bund area also prevents any leak from plantroom. Please confirm how this is tested or ensured that bund area will hold water following floor being drilled to mount plantroom equipment and all welding | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636878&prj=643&rqi=T0Yp6pGA2xLFCJAlkJHc0UGAMW
GI-045 | 322da97c-5db6-4552-b36b-9a4f036cad7c | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Flow meters have not arrived and it is the clientâ€™s concern that these will cause issue at flushing stage, for example, rather than installed before sending it to the project. Flow meter pockets are left at 90Â° horizontal for these to be installed. Please check with manufacturer if this is acceptable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636869&prj=643&rqi=QGwcsoyjDiBaGYBDAOdOivDysj
GI-046 | 0265a890-e7df-4d0f-aa2c-3f6ac4697bed | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ There is a requirement in script to prove that when multiple and identical assets are being used, it is important to prove that these are not from the same manufacturing batch. Please provide evidence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636871&prj=643&rqi=rlvEJfDPqruv7vjIL8ZXRNFWmP
GI-047 | ee2a8ea2-be65-4a24-b4f9-a68299f64a96 | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ There was a slight misalignment of bellows, manufacturerâ€™s confirmation to prove install is sound | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636873&prj=643&rqi=Wl4eswW0P3S48zhhyCwmPv6Sm6
GI-048 | 3690c747-3080-411e-95cc-cca32824fd4a | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Dosing pots are missing end caps/plugs at the bottom valve used to discharge liquid from pot itself | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636876&prj=643&rqi=Jn7yIezv8Mg11tBiX9FM8tspBs
GI-043 | d99a0cb6-3a23-4246-861d-85e52491a55f | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Tags and labels missing for pipework (water) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636865&prj=643&rqi=8Uipl9uGyiir3hUrggISzK6I8F
GI-042 | f762b675-d41b-489f-a192-48e37df12b8e | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“Covers to be fitted on studded rod hangers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636864&prj=643&rqi=fCWYzm8Pl6pKqORfxmx11r5ZMl
GI-050 | 886397a3-641f-4647-9ff5-59d15b1d4aae | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Dosing pots have pipework installed at high level, running above electrical equipment. Can you please review this and provide solution to protect any electrical equipment from potential exposure of liquid from these pipes? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636881&prj=643&rqi=RGLRYvFlu96o8yMVXLv5fIoBRZ
GI-051 | 206e0962-af3e-4eea-890c-4485c78e6683 | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation Damage | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller insulation was damaged in small amount of areas. Can you please rectify? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636882&prj=643&rqi=nfHsQTn36G0kGwgoVsPRbzcWWb
GI-052 | b9662614-9aec-449b-8194-1add68a955be | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Condenser side of chiller has no bellows fitted at point of connection with pipework. Confirmation is required that this is correct | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636883&prj=643&rqi=ARtEnkqdyqvygKS7oRwulxr1sd
GI-053 | fc0d99ef-ad98-4bf4-a3fb-d30066239e9e | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ There are still some opening to be cut into the structure/wall of plantroom. Please complete and provide evidence of works and include QA cleanliness checks following completion | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636889&prj=643&rqi=hKmvdvfIOk53dfFqT7sua0tW7i
GI-054 | 6fa125ec-7a69-4250-864c-6437bc81e34c | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Buffer vessel and other piece of equipment requires to be bolted down. Confirmation will be required that equipment located within bonded area had correct procedure applied ensuring water bund was not compromised. Expansion tank - Not fixed to floor Buffer vessel - Not fixed to floor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636890&prj=643&rqi=sFgDPRkFcow3YE0P9V3soHipd5
GI-056 | cdbeecde-c762-4c9f-9a83-dfb6a14812c0 | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Chiller has a number of small water valves with no end plugs. Please install to prevent any accidental leak in future | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636893&prj=643&rqi=LK7nc4m4l7TUIWqbNY9iTlFcpR
GI-055 | a200fbc7-143e-4649-b4de-a32e192d4d4e | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ There are HEX bolts yet to be protected by foam | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636892&prj=643&rqi=t96JclVcko8kDn83K1nKNqyyDR
GI-044 | 7abfa94c-4be6-465e-b9b8-e3bd4471e179 | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-04 04:00:00.000 +0400 | ARM -Armstrong |  | Labelling | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ General: Equipment labels are to be installed, while matching PIDs: Missing Trafolyte labels of Pumps Missiing traffolyte labels for VFD Missing labels on Pump Isolator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636868&prj=643&rqi=0pIKTisEd46XawhmzmFpkAjSxH
GI-036 | 55502b65-c35d-45d1-af64-d1bd9d949149 | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Cleaning | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ General Cleaning shall be carried out following completion of all installation. Swarf, debris, dust shall be removed from plantrooms, any panels and equipment prior shipment. This is particularly important prior to any energisation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636827&prj=643&rqi=g2LGjNpqmE6k8EAdTgR2IsOifY
GI-037 | 2ccefcf3-ba39-4fba-a81f-1a05a80da334 | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Number of test packs were provide, and some were yet to be provided. Test Packs are to be compiled and complete where required. Calibration certs to be included | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636829&prj=643&rqi=6wuTMUIZMC03BM9PrVeQBAo9lP
GI-032 | 135769bd-dc91-4c10-a2e7-14b6cc1544e5 | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Minor installation works are ongoing, and some of the kit is yet to be bolted down; ensure the bund area remains waterproof | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636819&prj=643&rqi=iPa68aAvDQo47GtnKTzB4Fb0L2
GI-038 | b80686c8-eee1-454b-85df-884482a77d20 | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Points list to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636830&prj=643&rqi=30mSak1q9WOfva8DcK9vTxPDKX
GI-039 | 379da171-9309-4532-9402-037b2ec5e248 | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | General Design Issue | Design | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ MU043â€‘RHKâ€‘XXâ€‘XXâ€‘SPâ€‘Mâ€‘XXXXâ€‘7110 â€“ CHW Buffer tank specify that buffer tank shall have inspection hatch. Buffer tank within PPCR has no inspection hatch. Can you please clarify if this was agreed? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636831&prj=643&rqi=3q3cYa3UEsFGTabfTV0nzOdNiz
GI-040 | a426f080-10f2-4cb7-8ada-502fe8ff2c29 | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Incomplete Connections | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Water discharge pipes from Pressure relief valves are to be mounted securely | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636832&prj=643&rqi=PfJedexI3pQBSpftLWkZnHuqHo
GI-033 | b629d254-e692-493f-a0bb-c3b444f82c14 | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Please review isolator switch panels. When isolator is used to deâ€‘energize equipment, opening the panel door poses a risk as incoming power is still live, while there is no physical restriction to touch live terminals/cable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636820&prj=643&rqi=FUHwykAu98gKuh0vrGyyqJXEl1
GI-041 | 1e380647-2431-4a50-801b-50d4ba5a9dea | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Update PID with correct model number of HEX | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636836&prj=643&rqi=0NlT0V4mdHNCSlfuJBAr1fpIIs
GI-031 | 80924a33-4a16-48a0-adca-b2c3ad4fcbb1 | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPCR FAT module 6 : The Unistrat channels have sharp edges that lack protective covering. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636809&prj=643&rqi=UHUkauNeD6BT0ppkD4lky48I3I
GI-034 | 834cbf38-a38e-4dfb-bee8-ecfdef40b5ca | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Commissioning Issue | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ MU043â€‘RHKâ€‘XXâ€‘XXâ€‘SPâ€‘Mâ€‘XXXXâ€‘7002 â€“ Pipework insulation states in pointâ€¯5 of additional comments that: All internal pipework that is indicated as â€œnot insulatedâ€ shall still be insulated inside the building after penetrating the outer wall over a length of minimumâ€¯2â€¯m to avoid cold bridges and condensation. Currently there is no insulation applied and it was understood that no insulation will be installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636825&prj=643&rqi=8LgeBz9400gA1olleEDH3hVxpt
GI-035 | 29a72a2a-bb8d-4c84-8430-184e6a61c501 | MU04-3 | 643 | N-EMEA | Open | P2 Medium CX | mahmoud.kheira@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [7 empty] | PPCRâ€‘FWTâ€‘Moduleâ€¯06 â€“ Ensure any missing panel dimension drawings, wiring diagrams are provided within panels or attached to equipment before leaving factory. Ensure all panels have a documentation holder aa well. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636826&prj=643&rqi=AlOzsGHgAFRpTvJiWWLrlRbda3
GI-020 | a917a4a1-8af6-45bc-ad3a-5d27ed5f5e79 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPR-FWT: The WCC PRV pipework contains an unfilled hole. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635557&prj=643&rqi=xYiTIOH1XTV9sO6lzKTB3ijsX0
GI-019 | dde2d14d-ad64-47b2-adac-71fb567b6ca2 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPR-FWT : The DX unit installation is incomplete because the cable tray requires a notch cut out and the pipework lacks sufficient lagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635556&prj=643&rqi=jcFIaIhFfdit4FeRNkP5FUzxje
GI-021 | 426eeb35-bb54-4f5c-a51f-1978f28e33b9 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPR-FWT: Trip hazards are not marked throughout the pump room, creating a risk of falls. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635558&prj=643&rqi=C4qp2AiwVaCsO2aRi5ztZQaCvF
GI-022 | f6658a03-d46d-4f8e-bfc0-16587cfd35e2 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPR-FWT : The required external opening was not constructed within the room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635559&prj=643&rqi=wNCnQvttiaVhw3w6p2wTeWJVLz
GI-018 | 899603d8-5b8b-42f2-93e1-5135b5eabeff | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Cleaning | Commissioning | [7 empty] | PPR-FWT : The waterâ€‘cooled chiller is extremely dirty. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635554&prj=643&rqi=bBs1lHBaYrm71hjUYEDJZ4HUCN
GI-023 | 229e523e-4331-48c4-912f-2f9cb44eb0af | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [7 empty] | PPE-FWT : The condensate pipe lacks sufficient structural support, risking sagging or misalignment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635560&prj=643&rqi=7O2fy8n2oM2XNT3h00IFEJi9ES
GI-017 | fefefef9-08c5-4204-8f9f-bbc390fe556a | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [7 empty] | PPR-FWT : The exhaust fan has not been installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635553&prj=643&rqi=eHRIWlgFZLexxsDTFPD6TlGvEU
GI-016 | cdaefca0-6fc7-4f3b-b1fe-ca82f945d8f5 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPR-FWT : The WCC lifting anchors are no longer required and must be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635552&prj=643&rqi=c157tl8ITXSGLXx7ul3OBWRZzn
GI-015 | efa2a8f7-a216-429a-9925-27d6799c2c26 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPR-FWT : The chiller cables are not properly terminated, leaving an open connection point. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635551&prj=643&rqi=pGPKoAfNPkoFz2E7w3nsCml7AJ
GI-014 | dff7b482-35d9-4971-86c1-48adf95fe4cf | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPR-FWT :The expansion vessel is not secured to the system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635549&prj=643&rqi=3pxhjcqxZVQgldq7asmTC2ba8Q
GI-013 | cf84872a-d6d8-45ca-bfec-6f80878f8bd0 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPR- FWT : Sheet metal on base not secure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635548&prj=643&rqi=Wh2gt08Z0WxYOR2t7pN7zvSFtE
GI-012 | 1bdda098-81d5-43ce-ab23-6ebe4cc3f3d2 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPR -FWT : Pump glands are loose and incoming cables lack proper labeling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635541&prj=643&rqi=O4a53StPXekbgGwEJjs0VkXApx
GI-011 | e014f976-fa5b-47c9-b00b-35bd94b7975f | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPR- FWT : Chiller panel cables need to be fixed and labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635538&prj=643&rqi=4j1DG0oylqjcacWxMM3ahlZTv2
GI-010 | 3e80af53-636e-433a-a3d6-93cb592b5c72 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Incomplete Connections | Commissioning | [7 empty] | PPR- FWT : The distribution panelâ€™s stuffing gland opening is left unsealed, exposing the interior to potential contaminants. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635347&prj=643&rqi=l7QlKApnmvayrZHaXXoWGbAGMo
GI-009 | 0a0d6ee4-6834-4b61-bd6a-7f8abd7da1ac | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Labelling | Commissioning | [7 empty] | PPR-FWT : The system lacks traffic labels and flowâ€‘direction markings, making it impossible to identify correct flow paths or routing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635340&prj=643&rqi=khPnNwmSVtqxuUZsZnHSejZEFr
GI-008 | 58b256ae-f69d-4838-9b96-e3450e59638e | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [7 empty] | PPR-FWT : Valves lack clutch clips, preventing proper mechanical engagement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635336&prj=643&rqi=Rtq7YxWPk9rIP0VFUma3RGp39W
GI-007 | 785c23ba-3019-4b13-b9ab-cbfd522505e7 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [7 empty] | PPR-FWT : The primary pump isolator is poorly installed: the cables are incorrectly terminated, lacks torque marks, and the door is not earthed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635330&prj=643&rqi=7fLuHHjC5dbquCQFaLthcQwF7E
GI-006 | 921dac01-498b-49f7-b356-4b410fa78099 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Cleaning | Commissioning | [7 empty] | PPR-FWT : All assets are very untidy and require a deep clean, including the panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635328&prj=643&rqi=aUErnIIq132bhsjtRlb4g1id7j
GI-005 | 875d640d-299c-4f42-b18f-303968cf65c4 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Torque required | Commissioning | [7 empty] | PPR-FWT : The DCOS panel lacks torqueâ€‘marking on its earth connection, making it difficult to verify that the earth bond is tightened to the required specification. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635327&prj=643&rqi=V6rsW9UHQ7fYnWdfteH81KDehY
GI-024 | bc938fbb-8e3a-4625-90f5-6101a0501b08 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [7 empty] | PPR-FWT : No documentation has been provided for the refrigerant circuit, including pressureâ€‘test, evacuation, and charge records. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635563&prj=643&rqi=BzNOZuE0EZncKDVDIsS3ZoWbBt
GI-004 | e939a5ac-c4f3-44b4-a54d-3003dd5cbfbb | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | DCOS General Issue | DCOS | [7 empty] | The PPR systemâ€™s DCOS panel has inadequate trunking and cable management, leading to cluttered, hardâ€‘toâ€‘inspect cabling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635326&prj=643&rqi=iQdekNskzpvZYGb5g1H15LwX7D
GI-025 | 1802c999-93e5-4a76-a9bb-511128005222 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Documentation not issued/ Required | Commissioning | [7 empty] | PPR-FWT: The pump room lacks a declaration of conformity plate, and no conformity paperwork has been provided for any assets within the area. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635565&prj=643&rqi=xtK5glOwLWMmNsn6vTskD83l2C
GI-003 | 68765749-b62a-44a5-b7b5-edb4c41f4dfc | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [7 empty] | During the FWT of the PPR systemâ€™s, it was observed that the DCOS panel is fitted with a UK socket, which fails to meet EU electrical standards. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635293&prj=643&rqi=ztns03aMHoZilG7zs8ZgtttR5B
GI-002 | f4f0ce6d-a431-40f3-8db3-1e4a1953dffe | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Missing Components | Commissioning | [7 empty] | The PPR system has no earth bonding on the main structure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635290&prj=643&rqi=SRB6m6L2msd8Vx2jv7pnj9LhBC
GI-026 | 1ad5b512-91d6-4559-bcb3-63d6b806d622 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not correct | Commissioning | [7 empty] | PPR-FWT : Secondary pump isolator - very poor install cable needs re-terminated, no torque marks, no door earthing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635573&prj=643&rqi=azb5lV4Md6VsPNKOZqrTfzuDat
GI-027 | b331171a-45ad-4d76-973f-9becfc87901f | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPR-FWT : Compressor glands loose on WCC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635574&prj=643&rqi=qIHNpIjN552dhXBUi7vVgHU0ap
GI-028 | 09ea0b99-9046-46c5-98e9-6593a9093223 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPR-FWT : Mains cable on VFDs not secure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635575&prj=643&rqi=opdpRHQmORZVhpFolA6V1lzgcV
GI-029 | bc8bd7cd-f65e-4a17-be89-08aeb906ec54 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPR-FWT: DCOS cables require termination into WCC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635576&prj=643&rqi=mN4pb2uCFYw0gXyMt9kzmAQxQP
GI-030 | 0b633443-f41e-43a3-8343-6adf5b1c1c92 | MU04-3 | 643 | N-EMEA | Open | P3 Low CX | mahmoud.kheira@bureauveritas.com | 2026-08-26 04:00:00.000 +0400 | ARM -Armstrong |  | Installation not complete | Commissioning | [7 empty] | PPR-FWT: Cable terminated incorrectly, no torque marks, no bonding on frames. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635577&prj=643&rqi=qPJy6FGfxIO332gkl3CynTrOcx
GI-001 | 5631949d-61ab-4276-bb6e-66b063d84f42 | MU04-3 | 643 | N-EMEA | Ready for Verification | P3 Low CX | serdar.tuccaroglu@bureauveritas.com | 2026-04-28 04:00:00.000 +0400 | AER - Aermec |  | Design not as specified | Design | [7 empty] | Dry Air Coolers and Waterâ€‘Cooled Chillers have been selected by the vendor for seaâ€‘level operation. MU4.3â€™s site elevation is over 500â€¯m, and the vendor expects at least a 3â€¯% performance degradation per DAC due to the reduced ambient air density. DACs will also be used to cool the condensers of WCCs, but the impact of the higher site elevation on WCCsâ€™ cooling capacities is currently unknown. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619831&prj=643&rqi=zuhnIiNxUmHOP4i9iwvlteedhf
GI-455 | e48f834a-9347-4637-ad3c-a243a4817436 | NY03-2 | 560 | AMER | Ready for Verification | P3 Low CX | Christopher.Federico@veolia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor - BMS |  | Component/Equipment Failure | Commissioning |  |  | system | CHW System |  |  |  | CHWSTR-ALL: Recharge valve "failed to start" nuisance alarm occurred when thermal storage remained in recharge mode but valve commend was zero because actual was close enough to setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635767&prj=560&rqi=BJuagMniiff1BMzWaNq1WOen3J | https://equinix.facilitygrid.co.uk/x/project/560/system/11494
GI-444 | c760df9b-48de-4dd4-9d31-fe9f1b05ee26 | NY03-2 | 560 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [7 empty] | Maximo Asset Number updated under Maximo Asset ID for below assets. Maximo Asset ID should be kept blank in DCOS. NY3.011050T00_1CRAH_H_07 NY3.011050T00_1CRAH_H_09 NY3.011050T00_1CRAH_H_10 NY3.022060T00_1CRAH_G_19 NY3.022060T00_1CRAH_G_20 NY3.022060T00_1CRAH_G_21 NY3.022060T00_1CRAH_G_23 NY3.022060T00_1CRAH_G_24 NY3.022060T00_1CRAH_H_13 NY3.022060T00_1CRAH_H_15 NY3.022060T00_1CRAH_H_16 NY3.022060T00_1CRAH_H_18 NY3.01040000_1PDU_E_01_01 NY3.01040000_1PDU_E_01_02 NY3.01040000_1PDU_E_01_03 NY3.01040000_1PDU_E_01_04 NY3.01040000_1PDU_E_02_01 NY3.01040000_1PDU_E_02_02 NY3.01040000_1PDU_E_02_03 NY3.01040000_1PDU_E_02_04 Check thr files for more issues associated, wrong assigment, shifted ones, etc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634367&prj=560&rqi=0AIVyVLrzwuAu73gmMXvKs8Dy6
GI-452 | 0737b7d4-5224-4748-ad6c-df89d5755e55 | NY03-2 | 560 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Design Issue | DCOS | [7 empty] | Alarm Configuration to be updated by SI in graphics for all CRAHs. Screenshot attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634505&prj=560&rqi=q4ksZguAouNa8OqIizkBnka6CZ
GI-449 | f21b81e8-2616-41a5-bbcf-b91fe71b2fca | NY03-2 | 560 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Design Issue | DCOS | [7 empty] | Wrong Naming Format of the asset. 022203T00_1GEN_G_DATA. Attribute should not be in Asset name. Numbers overlapping the box in graphics. Screenshot attached. Wrong Maximo Asset Number assigned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634436&prj=560&rqi=3YBE1JpCxLFEHXdAg2m51zHsqu
GI-445 | e3b2d30c-b472-41a6-8988-7c413975cc11 | NY03-2 | 560 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS | [7 empty] | Tags not performed once. To be corrected by SI | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634372&prj=560&rqi=xPfTRTrYp05rRxTtd3ZYsT5pFU
GI-453 | 06217051-b202-478d-ae92-3c9ae28995a7 | NY03-2 | 560 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [7 empty] | UOM to be added by SI. Image attached. To be updated for all the similar asset type points | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634511&prj=560&rqi=1KoIBlNYWy6hny7NoL1rPpz7M7
GI-448 | 9f0f8704-320d-497c-a610-7a0290a47b1f | NY03-2 | 560 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Template Issue | DCOS | [7 empty] | Assets missing in DCIM. Please use the correct template and add into DCIM. Screenshot attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634396&prj=560&rqi=ZKOtV4QBmwvbugfTXQ9T9m3YBN
GI-446 | 19305c6e-3cf3-4ad0-9759-7cd001fe7021 | NY03-2 | 560 | AMER | Closed | P3 Low DCOS | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Design Issue | DCOS | [7 empty] | Misspellings of Display Name to be changed by SI. All Heat Trace, Transformer and PID. Sample Image attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634374&prj=560&rqi=Oahip1zeWAI4zkIGeqyNz9SoWb
GI-447 | 58a3303d-90d1-4089-b089-04c138f2853c | NY03-2 | 560 | AMER | Closed | P3 Low DCOS | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [7 empty] | Negative and/or Non-standard values found in few points. SI to Check and correct the values. Sample images attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634391&prj=560&rqi=OjxBEEKgbpcWHirVx27yDtI2uJ
GI-450 | 5166e8c0-cc12-42f7-8785-59d87851b168 | NY03-2 | 560 | AMER | Closed | P3 Low DCOS | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [7 empty] | Non-standard Display Point name needs to be renamed by SI. Iâ€™ve attached screenshots with comments for non-standard points from one asset of each asset type. Please use the Standard Points List to rename all applicable assets accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634487&prj=560&rqi=A3hTAHM6ZiS88kqS3idbTqTLVJ
GI-451 | 04d18311-1142-4162-84e9-d955efae4bca | NY03-2 | 560 | AMER | Closed | P3 Low CX | snijamudheen@ap.equinix.com | 2026-08-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [7 empty] | State_text to be added to missing int points by SI. file already provided also in another INC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634504&prj=560&rqi=rHf3MftaAhoYw1A1E3jwogQ4tK
GI-442 | aa9a71e0-9daf-4633-a8ba-23591f5671f2 | NY03-2 | 560 | AMER | Open | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-08-14 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [7 empty] | Aalogmonitor errors and warning clean up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633738&prj=560&rqi=XHREjMhWg7PYeBdXttWhQzoLvm
GI-443 | fd9a1874-cb88-426b-a1e2-c95bed3dae15 | NY03-2 | 560 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-08-14 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Design Issue | DCOS | [7 empty] | MSB alarms incorrect naming and attributes. - the name can not include the "alarms" word -the asset type is switchboard, not generic template -the attrs are not the required ones | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633739&prj=560&rqi=7bYZ91kLjj6v2xzP7E2P2JEiE4
GI-441 | e57209cf-f7bd-4901-bf53-524b953535b0 | NY03-2 | 560 | AMER | Ready for Verification | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-08-14 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [7 empty] | Topserver errors and warning clean up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633737&prj=560&rqi=Fly1NUKprTGG3QgjFq19VFInsh
GI-435 | be1ee007-3745-43eb-9ebf-12fc57ea9cf0 | NY03-2 | 560 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS - PUE kW/RT Total - The calculation is incorrectly adding the kW/RT of each Chiller. Should do a total kW/total Ton calculation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630001&prj=560&rqi=BrXtBrp6wzco0PCSANv5LzVWsB
GI-432 | 93a00367-4a13-4148-8eb6-6bf3720eac77 | NY03-2 | 560 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS - UPS - PHS indicated that battery runtime provides an out of range value when UPS is not on battery so they mask the value as zero. Discuss with Equinix if there are ok with showing "0" when UPS is not on battery. May rather show as "unknown" or blank. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629998&prj=560&rqi=Hvb1epJmKznuXsuBncwuULlz4C
GI-437 | e49a194c-b84a-4b0d-8977-2620b52a07f7 | NY03-2 | 560 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS - On the LBSB Single Lines - Change all the UDP X to UDPR X for the boxes shown on the R spine (between "Block R1" and "LBSB") | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630003&prj=560&rqi=qMHXypsU0iioAp8jcXBdqjEOJG
GI-436 | 8b83aac4-336e-41a6-a3f7-0944f74b15fc | NY03-2 | 560 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS - On the UDP Block Single Lines - Show the feeds from the primary UDP to the tethered UDP with a hyperlink to the appropriate UDP page) (ie. UDP-F1 needs to show a new feed to UDP-J1-1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630002&prj=560&rqi=SYDUIjHTqdA5VcJHVKkNyI1cQk
GI-429 | 9cede3a7-3fa5-4379-b935-22ab97206dd9 | NY03-2 | 560 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS - UPS - "Bypass Not Available" is showing as a Priority 4. I was under the impression that Priority 4 is only for Communications alarm. Confirm with Equinix. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629995&prj=560&rqi=iBGtUHfP9XLdFDn32aX6rJvzPK
GI-430 | 34014246-fd18-4150-a78f-ec102c5dc571 | NY03-2 | 560 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS - UPS - "Bypass Not Available" is only coming in on UPS-F1/G1 and not on UPS-F2/G2. Need to confirm if this is an equipment or BMS issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629996&prj=560&rqi=ALnbeX9W5qNQHlOJgiUJhdaB40
GI-426 | 744f582d-39e8-45fd-a5d7-b71124f53af3 | NY03-2 | 560 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS - Generator - Confirm the difference in the alarm registers for "Battery Charger AC Fail Alarm" and "Battery Charger Fault". As far as I can tell, we only have one alarm wired from the battery charger, so I am not sure what the second alarm would be. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629992&prj=560&rqi=kgpfETRJNW8nrZ4TcJvGW41V6r
GI-433 | cb6bc898-a76c-4e2b-bde5-ab036cd3350f | NY03-2 | 560 | AMER | Closed | P3 Low DCOS | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS - MSB - "TVSS Alarm" comes in on transfers to/from generator due to power loss on TVSS. Discuss with Equinix a time delay to override nuisance alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629999&prj=560&rqi=W6AkFBPdGyyTxbfAPfw60M3dO8
GI-428 | ff718c15-2b3d-4c97-8a43-149d3982c90b | NY03-2 | 560 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS - Generator - When generator is running, the "Summary" reads "Stopped, Auto, Alarm". Not sure why it would show "Stopped". | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629994&prj=560&rqi=kT0I6y8HHlv5mcv36skt5Juypn
GI-424 | 8dbb3f4f-bbf2-4e04-8369-07f124a8fe03 | NY03-2 | 560 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS - Certain alarms (ie. generator & UPS) are not coming into the alarm banner. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629990&prj=560&rqi=XdsFqPAG4TyAKLKlxqSC9FLkWo
GI-431 | 98db6a8e-ebe3-4a95-8254-bc9e6a1d6c1d | NY03-2 | 560 | AMER | Closed | P3 Low DCOS | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS - UPS - "Bypass Not Available" and "Inverter/Bypass Out of Sync" and "Warning" intermittently come in on transfers to/from generator. Discuss with Equinix a time delay to override nuisance alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629997&prj=560&rqi=Wtj4TuBpwudXbQq4AlvhDSBH0r
GI-427 | 18878a27-ba71-4607-b314-457bcf362bb3 | NY03-2 | 560 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS - Generator - "Fuel Hours" show alarm and 0 when generator is running. Should show an actual value with no alarm. Also discuss with Equinix if there are ok with showing "0" when generator is not running. May rather show as "unknown" or blank. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629993&prj=560&rqi=hvOWqJR80cJD7f2hChYrzwsLNY
GI-440 | a3e3600a-4f0e-4137-a037-7a5672bbfabf | NY03-2 | 560 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS - RMU - The BARD unit template shows two units with a lead/lag setup but the actual controller only has one of two units connected. Recommend discussing with Equinix to update template to show just a single unit with no lead/lag. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630006&prj=560&rqi=2s9jQg5e1c5jbzXTRx9a8PkF4T
GI-425 | 2a1c46d7-d9d2-4a96-9400-ececbb04dfd3 | NY03-2 | 560 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS - Generator Faceplate - The acknowledge buttons disappeared from the Faceplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629991&prj=560&rqi=Hn0h39ymdaJVwwqYoWoG5wZV25
GI-439 | c3310796-48a9-4a3c-97b7-913be085045c | NY03-2 | 560 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS - Chiller - The timer for the recharge valve to open stopped at 234 seconds on the graphics though it appeared to run in the background and valve opened after the approximate 300 seconds. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630005&prj=560&rqi=vlkWUuYKmLguuaYeRmfQd2Cyrb
GI-434 | c1dbe8a4-16a9-4ee7-9de4-d1f55ca3282a | NY03-2 | 560 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-07-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS - PUE kW/RT - The calculation is incorrectly using input kW divided by runtime hours should be kW/Ton. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630000&prj=560&rqi=GuskIalHD8BuhOQCfa6hlBxchX
GI-423 | 390d4af4-1b95-4fcf-acf1-f2b2c2371040 | NY03-2 | 560 | AMER | Closed | P1 High CX | steve.mulakkal@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning | [7 empty] | During Electrical Pre-IST, the UDPR-G1 Main breaker was opened to simulate an 180 degree Out of phase transfer on the G1 STSs. However, when the UDPR-G1 main breaker was opened the following occured. - STS-G1-1, G1-2, and G1-3 transferred from S2 to S1 (Expected Response) - STS-J1-2-1 and J1-2-2 transferred from S2 to S1 (Expected Response) - STS-E1-1, E1-2, E1-3, E1-4 serving customer load transferred from S1 to S2 (Unexpected Response). - UPS -E1 registered a "INV Volt Abnormal-TR" alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629239&prj=560&rqi=I5WMxQvLNeR1P94QnYvyc7Vq9b
GI-422 | 48ca568a-9da3-4b07-8350-941ef05d47b6 | NY03-2 | 560 | AMER | Closed | P3 Low DCOS | jreitz@equinix.com | 2026-07-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCIM Platform issue | DCIM | [7 empty] | Yesterday we looked into and opened a ticket for Topserver at the NY3 site to address an issue with Quick Client. We did some initial investigation to better understand the problem and quickly realized that Quick Client is not connecting to Topserver. We captured a few relevant screenshots of the error, along with UAExpert successfully establishing a connection. The ticket opened with Software Toolbox (CASE Number #46222848275) describes the issue and includes the screenshots. It took a bit of time to gather the required information and work through their bot. It referenced a couple of knowledge base articles which were helpful but did not address this issue, and then connected us with John, a Technical Application Consultant. John walked us through a few additional steps to gather more information, including screenshots of configuration settings and, this morning, a basic set of logs. As he explained, Quick Client connects to Topserver using OPC-DA, while UAExpert uses OPC-UA, which explains the difference in results between the two tools. His next step in troubleshooting is to investigate a potential COM/DCOM permissions issue, despite everything running under the local system account. OPC-DA is enabled, and the configuration appears to be correct. Weâ€™ve submitted the log files and asked what indicators might point to the failure, as well as where we can find resources to review the logs on my own. We will keep you updated as we learn more. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627718&prj=560&rqi=2DPalPBqqWK0e64LS1pMXZvMbS
GI-419 | 25e29c80-a3d1-4644-87ab-3cf8739d8574 | NY03-2 | 560 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-06-23 04:00:00.000 +0400 | General Contractor |  | General Design issue | Design |  |  | equipment type |  |  |  |  | Generator Fuel Supplier pipe pressure - RFI#30 - pressure issue with the generator fuel supply line inside the generator enclosures specifically between the check valve and the high level solenoid valve. When the solenoid is engaged due to a tank high level alarm (set to 90% of usable fuel) the heat of the solenoid transfers to this section of pipe and builds pressure. Under this condition this section of pipe in generator C experienced a leak when the pipe pressure surpassed the pressure gauge rating. The tank high level alarms do not automatically clear when the conditions are met (ie the tank fuel level drops below the high level) and will require an operator to manually clear at the fuel supplier panel HMI. At this point and to alleviate the current issue, if a generator fuel tank enters high level alarm the operators can transfer fuel into a lower level tank to exit the high condition and clear the alarm at the fuel panel; however this would require constant monitoring of the fuel system if fuel levels are maintained close to 90%. Outside air conditions and generator runs will also affect the tank fuel temperature and may cause fuel levels to increase or decrease. In the case mentioned above for generator C, the high level alarm and solenoid were active for long enough to build temperature/pressure in this line and break the pressure gauge. One potential solution would be installation of a pressure relief line from the fuel supply line to the fuel polishing return line, as this is open to the tank; similar pressure relief lines have been installed on the NY5 generator fuel supplier/polisher lines. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626566&prj=560&rqi=75vNu4H9nFWN0rp6N5EZySJQGw
GI-417 | 2b316e8e-f55a-4293-a44a-68349654c4ad | NY03-2 | 560 | AMER | Ready for Verification | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - DCIM Quality | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626401&prj=560&rqi=5Fn1DjLqO5R9udgBe0bKDg3ikz | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-415 | 9ffa97bb-70f9-4b64-b225-3e60feb9750f | NY03-2 | 560 | AMER | Ready for Verification | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - DCOS Accuracy | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626399&prj=560&rqi=wSYjyIOfvbUFxmWEyfoEZdj5bG | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-418 | ea17b751-02bb-4c33-af79-7867aa8745a5 | NY03-2 | 560 | AMER | Ready for Verification | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - Asset Mapping | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626402&prj=560&rqi=ghM8p0ONqLbU9Zh4puBH7XSZI4 | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-414 | f24355e3-d694-4853-8403-a9a9306e7a7d | NY03-2 | 560 | AMER | Closed | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - DCOS Quality | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626398&prj=560&rqi=1lfRwlcH7mqLFVX0oih2EtfKBi | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-416 | 6ccd3ed0-2529-42e7-8127-3741cd14e800 | NY03-2 | 560 | AMER | Ready for Verification | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - DCIM Config | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626400&prj=560&rqi=ABb6jedHNWRxJTPDfAE6pDUfj7 | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-413 | 5d186a9d-f1f3-4f3e-afb8-57dc720aab29 | NY03-2 | 560 | AMER | Ready for Verification | P3 Low DCOS | jreitz@equinix.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | DCOS - DCIM Validation not completed - DCOS Config | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626397&prj=560&rqi=T5HR0M0gMxq5gTUvzn59ysinlx | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-411 | 3992065e-600b-40cf-bc36-e451b965df0e | NY03-2 | 560 | AMER | Closed | P3 Low CX | kyle.vogt@veolia.com | 2026-06-12 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | Transformer 1 Over Temperature and Transformer 2 Over Temperature Alarms are present locally but are not present on BMS for F and G PDUs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625142&prj=560&rqi=0xy8XuQGWsfO0qYeRc2Sb9k8hL
GI-409 | c26f9282-efa7-47a1-8576-b0a552e90cac | NY03-2 | 560 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Installation Not Complete | DCOS | [7 empty] | DCOS-DCIM Validation NOT COMPLETED Check the attached files for reference, but the Validator tool is the real source of truth: https://onboarding.dcim.corp.equinix.com/ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624915&prj=560&rqi=CjhJP8Pj4EYLYr313flOuzUqDi
GI-410 | 25a5494f-597c-4a44-b459-26de6c3d15b9 | NY03-2 | 560 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | All Electrical Skid CRAH's: The Electrical Skid Graphic at Skid F and Skid G always displays all CRAH's to have an M, indicating manual mode, whether or not the CRAH is actually in Manual Mode or not. The M on the graphic should appear only when the CRAHs are in Manual Mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624950&prj=560&rqi=8dndrUNoTD3G203HMqlNK15krx
GI-408 | 6a246f80-b428-4c35-92fa-9d17de886a09 | NY03-2 | 560 | AMER | Closed | P2 Medium DCOS | manuel.gomez@eu.equinix.com | 2026-06-09 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS General Issue | DCOS | [7 empty] | DCOS - DCIM Onboarding validation is not completed. Attached are the reports for evidence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624482&prj=560&rqi=82IrGRJwWqDJBATVKNyf8vLsRQ
GI-404 | d1935931-c01d-4841-ba2a-cc3fa1748c9a | NY03-2 | 560 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor - BMS |  | Component/Equipment Failure | Commissioning | [7 empty] | PDU-H1-2-2 - Initially this PDU was not communicating to the BMS. Upon troubleshooting, PHS discovered a bad ethernet cable between the PDU and the IBX network switch. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623986&prj=560&rqi=Mt3nHqA4fFD3KcyNZhR9TljwSD
GI-405 | 53791da1-a39e-4661-b912-d0b62650da92 | NY03-2 | 560 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-06-04 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Component/Equipment Failure | Commissioning | [7 empty] | PDU H1-2-1 Breaker 1 - Breaker is not communicating to the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623987&prj=560&rqi=eQJevkrjdR4ZKYPYY5hMylM8CO
GI-406 | cae02119-3788-49bf-a734-e9899c066b30 | NY03-2 | 560 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-06-04 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Component/Equipment Failure | Commissioning | [7 empty] | PDU H1-2-1 Breaker 2 - Breaker is incorrectly displaying a voltage of 375V when all other breakers are reading 405V. Hanley to investigate and rectify the issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623988&prj=560&rqi=EsJMZTwWcZmeXH6h1wexBg3Pfx
GI-403 | 748c8228-aa82-4e81-9f15-ec5e6bac134f | NY03-2 | 560 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - Electrical |  | Incomplete Connections | Commissioning |  |  | equipment type |  |  |  |  | PDU-H1-2-1 Breaker #6: While load banking the PDU, the A-phase pigtail connected to the load bank on CB6 reached 350 degrees F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623734&prj=560&rqi=MZnXc7tHj9KKW2uhBl6WdsIXJF
GI-402 | 4a606075-4072-4a07-88d8-c86d842b51f4 | NY03-2 | 560 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-01 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [7 empty] | DCOS - DCIM Validation not completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623552&prj=560&rqi=pqlHjA23RrDHPdy2GP7aFV6OeA
GI-399 | becd3057-8439-4c99-8d71-70c4547dcdd3 | NY03-2 | 560 | AMER | Closed | P3 Low CX | steve.mulakkal@veolia.com | 2026-05-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Component/Equipment Failure | Commissioning | [7 empty] | UDP-G2 (Spare Breaker): Lockout tab is stuck and can not be pulled out to LOTO breaker. Issue was originally discovered on STS-G2-2 breaker. and lockout out tab was replaced with part from spare breaker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623225&prj=560&rqi=6SbOtfTWkewyUM6QUpP8WnZGi4
GI-396 | 9e08787f-4200-4caf-b7c4-5b8a3b941a2e | NY03-2 | 560 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | MSB-"X" Alarms Symbol / Block E Graphic / Block C and D overviews include a "MSB-X Alarms" symbol and corresponding faceplate, but this is not included on Block E at this time. Does this need to be included on the Block E overview page? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622684&prj=560&rqi=LN8hPVMNMsVbNcV7h7Zx1TP4Kw | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-392 | f2ba0fbd-54ff-4aa7-bf17-25f7be9bf460 | NY03-2 | 560 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCIM |  |  |  | De-icing Manager - Fan Direction control timer analog input boxes - can not be edited from the faceplate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622680&prj=560&rqi=OMcbfQDqCKSCO3opzQygNHohQL | https://equinix.facilitygrid.co.uk/x/project/560/system/11779
GI-394 | bdfb987c-7ed9-4b26-a82c-c5b86f0a2d97 | NY03-2 | 560 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-05-21 04:00:00.000 +0400 | Design Professional |  | DCOS Design Issue | DCOS |  | Controls | system | DCOS |  |  |  | MUW-PMP-1 & 2 / Makeup Water Overview - Flow switch proves flow without the pump operating, head pressure from storage tanks is high enough to make up Cooling towers without starting pump - Pump in alarm on BMS currently sending "fail to stop" even though pump is not running. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622682&prj=560&rqi=pH6ZDDw7DUMfWSOiEux903gZQZ | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-393 | abe8489d-c6ca-4f9c-b063-f2ca443c40e9 | NY03-2 | 560 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS |  | Controls | system | DCOS |  |  |  | CWWT-A-01-CP-1 / Makeup Water Overview - Not communicating to BMS; MCE to check | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622681&prj=560&rqi=cr5O3q2LTWRzDlPjUpPnaZhXr9 | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-391 | ccb6085d-e49c-4eed-a451-7a2e2a9f8756 | NY03-2 | 560 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | Data Hall First Floor Area B East Graphic - Graphic needs to be updated by removing the half hot aisle closest to CRAH-F-1. See attached screenshots based on latest design documents. This may cause confusion since there is no CRAH hot aisle temperature sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622519&prj=560&rqi=K7QQ3lmhiF5eWd0mRvEJJ9EQcH
GI-388 | 5da357c4-276f-4035-b92b-83b45cd58afc | NY03-2 | 560 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-05-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Incomplete Connections | Commissioning |  |  | equipment type |  |  |  |  | WSHP F1, F2, G1, G2: Tripping the smoke detector does shut down the unit. MPS needs to update their wiring, so that a trip of the smoke detector is latching and remains in alarm until it is reset. Using the test button, the unit alarms until you remove your finger from the test button, and the alarm instantly clears. Similar issue we had with WSHP's E1 and E2 in the past. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622496&prj=560&rqi=vLU1Wk07Ou5s5Zo3k8nX6JKXeJ
GI-384 | f2dda411-5c3e-4c33-af4e-629f0eb956fb | NY03-2 | 560 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-05-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment type |  |  |  |  | Electrical Skid CRAH's: Supply air Hi and Supply air Lo setpoints are unable to write to on the BMS and do not display the correct values on the BMS. Correction: We are now able to write the BMS, however the unit itself does not take the setpoint value. There is no correlation between BMS setpoint input and actual unit HMI setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621227&prj=560&rqi=ueVymuLV9IzeUmPPDtDW7wBpiu
GI-383 | 4436353c-3b24-471d-ae2d-ce8469063e7b | NY03-2 | 560 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-05-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment type |  |  |  |  | Electrical Skid CRAH's: Cannot place units into manual mode from BMS. Changing the unit int manual mode from the HMI also does not correctly update to "Manual Mode ON" on the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621226&prj=560&rqi=LasznuzEtCt0aktjBmh5bqugNP
GI-382 | f6d9cca1-6fbf-4892-9d67-94049a190240 | NY03-2 | 560 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-05-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment type |  |  |  |  | Electrical Skid Delta CRAH's: Cannot write a supply temperature setpoint to each E-CRAH. The BMS also does not display the correct Supply Temperature setpoint value. Correction: We are now able to write the BMS, however the unit itself does not take the setpoint value. There is no correlation between BMS setpoint input and actual unit HMI setpoint. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621225&prj=560&rqi=KfPjuDRgFJB3sjPIciM19QBdnT
GI-377 | 1be0eb1a-136e-e4ad-1943-11eb41474f7d | NY03-2 | 560 | AMER | Closed | P3 Low CX | kyle.vogt@veolia.com | 2026-05-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Not Complete | Commissioning |  |  | equipment type |  |  |  |  | 1PDU_J1_2_1: ground cable lug damaged and disconnected from ground | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620823&prj=560&rqi=GNpmoQB8RyscVuuCSCKtbWjKvB
GI-370 | 2ed35c8c-1331-49c0-85bc-98dfe877a1f6 | NY03-2 | 560 | AMER | Closed | P3 Low CX | william.park@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Not Correct | Commissioning |  |  | equipment type |  |  |  |  | Data Hall CRAH's: Total CFM value is reading ~4500 CFM when all fans are powered off. When failing one fan, the current total CFM value would remain. In most cases, it appears that the HMI is presenting the average CFM output of each running fan and multiplying it by 4, even if only 2 fans are running. However, when failing all the fans from the breaker on a running unit, the total CFM indicator still reads 4500 CFM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620310&prj=560&rqi=50bch4MvvLpyz4pTF0iMbca3oV
GI-369 | f958d418-19a2-4700-a51e-acb65b591da2 | NY03-2 | 560 | AMER | Open | P3 Low CX | Christopher.Federico@veolia.com | 2026-05-01 04:00:00.000 +0400 | Equinix Project Manager |  | Installation Damage | Commissioning | [7 empty] | STS-JX-X: STS damaged during transport. Makes opening and closing unit very difficult. Delta to provide a quote for repair. (unit designation TBD) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620118&prj=560&rqi=Hf5hltbSwz5CdJgLRt2dSmc0Iy
GI-367 | 4470b6df-9ac9-4915-b97d-5aa6244d65ba | NY03-2 | 560 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor - Mechanical |  | General Design issue | Design |  |  | equipment type |  |  |  |  | Fuel Supplier/ Fuel Polisher - Upon MSB transfer to generator or Utility power, the respective pnuemercator is power cycled and sends alarms to the fuel supplier - critical low, low, full, high, and critical high alarms. These alarms are nuisance and require operator manual reset at the fuel panel. ISP has added a 30 second time delay to avoid these nuisance alarms on power transfers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619770&prj=560&rqi=kKPPLgH5tFqHozhuUDFWeQfJiT
GI-365 | 1efb8576-39f9-481a-829e-387cf906c696 | NY03-2 | 560 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-04-24 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS | [7 empty] | Phase 2 - BMS "Electrical One Line overview" page need to be updated for Blocks E, F, G, H to properly display the UPS to IOB breaker line animation. See attached images for discrepancies to match Blocks R1, A, B, C and D. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619348&prj=560&rqi=K9B2Ig8UJBYlx0QvyZolTF0Rkc
GI-395 | 7ba6c9cd-5a09-44ca-bd72-b679eb786990 | NY03-2 | 560 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-03-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS |  | Controls | system | DCOS |  |  |  | PDU-C-1-1 / Electrical One-Lines / Faceplate and graphic are different between phase 1 and phase 2 equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622683&prj=560&rqi=QhQBr29wuQGX88mdAXtBO5LU1M | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-340 | 8abdc314-f9c5-430c-ac52-0b5b340c2555 | NY03-2 | 560 | AMER | Closed | P2 Medium CX | steve.mulakkal@veolia.com | 2026-03-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | Phase 2B - All PDUs - Lexan covers for PDU bus protection is missing on majority of Phase 2B PDUs. Hanley to provide and install all missing Lexcan covers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615868&prj=560&rqi=uWPuXFSYb6E2kazdCgMV4lrpcS
GI-335 | 08f5b49d-21d2-4001-a21a-0ded2e7d85dc | NY03-2 | 560 | AMER | Closed | P2 Medium CX | nicholas.leber@veolia.com | 2026-03-11 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Comms Issue/Fault | DCOS | [7 empty] | Phase-2A - Chiller Manager - After completion of IST, the "number of chillers required" analog input box would not accept a changed value from OM11 BMS screen. The signal would send from OM11 and start the next in line chiller skid, however the chiller would shortly stage down as the manual input did not hold; rather it reverted back to the original value. Through troubleshooting, determined that OI01 and OM01 were overwriting this point. This issue was previously resolved prior to IST during the points mapping transfer effort reverification. This issue is now resolved, PHS removed the input from OI01 to OI11, such that the manual input to this "number of chillers required" is resolved again. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615344&prj=560&rqi=8OjHrcRtEaRhBuDGdcb7Tng7Db
GI-333 | 465525a4-b0ef-0ca3-49f8-9f7c209c3efb | NY03-2 | 560 | AMER | Closed | P2 Medium CX | Christopher.Federico@veolia.com | 2026-03-05 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | Phase-2B - PDU-J1-1-1: Breaker 01A, B-Phase on the breaker is testing 1200+ micro ohms while A and C phases are testing at <350 m ohms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614840&prj=560&rqi=WHc69WzK7FfFuqWOi3njhBmmaZ
GI-397 | af2b2c75-65af-40e5-957d-654a9d124d63 | NY03-2 | 560 | AMER | Closed | P3 Low CX | jreitz@equinix.com | 2026-03-04 04:00:00.000 +0400 | General Contractor |  | DCOS Comms Issue/Fault | DCOS |  | Controls | system | DCOS |  |  |  | 00027T00_City Water_PMP - Aveva Floor Layout - Popup Faceplate - Failure to communicate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622688&prj=560&rqi=hc0amjMHb8CC4SZbJ0NXJLg1bS | https://equinix.facilitygrid.co.uk/x/project/560/system/12623
GI-329 | 28ece7e6-a7cb-463c-b9d0-a9dc4ca79680 | NY03-2 | 560 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-02-13 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [7 empty] | MAU-B2 - Unit was still addressed by both the new and old OI Aveva systems causing conflicting control signals - which may have resulted in the damper actuators dysfunctionality and condensate build up in the unit. This was previously caught on MAU-A1 - mode control was not constantly fluctuating. This issue should now be closed, as PHS confirmed the old OI is no longer writing to MAU-B2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199219&prj=560&rqi=eueTPysfxl3sR2H7oid1tLip1e
GI-324 | 7ea3a2d8-7db8-45d4-8cd9-3d106b15812b | NY03-2 | 560 | AMER | Closed | P3 Low CX | nicholas.leber@veolia.com | 2026-01-28 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | PHASE-2A - Generators C & D - Fuel system page displays a leak alarm for both of these generator tanks, although there are no alarms at either generators or Pneumercators. Need to confirm if correct modbus point is used for this alarm and/or if point needs to be inverted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197784&prj=560&rqi=0UmqUspk8fW4qNXDCTcaI3BOC1
GI-279 | 02e777e1-83a9-49f7-aeac-97c98afe14d1 | NY05-P2 | 527 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-17 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [7 empty] | DCOS-DCIM Validation did not pass. Attached the doc as evidence and linked it below to the online tool. https://onboarding.dcim.corp.equinix.com/dataflow | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625659&prj=527&rqi=IAywROB4xNT9t0Ud7XrNMzLF4P
GI-269 | 6d77f1ae-d0ec-427a-9ef0-59550505ac8d | NY05-P2 | 527 | AMER | Closed | P3 Low DCOS | jreitz@equinix.com | 2026-06-08 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | Shows an alarm on sensor 2 when the value is within the acceptable range. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624326&prj=527&rqi=GvNYrccQZlwbnlyAvqN4jBoR7M | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-262 | a0933077-64ed-4dac-b57a-4463bd9fd421 | NY05-P2 | 527 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | We can not export the logs for topserver neither the project as the system have a poor performance and its crashing due to the huge amount of errors | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623748&prj=527&rqi=KHsmwVvaPZGGvpI53KpVhs6kmU | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-261 | ef715d3d-7ba5-46af-815d-2e03cc117dfa | NY05-P2 | 527 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Installation Not Complete | DCOS |  | Controls | system | DCOS |  |  |  | Missing PUE link on the home page, and the script is not using the latest standard either. Assign to PHS team, they are not currently on the list to assign | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623747&prj=527&rqi=46RFgCjTT8nLUoHfalleo5pkc7 | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-260 | c64a904e-7454-4f0c-9b0d-ce46beebd3fe | NY05-P2 | 527 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS |  | Controls | system | DCOS |  |  |  | Graphics not aligned as per stds. Numbers over lines. check screenshoot | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623740&prj=527&rqi=PH6dVp1cp9f57vpCveJlPnofaa | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-263 | 8c4e080b-8c1b-4cd3-b311-7524777f10d5 | NY05-P2 | 527 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS |  | Controls | system | DCOS |  |  |  | Links from different objects are not going to the proper page, eg Gens | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623749&prj=527&rqi=oZszjyhTQOeTGHDhn4JMa5gk06 | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-264 | b87ef1d0-e38d-4136-abeb-04ab3945b6d6 | NY05-P2 | 527 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Design Issue | DCOS |  | Controls | system | DCOS |  |  |  | These two alarms from the GENs must be suppressed if the GEN is not running : Frequency not within limits Voltage not within limits | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623750&prj=527&rqi=d6wOOJMVgnopm6Xe5cfdGFq6WF | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-278 | 95bfcebb-eec6-45c3-b0d4-e1de0671e680 | NY05-P2 | 527 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-05-26 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | Generetor Breaker Open and MSB switch not in AUTO are both stuck in initializing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624335&prj=527&rqi=Ny0hQeTyFcFHceDSyRIumpw4g3 | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-277 | fd2ba292-836e-4efa-b4d0-bf026bfddf39 | NY05-P2 | 527 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | When trying to control the electric room RTUs if you click on the unit it opens a faceplate with no actual controls other than to put the alarms in maintenance mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624334&prj=527&rqi=IkLsdd8KTF9ZvMpRxT1Eafbhn4 | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-276 | 377579ae-c9d2-401c-a2a2-2279640f989f | NY05-P2 | 527 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-05-08 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | TL:DR The system does not react to massive water use in an effective way. Recently on hot low humidity days we have been having a major issue with draw down on the MUW tanks. The system is not balancing correctly. City water pressure is varying wildly. The system needs to maintain a bare minimum psi of 22+ in order to replenish the tanks and lift to the roof. However maintaining that pressure requires significant valve manipulation. On 5/6 we burned through ~60k gal of water in the tanks before 11am. LC_PRIMUW_03 and LC_PRIMUW2_03 were open to >65% but the recirc valve PC_PRIMUW_04 was also open about 30% and the city supply valves were open to LC_MUWT1_03 ~13% and LC_MUWT2_03 ~30%. PSI was very lowon the city side of MUWT1_03 <20, but pretty high on MUWT2_03 >35. Tank levels were down to <163K per tank and dropping quickly. The Stilling basins had also dropped to below 12" By closing the recirc PC_PRIMUW_04, opening city feed MUWT2_03 to 100%, and setting city feed MUWT1_03 to 18% we were able to drive all PSI to >20 and start to reverse the draining of the tanks. My ask here is why the system was not modualting the valves to slow or reverse the tank loss? If those tanks had continued to drop at that rate and the conditions existed for more than a day we would have been in serious risk of running out of water. Is there any logic in the system to look at the tank depletion rate and open the city valves as far as they can be while still maintaining lift pressure? Once T2 was open to 100% and started reversing the water loss we opended the bypass valve which in turn slowed and then stopped water loss in T1 even though we could only open MUWT1_03 to ~18%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624333&prj=527&rqi=YYMLQjcR63yAIYFR6LE390AH4e | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-275 | bc3bf40e-de42-4ec5-aa6f-a2686707833f | NY05-P2 | 527 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-05-07 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [7 empty] | the history service is not running on OM11 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624332&prj=527&rqi=EQM2CoIp4xkE7lMCEMqUuPX7QN
GI-258 | bf6b847f-033a-4dbf-a328-4b7825e4de3d | NY05-P2 | 527 | AMER | Closed | P2 Medium CX | moutaz.abdelhamid@veolia.com | 2026-04-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | BATT-E2 | UPS Battery |  | X8U6UF75XD4806P35020X06MT16 | The end-of-life (EOL) was 21+ minutes, exceeding the expected 19 minutes. However, battery 13 of string 6 dropped 1V between minute 19 and minute 21. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618765&prj=527&rqi=vJJFTK1c0UNVBS09O1IKxYrzju
GI-274 | 04345cc3-a017-41dd-bbc4-d2ac67bb05d2 | NY05-P2 | 527 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-19 04:00:00.000 +0400 | Equinix Commissioning Manager |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | If you move the mouse off of a face plate, while attempting to change the value in any numerical text box contained therein, it will result in the disappearance of the "AnalogUserInputAnimation". The value can still be edited but only by using the keyboard while avoiding moving the mouse. The issue also occurs when attempting to edit values in boxes on the main BMS screen, such as in the Liquid Cooling Skids page, but it seems to be more forgiving. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624331&prj=527&rqi=A5hYLOKG2vzgrEPdcygEkfHbuP | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-273 | 37387147-29e1-411f-9eff-c7f904030d25 | NY05-P2 | 527 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-18 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | If one tries to change the command of LC_MUWT1/T2_03 in manual, the window where you can adjust the value disappears as you scroll over it | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624330&prj=527&rqi=rSK9lJGwc8fqQF2YkX4lUJrSci | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-272 | a329eb12-946a-490e-979d-770d3570af94 | NY05-P2 | 527 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-17 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | Loss of comms on both STSs. The Loss is constant on 3 intermittent on 4. The screens on both STSs are functioning properly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624329&prj=527&rqi=sm1BMWffWxdaLd00X4bJXqAb8G | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-271 | d1b99c8e-1d24-4547-8523-9594fc36daf9 | NY05-P2 | 527 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | Meter disable checkboxes are backwards | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624328&prj=527&rqi=c9DnwDL31YmAxWua2RTRCvZDTj | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-266 | e550184a-eb70-4f4c-af0d-5991bd8dd8e1 | NY05-P2 | 527 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [7 empty] | Setpoint of 190,000gal with a deviation of 10gal for hi and lo alarm. Deviation should be a percentage not a unit measure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624323&prj=527&rqi=iPW28xL8vVnFZqzSkJ0rnN4Gzf
GI-268 | e4824ba5-3f6f-4344-bc95-527aa0fb2072 | NY05-P2 | 527 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | Shows a chem treatment alarm with no other information what does this reference? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624325&prj=527&rqi=0s4Th0ejQx2efxf6CGPz8QtlIK | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-267 | a937b782-4d8b-44ec-8ce9-e585f55e506e | NY05-P2 | 527 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [7 empty] | Setpoint of 190,000gal with a deviation of 10gal for hi and lo alarm. Deviation should be a percentage not a unit measure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624324&prj=527&rqi=2xV5Xwor1I2QhYdtEqUQDu6cBj
GI-270 | f36b8c63-48ef-457e-9c98-cb462b214107 | NY05-P2 | 527 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | MSB header doesnt show what the values listed represent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624327&prj=527&rqi=6DYptdci1zfF8uFUOCc8SRz264 | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
GI-265 | 220d7eee-7406-4ae6-8e33-4231a9e56db2 | NY05-P2 | 527 | AMER | Closed | P2 Medium DCOS | jreitz@equinix.com | 2026-04-15 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  | Controls | system | DCOS |  |  |  | Cooling Tower Stilling Chamber Level Setpoint is not adjustable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624322&prj=527&rqi=dALuE7oW1mgoXAoSmIKzgVMt1L | https://equinix.facilitygrid.co.uk/x/project/527/system/12624
FPT-45-001 | a0bedd13-c859-4a00-993e-8016e0cc0318 | NY05-P2 | 527 | AMER | Closed | P1 High CX | moutaz.abdelhamid@veolia.com | 2026-04-14 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Design Issue | DCOS |  |  | equipment type |  |  |  |  | UPS H Mech does not appear to have an MBB mapped or available. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618154&prj=527&rqi=s91WuROeuv9AC0RiTo42duvdIR
FPT-45-002 | 66647bfa-ced9-490a-8dcc-d552d2240d2f | NY05-P2 | 527 | AMER | Closed | P2 Medium CX | moutaz.abdelhamid@veolia.com | 2026-04-14 04:00:00.000 +0400 | Owner | L4 | DCOS Comms Issue/Fault | DCOS |  | Electrical â€“ LV | system | H Block |  |  |  | UHD-H1 & UHD-H2 - MIB and MBB breakers are not reading voltage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618157&prj=527&rqi=xWdWePZbe1DunAAsUCQg3UtRIX | https://equinix.facilitygrid.co.uk/x/project/527/system/14170
GI-254 | 8b83b069-a011-45b7-aa21-6b0937df55ab | NY05-P2 | 527 | AMER | Closed | P1 High CX | moutaz.abdelhamid@veolia.com | 2026-04-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Not Correct | Commissioning |  |  | equipment type |  |  |  |  | UPS-E system design has been revised from six (6) VRLA battery cabinets to five (5). Confirm whether the existing single set of 4/0 cablesâ€”originally sized for six cabinetsâ€”remains adequate for the system with five cabinets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617227&prj=527&rqi=VYOlTOsht0qtzM2G8LEdewn7Y6
GI-252 | 44903037-f998-4bd9-aedf-231214591376 | NY05-P2 | 527 | AMER | Closed | P2 Medium CX | moutaz.abdelhamid@veolia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | Electrical â€“ LV | system | E Block |  |  |  | Arc Flash stickers currently installed are temporary. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616718&prj=527&rqi=kFiWTlcuzSwE7HVd4w56Yu0dI3 | https://equinix.facilitygrid.co.uk/x/project/527/system/11048
GI-248 | 7f02e272-3130-4614-b53a-d4eab9ae385a | NY05-P2 | 527 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning |  | Electrical â€“ LV | equipment | BATT-H2 | UPS Battery |  | 128S | Missing Labels for all strings on battery cabinet H2 Battery H2-1 Battery H2-2 Battery H2-3 Battery H2-4 Battery H2-5 Battery H2-6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616444&prj=527&rqi=8THlYLXYSLxD93lWxqXgNiOUkm
GI-247 | d8208375-ac7b-4a50-ba02-1f456d541526 | NY05-P2 | 527 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning |  | Electrical â€“ LV | equipment | BATT-H1 | UPS Battery |  | 128S | Missing Labels for all strings on battery cabinet H1 Battery H1-1 Battery H1-2 Battery H1-3 Battery H1-4 Battery H1-5 Battery H1-6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616443&prj=527&rqi=da6gVHTh0oLqXLAWLKj1CiDYDW
GI-246 | 6e1d7ed5-2b01-41fe-8bf6-5921003dcba7 | NY05-P2 | 527 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning |  | Electrical â€“ LV | equipment | BATT-E2 | UPS Battery |  | X8U6UF75XD4806P35020X06MT16 | Missing Labels for all strings on battery cabinet E2 Battery E2-1 Battery E2-2 Battery E2-3 Battery E2-4 Battery E2-5 Battery E2-6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616442&prj=527&rqi=sE9dbzmFBCIzkdMhjYGgytJUmy
GI-250 | f2ab48a8-ef66-4daa-b6d2-ae94b55f4d2a | NY05-P2 | 527 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | Electrical â€“ LV | equipment | BATT-MECH2 | UPS Battery |  | 93PM IBC-LW | Missing Labels for all strings on battery cabinet Mech UPS2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616446&prj=527&rqi=xTodyg3tIfPmcYm4p89TIIQYnY
GI-249 | 50d176c4-fe74-4351-ba33-df40a8eafe54 | NY05-P2 | 527 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | Electrical â€“ LV | equipment | BATT-MECH1 | UPS Battery |  | 93PM IBC-LW | Missing Labels for all strings on battery cabinet Mech UPS1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616445&prj=527&rqi=aZFfL1nzDsn9y2V7PjDRGTGFTC
GI-240 | c8714aa6-f251-46f1-8417-6bb08f2134a6 | NY05-P2 | 527 | AMER | Closed | P1 High CX | moutaz.abdelhamid@veolia.com | 2026-03-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | MSB and UHD MTZ Schneider breakers all lost BMS communication. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616431&prj=527&rqi=P3SLLhM8WMGvhJa6dbCN3fFGs0
GI-245 | 8faae809-3097-4fef-a7d6-77f98f9d32b9 | NY05-P2 | 527 | AMER | Closed | P2 Medium CX | jack.mino-altherr@veolia.com | 2026-03-25 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning |  | Electrical â€“ LV | equipment | BATT-E1 | UPS Battery |  | X8U6UF75XD4806P35020X06MT16 | Missing Labels for all strings on battery cabinet E1 Battery E1-1 Battery E1-2 Battery E1-3 Battery E1-4 Battery E1-5 Battery E1-6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616441&prj=527&rqi=ynjpd9I66dIgrjt4S3bSqwragp
GI-239 | e3139156-2ce5-4d1b-a203-a73ad225fb00 | NY05-P2 | 527 | AMER | Closed | P1 High CX | moutaz.abdelhamid@veolia.com | 2026-03-24 04:00:00.000 +0400 | Mechanical Contractor |  | Design Correction Needed | Design |  |  | equipment type |  |  |  |  | The Generator tanks were not manufactured with an internal drop-down line for the polisher return. A possible option of rerouting the 2â€ line into the 4â€ opening then extending into tank. Foley to review and confirm. See attached markup showing current site install and possible alternative. Also attached are the submittals from P1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616323&prj=527&rqi=kZR1txFtQGGWG6n5SF1rmKlCwc
GI-233 | 58cea49c-1462-463d-9cfd-af97508b1438 | NY05-P2 | 527 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | Provide labelling to all ports for Generators E&H. See attached Image of generator E as example. Labelling format to match exisiting generators. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615731&prj=527&rqi=C7fHKexhAqQNq3fHmi1x0FrXkI
GI-237 | b8016880-fc48-465c-8d44-c63e98dd7233 | NY05-P2 | 527 | AMER | Closed | P1 High CX | moutaz.abdelhamid@veolia.com | 2026-03-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | The fuel water separator system has an NTP thread nipple connection instead of a STOR thread, which is causing the leak. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615738&prj=527&rqi=OZig6dRIpjdNsElHmVPpvh4sJ3
GI-238 | 714c9944-597b-4bfe-a698-bf5de4a8d06e | NY05-P2 | 527 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | Generator fuel oil back pressure relief pipe is high off the ground causing a trip hazard. Similar pipe on other Gens are are labelled and painted bright color to prevent tripping. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615739&prj=527&rqi=XiwixjGYyWBoeK4h4xfecD5CoI
GI-236 | dc919426-b231-47c8-a9b4-43ab1da98030 | NY05-P2 | 527 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-16 04:00:00.000 +0400 | DCOS - Equinix |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | The approved ECMP 4.0 controller is currently installed; however, its firmware version differs from the version specified in the approved Modbus point list. I am reaching out to Angel Gray to confirm the latest controller-approved firmware version. The current installation runs FW 4.13, which Foley believes is the most recent version available. I will let you know as soon as I hear back from Angel. All the points from the attached approved list proved functional except for LowCoolantLevelAlarm. The register used was 400354.6 instead of 400351.7. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615734&prj=527&rqi=1G6pH5So2QEw0jPF3W75SgH6gE
GI-232 | 35beceaf-33ec-4a67-a3b6-ba815d40d528 | NY05-P2 | 527 | AMER | Closed | P2 Medium CX | moutaz.abdelhamid@veolia.com | 2026-03-12 04:00:00.000 +0400 | Engineer |  | Documentation Not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | UHD E1/E2 MTZ breakers maintaince mode settings not specified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615478&prj=527&rqi=kbo3rDdDFFzei9bk2xApEUspQi
GI-227 | 4aff023c-040f-44d0-9631-db26d40a13a5 | NY05-P2 | 527 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-09 04:00:00.000 +0400 | Engineer |  | Documentation Not issued/ Required | Commissioning |  | Electrical â€“ LV | system | E Block |  |  |  | E-509 review comments - Arup to incorporate comments (Attached) as part of NY5-P2 As-built record drawings for both Capacity and Liquid cooling E509E and E509H drawings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615135&prj=527&rqi=ng2v4dDcdU4zBRDoOKarYR5IAr | https://equinix.facilitygrid.co.uk/x/project/527/system/11048
GI-226 | f69e0591-0a24-4720-86fc-47b5f89b8984 | NY05-P2 | 527 | AMER | Closed | Outstanding Paperwork/Documentation | moutaz.abdelhamid@veolia.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Documentation Not issued/ Required | Commissioning | [7 empty] | GC to provide required documentation for project closeout, this includes Torque sheets, balancing reports, Meggering reports...etc. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615134&prj=527&rqi=Uujux8wVAIDWOgbiGPM78ZRVJG
GI-225 | 14d87f16-f049-461a-91ee-40e627151e28 | NY05-P2 | 527 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Not Correct | Commissioning |  |  | equipment type |  |  |  |  | The UHD-E1 and UHD-E2 key interlock SOO placards are has incorrect statment to return loadbank K21 key to SCC, which is incorrect and required to be updated as called out in Veolia submittal review comments for NY5-P3. AMG will need to reprint and replace the placards on the previously installed UHD-E1 and UHD-E2 units to ensure consistency. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614812&prj=527&rqi=USobu6WDfgoGYMuSMSnPiYp8GV
GI-224 | 4dd8de3c-7c85-4354-93b4-1fcec9b0cc6e | NY05-P2 | 527 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-03-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Not Correct | Commissioning |  |  | equipment type |  |  |  |  | The MSB-E and MSB-H key interlock SOO placards are inconsistent with the placards provided by Eaton. Veolia identified this discrepancy during the NY5-P3 scope review; however, AMG will need to reprint and replace the placards on the previously installed MSB-E and MSB-H units to ensure consistency. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614810&prj=527&rqi=8kc1m7UfrRMMSSCt1apAV5NkIj
GI-010 | 335d7a73-ea23-98a3-b85d-f343a45db115 | NY10-EW | 696 | AMER | Open | P3 Low CX | jimmy.mendoza-farfan@veolia.com | 2026-07-06 04:00:00.000 +0400 | Mechanical Contractor |  | Installation Damage | Commissioning | [7 empty] | Upper top left lip of cabinet is bent. Door can be opened somewhat easily, but closing the door is difficult. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628101&prj=696&rqi=EIdrqWVSNztbGWpVcHFAIretfV
GI-009 | 9fa87e6a-ffad-9f11-6b09-c88a76835a67 | NY10-EW | 696 | AMER | Closed | P3 Low CX | jimmy.mendoza-farfan@veolia.com | 2026-07-06 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not complete | Commissioning | [7 empty] | P-trap is not installed on the condensate drain line as per contract drawing M501 detail 4. TYP for both units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628100&prj=696&rqi=j017LKpuuPg0GBm1gx2PyOKNUI
GI-008 | edb137d6-5c0e-2301-2c12-a4e40591039a | NY10-EW | 696 | AMER | Closed | P2 Medium DCOS | jimmy.mendoza-farfan@veolia.com | 2026-07-06 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not complete | Commissioning | [7 empty] | RTU power exhaust power and control wiring has not been pulled/terminated inside of the unit. Power exhaust was shipped loose and field installed. TYP for both RTUs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628099&prj=696&rqi=kdmFDD0UT7iD6ah1Y4hFcYZJYO
GI-003 | 502ff159-3122-4859-b50c-f7369ea608b5 | NY10-EW | 696 | AMER | Open | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [7 empty] | PNL_H8A panel schedule shows a 15A breaker for heater box but submittal shows 20A. DLB confimed that the most current submittal is 15A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624561&prj=696&rqi=I4jH0yZALpM6J9BRWaB9sXKjaI
GI-001 | 74e11317-e9a4-448e-b4e9-ef9478fc7de8 | NY10-EW | 696 | AMER | Open | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-06-08 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  |  | system | Electrical - LV |  |  |  | Temporary Arc flash stickers are currently installed on site equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624346&prj=696&rqi=81fhmEnly5QWmhWXKsiDcZc0Tv | https://equinix.facilitygrid.co.uk/x/project/696/system/14658
GI-002 | 25c19ef6-86c9-4900-9241-726bd73fd838 | NY10-EW | 696 | AMER | Closed | P3 Low CX | moutaz.abdelhamid@veolia.com | 2026-06-08 04:00:00.000 +0400 | Electrical Contractor |  | Labelling | Commissioning | [7 empty] | Breaker feeding PNL_H8A within the exisiting HMD-8 panel require a permenant Phenolic label. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624350&prj=696&rqi=U0lBAnh74t2IcGl91EeCgOBGsm
GI-200 | e11df97d-1408-422b-b67e-5d611bf5762c | NY11-5 | 552 | AMER | Closed | P3 Low CX | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | Electrical Contractor |  | DCOS General Issue | DCOS | [7 empty] | Thermal Monitoring - Need to confirm procedure and test thermal monitoring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623656&prj=552&rqi=HGV58v7lvpM31jIG2sZWHH3PNL
GI-201 | 369181ca-fe6d-42c1-b7c5-6c5fac46fea3 | NY11-5 | 552 | AMER | Closed | P3 Low DCOS | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | Configuration | DCOS | [7 empty] | Need to complete BMS Aveva License Transfer - Rovisys is in talks with Equinix controls to complete. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623657&prj=552&rqi=fpHuTLnjM2N20cvU5ZUzq2X53m
GI-202 | 02fdc0b2-1944-4daf-b526-f1136f927db7 | NY11-5 | 552 | AMER | Closed | P3 Low DCOS | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | General Contractor - BMS |  | Installation Not Complete | Commissioning | [7 empty] | RPP BCM's - Some of the NY11-5 RPP's were being moved by Site Ops. Need to be informed when construction is complete. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623658&prj=552&rqi=Bg0T5D1djVFXVpyqgRLmqwB33l
GI-199 | d8212bce-48c2-4d01-8964-690d9eb0f147 | NY11-5 | 552 | AMER | Closed | P3 Low CX | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Configuration | DCOS | [7 empty] | Chillers - Need to setup time sync server capabilities. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623655&prj=552&rqi=58YYIhEgdb3cMd25Zhs9jYfMA4
GI-196 | f2194cd2-5470-408f-8f4d-1b6bca08dea6 | NY11-5 | 552 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-03-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | BMS Single Line - Need to verify the single line graphic is correct after the tethers have been removed/Changed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614925&prj=552&rqi=kFmn22CVm0jwfIpU6Zl1peZIFz
GI-195 | eabe24ee-909c-4ebf-8f4e-5b8cb73d2671 | NY11-5 | 552 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-03-04 04:00:00.000 +0400 | Design Professional |  | Design Correction Needed | Design | [7 empty] | CHWP-ALL - The breaker tripped when the VFD was used in Bypass. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614746&prj=552&rqi=PodBR2pEKK0lt0z4z7IearUfZ2
GI-185 | 5600453a-1fa0-48d4-9f59-b5e203f817cf | NY11-5 | 552 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-02-07 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | MSB-B SPD Alarm: The unit appears to not to be in alarm. But the alarm is active, and the unit is working correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198735&prj=552&rqi=miUWfkN7F3U8SoB1j9NiSNY0zq
GI-184 | 2917e3f2-1433-4609-806e-1ccbf1fba093 | NY11-5 | 552 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-02-07 04:00:00.000 +0400 | Controls Contractor |  | DCOS Template Issue | DCOS | [7 empty] | ALL UPSs for NY11-4 and NY11-5: Need to have the Alarm limti set to the correct values on KW, KVA and output current. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198734&prj=552&rqi=vcEMXrTVDJpQ0QbVLy6zMfCYE2
YT1ELEC-45-007 | 419cf6e0-e5a0-4158-957c-4eaed66765e5 | NY11-P1 | 660 | AMER | Open | P3 Low CX | edward.woodruff@veolia.com | 2026-09-18 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C HMI: Need to verify the jumper is installed at the PLC level to prevent any closed transition can occur with the K5 key. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638735&prj=660&rqi=apNl1R6I5QZk4R64UV4teeNsr3
YT1ELEC-45-006 | 3ec0ba94-1dc5-48cc-9aa3-13794bf6d93e | NY11-P1 | 660 | AMER | Open | P3 Low CX | edward.woodruff@veolia.com | 2026-09-18 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C HMI: When Gen/Main breaker trips it only shows the one breaker locked out. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638734&prj=660&rqi=XYPCVX8lQDxfhld4toz6aZluIm
YT1ELEC-45-008 | 426756ed-537d-45fd-9d78-ef83ce78864f | NY11-P1 | 660 | AMER | Open | P3 Low CX | edward.woodruff@veolia.com | 2026-09-18 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: Marshalling cabinet doesnt have enough control wiring ground points. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638737&prj=660&rqi=afvgdQZIqi6AvJ3idikjSbaB7Y
GT1ELEC-42-001 | 8c00b15b-33dc-feb4-e7cb-0461680c1a1c | NY11-P1 | 660 | AMER | Open | P3 Low CX | edward.woodruff@veolia.com | 2026-09-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: The generator breaker doesn't change state on the trip unit display and the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638599&prj=660&rqi=6E0KD3KNE6HXFNLmUrPepm4S55
GI-050 | fef0f58c-9c0a-4ba8-91e9-d6380b988f69 | NY11-P1 | 660 | AMER | Closed | P3 Low CX | dustin.haugh@veolia.com | 2026-09-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | Cubical 07A door need adjustment for opening and shutting. The top 5 hinges on cubical 8 collide with the door preventing normal operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638190&prj=660&rqi=UWrmHViun787YgINwcVkz6DrCg
GI-049 | 62df0bb1-aa28-4416-86db-f2dba3c9f070 | NY11-P1 | 660 | AMER | Open | P2 Medium CX | dustin.haugh@veolia.com | 2026-09-15 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_C_1 | MDSB - Mechanical Distribution Switchboard |  |  | Control wires enter and run with 480v load wires. Wires need routed in factory looms to prevent EMF issues. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638189&prj=660&rqi=FtSsA66E7e0ckWhYmuJml9X7NY
GI-048 | 6efdf0f1-f6df-43f7-83ea-8c86bb1aa84b | NY11-P1 | 660 | AMER | Closed | P2 Medium CX | dustin.haugh@veolia.com | 2026-09-15 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | Low voltage control wires ran with 480v loads. Blue wires in attached pictures should enter cabinet in provided low voltage knockout at top of control cabinet.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638160&prj=660&rqi=sUXYZQ6FNR15zlzTq78IXbKzHg
GI-046 | d83b5073-d45e-9007-55ca-9f538f9e0802 | NY11-P1 | 660 | AMER | Closed | P2 Medium CX | Christopher.Federico@veolia.com | 2026-09-10 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_C_1 | MDSB - Mechanical Distribution Switchboard |  |  | MDSB-C-1: Top breaker has incorrect lug size. correct lugs need to be ordered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637609&prj=660&rqi=1ZFiQ6AjqTLN0yMYwDCstuC88C
GI-045 | 072d5a3c-52b9-6e83-bc41-30506bda8978 | NY11-P1 | 660 | AMER | Open | P3 Low CX | Christopher.Federico@veolia.com | 2026-09-09 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1PNL_C_H1_2 | DB - Distribution Boards |  |  | PNL-C-H1-2: Two set screws on line side of breaker are stripped. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637528&prj=660&rqi=f8swCnsIIrMyk0x6zWm1G31m4W
YT1ELEC-45-005 | 255c394b-ffe2-46f2-9af9-9eccfa9ba51f | NY11-P1 | 660 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-09-01 04:00:00.000 +0400 |  | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: The Mimic lines on the swbd are incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636375&prj=660&rqi=9TaHobV7L5OiMvxlGso6Jyqmpq
YT1ELEC-50-004 | 0ba67013-5813-4bc5-ac4d-9b5cecfd80b9 | NY11-P1 | 660 | AMER | Open | P3 Low CX | edward.woodruff@veolia.com | 2026-09-01 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | UMDSB-C: Breaker Q3 (MBB) only has one Aux NO/NC contact. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636371&prj=660&rqi=hboKJLfJxjUm7XnzWT7zToBVnh
GI-043 | 66a9f421-5dd4-f91c-b156-46278fb95d32 | NY11-P1 | 660 | AMER | Closed | P2 Medium CX | jimmy.mendoza-farfan@veolia.com | 2026-08-28 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Check valves need to be rotated in the correct orientation. Currently the check valve is oriented to prevent backflow into the return line. Check valve should be installed to prevent backflow into the chilled water supply line. Typ for both chiller skid piping. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635983&prj=660&rqi=f9rzPZkf6aKJLkzHbpq4oH9lnM
GI-044 | 28ad1fb0-c165-eac8-d2f8-9674302a42a3 | NY11-P1 | 660 | AMER | Closed | P3 Low CX | jimmy.mendoza-farfan@veolia.com | 2026-08-28 04:00:00.000 +0400 | Mechanical Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | CHW recharge line for ACC7 has the wrong Series 70 Bray valve model installed. Note the different part number for the Series 70 Brays. The DA Bray model is only supports ON/OFF control. The G0 Bray model has modulating control. ACC7 has a DA Bray valve installed on the recharge line that needs to be swapped out with the extra G0 Bray valve installed on the ACC8 discharge line. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635986&prj=660&rqi=eRXhom3MFzHI7ZNfvqlwIk2cG7
RT1ELEC-57-002 | 9d12f463-13e6-420c-8d97-793e91ae81f5 | NY11-P1 | 660 | AMER | Open | P3 Low CX | dustin.haugh@veolia.com | 2026-08-27 04:00:00.000 +0400 | General Contractor | L2A | General Design Issue | Design |  | Controls | equipment | REMOTE HMI | HMI - HMI Panel |  |  | No drip pan below AC condensate drain connection. Drip pan above AC unit not tied into the drain.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635631&prj=660&rqi=BjWiv8ey7ZRvhUYyM4jqGIAoOB
GI-042 | 6411ae0e-f7aa-430a-bbae-579a581705cc | NY11-P1 | 660 | AMER | Closed | P2 Medium CX | dustin.haugh@veolia.com | 2026-08-24 04:00:00.000 +0400 | TRN - Trane |  | Installation Damage | Commissioning |  | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Control wiring to chiller sensor damaged. Right cabinet on back of chiller, top middle area. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635063&prj=660&rqi=RiTfrvP1hQ5Q06aCtytSWWAjom
YT1ELEC-45-004 | b05b73e5-6855-8313-a4ab-f07339c70925 | NY11-P1 | 660 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: All CT polarity's appear to be reversed on all PQMs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630734&prj=660&rqi=tFClSp9sjgTd7t7YStKO6H0Mbq
YT1ELEC-50-003 | 57d54a39-7d0a-69f2-939a-ac2f1cd5b86f | NY11-P1 | 660 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | UMDSB-C3: The polarity appears to be reversed on the PQM CTs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630733&prj=660&rqi=vnACNBxloOAMp5vcKN7nrymoVw
GI-039 | b365106d-1aa6-ad1e-6fa9-88edb89f877f | NY11-P1 | 660 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-23 04:00:00.000 +0400 | VER - Vertiv |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | IT AND MECHANICAL UPS Batteries: the cabinets are missing the barrier and spacing required by fm global for lithium batteries and cabinets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630725&prj=660&rqi=T4MAxlq39h8lT9ypAi3Zi6FyoK
YT1ELEC-45-003 | 6d6ce5f2-8f1d-44b3-b906-93e2f8b4c954 | NY11-P1 | 660 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | 1MSB-C: The high contact resistance found on Camlock section 8 and 9 from LBB (both) to the Phase A camlock. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629837&prj=660&rqi=doBT1YxXO6MHBMIEp0EQhroQOI
YT1ELEC-50-002 | ca070fa0-92ce-c791-0f99-90079019611d | NY11-P1 | 660 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-14 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | 1UMDSB-C: Breaker Q7 has failed NETA testing due to contact resistance. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629169&prj=660&rqi=AzZUc1a9WPmec29imRjnUGrY5V
YT1ELEC-50-001 | c043e40d-c16f-6ff9-54fd-0c5c489d9f61 | NY11-P1 | 660 | AMER | Closed | P2 Medium CX | edward.woodruff@veolia.com | 2026-07-14 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | 1UMDSB-C: Breaker Q1 has failed NETA testing due to contact resistance. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629168&prj=660&rqi=w33xZSe1r03uK9xWNhNgFkxtSt
GI-037 | 6729ac62-aa0d-8893-f3ba-c24988c81a8f | NY11-P1 | 660 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-13 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_C_1 | MDSB - Mechanical Distribution Switchboard |  |  | MDSB-C: The as built breakers sizes don't match the submittel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629035&prj=660&rqi=XSvTrBLYdYPZ31Tbi0Yrszqiy0
GI-038 | d884db4c-d2b5-e657-dee4-afa803e21fe5 | NY11-P1 | 660 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-07-13 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_C_3 | UMDSB - Mech Distribution Switchboard (fed from UPS) |  |  | 1UMDSB-C: The as built breakers sizes do not match the submittel sizes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629036&prj=660&rqi=SLSJs6dD8N6z4UQ0GNtjRIUyvX
GI-029 | 1b67f6e7-c091-4b55-8f11-13871a591ff6 | NY11-P1 | 660 | AMER | Open | P3 Low CX | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | CMM - Cummins |  | Design correction needed | Design | [7 empty] | GEN-C - As observed on other jobs, the battery charger failure is now an alarm that appears instantaneously on a power failure and creates a nuisance alarm. In the past, we believe we had a 30 second time delay to override momentary power blips to the battery charger before an alarm was initiated at the generator. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623651&prj=660&rqi=c3D0Mfne2RqIRl00yi5hbsro6K
GI-028 | 87f463fe-2309-439f-ad40-589c20dec660 | NY11-P1 | 660 | AMER | Closed | P3 Low CX | ralph.ciardulli@veolia.com | 2026-06-02 04:00:00.000 +0400 | HAP - Hitachi Energy |  | Documentation not issued/ Required | Commissioning | [7 empty] | MLTX-C - The submittal did not include the proper primary side cabinet and associated accessories. Components were installed in field. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623649&prj=660&rqi=R8HswT8rOfEyDaDGNOyVbI82W8
YT1ELEC-45-002 | c230c50f-9238-40cc-b4b8-3d043ef84f9f | NY11-P1 | 660 | AMER | Closed | P3 Low CX | ralph.ciardulli@veolia.com | 2026-05-27 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C - Section 4 Load Bank Breaker - Factory connections for vertical bus were disconnected for the installation of a bus duct flange. While reinstalling the Phase B left side (when viewed from front) vertical bus into the insulator, the bolt was torqued to 51 ft-lbs and clicked well before the connection was fully torqued down. The washer the spacer was still spinning. The volt was backed out and the same issue repeated. Upon further investigation, it appears that the insulator is spinning as the bolt in the back does not move. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623234&prj=660&rqi=BtBeUzUvSxGNTuiQgapRUKYTcO
YT1ELEC-45-001 | 14e65e10-de2e-17d1-71e9-ef72d4b04670 | NY11-P1 | 660 | AMER | Ready for Verification | P3 Low CX | edward.woodruff@veolia.com | 2026-05-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB B: IOB1 K7 key assembly is not in the breaker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622527&prj=660&rqi=iHPsSge2TaL5DCg0P67cyIm5u5
GI-026 | a1d6cdf3-bc1d-4e22-aa1e-bde597b95d3e | NY11-P1 | 660 | AMER | Closed | P3 Low CX | jimmy.mendoza-farfan@veolia.com | 2026-05-14 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | Bottom section of SWGR needs to be fixed. Refer to photo attached. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621916&prj=660&rqi=ZveAfQVVunAFQP0ED2khpk1ZC9
RT1ELEC-57-001 | 8e664845-11ae-3f39-bb17-edc082afa1df | NY11-P1 | 660 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-05-08 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning |  | Controls | equipment | REMOTE HMI | HMI - HMI Panel |  |  | MSB-C HMI: Above KS1 the placard should read " Auto Auto/Man Man". all on the same plane. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621005&prj=660&rqi=WI8GVj29TMa21YKt5q93AEMe2A
GI-015 | 6c4565ed-848f-79b3-9a86-25bd7bffa248 | NY11-P1 | 660 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Several control wires failed a tug test. See photos for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618147&prj=660&rqi=CISfRDT1whATSziAGhWfy9gHlT
GI-023 | 5714534b-ea03-87fc-4781-797b293b34f5 | NY11-P1 | 660 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1-ACC-C-8 | ACC - Chiller - Air Cooled |  |  | Control wiring located on the left side of the control panel enclosure needs to have wires reorganized. Typical for both chillers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618178&prj=660&rqi=tPonCkZd6oQIqU2PPchxuqmrHS
GI-017 | 28a778dc-dc88-f80f-05e0-d2af40abdc36 | NY11-P1 | 660 | AMER | Ready for Verification | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Missing Components | Commissioning | [7 empty] | Fan guard is missing inside the 480V cabinet. Typ for both chillers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618149&prj=660&rqi=ZRP0b1zBjkkBHzBv8ERzQhi3bQ
GI-018 | 11948c02-f6d2-ecbf-3575-5a8b34eab245 | NY11-P1 | 660 | AMER | Open | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [7 empty] | Provide protective enclosure for transformers inside the 480V cabinet similar to the lugs. Typical for both chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618150&prj=660&rqi=nvtQlOSaFhIcewpJPjCN9uc4Pe
GI-022 | 86e41783-af34-3423-8019-4b043b61d71b | NY11-P1 | 660 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1-ACC-C-8 | ACC - Chiller - Air Cooled |  |  | Several control wires failed wire tug test | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618177&prj=660&rqi=DtAkzjJNdGFF8Vexd1aHjHAcRf
GI-019 | 8646e892-ddeb-2957-458e-5a453a0cf940 | NY11-P1 | 660 | AMER | Ready for Verification | P2 Medium CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Missing Components | Commissioning |  | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Chiller came equipped with 2 position bray valve for freeze protection. Per equinix EBCS-3 control valve should be fully modulating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618169&prj=660&rqi=5gagFfGCTmKaGQBdglVmuCGR7A
GI-020 | e17fa06c-a52f-4c65-7f9a-11424308bfd4 | NY11-P1 | 660 | AMER | Closed | P2 Medium CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Missing Components | Commissioning |  | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Onicon provided with the chiller skid does not match the approved submittal. Flow meter provided is FT-3000 series (FT-3206). Model number on the approved submittal notes FT-3400. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618171&prj=660&rqi=dgDDEijJ290O2A8wAwKCDtfHQs
GI-021 | d49d03aa-7381-174f-89aa-2f2ca063bcbe | NY11-P1 | 660 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Missing Components | Commissioning |  | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Provide additional neoprene pads (4 total, 2 per chiller) for chillers. See photos for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618172&prj=660&rqi=FLrP3uMhMF8FjWZMDKApofdT6v
GI-016 | 5bfd6b4c-2cef-b1af-b1bf-9c5be5a0cb82 | NY11-P1 | 660 | AMER | Closed | P3 Low CX | samet.ozdemir@veolia.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Installation not complete | Commissioning |  | Mechanical â€“Air | equipment | 1-ACC-C-7 | ACC - Chiller - Air Cooled |  |  | Ground wiring is not terminated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618148&prj=660&rqi=5QceKxpzAyatpeP6twdoSSj58T
GI-009 | eac2b62f-baf5-4881-b996-01e18057ae9e | NY11-P1 | 660 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-03-09 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: the Cam loc section of the MSB-B Kirk key does not match existing K2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615142&prj=660&rqi=PuNYr85PEZ3mpnvKFsF5dIZwV7
GI-008 | f5b18d8d-52e4-31a5-821b-b785e5a269dd | NY11-P1 | 660 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-03-09 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: the LBB K2 Kirk key does not match existing K2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615125&prj=660&rqi=htXAtg5cSNpUDqwV0RwyYL6xuy
GI-007 | f816606d-53bd-7abe-8890-cead9fe22979 | NY11-P1 | 660 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-03-06 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C- the main CTs are not ridgedly supported on the main bus | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614899&prj=660&rqi=58vajmy3yFUC0edawMz3izHlTM
RT1ELEC-46-002 | 9b9e167b-044a-4872-9ba8-ab7958c40450 | NY11-P1 | 660 | AMER | Closed | P2 Medium CX | Christopher.Federico@veolia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | UDP-C1: Needs phase transition piece to properly terminate busway into the gear. Different phasing between manufacturers was not taken into account. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483376&prj=660&rqi=LAJmaAfZfnB2wcycSvxjdVs1dy
RT1ELEC-46-001 | 3785d939-f255-155b-7df3-f547bc6f721f | NY11-P1 | 660 | AMER | Closed | P3 Low CX | edward.woodruff@veolia.com | 2026-02-25 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: MSB skirt pieces were damaged and dented during shipping. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221109&prj=660&rqi=COuhSkrchCZx5ncSo58VGJW0EP
GI-001 | 78f0dfe5-747c-a563-59a0-95938931f507 | NY11-P1 | 660 | AMER | Closed | P2 Medium CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design not as specified | Design |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C HMI: Key switches do not release in all positions like they should. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199687&prj=660&rqi=tTcg8kgPRkRBM5HhQSWxx0FpDa
GI-004 | 19c58c8e-6175-b564-117b-d57f6ba04274 | NY11-P1 | 660 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design not as specified | Design |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: All voltage indicator lights on the board are white instead of amber. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199690&prj=660&rqi=76EEklFldOltXITpFuihhTDfyM
GI-005 | ee2ce579-6a09-e51f-45a8-aa67e00f116c | NY11-P1 | 660 | AMER | Closed | P2 Medium CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design correction needed | Design |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: Design of the glastic barrier behind the section 03A incoming cable entry prevents clean installation of the 13th cable that will be landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199691&prj=660&rqi=Nbxjz0Z6vP1WikVVR3kbdcDOPy
GI-006 | 9785c050-8bcc-6746-651a-91070824699b | NY11-P1 | 660 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design not as specified | Design |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C: Circuit breaker slots for UPS LBBs in sections 08B and 09B currently have a metal plate over the cutout intended for the breaker when instead it should have a bubble-type enclosure installed on the front in order to lock up the breaker when in use. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199692&prj=660&rqi=zM9vmlOnGspigHIbozXhRqorrW
GI-002 | 0558ede1-0477-f8fd-aa14-7a3e2185eebf | NY11-P1 | 660 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design not as specified | Design |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C HMI: Labels on HMI are all blank. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199688&prj=660&rqi=JkFPwAzrJH7dg2ckZfprfiAgQb
GI-003 | 2442387e-7f42-a856-dc38-4185582c4dcd | NY11-P1 | 660 | AMER | Closed | P3 Low CX | Christopher.Federico@veolia.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design not as specified | Design |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  |  | MSB-C HMI: Unnecessary K5 switch is installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199689&prj=660&rqi=FpXQLVAmTM6ecr6N5XltCTzwgG
GI-052 | a206d4ce-d153-4ad2-8366-302821b71418 | OS03-4 | 519 | APAC | Closed | P3 Low CX | milanshrestha@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | SAT Electrical During the "System Star-up and Check" on Bus Duct Temperature Sensor, temperature was displayed as "zero" on the GX20(BMS) for BD29 to BD32 (highlighted in red color in figure) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352253&prj=519&rqi=MBYISRlTf1sJsxNqbP1AbSMJ1K
GI-051 | f6e42518-2cd5-4bee-895f-3fdacdabe14b | OS03-4 | 519 | APAC | Closed | P3 Low CX | milanshrestha@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | SAT Bus Duct Test Script (Page 14) Kinden said that the Bus Duct Temperature sensor path was changed (indicated by arrow and cross mark below). Please make the correction when submitting the Test Result. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352252&prj=519&rqi=xfiTLAMnXhZn05Ay8bTpCE6rCg
GI-050 | 193f4be5-a630-4c33-b046-8615060c8563 | OS03-4 | 519 | APAC | Closed | P3 Low CX | milanshrestha@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | FAT Mechanical OS3-P1 CRAH/AHU Regarding the performance test, the actual average value is 173.4kW. Please explain why it is 173.4kW. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352251&prj=519&rqi=Vbo9JfmFWBu7xSq4kuQkeZi5KT
GI-049 | 44a92c40-81d0-4b77-b450-1052e960dfe4 | OS03-4 | 519 | APAC | Closed | P2 Medium CX | milanshrestha@commtechasia.com | 2026-01-27 04:00:00.000 +0400 | Commissioning Authority |  | General Contractor [GC] | Commissioning | [7 empty] | SAT OS3-P1 Primary UPS no. 5 (12F) : Mitsubishi Electrical - UPS - 2400kVA - 24-7MP4093 EF - Cx4 During the UPS functional performance test (load test), a fan temperature abnormality alarm occurred. This issue caused the UPS thermal load test to be terminated. Cause: The required blanking panel (divider plate) was not installed between the UPS module panel and the bypass panel. This blanking panel prevents the inflow of hot air from the module panel to the bypass panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197649&prj=519&rqi=5Z4iRFBuOb5jbIP6CsTgadBnVg
GI-082 | 97a2bfc5-39d1-4b8f-92ec-c2df6041831f | OS05x-1 | 521 | APAC | Ready for Verification | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-11-05 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  |  | equipment type |  |  |  |  | HLT : - Mechanical - (PAC) [Daikin - PAC - FVYCP560MA - Cx4] [HLT Issue No.1]_Mechanical_(DH 3-1-2) During the 100% load test, the RA of PAC No. 40 in UPS Room 3-1-2 recorded a temperature of 30.1Â°C. The temporary data logger also recorded a temperature of 32.3Â°C. At that time, four PAC units were in operation, and the SA setpoint was 23Â°C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622086&prj=521&rqi=3P0pprkCoEIYUCGBVf1GzUq0e5
GI-131 | c64def73-819b-43cd-9986-08e3766a0bfe | OS05x-1 | 521 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-09-07 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  |  | equipment type |  |  |  |  | SAT: - Electrical - (Diesel Engine Generator) [CAT / BEMAC - Diesel Engine Generator / DEG Panels - 4875kVA - C175 - 20 - Cx4] On the third day of the UPS No. 9 test, when the power supply switched from the mains to the generator, alarms were triggered on the Fuel Tank No. 1, No. 2 and No. 4 transfer pumps. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637041&prj=521&rqi=IDf75yBXfGmoxZOgblqDfIIhMd
GI-132 | 63e35a47-91a1-42df-bc20-f81b1d7d133f | OS05x-1 | 521 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  |  | equipment type |  |  |  |  | SAT : - Electrical - (UPS) [Mitsubishi - UPS - MELUPS 9800G - Cx4] During the 3rd day of the UPS No. 9 test, an overload test was conducted while the UPS was supplied by the generator. The test scenario required the UPS load to be increased to 110%. If the load remained at 110% for 10 minutes, the UPS was expected to transfer from inverter supply to internal bypass. The UPS successfully transferred to internal bypass as expected, and the operation was completed without any issues. However, when the load was subsequently reduced from 110% back to 100%, the UPS was expected to automatically transfer from internal bypass back to inverter supply. This transfer did not occur as expected, and the UPS remained on internal bypass. After the synchronization switch was turned off and the test was done, the UPS successfully transferred from internal bypass back to inverter supply without any issues. However, a failure alarm was triggered on the UPS during the transfer. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637042&prj=521&rqi=fRGaKzG7qAutYtEXiBG09xrXmg
GI-126 | 5c338ac0-cd51-4dd8-876b-70962366ea4f | OS05x-1 | 521 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | [Building Electrical IST Day 2 Preparation Issue No. 32] Regarding the BMS display for the fuel system, â€œLocalâ€ is shown in green and â€œRemoteâ€ in red, but it should be the other way around. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630214&prj=521&rqi=rARb2hd7r9jmWp6iqeZcVBoNuA
GI-127 | 9e1ac749-4b72-4450-b9b3-b4cbabba2abf | OS05x-1 | 521 | APAC | Open | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | [Building Electrical IST Preparation Issue No.33] Not completed the mapping of additional points and the point-to-point check for the BMS display related to generator fuel systems. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630274&prj=521&rqi=VLKrJ2HyY1o1snqADVH5h1v2mP
GI-123 | 48b9c765-3a45-4900-af4f-332cacab7a00 | OS05x-1 | 521 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | [Building Electrical IST Day 2 Issue No.29] Building Elec IST Preparation: Since the power factor display on the BMS shows -100%, correct it to 100%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630070&prj=521&rqi=Mslz4uvCR64etkQsNoGKfrE5zo
GI-124 | 6accef5c-fa84-4599-9079-0583eaa0ca6e | OS05x-1 | 521 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | [Building Electrical IST Day 2 Issue No. 30] Building Elec IST Day2 Test No.8 After power was restored to Test-8 on Day 2 of the Building Elec IST, a minor fault for DEG No. 5 was reported on BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630071&prj=521&rqi=kFkhT0K61vwYmAhSp9dulV3wkU
GI-125 | 2fe6abfa-f386-4b97-ab7d-096fcc9a4e66 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  |  | equipment type |  |  |  |  | IST : - Electrical - (Diesel Engine Generator) [CAT / BEMAC - Diesel Engine Generator / DEG Panels - 4875kVA - C175 - 20 - Cx5] [Building Electrical IST Day 2 Issue No.31] Building Elec IST Day2 Test No.9 During the building power outage for Test-9 and the subsequent generator startup, major, middle and minor alarms were triggered on Generator No. 5, causing the equipment to shut down. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630072&prj=521&rqi=7Q8WYBC8E09WYo2dv2yBZ7KUiU
GI-122 | a8b74c88-8b6d-4d77-bfb9-a8f327e9edd8 | OS05x-1 | 521 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | [Building Electrical IST Day 2 Issue No.28] Building Elec IST Preparation: Before the start of the Building Elec IST Day 2, offline alarms were triggered in 2-3-DP-12-U4-2-1 and 1-3-DP-12-U5-2-1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630069&prj=521&rqi=gywMrVnOpxVPBLn69H3YIrAtf0
GI-118 | 5a673c49-a79e-49bb-b995-737f7e706f72 | OS05x-1 | 521 | APAC | Ready for Verification | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-07-16 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  |  | equipment type |  |  |  |  | IST : - Mechanical - (PAC) [Daikin - PAC - FVYCP560MA - Cx5] [Building Mechanical IST Issue No.24 Day 2] High Return Air Temperature alarm generated by the PAC unit that was in standby in UPS Room 3-2-1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630063&prj=521&rqi=E2DhNgJwdD4waYZa338Irs4gcA
GI-121 | 434a2026-97bf-4c58-9be5-18784552195f | OS05x-1 | 521 | APAC | Open | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-16 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | [Building Mechanical IST Day 2 Issue No.27] Update the Sequence of Operation (SoO) for the heat source area to the latest version and send it to the relevant parties. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630068&prj=521&rqi=gqgHlDRJ3jTYtUwd7Ymah625Eo
GI-120 | a2533202-9043-4d85-8109-c15d088c9bc5 | OS05x-1 | 521 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-16 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | [Building Mechanical IST Day 2 Issue No.26] L2 No. 2 Riser Return Flow Rate Discrepancy: - BMS Display: Constant 4,436 L/min - BMS Trend Data: Fluctuating between 4,435 - 4,456 L/min - On-Site Meter: 0 L/min - Onsite current output measured at control panel: 0 mA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630067&prj=521&rqi=OdIlalDca1u27a6tmnPmsJcJZB
GI-119 | ef549414-43fd-495b-9913-d5dcc456ae53 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-07-16 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  |  | equipment type |  |  |  |  | IST : - Mechanical - (PAC) [Daikin - PAC - FVYCP560MA - Cx5] [Building Mechanical IST Issue No.25 Day 2] High Temperature Alarm for UPS Room 3-2-1: High temperature alarm for UPS Room 3-2-1 was observed during the PLC failure tests. Upon inspection of the temporary data loggers: the max temperature around the modules was observed to be 34 and battery at 23.7â„ƒ (approx 12:30) Temporary data logger Max readings at approx. 16:45: - Module area: Max 36.9Â°C - Battery area: 25.9Â°C | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630066&prj=521&rqi=WbYp5Cwg0CNlKIB2MHiYt1GyrZ
GI-115 | cad6738c-3796-416a-a8bc-e3902c5ee278 | OS05x-1 | 521 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | [Building Mechanical IST Preparation Issue No.21 Day 1] DH Load Adjusted to 2,400 kW Condition -> At the beginning of IST Day 1, the DH load was below 2,400 kW. After consultation with the vendors, the DH load was adjusted to approximately 2,404 kW for both data halls. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630060&prj=521&rqi=nieuNVcPDhKEJIEyclEPtZIXTI
GI-116 | 617e65bb-77c5-443a-804f-383f2e868277 | OS05x-1 | 521 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | [Building Mechanical IST Preparation Day 1 Issue No. 22] IT Server Breaker Monitoring Clarification Required -> Clarification is required on why some breakers supplying power to IT servers are not monitored. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630061&prj=521&rqi=xFzTCaoib23zvsakC7CHMil9Zg
GI-117 | d0154361-003c-47a1-8526-f879424e1efb | OS05x-1 | 521 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | [Building Mechanical IST Issue No.23 Day 1] During the A-to-B changeover, high-temperature alarms were observed on Risers 1 and 3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630062&prj=521&rqi=yte18yasxv4bAG5gw5afKEqtOe
GI-114 | 7a8be9ad-f823-40a3-9bf9-9c645e4ae520 | OS05x-1 | 521 | APAC | Open | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | [Building Mechanical IST Preparation Day 1] Supply Air Temperature Fluctuation During DH Load-Up -> During DH load-up, supply air high-temperature alarms were observed on the BMS for the Cool Array Units. Trend review indicated that the supply air temperature on the smaller coils (Top Left and Top Right) was fluctuating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630059&prj=521&rqi=taYYwVMOnTudftXKHGueNuQjpn
GI-113 | 983ead80-bdad-4e34-8986-29f0455f688d | OS05x-1 | 521 | APAC | Ready for Verification | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-09 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | Mechanical IST Issue No.19 <Cool Array> DH 3-2-1 During the lunch break on the second day of IST, a communication error occurred in the BMS measurement display for 2-3-CRAH-12-2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628796&prj=521&rqi=jIQrNYrehHLAXi1gM1EXU3ZAs3
GI-111 | e541b315-6510-4759-aa7f-ab7c23b99563 | OS05x-1 | 521 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | Mechanical IST Issue No.17 <PAC> DH 3-2-1 Mechanical UPS PAC (2-3-FCU-12-PAC29) exhibited abnormal noise during the pre-IST inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628794&prj=521&rqi=ygKuQr8AuxhOFY1hZIjnoCPUjY
GI-112 | b5d05a8c-8e11-4e15-9729-06ad32fa3aff | OS05x-1 | 521 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-07-08 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | Mechanical IST Issue No.18 <Chillers> DH 3-2-1 4-3-CH-12-8 & 4-3-CH-12-9, all compressors stooped due to low flow during test 12 [Simulate the failure of one Cool Array at a time in the Data Hall (fan stopped), record the temperature rise to above 35Â°C, and then restore the temperature to the SLA tolerance as soon as temperature rise to above 35Â°C] | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628795&prj=521&rqi=EEkE2CAL79BfahmVGUtKi1dKhw
GI-110 | bf5ff01a-684f-4d3c-bc5c-c110b2e94b5e | OS05x-1 | 521 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  |  | equipment type |  |  |  |  | IST : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx5] MECH IST Issue No.16 <Chiller> During the monthly inspection on 5 July, discolouration of the thermal labels was discovered on OS5x, PHF floor, units 4-3-MDSB-12-P402 and 4-3-MDSB-12-P411. (Discolouration at a maximum temperature of 80Â°C) It was also found that the circuit breakers for compressors on Chillers No. 2 and No. 11 had tripped due to overcurrent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628793&prj=521&rqi=1BkYfHC6AfmbWNw9iWSM7Gpt5k
GI-109 | b8eb7878-8e08-444c-9839-d4416e924c9a | OS05x-1 | 521 | APAC | Ready for Verification | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-07-02 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <Chiller No. 5 & 10> DH 3-2-1 During the 100% load test of Chiller No. 10, Chiller No. 5, which was under exclusion, unexpectedly went offline and then automatically returned to an online status shortly afterward. A major alarm was generated on the BMS when the chiller went offline. Once communication was restored and the chiller returned online, the major alarm was automatically cleared from the BMS. The event was transient, and no further abnormalities were observed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628792&prj=521&rqi=k4jbVavSXiZDG1180uJIiVh4En
GI-108 | 538dbd32-21cc-48dd-990c-a81f9c95e258 | OS05x-1 | 521 | APAC | Ready for Verification | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  |  | equipment type |  |  |  |  | SAT: - Mechanical - (Cool Array) [Vertiv - Cool Array Unit - TW240 (5 coil) - Cx4] SAT L4 <FPT Issue No.22> Cool Array 3-2-1 During the ATS switching test (A â†’ B), all CRAHs went offline and then recovered. However, 2-3-CRAH-12-3, 2-3-CRAH-12-8, and 2-3-CRAH-12-9 tripped again (offline) before returning to normal operation. During the return switching (B â†’ A), 2-3-CRAH-12-1 went offline before restoring, while all other CRAHs transferred back to source A without interruption. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627200&prj=521&rqi=euAfvL3I0LoB8w2mYnKA2uftqL
GI-103 | 37e77cfe-49ed-485b-8147-16400705caf4 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-19 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  |  | equipment type |  |  |  |  | IST : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx5] (DH - 3 - 2 - 2 Mech IST No.11, Day-2) During the Chiller Failure and Restoration Test, the chiller was restored successfully at the site and resumed normal operation locally. However, the chiller remained in an offline status on the BMS and did not return to its normal operating condition within the BMS interface. To restore proper communication and status indication on the BMS, Main breaker (é›»æºå…¥åˆ‡ã‚Š) was performed. Following the action, the chiller status was correctly reflected on the BMS, and normal operation was confirmed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626671&prj=521&rqi=i9lW8zSPgcO91HKbToerAQbebW
GI-102 | ee2740cd-75e3-4a3d-a80d-39b366ea5d70 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  |  | equipment type |  |  |  |  | IST : - Electrical - (STS) [Kokubu Electric - STS - 0304301 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0304401 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0304501 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0304601 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0304701 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0304801 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0303701 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0303801 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0303901 - 1150 kVA- Cx5] Mechanical IST Issue No.10, DH 3-2-2. During the site inspection, a high temperature(data logger) of approximately 32Â°C was observed in the STS room under 100% load conditions. A similar temperature trend was also confirmed in the BMS data for the HLT on 17 June. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626660&prj=521&rqi=K6mO7PPA9rTiJtClDOx3mYbys5
GI-107 | f325bab8-53c4-4abc-8d1c-7dd1319df626 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design | [7 empty] | HLT/IST : - Mechanical - (Hot Aisle Capping) [Shinryo - HAC - N/A - - Cx4/Cx5] Lessons Learned (DH3-1-1) The SLA temperature exceeded 27Â°C during 100% HLT load. It is believed that a problem with the temporary HAC structure caused a short circuit of cold air, resulting in a rise in the cold aisle temperature. Since the upper limit specified in MSFT's SLA requirements is 35Â°C, the test continued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627199&prj=521&rqi=OC9BZPwWB1SNaMEVqzofKrD4bE
GI-106 | 165cf1bf-5543-4420-a856-41462fb83cb6 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | Commissioning Authority |  | General Contractor [GC] | Commissioning | [7 empty] | IST : - Mechanical - (Sensor) [N/A - Sensor - N/A - Cx5] (DH 3-1-1, DH3-1-2) Lessons Learned Since the cold aisle sensor is installed on the ceiling, move it to the correct position below the ceiling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627198&prj=521&rqi=APMYqC6vd1n3MbEn9AylwagVSK
GI-101 | 1294db57-77f7-4130-91af-588511b1b19b | OS05x-1 | 521 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  |  | equipment type |  |  |  |  | HLT: - Mechanical - (Cool Array) [Vertiv - Cool Array Unit - TW240 (5 coil) - Cx4] HLT Issue No.9 HLT DH 3-2-2 During the step load test, Supply High Temperature Alarm was triggered on the BMS for several CRAY units at 25% and 50% load. Upon investigation, was observed in the SA temperature for several CRAY units at DH3-2-2. For the 5-coil CRAY units, two different coil sizes exist, and the hunting was observed only in the smaller coils. The SA temperature for the larger coils was stable. The hunting was observed only at low load conditions (up to 50%). The SA temperature became stable from 75% load onwards. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626659&prj=521&rqi=rpw9DoWqUT8DOXYdp6IZ7P49dd
GI-098 | 7676f111-aeda-418c-981b-6f2f278100e7 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-12 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  |  | equipment type |  |  |  |  | SAT : - Electrical - (UPS) [Mitsubishi - UPS - MELUPS 9800G - Cx4] SAT L4 [FPT Issue No.19] UPS No.4 DH -3-2-2 During the UPS-4 L4 line changeover test, a discrepancy was identified between the electrical current and power readings indicated by the UPS-4 metering system and the corresponding values supplied from the extra-high-voltage (EHV) source. The difference in measured values has been recorded and will be investigated further. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626651&prj=521&rqi=X0LthiOIuydGlCPtn69OurSJKq
GI-097 | 6b31b519-d176-4a17-9686-e045e5221cb3 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  |  | equipment type |  |  |  |  | SAT: - Mechanical - (N2 gas sensor) [Nohmi Bosai - N2 Gas Sensor - 4083 (LGF, DH 3-LG-2) - Cx4] [Nohmi Bosai - N2 Gas Sensor - 4205 (LGF, DH 3-1-2) - Cx4] SAT L4 <FPT Issue No.18> DH 3-2-2 (2F) An alarm was generated on the BMS screen from the Nâ‚‚ Gas Detection Sensor 5093 associated with DH3-2-2. Upon investigation, it was confirmed that the alarm was caused by a faulty detector as there were not any reason for the sensor to activate. The defective sensor was subsequently replaced, restoring normal operation. The faulty sensor has been sent to the manufacturerâ€™s factory for detailed failure analysis. The investigation is expected to take approximately one month, after which the root cause of the failure will be reported. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624066&prj=521&rqi=jPixtxtf8xg4sbEVs4Iz6gHSIv
GI-096 | c8a53abc-f973-4f0e-b74a-36e3fa990dfe | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-04 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  |  | equipment type |  |  |  |  | SAT: - Mechanical - (Cool Array) [Vertiv - Cool Array Unit - TW240 (5 coil) - Cx4] SAT L4 <FPT Issue No.17> Cool Array 3-2-2_ The wall-mounted temperature sensor in DH3-2-2 indicated a temperature exceeding 35Â°C, reaching approximately 36.4Â°C, which is significantly higher than the expected operating range. Upon investigation, it was suspected that the cool air discharged from the Cool Array was unable to effectively reach the area where the wall-mounted sensor is installed. This condition is believed to have been caused by the replacement of the fan cover in accordance with Microsoft's specifications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624063&prj=521&rqi=Tve9XXrZtOidzRJzKuB9inFS8m
GI-093 | 2a7d256e-af25-4f2a-8962-10ad2133eb82 | OS05x-1 | 521 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-06-01 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  |  | equipment type |  |  |  |  | IST: - Electrical - (Diesel Engine Generator) [CAT / BEMAC - Diesel Engine Generator / DEG Panels - 4875kVA / C175 - 20 - Cx5] <Mech & Elec IST Issue No.8> BMS (3-1-1) A â€œMajor Control Power Failureâ€ alarm was observed in the BMS during a power outage (generator power supply). This alarm was triggered by a momentary loss of power to the fuel pump panel during the outage. A UPS for the fuel pump panel is scheduled for installation in August to prevent recurrence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624055&prj=521&rqi=NfpmWyUVxVEVIzKCiQwqteP2vp
GI-089 | 1e55682d-6134-409d-9250-298fc5d26958 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-15 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  |  | equipment type |  |  |  |  | SAT : - Mechanical - (PAC) [Daikin - PAC - FVYCP560MA - Cx4] SAT L4 <FPT Issue No.11> DH - 3-1-1 (DH3-1-1) During testing of Cool Array and STS L4, the temperature in UPS Room 3-1-1 rose under 100% load. The wall-mounted sensor recorded 38.6Â°C, and the PAC intake near the UPS module rack recorded 44.4Â°C. This is believed to be caused by exhaust from the UPS module blowing toward the PAC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624048&prj=521&rqi=J1fivEe2oq5gEf7R9syQIRBExD
GI-086 | ed53f446-6736-40ae-bbad-7f387c8bac56 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  |  | equipment type |  |  |  |  | IST : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx5] <Mechanical and Electrical IST Issue No.5> (DH 3-1-2) It has been determined that the method for obtaining chiller status and the chiller skip logic do not comply with Equinix standards. ãƒ»Chiller status must be obtained via a hardwired connection from the chiller controller. ã€€Current situation: Chiller status is not obtained directly from the BMS; instead, a judgement is made based on the pump status. ãƒ»The chiller must be switched to the standby unit if it fails to meet both of the following conditions for a period of 5 minutes: >>Flow rate at the chiller flow meter is at or above the minimum required flow rate >>Chiller outlet temperature is 21.5Â°C (specification +1.5Â°C) or below | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622091&prj=521&rqi=wJIPlS5V7cFKuVk27qKJeXfeEW
GI-085 | 89efdf47-bd30-436b-a6f5-3799ece6d7cb | OS05x-1 | 521 | APAC | Ready for Verification | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  |  | equipment type |  |  |  |  | IST : - Mechanical - (PAC) [Daikin - PAC - FVYCP560MA - Cx5] <IST No.4>_Nikken_Shinryo_(DH 3-1-2) While the system was under 100% load, a high-temperature alarm (60Â°C) was triggered in the UPS DH 3-1-2 bus duct. It was believed that the cause was a rise in temperature in the UPS room. At that time, the temperature on the front of the UPS module panel was recorded at 32.7Â°C. 4 PACs were operating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622090&prj=521&rqi=MKeHkB5RErMhYxymXUoaYh91ig
GI-087 | 64aee38a-1e2e-46b7-ab72-76a39f6fc45e | OS05x-1 | 521 | APAC | Open | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  |  | equipment type |  |  |  |  | IST: - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx5] <Mech & Elec IST No.6> (Mech and Elec IST for DH 3-1-2) There are chillers on both the OS4x side and the OS2x side. When two units were operating on one side and a unit on the other side started up, chilled water (return) did not flow, causing the return temperature on the other side to rise. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622092&prj=521&rqi=JEfY0IhOWNcotWYpieqgJox1Xg
GI-088 | c52b2849-0f48-4d42-be62-2ec4514407df | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  |  | equipment type |  |  |  |  | IST: - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx5] <Mechanical and Electrical IST issue No.7> (DH 3-1-2) If a power outage occurs while the chiller is operating in tank charging mode, there is a risk that high-temperature chilled water will continue to be supplied to the Cool Array until the chiller restarts, in order to maintain tank charging mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622093&prj=521&rqi=u7tF8uJ7PQqt0GdO15Z32yGURY
GI-084 | 1b1c3f8c-e4e7-402e-9a43-39d190b016b2 | OS05x-1 | 521 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | <HLT/IST No.3>_JCI_(DH 3-1-2) On the BMS screen while the generator is supplying power, the power transmission line remains green, should be red. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622089&prj=521&rqi=wZdu8GxnwuCvwAawWgekuSE81q
GI-104 | c44b6676-fc69-4ec1-bd2c-6d15174e83a8 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Commissioning Authority |  | General Contractor [GC] | Commissioning | [7 empty] | (DH 3-1-1, DH3-1-2) Lessons Learned Issues regarding the installation of Temporary HAC / ä»®è¨­ã‚­ãƒ£ãƒƒãƒ”ãƒ³ã‚°ã®æ§‹ç¯‰é–“é•ã„ â€¢ The HACs are opened from front and back of the aisles, causing a short circuit between cold and hot aisles. This is different from what a DH with permanent HAC would look like and seems to be giving higher temperature reading. â€¢ It seems that to avoid reading too high temperature at the coil, they have put vinyl sheet blocking the airflow. This is basically manipulating the results and needs to be fixed. â€¢ The HAC installation quality is not very good and it seems to be coming off from many locations. Is it purposefully opened? If not, please ask GC for a proper installation. â€¢ The HAC start (in the CRAY side of DH) seems to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627196&prj=521&rqi=AulRrGGMEhN03d6mEgI1UOoy8S
GI-105 | b0325d75-c358-4ef0-b759-4469d6c28f2b | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Commissioning Authority |  | General Contractor [GC] | Commissioning | [7 empty] | (DH 3-1-1, DH3-1-2) Lessons Learned Incorrect Data Logger Installation Location/ ãƒ‡ãƒ¼ã‚¿ãƒ­ã‚¬ãƒ¼ã®è¨­ç½®å€‹æ‰€é–“é•ã„ The temperature data loggers supposed to be installed at the same location as SLA sensors are not equidistant. E.g. below pic, gap between two adjacent data logger locations is significantly different. Is this as per the Exhibit C section I shared before, or as per the OS4x SLA sensor locations. Please confirm that the data loggers are in same position as the SLA sensors. Pressure sensor locations are also different from aisle to aisle. Please confirm those as well. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627197&prj=521&rqi=6RatI593iHtpDg1sIVA9URsfHw
GI-083 | 9586b6f1-b830-4a0e-b17b-1e971cc074b6 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-11 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  |  | equipment type |  |  |  |  | HLT : - Mechanical - (Cool Array) [Vertiv - Cool Array Unit - TW240 (3 coil) - Cx4] <HLT No.2>_Nikken_Shinryo_DKSH_(DH 3-1-2) The Î”T setting for the Cool Array was changed from 12Â°C to 11Â°C, resulting in an increase in the design airflow rate for the Cool Array (66774CMH/unit >> 72000CMH/unit). During the L4 HLT, a temporary capping was installed and an airflow measurement was conducted at 100% load; the results showed that the airflow was insufficient relative to the total design airflow rate following the design change. At that time, the maximum fan speed for the Cool Array was set to 70%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622088&prj=521&rqi=SViAFKO8FPjfRzwPPwqQe63cNK
GI-081 | 6a8188ad-896b-44e1-8a90-c04a484c31d0 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.10> (Chiller) DH - 3 - 1 - 2 During Adjustment of flow rate fluctuation during chiller stage-up/down, minor alarm on Chiller No.6, compressor No. 2 was generated. Upon confirmation it was identified as Rotor Starting Torque Fault. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621055&prj=521&rqi=v9gMViMrONkPfCZ1Jl14bNjmQl
GI-136 | 87ddc161-1475-411a-a54f-5c13872ebb44 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.5> (Mechanical) Chiller DH 3-1-2 During Chiller failure test, 3 phase overcurrent alarm (Chiller No. 1Compressor No.1, 2 and 4) was generated when Chiller No. 1 started. Subsequent investigations revealed that approximately 200 seconds after the chiller started up (with a 120-second stage delay), the condenser fan speed dropped to 0%, causing the compressorâ€™s power consumption to rise and triggering a â€œ3-Phase Overcurrentâ€ alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620845&prj=521&rqi=nfillfdWTfvEEJ8jdJL06kZquA
GI-080 | 67466242-9be4-418e-a0fb-3d8f0eb64108 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.9> [Chiller] (DH - 3 - 1 - 2) During Chiller failure test, a major alarm was generated on Chiller No.10, which was in operation.(temperature sensor fault) After resetting the alarm once, normal operations resumed. NTTF is currently investigating the cause. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620895&prj=521&rqi=KDsJYkQDPlPdTnjqgkc0LUZGWt
GI-077 | 087aba2f-27f7-4392-8518-d0c1ed8f768a | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.6> (Mechanical) Chiller 3-1-2 Before Chiller No. 6 failure test, all compressors stopped due to low flow protection. It was continued the test after the alarm was reset, but the issue was not observed again. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620847&prj=521&rqi=RvyPfTgJMjYrIptBOFGgqv8mjK
GI-079 | 87127692-153d-42d4-ad13-069ec59cf298 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.8> [ Chiller] DH - 3 - 1 - 2 During Chiller failure test, 3 phase overcurrent alarm (Chiller No.9 Compressor No. 1) was generated when Chiller No. 9 started. Subsequent investigations revealed that approximately 200 seconds after the chiller started up (with a 120-second stage delay), the condenser fan speed dropped to 0%, causing the compressorâ€™s power consumption to rise and triggering a â€œ3-Phase Overcurrentâ€ alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620894&prj=521&rqi=oEjHMfqGiEA3ugYGd8KVQUIkyH
GI-078 | 98b1a63e-30dd-4a1f-9340-272ce4c25c00 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.7> (Chiller) (DH - 3 - 1 - 2) When the connector between the chiller controller for the Chiller No. 6 and the UPS battery was disconnected, no major fault alarm was triggered. After that, only the pump continued to operate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620893&prj=521&rqi=mIMa8kwd7zIgFi4SoIDjvXzIQl
GI-073 | a36d23ef-b8f4-45e4-a7e2-a2758a8097dc | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-04-24 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.2> [Mechanical] <Chiller No.7> (3-1-2) During the pre-startup check for L4, a communication error was detected in condenser fan 10B (#20) of Chiller No. 7. This communication error did not occur during the L3 test. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619436&prj=521&rqi=hTbB2DkuSwQaAk3zhEDlpdNrmD
GI-074 | 9a9baae6-b4d2-41fa-b02d-ddb2bd3efde9 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx4] SAT L4 <FPT Issue No.3> (Mechanical - L4) (3-1-2) Chiller No.8, System - 1 Chiller No.9, System - 2 Chiller No.12, System - 1 During the pre-startup check for L4, the refrigerant liquid level sensor reading was showing 0% on the chiller screen. This communication error did not occur during the L3 test. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619437&prj=521&rqi=oY7XT8fMp9M9yvhjfdAPosrSjO
GI-072 | 17ecb18d-403a-4e89-88da-0d46e46419b4 | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-04-21 04:00:00.000 +0400 | Commissioning Authority |  | Design | Design |  |  | equipment type |  |  |  |  | SAT : - Mechanical - (PAC) [Daikin - PAC Unit - FVYCP560MA - Cx4] During the L4 test of cool array , UPS Room 3-1-2 recorded a peak temperature of approximately 46.4Â°C at 100% load. It was confirmed that exhaust from the UPS module was blowing directly onto the temperature sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618787&prj=521&rqi=TNUIgmNc1Gg2WRviVvlOrztgRH
GI-070 | cb0f97bf-9c5c-4fdc-8864-4dada0d29d25 | OS05x-1 | 521 | APAC | Closed | P3 Low CX | takahirowatanabe@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | A scratch was found on the condenser of Chiller No. 4-3-CH-12-13. Please carry out the necessary corrective action. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618234&prj=521&rqi=gK6ynbxvfsF8iyUwsB6c1hPNch
GI-071 | 85ff59db-b5c4-4bad-9a59-c3a32924a81e | OS05x-1 | 521 | APAC | Closed | P2 Medium CX | takahirowatanabe@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  |  | equipment type |  |  |  |  | SAT : - Mechanical - (Chiller) [SMARDT - Chiller - AE150 - Cx3] Discoloration of servo labels inside the power distribution panel. ãƒ»The report revealed that the servo labels inside the panel had discolored (It is believed this occurred during the commissioning and adjustment phase) ãƒ»During the commissioning and adjustment phase of this project, when the CRAH was operated at 100% capacity, an incident occurred where the fans stopped (breaker tripped) for units equipped with AHF (LG, 1st floor). ãƒ»From April 8 to 10, we performed AHF readjustments on the 22 CRAH units in the north and south sections of the first floor. ã€€For the CRAH units in the south section of the first floor, we operated the CRAH at 100% capacity overnight with the AHF turned on, ã€€and upon measuring the temperature, confirmed it was approximately 45Â°C. (We will continue to perform these adjustment tasks.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618236&prj=521&rqi=4MyklQp64hZOk4V0RHhlCMwARw
GI-068 | 90ce32bb-adad-4c17-85d6-2d2ce4259fba | OS05x-1 | 521 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | SAT <General> There were electrical equipment that are not included in the Tag tracker which was previously confirmed by Vendor. Such as Panel (LG-3-MDSB-12-PCP-1, LG-3-MDSB-12-PCP-2). We advice to Kinden again to verify the Tag Tracker if any equipment are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197430&prj=521&rqi=YucB7f0zbO6UPTrrPCS74mm88k
GI-065 | 248b2c06-9a0c-4e3a-9fea-e4ad31c51032 | OS05x-1 | 521 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | SAT <DEG Indoor Panel> The actual nameplate of the DEG (indoor) panels were different from the entries in the Tag Tracker, as confirmed by Kinden. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197427&prj=521&rqi=bbWqMnUtz28ngAgkYwYiLwV3uD
GI-069 | c1064ac5-c268-4eaf-98a7-b1b0bfacc38b | OS05x-1 | 521 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | SAT <General> There are lot of equipment which are not yet finished (example : cable installation) but the vender declared L2A completed on the Tag Tracker. (UPS, STS, etc) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197433&prj=521&rqi=zQsSj8OI7bEXp6m3TGAFHzqzSq
GI-066 | ed8b0bf1-c0d2-4543-89ac-733d202906c8 | OS05x-1 | 521 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | SAT <Generator> The generator panel Tag seal has not been signed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197428&prj=521&rqi=kbAlGFnUhASugKP5nQAOr7mFU5
GI-059 | 85eb72ef-e6da-48f7-969a-81b777119713 | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | takahirowatanabe@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | Fire IST DH 2-2-2 During N2 exhaust fan (4-2-EF-12-N2-4) startup, local operation of MD1-N2-4 was confirmed, but display operation on the BMS could not be verified. Subsequently, it was confirmed that the point for the subject MD was not being acquired by the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483407&prj=512&rqi=IKKzBoHPkLD4TlhkRO0oc0THUz
GI-052 | dc317a27-eac2-4582-a6b9-2b06d02a2ef7 | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 5.) <IST> <DH 2-2-1> <Mechanical> 2026/02/05_ In IST Test-14 (Chiller Failure), the chiller was simulated to fail by disconnecting the connector between the chiller controller and the UPS battery. The chiller was restored according to the procedure written in the script, but the unit on-site and display on the BMS did not return to normal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199318&prj=512&rqi=s3nFlKEZMHrnCOedqCcAlsDRjP
GI-042 | 08b178ec-1459-4fb5-a5dd-6dc92b072017 | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 6.) <HLT> <DH 2-2-1> <Ductwork> 2026/02/03_ After HLT Test-5 (100% load) test, the wall-mounted temperature sensor in UPS room 2-2-1 recorded 29Â°C. Check the design temperature and the recommended environment for the UPS unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199306&prj=512&rqi=z7FuYZv76VAlKhtvMDl8oWBss1
GI-046 | d7be2e12-2e40-4162-a327-07932f786f18 | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 10.) <HLT> <DH 2-2-2> <Mechanical> During the HLT and IST, the following unexpected alarms were raised: DH2-2-2 HLT 13:49 CH6 COMP4 Bearing Fault [During Test 5 (100% Load) ] 17:28 CH6 COMP4 Bearing Fault [During Test 6B (Cool array power supply switching test) ] DH2-2-1 IST CH6 COMP4 Bearing Fault [During Test 13 (Cool Array communication failure ) ] | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199310&prj=512&rqi=6iUbTBJmATsfO05yTj8eEzaRzg
GI-043 | 18f60922-3173-4680-bfdf-5dbd05b2d224 | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 7.) <HLT> <DH 2-2-2> <Mechanical> During the HLT, the following unexpected alarms were raised: DH2-2-2 HLT 12:50 CH5 COMP4 Inverter Temperature Fault [During Test 5 (100% Load) ] 16:44 CH5 COMP4 Inverter Temperature Fault [During Test 5 (100% Load) ] 17:27 CH5 COMP4 Inverter Temperature Fault [During Test 6B (Cool array power supply switching test) ] Although a manual reset temporarily restored the system, the same fault occured three times in the same compressor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199307&prj=512&rqi=VjlzdHNX4aQxDV8rTjZEQVPlKa
GI-048 | 783b48f3-bca0-45d0-90e2-e54332a8b7e7 | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 1.) <IST> <DH 2-2-1> <Electrical> 2026/02/05_ During the simulation of failure of three modules on UPS No. 1, the specification states that the system should transfer to internal bypass after one minute. However, during the actual test, the power transferred to bypass immediately. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199312&prj=512&rqi=pCIVCMCTfiX1DJJg1aB2YLCztZ
GI-038 | 043a75cd-c5f5-4697-8c61-6265546d389f | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 2.) <HLT><DH 2-2-1> <MECHANICAL> 2026/02/03_ During HLT Test-4 (75% Load), an unexpected alarm was triggered due to a condenser fan communication error while chiller unit 10 was operating, and a minor alarm was reported by the central monitoring system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199301&prj=512&rqi=KrDq9vPlxkwA63WwylUwSdQyRN
GI-050 | 0ae8ef4a-657e-47a4-9716-4743467cc36c | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 3.) <IST> <DH 2-2-1> <Mechanical> 2026/02/05_ During test No.13 in chiller No. 6, bearing fault alarm was generated. ã€Motor Single Phase Overcurrent Faultã€‘ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199316&prj=512&rqi=ygAIQbKeNIc9Llq2vyRdpLLZ00
GI-049 | 0099171b-3cd0-43e6-a889-7472605e538c | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 2.) <IST> <DH 2-2-1> <Mechanical> 2026/02/04_ IST Test 9 â€“ Simulated Failure and Recovery of One Representative Cool Array Unit (Coil Failure to N) (Confirmation of Operation without Redundancy): After the communication cables for the CRAY fan and valve were disconnected, the cables were reconnected as part of a recovery operation, but the BMS and the site did not return to normal operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199315&prj=512&rqi=dtbI2uXqjJwfcvUMUKNgHFmEtl
GI-051 | 4025e965-1e9c-46a7-a34e-533c2c061e10 | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 4.) <IST> <DH 2-2-1> <Mechanical> 20206/02/05_ During test 12 minor alarm (Heat source unit alarm.) on chiller no. 7 was generated. ã€Motor Single Phase Overcurrent Faultã€‘ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199317&prj=512&rqi=B2T7DrlvUmo8inxQchzwLOZ738
GI-055 | 094a791c-6314-4ccc-8ed4-f01ef66a8796 | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 8.) <IST> < DH 2-2-2> <Mechanical> 2026/02/12_ In Test-9 (Cool Array Coil Failure), after disconnecting Valve-5 of 2-2-CRAH-12-19, Valve-3 became offline. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199322&prj=512&rqi=Efy23mrsRrwQ3Mh2NvtC7aWdkX
GI-047 | a83b4374-931e-4280-85c2-8fb0559811bc | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 11.) <HLT> <DH 2-2-2> <General> 2026/02/10_ There is hole found in the SLA sensor bracket. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199311&prj=512&rqi=ON2RCljqEmKTqYVnp4ZyIP2h9N
GI-057 | 8f49c63d-c648-4834-91b0-5c0e709d004f | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 10.) <IST> <DH 2-2-2> <Electrical> 2026/02/13_ During IST Test-15 (utility power failure/ restore), An insulation caution alarm was triggered at 2-SS2-TRB1. Since the affected system is an air conditioning outdoor unit, the test continued while investigating the cause. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199324&prj=512&rqi=qMT1J9SH4K9ghr0oymoa8PWvHi
GI-037 | d91cade3-7c5d-4b67-9ad2-2f1a665bb9eb | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 1.) <HLT> <DH 2-2-1> <BMS> 2026/02/03_ The hot aisle containment was not drawn correctly in the BMS, so this needs to be corrected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199300&prj=512&rqi=kjmHmzL7pYSxYKoKSLvKDO2XHx
GI-045 | 23313828-a2c7-478d-b1ad-6644ff9852d5 | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 9.) <HLT> <DH 2-2-2> <Mechanical> 2026/02/10_ DH2-2-2 HLT During the HLT, the following unexpected alarms were raised: 13:21 CH6 COMP1 Rotor Starting Torque Fault [During Test 5 (100% Load) ] 13:49 CH6 COMP1 Rotor Starting Torque Fault [During Test 5 (100% Load) ] Although a manual reset temporarily restored the system, the same fault occured twice in the same compressor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199309&prj=512&rqi=9srCvU2GFtiAL9fnrNeYYMh3GM
GI-054 | ea101de4-3293-4030-8501-ebf34066e9cf | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 7.) <IST> <DH> <Fire> 2026/02/05_ As there were no changes to the automatic fire alarm system or gas fire extinguishing system in this project, the test script agreed upon in advance did not include a Fire IST. On the day of the IST, MSFT requested that the test be carried out, and it was adjusted the schedule. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199320&prj=512&rqi=KStONJ6KbtEx2FMlghy3XcwZ8n
GI-053 | 180ff4a9-3f54-49d7-9eb4-cba8d9861cab | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 6.) <IST> <DH 2-2-1> <Electrical> 2026/02/05_ In IST Test-18 (STS MCDT automatic switching), the control panel of the simulated load banks was connected under a DP panel that did not have a switching function, so if the target breaker on the UPS output panel was opened, the load banks would lose power and the device could have failed. Therefore, the UPS output breakers other than the one on the load banks control panel were opened and the test continued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199319&prj=512&rqi=ZM0kLzCpW8q0JUzQRF6QKpgBVE
GI-056 | c976bb7b-f2e7-471c-a45f-7a9506e54d9d | OS4x-F1 | 512 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning | [7 empty] | IST : - Electrical - (Diesel Engine Generator) [CAT / BEMAC - Diesel Engine Generator / DEG Panels - 4875kVA / C175 - 20 - Cx5] 9.) <IST> <DH 2-2-2> <Electrical> 2026/02/13_ During Test-15 (A, B-line utility power failure), an alarm was triggered on the BMS after starting Generator No. 7. Power supply were performed without issue. ãƒ»Auxiliary equipment failure batch alarm ãƒ»Charger 2 failure alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199323&prj=512&rqi=JrA5XYl1LuYqECvqkNdfWS82Wp
GI-039 | 27187499-1952-4353-a1d1-84234cb93b20 | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 3.) <HLT><DH2-2-1><Mechanical> 2026/02/03_ During the HLT and IST, the following unexpected alarms were raised: Although a manual reset temporarily restored the system, the same fault occured multiple times. DH2-2-1 HLT (Issue no. 39) During HLT Test 5 (100% step load test), a minor alarm (Motor Single Phase Overcurrent) was generated on Chiller No. 8. COMP3. DH2-2-2 HLT (Issue no. 44) 13:29 CH5 COMP4 Motor Single Phase Overcurrent Fault [During Test 5 (100% Load) ] 15:37 CH5 COMP4 Motor Single Phase Overcurrent Fault [During Test 5 (100% Load) ] DH2-2-1 IST (Issue no. 51) During test 12 minor alaram (Motor Single Phase Overcurrent Faul.) on chillor No. 7 COMP2 was generated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199302&prj=512&rqi=Den1nn4z9FrPhAOZXE2oiy9uQQ
GI-041 | 0fd2fa94-2323-4f87-ac3b-48873d060eb2 | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 5.) <HLT> <DH 2-2-1> <Mechanical> 2026/02/03_ During the HLT test, MSFT pointed out that the CRAY ATS enable/disable and selected priority might be required to be displayed on the BMS screen. The same are not displayed in T1. MSFT will confirm internally and revert back on this requirement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199305&prj=512&rqi=9IVdPqv0qhU5NZxImdTouwCMVH
GI-044 | 631ef96b-c077-4772-b993-a5aaa70bb9d6 | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 8.) <HLT> <DH 2-2-2> <Mechanical> 2026/02/10_ 13:29 CH5 COMP4 Motor Single Phase Overcurrent Fault [During Test 5 (100% Load) ] 15:37 CH5 COMP4 Motor Single Phase Overcurrent Fault [During Test 5 (100% Load) ] | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199308&prj=512&rqi=8EbRkDfWWlNVrqdlnbEFu6OL4q
GI-058 | 71eab068-0323-4ace-bbfc-81840d8b1e2d | OS4x-F1 | 512 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | General Contractor [GC] | Commissioning |  |  | equipment type |  |  |  |  | IST : - Electrical - (STS) [Kokubu Electric - STS - 0300101 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300201 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300301 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300401 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300501 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300601 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300701 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300801 - 1150 kVA- Cx5] [Kokubu Electric - STS - 0300901 - 1150 kVA- Cx5] 11.) <IST> <DH 2-2-2> <BMS> 2026/02/13_ During Test-19 (STS MCDT Switching), The signal wire used to transmit status information to the BMS was found to be disconnected. As a result, the â€œPower ONâ€ indication was not displayed in the operational section of the STS status screen on the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199325&prj=512&rqi=A9Nn3OV1csCaSdxHCokslJbGB0
GI-040 | a8d7b8d6-3030-45d2-a0f1-54627e788c42 | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | 4.) <HLT> <DH2-2-1> <Mechanical> 2026/02/03_ HLT Test 6B â€“ Cool Array Power Supply Switching Test (Common UPS to AC UPS): In the test script, the ATS switching time to be changed from 25 minutes to 5 minutes in order to shorten the test time, but the CRAH-1 ATS switched after 25 minutes instead of 5 minutes | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199303&prj=512&rqi=MbBH7zdRlUeocIcd9RQ3Y7tTKL
GI-034 | f6a62aae-b465-43bf-a66c-05ac57c8f683 | OS4x-F1 | 512 | APAC | Closed | P2 Medium CX | borshinhernandez@commtechasia.com | 2026-01-26 04:00:00.000 +0400 | Commissioning Authority |  | Root Cause Analysis [RCA] | Commissioning |  |  | equipment type |  |  |  |  | SAT : - Electrical - (UPS) [Mitsubishi - UPS - MELUPS 9800G - Cx4] <SAT, Electrical> DP Panel, OS4x-F1(T2) During the load test of the DP panel, the UPS triggered an overload alarm and switched to bypass operation. Since the test was conducted at 96% load (2300 kW), investigate the cause of the overload alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197562&prj=512&rqi=pXXDYjXLZ7gXvb54dyra4yxZcJ
GI-036 | 312ac4cc-6981-41e3-b3f1-313906cbc067 | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-26 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | <SAT Mechanical> Cool Array, OS4x-F1(T2) The vendor is required to provide the technical specifications for the Cool Array temperature sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197565&prj=512&rqi=b3JvIz68FbCRauCHdtIktKSMp4
GI-035 | e40d2b8d-b618-4940-89b2-be0a2efa55b6 | OS4x-F1 | 512 | APAC | Closed | P3 Low CX | borshinhernandez@commtechasia.com | 2026-01-26 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | <SAT Mechanical> Water Leakage Sensor, OS4x-F1(T2) The water leak detector sensor in the PAC location was found with a loose cable. Verify that all sensor cables are properly secured before conducting the IST. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197564&prj=512&rqi=AvlJyVUU7hShG2egl6v2gSpEV3
DCIML3-1-001 | 37cc32cd-1756-44d3-9aac-1ee2853f9d6a | PA10-P1 | 613 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS Template Issue | DCOS |  | Integrated Automation | system | DCIM |  |  |  | List of assets cannot be upsert on DCIM, sync issue 1_GEN_A 1_GEN_A_DT 1_CWST_01_FCV03 1_MVTB_A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614807&prj=613&rqi=c0SOZziCHEduy4u8s3q2OZqOUs | https://equinix.facilitygrid.co.uk/x/project/613/system/12280
DCIML2B-1-001 | 6a19b7c5-03ec-492d-b37d-2f4ca79382ea | PA10-P1 | 613 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS | L2B | DCIM Maximo Issue | DCIM |  | Integrated Automation | system | DCIM |  |  |  | Maximo ID asset missing for all PA10.P1 assets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614798&prj=613&rqi=nuKant83nvb7Y3wBVOGJqI82dR | https://equinix.facilitygrid.co.uk/x/project/613/system/12280
BT1DCOS-1-001 | e5694f24-1987-4d29-8633-e66d1e9bad70 | PA10-P1 | 613 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCIM Cooling Zone Issue | DCIM |  | Integrated Automation | system | DCIM |  |  |  | Location Vector missing for Mech assets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614797&prj=613&rqi=rFwraSu6uLskteMIF9Qo9LsRTi | https://equinix.facilitygrid.co.uk/x/project/613/system/12280
DCIML3-1-002 | e3f2dd8a-60a2-467a-a608-456e6a177522 | PA10-P1 | 613 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS Template Issue | DCOS |  | Integrated Automation | system | DCIM |  |  |  | UPS Resiliency Calculation must be update to integrate UPSs of Block A Generator Resiliency Calculation must be update to integrate Gen Block A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614833&prj=613&rqi=rfzkrIgaA8dnuuH38pvdBPrEiZ | https://equinix.facilitygrid.co.uk/x/project/613/system/12280
DCIML4-2-001 | d7e33e46-ac14-4abc-98ab-8e21fed45e3b | PA10-P1 | 613 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCIM Cooling Zone Issue | DCIM |  | Integrated Automation | system | DCIM |  |  |  | Zone informations (Location Vector) missing for all assets concerned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614809&prj=613&rqi=F4VXoNcpmMGMP0iSZmfa6vQzAK | https://equinix.facilitygrid.co.uk/x/project/613/system/12280
GI-010 | 396cd4ce-462d-43ca-bf3c-fa181e43370d | PA10-P1 | 613 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-02-26 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning |  | Mechanical â€“Air | equipment | 1-CRAH-M1-043 | CRAH - Computer Room Air Handler (CHW) |  |  | During L4 redundancy testing of the CRAH, The Kopex condensate drain pipe of the CRAH became loose as fans were rotating and became lodged. This caused an audible noise and CRAH was disabled to investigate and test was paused. After investigation was carried out by VERTIV representative, it was agreed the CRAH was not visually damaged and to continue the redundancy test to completion. Replacement of damaged pipe plus any further inspection may be required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352274&prj=613&rqi=eTKkRQ5yHyRGQvBRkZZLCH8oCt
GI-009 | 85860ab4-7011-4ca3-886c-630e210c9fbc | PA10-P1 | 613 | N-EMEA | Closed | P2 Medium CX | paulm@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  | Direct Expansion â€“ DX | equipment | 1-FCU-R1-01 | DXID - FCU/DX Indoor Unit |  |  | Asset name is incorrect. DCOS naming indicates 1-FCU-R1-30 Clarification is urgently required as RT, YT, Test reports and Facility Grid will require amending to the correct asset name. Formal proof of correct name required to close issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198245&prj=613&rqi=vRHouiyV7vXpJgnPzrNEh4R8sH
SOR-10-001 | 468a938a-352b-b6f2-16e7-8b99f863d4f9 | PA10-P1 | 613 | N-EMEA | Closed | P2 Medium CX | andrewa@straightlineconsulting.co.uk | 2026-01-30 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | Racking out system of the G2 Breaker is faulty | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198014&prj=613&rqi=euXgyfFqGffoMiHvdGWYjOyI4H
GT1ELEC-2-001 | 67135777-b310-480f-b7eb-4def8110ef9c | PA10-P1 | 613 | N-EMEA | Closed | P2 Medium DCOS | mirceag@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS Graphics Issue | DCOS |  | Electrical â€“ MV | equipment | 1-MVTB-A | MVTB - Medium Voltage Transfer Board |  |  | 1-MVTB-A Point to graphic issue As shown in the attached screenshots, the status displayed does not match the graphical status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197719&prj=613&rqi=1e1C7O0B9IiTFpK7jEnLDYDwuw
SOR-6-002 | 179ff887-a0ab-4b10-965d-dcedf8519810 | PA10-P1 | 613 | N-EMEA | Closed | P3 Low CX | mirceag@straightlineconsulting.co.uk | 2026-01-23 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1-GEN-A | GENL - Generator (LV) |  |  | 1-GEN-A FUEL SYSTEM CONTROL PANEL CPA10c During the visit of the CPA10c control panel i found the new cables installed are not labelled and some existing cables but not connected to any terminal .(currently loose) , they should be at minimum isolated and terminated into WAGO | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197505&prj=613&rqi=miBjA1PaymrTj4aUOLRfP8qxlL
YT1ELEC-53-001 | d93f0c84-33e2-4dca-8a34-e5da228832c0 | PA10-P1 | 613 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-01-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1-MLTX-A | MLTX - Transformer (MV-LV) |  |  | Arc Flash Labels are not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197504&prj=613&rqi=isWkkJTO4dCnuS5tS4y8uSgSEa
YT1ELEC-2-001 | 90cdd365-73fa-4b00-8bf5-39cc11db42f7 | PA10-P1 | 613 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-01-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1-MVTB-A | MVTB - Medium Voltage Transfer Board |  |  | Arc Flash Labels are not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197506&prj=613&rqi=VhVq3mExZYQCqV5N4ko2bNMBaH
RT1ELEC-22-002 | 17ad3bd9-8b51-4e7d-a077-86950565dad0 | PA10-P1 | 613 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | CMM - Cummins | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1-DP-A-3 | DB - Distribution Boards |  |  | The label for Q7/10A the labels shows Q7/2A . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196767&prj=613&rqi=lRkP4WrcBKEBrkQJdrnEgiN7TG
RT1ELEC-22-001 | 39d1bd03-94ba-5bbd-3231-119fddc4392b | PA10-P1 | 613 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | CMM - Cummins | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1-DP-A-3 | DB - Distribution Boards |  |  | Permanent equipment labels affixed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196763&prj=613&rqi=3NmGGiiEuMI0Ygv4uGpUw7yu9O
YT1MECH-27-004 | 7b8f1830-f635-469b-b6a5-5ffa47d2822f | PA10-P1 | 613 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Documentation not issued/ Required | Commissioning |  | Direct Expansion â€“ DX | equipment | 1-CU-R1-30 | CU - Condensing unit |  |  | Vendor L3 Start Up Method Statement not available on Project Portal | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196711&prj=613&rqi=onMNhwpUxz3WtBux5F8NjofWPH
YT1MECH-26-001 | 8bf67055-3b29-47b7-8b9d-875834d60c5e | PA10-P1 | 613 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Documentation not issued/ Required | Commissioning |  | Direct Expansion â€“ DX | equipment | 1-FCU-R1-01 | DXID - FCU/DX Indoor Unit |  |  | Missing Installation and Start-up Manual for DX | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196708&prj=613&rqi=Bubh3kOAKf2k2JFPBizZlSKM6s
YT1MECH-27-003 | 76fe30a2-47f7-4af3-b498-fe34aecd7e39 | PA10-P1 | 613 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-12 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Installation not complete | Commissioning |  | Direct Expansion â€“ DX | equipment | 1-CU-R1-30 | CU - Condensing unit |  |  | Drainage Lines are not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196710&prj=613&rqi=joA1y2xBzd6KPyFlWD5Om0lKfD
GI-008 | 2fcd8535-1a8a-412b-96f2-50158351936d | PA10-P1 | 613 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-08 04:00:00.000 +0400 | Electrical Engineer |  | Documentation not issued/ Required | Commissioning | [7 empty] | DX Sequence of operation - PA101-BYE-ZZ-ZZ-TS-M-ZZZZ-0053 Below EQX comments to be updated to SOO and new revision uploaded to ASITE. Part 6 - How are PPR/PCR room low temperatures managed? Part 7.1 - Temperature setpoint adjustment is via DCOS only. How are wall mounted thermostat adjustments restricted to users? Part 7.1 - Battery room conditions are quoted as 22*C +/- 2*C which implies heating-not described here. Clarify including how units are configured to ensure they do not fight each other Part 7.2 - What are major / minor faults? Part 8.1 - Temperature setpoint noted as 22*C-does not cover PCR/PPR rooms Part 8.1 - Does not detail how thermostat is locked against future user adjustment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196595&prj=613&rqi=3k6ldkr2XAmuz7VkO3cbTgLNdt
YT1MECH-31-001 | aac29b5c-a855-8ad0-2cb6-3e6c2b66f1f8 | PA10-P1 | 613 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | equipment | 1-CWST-01-CWP-M1-03 | CWP - Condenser Water Pump |  |  | Correct source / destination cable required to indicate where equipment fed from. Issue applies to 6no. pumps in PPR room. Photo required of all labels to close issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196503&prj=613&rqi=O1jNgOtO1PbVSoABly0KbLRCuq
YT1MECH-29-002 | 61c606d5-849f-640a-f78d-62f83d808b46 | PA10-P1 | 613 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2B | Labelling | Commissioning |  | Direct Expansion â€“ DX | equipment | 1-CU-M1-30 | CU - Condensing unit |  |  | Power Source / Destination cable label missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196384&prj=613&rqi=GgaaRBzRly7SKnpSA9yZRClU4M
YT1MECH-29-001 | 26cef3ac-d3a2-7cce-8313-c77c88d9fc6d | PA10-P1 | 613 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Direct Expansion â€“ DX | equipment | 1-CU-M1-30 | CU - Condensing unit |  |  | No drainage lines are installed on unit for condensation. Unit installed inside electrical room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196382&prj=613&rqi=kLbN5d8PDiyhxHGd7qgfXDasQk
YT1MECH-27-002 | 170ffa3a-86ce-4a03-1640-66da2a0af06a | PA10-P1 | 613 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-06 04:00:00.000 +0400 | General Contractor | L2B | Installation not complete | Commissioning |  | Direct Expansion â€“ DX | equipment | 1-CU-R1-30 | CU - Condensing unit |  |  | No drainage Lines are installed on unit for condensation. Unit installed inside electrical room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196383&prj=613&rqi=kCkCZ8iBYHJsA8vrf2oARwb57D
GT1MECH-51-001 | 3189fcca-fee2-da11-c508-c7a2a383f9b7 | PA10-P1 | 613 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-05 04:00:00.000 +0400 | Electrical Engineer | L3 | DCOS General Issue | DCOS |  | Mechanical â€“Air | equipment | 1-CRAH-M1-043 | CRAH - Computer Room Air Handler (CHW) |  |  | When simulating return air temperature / humidity sensor fail, the alarm appears on the CRAH HMI as normal. There is no indication on DCOS of sensor failure or appears in issue log. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196340&prj=613&rqi=zC3gGKyjtzYjEfoShjKFmPD9yV
GT1MECH-51-002 | a05e6747-c8d3-8fc6-d4d2-c537de40c9e1 | PA10-P1 | 613 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-01-05 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Commissioning Issue | Commissioning |  | Mechanical â€“Air | equipment | 1-CRAH-M1-043 | CRAH - Computer Room Air Handler (CHW) |  |  | When CHW inlet supply is isolated, high supply temperature alarm is raised at the DCOS but CRAH HMI shows no indication | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196347&prj=613&rqi=MuEi4HpUnjGfN2nFQ1wrAmD2yn
GI-012 | bc58e731-7065-45f0-a925-6485af9b25a8 | PA10-P2 | 661 | N-EMEA | Closed | P2 Medium DCOS | andrewa@straightlineconsulting.co.uk | 2026-07-23 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning | [7 empty] | Temperarture sensor not installed on a section of the Redundant Busbar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630651&prj=661&rqi=eYsJebP7HVeiH05Wp0u6A28AEW
GI-011 | ffa5c048-ff45-4882-9ef3-e0be0b143513 | PA10-P2 | 661 | N-EMEA | Closed | P3 Low CX | magatte.sene@eu.equinix.com | 2026-07-16 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | [7 empty] | The Transformer door cannot be opened from the inside. it's imperative to resolve the issue to ensure the safety of personnel working inside the transformer enclosure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629805&prj=661&rqi=6N8tdXZbwtof5GcA7OoPLCZKuX
GI-008 | 739601a2-11d2-4394-a7fa-18ed1b75c546 | PA10-P2 | 661 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-06-29 04:00:00.000 +0400 | Electrical Engineer |  | General Design Issue | Design | [7 empty] | Concern has been raised regarding gaps in the false floor around some equipment in UPS. This may affect room cooling when carrying out redundancy testing of the CRAHS during full load testing of electrical equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627321&prj=661&rqi=mPCL1CQ8Pk2QUoWwoYZKE0MEVc
GI-005 | 2f0c6bd9-b7ff-4660-a0df-f6a0e89a4a86 | PA10-P2 | 661 | N-EMEA | Closed | P1 High DCOS | andrewa@straightlineconsulting.co.uk | 2026-05-06 04:00:00.000 +0400 | General Contractor - Electrical |  | DCOS Comms Issue/ Fault | DCOS | [7 empty] | IP Address and VLAN not configured like describe on the SE document DCOS IP Address Schedule. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620645&prj=661&rqi=LshBYepfUoq3BdxWhViFw91Vjf
YT1FD-4-002 | 40238134-295d-e735-0b0a-eb8d9edb574d | PA10-P2 | 661 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning |  | Fire Detection | equipment | 1-MSD-21 | MSFD - Motorised Smoke Fire Damper |  | VU12 | Cable labels not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619094&prj=661&rqi=AmycmZeeAfox28bIKv7FYKbBFO
GI-004 | 33d79f6a-6607-41dd-a1af-a2ebd8b032fd | PA10-P2 | 661 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-04-22 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [7 empty] | MV Scada issues on SUDB-2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619212&prj=661&rqi=N5919MnZ2JK9hx5RdE7s22tFoC
YT1FD-4-001 | fdb9665b-51b4-50ee-bee8-708dc747fb3f | PA10-P2 | 661 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-22 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Documentation not issued/ Required | Commissioning |  | Fire Detection | equipment | 1-MSD-21 | MSFD - Motorised Smoke Fire Damper |  | VU12 | Static Cable Tests and Inspection Reports (power) documentation not available | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619093&prj=661&rqi=StU3Mgr2OMoDoZH5PqzyWXr0FY
GI-003 | 1d6d8206-7bd8-4af2-a9cf-27e24ff796e3 | PA10-P2 | 661 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-04-22 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [7 empty] | There is an HMI operational issue on SUDB-2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619211&prj=661&rqi=qZo9821pMQg7Rs1fWxyB3lZtmI
GI-002 | 41c9c306-f9f3-4f93-8d2c-ab157e26ebc8 | PA10-P2 | 661 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-04-16 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [7 empty] | There is a issue with the Power factor on the MVTB-E. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618490&prj=661&rqi=Yf4py3KDTsh6Vaq6zYTNf9PHAO
YT1FS-4-001 | 4f714b28-d479-8f66-74d0-be110087e875 | PA10-P2 | 661 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning |  | Fire Suppression | equipment | 1-MFD-152 | FD - Fire Damper |  | CR60-1S VIM | Both cable labels missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617653&prj=661&rqi=cD64kiTl0gU8GneHILxGLQai7S
YT1FS-9-001 | c322a673-d722-63e1-120a-0a83952ab89f | PA10-P2 | 661 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning |  | Fire Suppression | equipment | 1-MFD-155 | FD - Fire Damper |  | CR60-1S VIM | Both cable labels not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617669&prj=661&rqi=OGdeE8ajFqmW82r8fb3nbgmya2
YT1FS-3-001 | ebb2d6da-7434-131d-f056-e3a84d55340c | PA10-P2 | 661 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning |  | Fire Suppression | equipment | 1-MFD-151 | FD - Fire Damper |  | CR60-1S VIM | Both cable labels not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617667&prj=661&rqi=mh4xqR6zclJOzCMfsUtpb0Cc5M
YT1FS-6-001 | ee1c1a02-ed34-50b2-dea1-a5463c709f3f | PA10-P2 | 661 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Labelling | Commissioning |  | Fire Suppression | equipment | 1-MFD-39 | FD - Fire Damper |  | CR60-1S VIM | Both cable labels not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617668&prj=661&rqi=lFALlOSOyV7NWV37ptQn86ugYh
YT1ELEC-74-001 | 9f6d353f-17b4-4479-8780-1a37233c3661 | PA10-P2 | 661 | N-EMEA | Closed | P3 Low CX | paulm@straightlineconsulting.co.uk | 2026-03-24 04:00:00.000 +0400 | General Contractor - Commissioning | L2B | Documentation not issued/ Required | Commissioning |  | HVAC | equipment | 1-HT-M2-01-1 | TRACE - Trace Heating |  | Eltrace | L3 Green Tag Cx method statement not available on Asite. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616345&prj=661&rqi=oNGYSW8vtrHivhZ6JpXFnoA96o
RT1ELEC-80-001 | 15f7e2d2-86ca-4758-989c-8206ce5fc76f | PA10-P2 | 661 | N-EMEA | Closed | P3 Low CX | andrewa@straightlineconsulting.co.uk | 2026-02-26 04:00:00.000 +0400 | General Contractor - Commissioning | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1-UMDSB-M1-2-11 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | Permanent equipment labels affixed and are as per approved colour scheme. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483354&prj=661&rqi=70JAorlxxklXYb0YsU9Sv3tyY7
IST-32-002 | ede03d2c-a4b4-4a3e-96d7-b29f548b5db3 | PA12x-1 | 263 | N-EMEA | Open | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-09-19 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Complete | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Smoke Extract (ZF) reset key switch not working, Connected via Ewall H Block. Dampers have to be manually closed. Working on battery only. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638824&prj=263&rqi=lZOT6TP8v7NxVjiEwydobIuTQR
IST-32-003 | 86237cc2-3a67-49f9-b7c6-abc7db520f8e | PA12x-1 | 263 | N-EMEA | Open | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-09-19 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Incomplete Connections | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - UPS room DSF system does not shut down upon activation within UPS room | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638825&prj=263&rqi=qBC3XPk63ialhaj0ereRw2hlKm
IST-32-001 | a3c8c36a-7355-4e91-8b39-a38910d774d3 | PA12x-1 | 263 | N-EMEA | Open | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-09-19 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Labelling | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Labelling as per old ZDA numbers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638823&prj=263&rqi=axGzebHp4BgZpJ4AyNeXJg4C90
IST-32-004 | 0bdf2c0f-3c55-438d-9d61-fdac5354b9ec | PA12x-1 | 263 | N-EMEA | Open | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-09-19 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Correct | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - AHU_M5R2_07 not operation due to phase 2 works. Temp solution within R2 and M4 Battery rooms should work as per permanent AHU under fire condition. Temp solution still stays operational after Fire activation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638826&prj=263&rqi=qaScrG2jdm8riqq1ZK5afyZrE4
GI-664 | bf40363e-1f66-4336-bd4f-c50b04addcfc | PA12x-1 | 263 | N-EMEA | Open | P3 Low DCOS | aarond@straightlineconsulting.co.uk | 2026-09-10 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | Schneider is required to revise the schematics to show the Max Cool activation contact as Normally Open (NO), as specified in the approved SOO. The current schematics incorrectly show the contact as Normally Closed (NC). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637586&prj=263&rqi=TnTSU8KSIkixjIjEfzhGNnypuO
GI-661 | 37e4edcb-7c4a-4c15-84e0-9b226c96696e | PA12x-1 | 263 | N-EMEA | Closed | P3 Low DCOS | aarond@straightlineconsulting.co.uk | 2026-09-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS | [7 empty] | MOT - MECHANICAL - CRAYS The Enable Setpoint Shift function changes the supply temperature setpoint from 25Â°C to 24Â°C when the coil supply temperature remains 5Â°C above setpoint and the valve position is greater than 80% for more than 60 seconds. The setpoint shift is visible on the Vertiv controller but is not displayed on DCOS. DCOS/Vertiv to investigate and confirm that the active shifted setpoint is correctly communicated and displayed on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637433&prj=263&rqi=lmEWvtyXtpzimtrhNwSRJIze1o
GI-662 | 1a7f1667-cc54-4338-812e-39da249bb8a3 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-09-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | Mechanical - Max cool system - in event of loss of power to Max cool panel both supplies, SOO Max cool indicates it max cool should be operated but wiring of the panel & schematics do not. schneider to confirm to if max cool should operate under full power loss | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637431&prj=263&rqi=O8l9Krd1xSfXCLUdVksFskBXIB
GI-656 | 850c23fe-fcf5-4595-a681-e9ecf8f4466c | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-09-03 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | Mechanical - Max cool sensors / DCOS gateway sensors - multiple TT sensors are mixed up & wrongly labelled between Max cool system & DCOS GW TT Sensors, All Data halls to be checked 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636671&prj=263&rqi=YHCF2WS4UCpWUgDwl1QKHwyr8n
GI-655 | 58545785-6f4e-4aa5-b2bf-830f6dd86e8c | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | MOT â€“ CRAYs DH03 Prior to testing the fanwalls, it was observed that multiple sensors were not reporting to DCOS. This issue was first noted following completion of the permanent fanwall shielding rectification, which replaced the temporary fix. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636536&prj=263&rqi=cDkiTBuEvH3hezxPfqVOkRMsMt
GI-622 | 9c380a0b-fe30-4048-99e5-de51b9bef543 | PA12x-1 | 263 | N-EMEA | Open | P3 Low CX | gabrielsokolowsky@sygna-emea.com | 2026-08-21 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Commissioning Issue | Commissioning | [7 empty] | 1MSB_R1-Q28 : The micrologic menu cannot be accessed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634590&prj=263&rqi=Tiurz85Ww5yPxh4Fx79wQmlgXT
GI-623 | 2233480c-4492-46b3-8455-6a4668bd4528 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gabrielsokolowsky@sygna-emea.com | 2026-08-21 04:00:00.000 +0400 | General Contractor |  | Cleaning | Commissioning | [7 empty] | Pigeon nest on busbar, phase 1, third floor, above emergency stairs door, MeWall M3 corridor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634595&prj=263&rqi=kJy37x2SwHCyi3wmNulzjZv9rY
IST-23-003 | 9dd78f50-d2a3-4ca4-b46d-f891692d5d98 | PA12x-1 | 263 | N-EMEA | Open | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | REH - Rehlko Gens | L5 | Installation Not Correct | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | IST 2 - Generator - Fire curtains on ground floor rooms B+C failed to close correctly. during IST activation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634211&prj=263&rqi=3S8Q1TjLthtbTbsuLrqNihjkE9
GI-621 | 2c04ada7-49ff-4969-acbd-26557e1d9000 | PA12x-1 | 263 | N-EMEA | Open | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | General Contractor - Electrical |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment | IST Phase 1.2/1.3 - Test 3.0 Dead Bus Test on String F | integrated systems testing halls 3,4,5 and 6 |  |  | IST 2 - Mechanical - The leak detection alarm for Cable_3_02 was triggered during the test and appeared in the alarm log; however, it was not displayed on the graphics. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634232&prj=263&rqi=QPFKYu51VBKA9eA9oeGtbbvzyr
GI-619 | e69815c8-0f77-45d6-a602-abe7a193f44e | PA12x-1 | 263 | N-EMEA | Open | P3 Low DCOS | jayb@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | REH - Rehlko Gens |  | Component/Equipment Failure | Commissioning | [7 empty] | IST 2 - GEN SCR F,B,M1 and M3 - Power line/ gen graphics showing live on DCOS intermittently even though gens not running. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634229&prj=263&rqi=X2XO3m8FPzcF0rWy06ibziaWP5
IST-31-001 | e768ee9c-440b-40f4-9cbd-a4a75edc3698 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | jayb@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | General Contractor - Commissioning | L5 | Installation Not Correct | Commissioning |  |  | equipment | IST Phase 1.2/1.3 - Test 7.0 Failure of Mechanical Block M2 and IT Block B | integrated systems testing halls 3,4,5 and 6 |  |  | IST 2 - MLTX B core temps showing high core temp on L3 when all other MLTX show higher core temp on L2, suspected incorrect sensor termination in MARS panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634221&prj=263&rqi=goVuuw2LXuY0J4ms4Cll1hqH3J
IST-23-004 | 4c4772a3-3efa-4f2b-8080-c7ff7d7a0600 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | General Contractor - Commissioning | L5 | General Design issue | Design |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | IST 2 - Fire alarm - Thermal detectors in all Gen rooms to be replaced by Smoke detector. during IST 2x thermal detectors activated due to heat from Gen B+C. All thermal detectors are currently isolated via Graphic operating PC for SSI system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634213&prj=263&rqi=PjlK9SVuIwObjf9NiFHZkhfKNy
GI-620 | cb3658a2-b02d-4617-aaf2-cae61dca8555 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | jayb@straightlineconsulting.co.uk | 2026-08-19 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning | [7 empty] | IST2 - GEN C showing comm alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634230&prj=263&rqi=g8vbCFrsNmgjk56pfG5DgwUrJZ
IST-24-014 | f9b26aa3-a045-486d-a09f-f19c6fb366a0 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-08-17 04:00:00.000 +0400 | General Contractor - Commissioning | L5 | Documentation Not issued/ Required | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Block R2. All testing documentation to be submitted for Vesda and Smoke Detection ZDA213 ZDA205 ZDA207 ZDA212 ZDA090 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633938&prj=263&rqi=7oFrUbDtkkDw3Y1LKgzaLlbhBW
IST-32-005 | 1a57a818-9eb0-48ad-819e-1e8785c1a529 | PA12x-1 | 263 | N-EMEA | Open | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-17 04:00:00.000 +0400 | General Contractor - Commissioning | L5 | Installation Not Complete | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - SSI Graphic PC not yet tested for Phase 1 system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633936&prj=263&rqi=vN5cCgFZ18sirjpX2RcNhNsSwl
GI-614 | 4563ecba-8acb-4d93-a77a-990abcc51c91 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low DCOS | joshw@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | DCOS - HLT 2 Ras_04 deviation alarms - 6,7 13,15,16,17 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633775&prj=263&rqi=TUEOVuboudgSBF2yYBdlY0sEeR
GI-611 | 12ea57fa-0394-4dab-a53d-10648c136e1b | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | HLT 2 -Mechanical - AHU's Not working at correct temperature control & operation. Control of heating and cooling systems to be investigated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633770&prj=263&rqi=0IGq4MdQh8r6p05X5m72jY4hWF
GI-616 | 1392d4ce-0a46-4bb0-85d0-76a3c2a439ee | PA12x-1 | 263 | N-EMEA | Open | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | General Contractor - Electrical |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | Electrical - HLT 2 - AHF 02 & 03 - General warning on both units to be investigated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633781&prj=263&rqi=A2tWlX5p2lB8sxVaEVWJM88bsD
GI-613 | 95e69d0f-7d04-45ab-b308-52869373fb6a | PA12x-1 | 263 | N-EMEA | Closed | P3 Low DCOS | joshw@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [7 empty] | Mechanical - HLT 2 - Ras_04 devation alarms - 6,7 13,15,16,17 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633774&prj=263&rqi=1iGCQSpKsosYWKsNG1nzdDW0ng
GI-612 | bab0c682-32b0-43ef-bb2e-9533acdeed99 | PA12x-1 | 263 | N-EMEA | Open | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Not Correct | Commissioning |  |  | equipment type |  |  |  |  | HLT 2 -Mechanical - All Cool Array panels wiring has been amended with poor install & needs correctly installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633773&prj=263&rqi=c3S7YTBLvkAIfK4M5T799QEvMc
GI-609 | 1a4e746b-4405-402b-a460-787ffa5150e9 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low DCOS | markb@straightlineconsulting.co.uk | 2026-08-15 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | LLT - During Fuel Control Panel Controller Failure - DCOS alarm to be changed to red critical alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633764&prj=263&rqi=v1wCq0AKXIFonsOZXTeiP7zmnq
IST-24-013 | bf989327-7212-4579-be2c-8770e2594565 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | jayb@straightlineconsulting.co.uk | 2026-08-14 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Complete | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | sounder Head has been removed from wall | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633616&prj=263&rqi=5OeXu9anocwtb3QRn3yY32IOKV
GT1MECH-744-001 | b4bbc7ce-17fb-42d7-9981-735f2bd9f6ae | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-08-14 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Documentation Not issued/ Required | Commissioning |  | Mechanical â€“ Water | equipment | Leak detection - TQ Panel ( Refrigerant) | LEAK - Chilled water system leak detection |  |  | Electrical - Missing live cable test results | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633617&prj=263&rqi=yfsPkyGr0jwooo8gybMnAX839h
YT1MECH-671-001 | d97a1ce5-f720-484f-b66a-b2083471f6e4 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-08-14 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Documentation Not issued/ Required | Commissioning |  | Mechanical â€“ Water | equipment | Leak detection - TQ Panel ( Refrigerant) | LEAK - Chilled water system leak detection |  |  | Electrical - Missing Dead cable test results | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633618&prj=263&rqi=niy7LC0BgCg7AM7EKSXxHODks6
IST-24-012 | 19ff6dd4-b154-4b10-8e87-aeb122b1bb2a | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-13 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Component/Equipment Failure | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - During HLT ZDA228 activated 2 times without any smoke present in the area. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633394&prj=263&rqi=kPyh4XQazRa4mmXfpfKg6DlwS6
GI-607 | 128190f5-ae9e-4e68-81df-c548ebd701e0 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gabrielsokolowsky@sygna-emea.com | 2026-08-10 04:00:00.000 +0400 | Customer Access |  | Commissioning Issue | Commissioning | [7 empty] | XX | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632883&prj=263&rqi=jUHBo0JP2bwKdbZomkoEJkoWEb
IST-24-010 | 13ff44ac-3aa4-428e-a362-31be1a2cee95 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-08 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Design Correction Needed | Design |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - A100/Securitas Security panel to be moved. the placement of this panel stops the door holder magnet to align. Door magnet holder cannot be extended as this would then stop clear Security access being granted to the Access control reader and panel. Location: Ground floor FoH entrance to Phase 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632775&prj=263&rqi=yH469Wkznf8saQMnZGP8lUCGaz
IST-24-011 | e420e987-9d52-4f22-b5c7-7e9be666f99a | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-08 04:00:00.000 +0400 | General Contractor | L5 | Installation Damage | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Fire Door damage. Location: ground floor FoH entrace to phase 1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632776&prj=263&rqi=bMHCmEZyI8NMmQUQJuKtY4Thvf
IST-23-002 | c3c6995f-e1fc-4a15-b4ea-8077ab49735a | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-08 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Documentation Not issued/ Required | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Design documentation to be submitted to PPA and approved for Sign off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632774&prj=263&rqi=7YExRQ53Qh6IKvrc7eDvqRxJ5V
OPR-1-001 | e31bfefe-1b63-4875-a1a2-f6d0cd8e0d4f | PA12x-1 | 263 | N-EMEA | Closed | Outstanding Paperwork/Documentation | gregb@straightlineconsulting.co.uk | 2026-08-06 04:00:00.000 +0400 | General Contractor - Commissioning |  | Design Correction Needed | Design | [7 empty] | Asset List - Missing assets from Phase 1 construction. Stairwell Smoke Vents Nitrogen System Sprinkler Control panel Life safety remote modules (various locations in riser cupboards) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632572&prj=263&rqi=TCKOtmyIKXUlzKLb4aZwoPzUP5
IST-24-009 | e488278c-c354-4039-97d2-3d4410d4860f | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-06 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Correct | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Poor workmanship in Riser 1288 and 1289. images sent to Essais SSI whatsapp group | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632569&prj=263&rqi=nyG49iHKJ1Elylc9Bu86qQTa1w
IST-24-007 | 55314d5f-5a3a-42c0-b8ac-062664a7bbc7 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-05 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Labelling | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire alarm - Yellow Ex call points have some labelling errors some examples attached. all Yellow Callpoints to be checked with Photo of each call point and location | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632243&prj=263&rqi=Zj6h74ILhEyk0ZOs4vqEt2DiAs
IST-24-008 | 45d4bb04-739f-4ad7-ac20-43a28a49b738 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-08-05 04:00:00.000 +0400 | General Contractor - Electrical | L5 | General Design issue | Design |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm DCOS - Due to incomplete Phase 2 the trouble signal is constantly active due to Phase 2 Rack being incorporated with Genset rack. Equinix to confirm if DC OPs will accept this constant fault. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632254&prj=263&rqi=FSJ2FnTRXl9BpXsKkkCeoHfEXW
GI-593 | 176b3241-488c-49eb-8599-90e061a4e49e | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-07-29 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Damage | Commissioning | [7 empty] | Mechanical - 1CU_M2R1_58 - condenser fan damage. to be replacedÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631220&prj=263&rqi=cWleECdV8kujwh7fFk2oaYGbbJ
GI-592 | 8546b2d8-c77c-470c-be0e-6226579a88f3 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gabrielsokolowsky@sygna-emea.com | 2026-07-28 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [7 empty] | Emergency floodlights are not well installed in MVTB rooms : the wall plugs in place seem to be a model for concrete/brick wall but not for a hollow wall. The statement has been done in block D but it would be probably the same in all MVTB rooms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631057&prj=263&rqi=tJKnZCGQLMlQbtvKJp9HA1DWB9
GI-590 | d3c759e9-69ea-46c3-b5c9-ae2837f5cd89 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gabrielsokolowsky@sygna-emea.com | 2026-07-24 04:00:00.000 +0400 | General Contractor - Electrical |  | Component/Equipment Failure | Commissioning | [7 empty] | 1MDSB_M1R1_3-Q13 During SCCS shift for LV breaker control settings, the authorised person was not able to open the chamber door to access the breaker. This breaker has not been yet checked. Control must be done on W31. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630649&prj=263&rqi=IQvH7kqw2uwM3ZDNoVIyYwWTRT
GI-591 | 9fbbf865-572a-40c1-ba72-c9dc923ef88a | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gabrielsokolowsky@sygna-emea.com | 2026-07-24 04:00:00.000 +0400 | Commissioning Authority |  | General Design issue | Design | [7 empty] | NEUTRAL PROTECTION ON BREAKER 1) ALL CALCULATION NOTES ARE NOT YET FULLY VALIDATED 2) ACCORDING TO THESE NOTES, NEUTRAL PROTECTIONS ARE 4P4D ON A LARGE NUMBER OF CIRCUIT BREAKERS 3) FOR EXAMPLE ON BLOCK D, breakers 1COP_DR2_1-Q01 and 1COP_DR2_1-Q02 WERE FOUND WITH NEUTRAL PROTECTION OFF (4P3D) WHEREAS ON THE NOTE IT IS 4P4D | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630650&prj=263&rqi=ng6VN3bMPvhksYioWA1WZ2mtkQ
GI-589 | 0c8120f2-f261-49db-b2a8-58431f082e03 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gabrielsokolowsky@sygna-emea.com | 2026-07-24 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Component/Equipment Failure | Commissioning | [7 empty] | 1COP_ER2_1-Q07 The MTU buttons for accessing the menu are not working. It needs to be determined whether all or part of the circuit breaker needs to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630648&prj=263&rqi=ZcIXsTWbZUTshPmPt0xnBtWBjA
GI-587 | c11f00fe-056c-4c95-a971-1ee6a8885e77 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gabrielsokolowsky@sygna-emea.com | 2026-07-24 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation Not issued/ Required | Commissioning | [7 empty] | No on-site acceptance specific documentation was found for the installation of the (16A TP+N) MCBs of the fan walls, installed on the cool array's BB. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630646&prj=263&rqi=ZJvixSju8v6WPSXq7ypBItHXKU
GI-588 | a23aa2aa-abf9-4c61-97cb-99fa00837b6d | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gabrielsokolowsky@sygna-emea.com | 2026-07-24 04:00:00.000 +0400 | Equinix Project Manager |  | General Design issue | Design | [7 empty] | For LV SCCS (breaker discrimination study - settings control) : 1UDPR_R2-Q29 breaker is used for the needs of the construction site on phase 2. No control possible for the moment. To be deferred to a future verification session dedicated to phase 2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630647&prj=263&rqi=OkdJn9NWUSeeztIPGcUoupqQNV
GI-573 | a592f04d-7831-4be0-99b1-049f4f65f090 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | garyd@straightlineconsulting.co.uk | 2026-07-22 04:00:00.000 +0400 | General Contractor - Electrical |  | Cleaning | Commissioning |  | DCIM/DCOS | equipment | 1DCOS_1_HMI_02 | DCOS - HMI Panels |  | SCH - Schneider | mechanical asset need cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630276&prj=263&rqi=YAI0NIuaQAaqVyzKYZvKPZeThx
GI-539 | 1f7c9bf7-3317-b979-23c5-8102d0ef2222 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | garyd@straightlineconsulting.co.uk | 2026-07-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Correct | Commissioning | [7 empty] | mechanical earth cable stuck in cover 1EXFM_M1R1_02 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629908&prj=263&rqi=zPG18sEqK7O8aaEkRPvmHP2Rsw
GI-536 | 00494532-e0fb-45a1-b07b-af5c5af26102 | PA12x-1 | 263 | N-EMEA | Closed | P1 High CX | daniel.loayza@eu.equinix.com | 2026-07-16 04:00:00.000 +0400 | SCH - Schneider DCOS |  | General Design issue | Design | [7 empty] | During full load testing of chillers, 3 chiller breakers tripped: MSB M2 - Q-06 - Chiller 1-1 Q-10 - Chiller 3-1 MSB R1 Q-09 - Chiller 1-1 Early indication from AERMEC is that chillers have not over-amped, and early trends from DCOS suggest the breakers in the MSB's did see an overly high current. This leads us to suspect a potential AHF issue or breaker issue that needs to be investigated. BYES need to deploy Danfoss to begin trend gathering and analysis and ITEC need to confirm their equipment is functioning correctly. AERMEC need to provide relevant trend data on those chillers for analysis by the group. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629713&prj=263&rqi=20xJyp3Dq8HsetZkYI9hq1qeAh
GI-537 | 0fb16bed-d291-4857-9989-a171e2d34f6a | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-07-16 04:00:00.000 +0400 | REH - Rehlko Gens |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | MOT - Â TTK fuel leak detection system in the pump rooms is now fed from batteries. This change was implemented after IST. Actions required: 1. Provide the intervention report for this change. 2. Provide updated drawings reflecting the new power supply configuration. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629772&prj=263&rqi=rZPuviC1S0VP9bCE4rrWFoNtst
IST-24-004 | ed44d32f-b7e7-46ee-affd-213ed9d07a44 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-08 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Correct | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - DH1-6 Dampers do not open after fire signal is received. Belimo seems to operate correctly but the damper blades do not open 1SSIRCFD_NO_0159 1SSIRCFD_NO_0160 1SSIRCFD_NO_0161 1SSIRCFD_NO_0162 1SSIRCFD_NO_0163 1SSIRCFD_NO_0164 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628292&prj=263&rqi=Kjss64gsOGztu8Lkpw6LTD4mym
IST-24-005 | fcfce782-16e3-42ea-b2b6-140358672228 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-08 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Correct | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Smoke extract dampers failed to operate correctly. Dampers didnt open activation and/or close on reset. 1SD_NC_0021 1SD_NC_0022 1SD_NC_0023 1SD_NC_0024 1SD_NC_0025 1SD_NC_0026 1SD_NC_0027 1SD_NC_0028 1SD_NC_0029 1SD_NC_0030 1SD_NC_0031 1SD_NC_0032 1SD_NC_0033 1SD_NC_0034 1SD_NC_0035 1SD_NC_0036 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628295&prj=263&rqi=rvbOFyi4vx4A77z0XH0lmbTXdK
IST-24-006 | c722425b-5e30-414d-b5f2-646b49c3b18f | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-08 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Complete | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - DCOS connection not completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628298&prj=263&rqi=EnvR3QNtMtZf7RsRUQZN0u6li9
GT1FD-80-002 | 84aadf88-18a9-48ce-9c84-4cb19a1d8300 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-07-07 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Design not as Specified | Design |  | Fire Detection | equipment | SSI_RACK_1 | FACP - Fire Alarm Control Panel |  |  | Electrical - ZDA. PPA stated thresholds differ from the BYES Aspire design calculations. Should PPA values be adhered too in Design for smoke activation levels? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628249&prj=263&rqi=e05VdzES6fnYZbEpNi85zrvkju
GI-504 | 3fa05696-12bb-45e5-9a56-8c4a54c97089 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-06 04:00:00.000 +0400 | General Contractor - Electrical |  | Cleaning | Commissioning |  |  | equipment type |  |  |  |  | Fire alarm - All DH1-6 require Vesda pipework to be cleaned. extremely dirty with Dust from construction works in all Halls | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628014&prj=263&rqi=hMgYjLNBL96seRgEAZYnjxm0u3
IST-24-003 | d17d30bf-7672-480d-ad2f-8440587e3c51 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-07-05 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Documentation Not issued/ Required | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - All updated drawings/documentation to be submitted to PPA for approval prior to C&E testing. As built drawings, C&E Matrix to show agreed changes to allow Testing and checklist to be signed off against valid documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627945&prj=263&rqi=hJsLpBKwYpjIk068w0i197yN2l
IST-24-002 | 50859f5c-4ecd-41a4-89f2-c14e6a27269f | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-05 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Correct | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire alarm - Automatic fire compartment doors are not closing sufficiently to seal the barrier of compartment. Air balance could be the issue stopping doors fully closing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627942&prj=263&rqi=50Q7s0g7ricxzgILO5HlIB7MgB
GI-502 | 7a074b25-1b23-4e93-a32a-f7e4ce7dac0a | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-07-02 04:00:00.000 +0400 | General Contractor - Electrical |  | General Design issue | Design |  | Fire Detection | system | Fire Detection |  |  |  | ZDA - within all DH's 1-6 , in certain HAC's the smoke extraction ductwork and sprinkler pipework is obstructing the Vesda detection holes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627688&prj=263&rqi=YWvDykJjJ9oHFUI6XL2YuCQxr7 | https://equinix.facilitygrid.co.uk/x/project/263/system/14098
GI-610 | b5776389-55e6-40a4-9b4f-f56037f127dc | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | HLT â€“ Mechanical â€“ Vertiv White Space Sensor Naming Discrepancy The Vertiv White Space (Cold Aisle) sensor naming convention does not align with the naming used in DCOS. In the field, the cold aisle sensors are labelled as White Space 3 & 4, whereas DCOS identifies these same sensors as White Space 5 & 6 for all standard Cold Aisles (with the exception of the Extension Units). This discrepancy creates confusion when comparing field readings with DCOS data and during fault investigation. Vertiv is requested to confirm the correct sensor naming convention and ensure all White Space sensors are clearly labelled in the field to provide consistency between the physical installation and the DCOS interface for operations and maintenance personnel. Evidence: DCOS screenshots for DH05 and DH06 are attached, showing the Cold Aisle sensors identified as White Space 5 & 6, highlighting the discrepancy with the Vertiv field labelling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627523&prj=263&rqi=2tAAVW7546zYiCdvVmZ0h9M9Gt
GI-501 | 2c4b2623-3ef2-484a-a515-d85e5c204c97 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | HLT â€“ Mechanical â€“ DCOS Temperature and Max Cooling Sensor Labelling The DCOS Temperature Sensors and Max Cooling Sensors throughout Data Halls A, B, C, D, E and F have not been labelled as previously agreed with BYES. The absence of clear identification is causing difficulties when validating sensors during commissioning and fault-finding activities. It will also present ongoing challenges for operations and maintenance personnel when identifying and verifying individual sensors in the future. All DCOS Temperature and Max Cooling sensors should be permanently labelled in accordance with the agreed naming convention to ensure clear identification and maintain consistency with the project documentation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627524&prj=263&rqi=1I7LoaRnmlxRZ4mQc4MEjuvtml
GI-500 | 23073868-a232-47c6-82b0-9d06ba1bb433 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | Multiple drawing folders have detached and fallen inside the cooling corridors. The folders are not securely fixed and should be re-secured to prevent obstruction, damage, or a potential housekeeping/safety hazard. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627516&prj=263&rqi=18mjpNLiD9ZmvBgvgRmpLar0ax
GI-478 | c892e860-14c3-4f4e-8c67-76aa01d72327 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | General Design issue | Design |  |  | equipment type |  |  |  |  | MOT - Multiple strings have buffer tanks in bypass mode during steady-state operation. In case of a utility outage, the buffer tanks will not support the critical load (TT05: below 21.5Â°C). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627373&prj=263&rqi=z5ucEA6482NdjgNIHkXrHTe7Ad
GI-463 | c743c2dc-ae7d-4045-a8fb-572d0b7c0f2e | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment type |  |  |  |  | LLT - ,BMS monitoring was observed to be intermittently lost and restored. The vendor confirmed that this is a recurring issue. Schneider attempted to reboot the BMS server on-site; however, the reboot did not restore BMS monitoring. Schneider subsequently conducted an unplanned intervention during the night to restore the system. Actions required: 1. Provide the intervention report for the night activity. 2. Provide RCA for this recurring BMS monitoring loss. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627355&prj=263&rqi=VunLrBeXj4RXi3JOL5DzN98L64
GI-472 | 49b69d80-81a5-4fc3-8df8-96478f8cd22d | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | MOT - Testing at the generator control panel for daily tank levels No alarm received on the BMS when failing the analog level sensor on the daily tank. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627366&prj=263&rqi=h7uqSLv2pZeFJHzFaaJxTTsXbd
GI-647 | 19f5a52e-8e43-4bc9-bc45-fc0bf58db47c | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ Mechanical â€“ 1MAU_M3R1_02 generated a SAT High Temperature Alarm (34.5Â°C) at 15:55. At the time of the alarm, DX Unit 1 was OFF and DX Unit 2 was ON. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627320&prj=263&rqi=hMI68qmIKj7WLo6Q4us3zbBHLj
GI-474 | d6b28199-2a9b-470c-a132-28db58a38cc7 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | General Design issue | Design |  |  | equipment type |  |  |  |  | MOT - Testing at the generator panel for TTK leak detection on Gen room. The TTK system is now fed from generator starting batteries. This change was done after IST. No schematic drawing exists for this change. Actions required: 1. Provide the intervention report conducted after IST. 2. Provide updated schematic drawings reflecting the new power supply configuration. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627368&prj=263&rqi=6dQq6Myvk8TlaNfqGKKTeVNmnT
GI-482 | 9c061e15-9268-4b5d-87e1-7ccf0eeb76bd | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  |  | equipment type |  |  |  |  | MOT - Loss of power to out of sequence SCP (2 chillers in standby). The two pumps of the affected string started and went to 40 Hz. The chillers of the affected string started, then different chillers began to lock on flow. The PCP then started other chillers, creating multiple failures on the cascade. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627378&prj=263&rqi=6kNn98gQ3T2C7YziqyTCEo8fnK
GI-468 | 3f577187-4139-41ea-8a1a-fa47ce29b77a | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | DCOS - Equinix |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | MOT - Testing Diesel pump for loss of communication from the PLC. A bad/loose connection was found on the pump flow switch and FCP 1. Rehlko technician intervened and corrected the connection. The flow switch is wired back to FCP 1 through a junction box fixed in a location exposed to vibration, making loose connections likely to recur. No alarms are received when losing power or connection to the flow switch, leaving the system in an unhealthy state until a fuel call occurs to initiate troubleshooting. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627362&prj=263&rqi=lPZcNhCsRJMeFHtogT1opuJROg
GI-480 | b934a5f9-b23a-4c70-ba01-982f63b6a9ab | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  |  | equipment type |  |  |  |  | MOT - Loss of 24V to out of sequence string SCP (2 chillers in standby) The two pumps of the affected string started and went to 30 Hz. The chillers of the affected string started, then different chillers began to lock on flow. The PCP then started other chillers, creating multiple chiller failures on the cascade. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627375&prj=263&rqi=0fqess8ECRfEKvH5qEKuZv2Y2x
GI-652 | 873b060f-8498-41a2-a705-fc57b8eaebae | PA12x-1 | 263 | N-EMEA | Closed | P1 High CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Not Correct | Commissioning |  | HVAC | equipment type | Data Hall Heat Load Test Phase 2 | Data Hall Heat Load Test Phase 2 |  |  | HLT - Cool Array sensors calibration discrepancies across all halls. HLT â€“ Mechanical â€“ Calibration discrepancy identified between 1CA_M1R1_20, 1CA_M1R1_18 and the Data Hall temperature readings, with deviations of 1.1Â°C and 1.4Â°C. Further investigation - All Vertiv sensors have calibration discrepancies, Sensors have been replaced, software downgrades/upgrades, Factory support on sensors and still issue remains across all halls with calibration discrepancies 3-4+ degrees out | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627337&prj=263&rqi=nkgSYYzCn5SpFdJY7bnq42CFEH
GI-467 | bb56e50b-2fbe-4ae3-8f4a-344df4a92230 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | MOT - Testing Diesel pump for loss of communication from the PLC The way both FCPs are connected to both pump contactors differs between FCP 1 and FCP 2. Having identical systems each wired in a different way makes troubleshooting difficult. Only the Rehlko technician who installed the system is aware of the wiring differences. action to audit the two FCP's and ensure they are wired in the same way as per design intent and provide the as-built drawing (drawing not available on site during testing) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627361&prj=263&rqi=YrGoYsZKEPpaOW35lKpt7QcNZW
GI-493 | 4a3602a9-6037-4116-a3f5-aaf3476bf092 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  |  | equipment type |  |  |  |  | MOT - Chiller flow switch sensitivity target approx 28 L/s which is noted as below AERMEC setting | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627394&prj=263&rqi=Uo8jf07Uk5V1vg5lqWpdk6nEXt
GI-499 | 6fb19732-5115-4caa-b961-3c7a696b55e4 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Component/Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1CHWSTR_M3R1_6_ELC_1 | CP - Control Panel |  |  | Mechanical - found blown fuses during tests today. That requires further investigation as it has happened previously. RCA to be provided for each blown fuse. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627472&prj=263&rqi=rMCzd1FzWchfmETdUcpl8VYDcq
GI-473 | f84a939b-ae1b-478c-92da-1caee91bb66d | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Electrical |  | General Design issue | Design |  |  | equipment type |  |  |  |  | MOT - On the day of testing, it was informed that a fire signal from the fire system stops the generator. Rehlko vendor could not provide further information. The signal wired from the fire system to the generators was not identified. No schematic drawing exists showing how the fire system is connected to the generators. One fire panel sends hard-wired signals to stop the generators in case of fire . A centralizing panel sending a shutdown signal to each generator poses a high availability risk. High availability risk if there is a common dependency with signals wired from the same location to all generators. In addition, a fire curtain was observed in place. No one could explain how the system works and its impact on generator availability. All relevant documentation must be submitted to assess the risk. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627367&prj=263&rqi=MutlJz7t9c2ZT5WTqQhOrj2ezQ
GI-641 | 69335312-c621-4966-b0b8-72583a82e114 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR_3_1 â€“ Evaporator Low Alarm received at 12:40 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627309&prj=263&rqi=Wt2otNTnE5O4BIP3Xyd5bU81PJ
GI-642 | 1f482806-0c55-4170-892a-db288d2d666a | PA12x-1 | 263 | N-EMEA | Closed | P3 Low DCOS | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | DCOS Comms Issue/Fault | DCOS |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CRAH_ER1_27 Had a communication alarm present during the heat load testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627310&prj=263&rqi=eMzdhDyLdkOBiMD0IrAbwAUJbC
GI-469 | ac0401b5-9ffc-4088-80ba-ff3a32d42f7b | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | MOT - Testing at the Fuel Control panel for loss of external fuel pipe heaters. The alarm on the HMI is not matching the labeling on the unit in the field. The system is not monitored by the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627363&prj=263&rqi=GP0i3MO1ojj4z2hM0vJEHpFSzX
GI-475 | 1913a22a-e362-4b1c-b8aa-9945685ab282 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | Design Correction Needed | Design |  |  | equipment type |  |  |  |  | MOT - Testing at the generator panel for TTK leak detection on Gen room. It was informed that triggering fuel leak detection in the Gen room will open the GRMU breaker, which poses a high availability risk. Stepping on the TTK cable resulting in opening the MV GRMU breaker is not an accepted design. Actions required: 1. Provide all details related to this design. 2. Provide a list of alarms that open the GRMU without impacting generator operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627369&prj=263&rqi=VX0gup9zAT5mC23r4Ysfm5jMIC
GI-653 | a653e23d-0c6a-477f-8802-d5900cc77dbf | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall E | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ Mechanical â€“ 1CA_M1R1_20 generated a Differential Pressure Alarm (DP1 Out of Range). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627338&prj=263&rqi=q8w1F0RtUC5G5Zux3npex5C4jA
GI-496 | 0d55118e-f579-4347-adff-af2e1f66ea8c | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment type |  |  |  |  | MOT - DPT Riser 3 should also be tested for filtering or scaling behavior. A value jump is noted, but the exact numerical values should be confirmed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627396&prj=263&rqi=aOcyoF6HUQ8GLuH9JaSOYNhhiD
GI-487 | 52cd2461-85fd-4f59-946e-91517e498cc8 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Design Correction Needed | Design |  |  | equipment type |  |  |  |  | MOT - Gas Leak Detection The panel is considered as a separate asset and did not have any commissioning tag. Some wiring in the panel is not labeled, and the schematic drawing inside the panel has hand-written modifications (updated wiring of what was installed on-site was not in place during the testing day). The panel is not connected to the BMS system. A battery connection was found inside the panel while there were no batteries connected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627385&prj=263&rqi=bNOIOwNp1XGhobGASfcHIdlJXf
GI-476 | 30a21a4e-ca35-4200-930e-41cc2c0ea4bb | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | Design Correction Needed | Design |  |  | equipment type |  |  |  |  | MOT - Testing at the Fuel Control panel for loss to individual relays supplying components. Failing one relay inhibits the entire fuel system functionality. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627370&prj=263&rqi=VVTZwW9aNwLwZQDl5783ReBVYK
GI-470 | 6a7d8d5e-0ed5-4ab4-840f-f86885cb4f04 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | Design Correction Needed | Design |  |  | equipment type |  |  |  |  | MOT - Testing at the Fuel Control panel for loss of external fuel pipe heaters. The heat tracing units are placed on site in proximity to MV cables, and some other units are installed behind GRMUs in non-accessible, high-risk safety areas. Maintainability and accessibility issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627364&prj=263&rqi=BUM1NP4DmUc1JvmvuNq2LUJayB
GI-477 | 5f8e5917-2da1-4512-9a92-ff42ef44bc3c | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design |  |  | equipment type |  |  |  |  | MOT - All 8 SCPs are located in the same fire zone. A loss of all 8 SCPs will start all associated chillers and pumps at 40 Hz. Risks identified: 1. Risk of over pressurizing the loop. 2. Strings that are out of sequence will start and overload the electrical line-ups. 3. Proof that the cooling plant will be able to manage full load without SCPs is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627372&prj=263&rqi=AUDfqrcRcGxXz5OrTmLcfGRjZl
GI-488 | 7240ba2e-3b26-4067-a7a0-62c15da2587b | PA12x-1 | 263 | N-EMEA | Open | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning |  |  | equipment type |  |  |  |  | MOT - 1. There is no site schematic electrical drawing for the unit. 2. The valves and sensors on the unit labels are not matching the names shown on the local system HMI. 3. Updated operation manual and system settings need to be shared. 4. Flow meter for the water supply to the pressurization unit is not connected to the BMS (information shared by the vendor). 5. The PRV is not sealed and the bar value tag is not in place. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627386&prj=263&rqi=vpTBTpyHnExLxme1ZbSfmQmEWc
GI-490 | 8c19e655-5f99-4948-935b-4b18359b7efb | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning |  |  | equipment type |  |  |  |  | MOT - 1. There is no wire labeling on the unit. 2. A bad wire connection (exposed wire) was found. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627388&prj=263&rqi=75rUvLClap19gyedtvX5oNJfju
GI-492 | 0ddb9c35-5207-48f9-aa4a-62e438f78e5c | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design |  |  | equipment type |  |  |  |  | MOT - FCV valves remain at last know when power loss / comm loss and potentially result in the other chiller on the same string going to low flow situation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627392&prj=263&rqi=E4QN3CWKBrLQIDuyI5CmK0DN68
GI-479 | 10ce927f-dd56-4d8c-b3b7-ab60bf62669b | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  |  | equipment type |  |  |  |  | MOT - Loss of 24V to SCP of string (2 chillers running). The two pumps of the affected string went to 30 Hz. The chillers of the affected string still had the run command but were locked on flow. The PCP started the next chillers on the cascade, resulting in multiple chiller failures on flow, while the two pumps kept recycling hot water from return to supply and overpressurizing the loop. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627374&prj=263&rqi=k862rzZVwNCEcD8EZWboMnFPWk
GI-491 | e1cdcd0c-24b8-4120-9788-766f6cb0e036 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design |  |  | equipment type |  |  |  |  | MOT - Gas Leak Detection When the refrigerant leak detection system tripped all operating chillers, after restarting the chillers, PRV valves operated and a huge amount of water was observed in the pressurization unit room. The cooling loop PRV valves operating value tags are not in place and the valves are not sealed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627390&prj=263&rqi=cZVjAcD8MkqNjoNN7ov7dBNEsV
GI-644 | bee844f7-3a5c-4d38-aecc-165f3eba7ec7 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Not Correct | Commissioning |  | HVAC | equipment | Heat Load Test Hall C | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CA_M1R1_41 - White space temperature sensor reading 29.1 (High High Alarm) when 100% Load is applied | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627314&prj=263&rqi=K2YJ3C5aF7NL6f7UDDyMTJvtEi
GI-494 | 574f56d1-dd0e-46c1-8acc-da0898544af7 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment type |  |  |  |  | MOT - DPT Riser 1 should be tested for communication failure. The notes mention a fault with a negative pressure value, approximately -32 Pa. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627395&prj=263&rqi=BfwFHuDj0Xp5vderNKb5sLkSpA
GI-650 | f9f06800-1176-42b3-96cd-ba0cb4cbde1b | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR â€“ Chiller M2R1_6_CH_2 tripped, generating a Chiller Fault alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627335&prj=263&rqi=UINu5dYHEa1YczX0M3R5EXR6iO
GI-640 | 163c90ed-b906-4f28-a85f-72b15228174f | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR_1_2 â€“ Evaporator Low Alarm received at 16:14. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627307&prj=263&rqi=GKH5GXuJjERnhdwd6lWksQIgY9
YT1DCOS-225-001 | 87f1dec1-0b6a-b456-ee92-3615b97c2636 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS | L2B | Installation Damage | Commissioning |  | DCIM/DCOS | equipment | 1DCOS_1_HMI_23 | DCOS - HMI Panels |  | SCH - Schneider | Protective plexiglass broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627329&prj=263&rqi=2hqzuoCXkafDI3x5tdqe7DIT1L
GI-462 | 76e6b0d9-f8eb-4b77-a4bc-df67ef6989fb | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Cleaning | Commissioning |  |  | equipment type |  |  |  |  | HLT â€“ Mechanical â€“ The cleanliness of the cooling corridors requires review. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627339&prj=263&rqi=JkHsPD3O0sfqTj4mgfd3QyY0yz
GI-651 | ebd2506d-5046-4b19-9208-902b124a137d | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR â€“ Chiller 5_1 HMI recorded multiple alarms between 14:37 and 14:48, including Compressor 2 & 3 Overloads, Turbocor 2 Inverter Temperature Alarm, and Turbocor 1 Offline. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627336&prj=263&rqi=YMmNCTucPMjBxWyDaszqjc3l8t
GI-649 | 8eb424d3-fcbe-44a5-8a15-e2aa4be0df76 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR â€“ Chiller M2R1_3_CH_2 tripped, generating a Chiller Fault alarm at 15:48pm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627334&prj=263&rqi=guaqUXnQ4nsy3g6eY22kBjJXlv
GI-648 | d1ae4de3-86ac-495f-962e-06641d4e0ab3 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR â€“ Chiller M2R1_2_CH_1 tripped, generating a Chiller Fault alarm at 15:48pm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627330&prj=263&rqi=X4ZlmluGnDUpQqYGYMF7ToGWnt
GI-639 | 4c47069c-cabb-4c19-94b2-029983ab6abb | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR_5_2 â€“ Evaporator Low Alarm received at 15:05. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627305&prj=263&rqi=9xSEyLYy3TyBpqSNVxMC37NSfU
GI-645 | fdceb8ca-2467-47d6-a47f-d9ce9eb6db75 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Damage | Commissioning |  | HVAC | equipment | Heat Load Test Hall E | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ Mechanical â€“ A fan fault was identified on 1CA_M1R1_36 (Fan 22) during testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627315&prj=263&rqi=U6iHIvXm5WYUmFzzdr7H38pGD6
GI-466 | 9bbd2e23-fd16-44c4-8ef0-e38a316164c0 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | M0T - Testing (ER) Circulation fans loss of communication and loss of power Two circulating fans in the UPS room were found not connected to the CRAHs in the same room. Power supply verification testing and operation testing need to be performed on these fans in relation to the CRAHs in the same room. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627360&prj=263&rqi=8dJykbbsbfU9lXmTSDErhZxaGx
GI-483 | d6eaadf5-220d-410b-a376-e877a322482f | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  |  | equipment type |  |  |  |  | MOT - Loss of flow transmitter FT01 - Evaporator FT on running chiller 1.1. Initial status: Running chillers: CH 1.1, CH 2.1, CH 2.2. Upon failing the FT sensor at CH 1.1: CH 1.2 in the cascade started and CH 1.1 locked at low flow. The bypass valve opened to maximum rapidly due to loss of FT reading. On String 1, with CH 1.2 running: Due to the bypass valve's fast opening reaction, reverse flow occurred from the supply side of the network to the return (dropping the loop pressure). CH 1.2 with pump at 100% could not push water into the supply side loop network. Due to the pressure loss caused by reverse flow, additional chillers started in the cascade. The system took excessive time until the bypass valve closed and the system began dropping the unnecessary chillers. More than -40 L/S reverse flow!!. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627379&prj=263&rqi=aF3OHeMY34fNGLWmiEIQReMbDx
GI-481 | c41fda45-fb88-4a4b-ad25-07b42ff4d315 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Design Issue | DCOS |  |  | equipment type |  |  |  |  | MOT - Loss of power to running SCP (2 chillers running). The two pumps of the affected string went to 40 Hz. The chillers of the affected string kept running, then later locked on flow. The PCP started the next chillers in the cascade, resulting in multiple chiller failures on flow, while the two pumps kept recycling hot water from return to supply and overpressurizing the loop. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627377&prj=263&rqi=B5zhvGBmRfShqpma9z1foIOHBb
GI-646 | 5db94433-8f22-4d7d-b834-2e72647ba241 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR_2_1â€“ Evaporator Low Alarm received at 13:00 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627317&prj=263&rqi=BQYN0uzr2Pi7bU2CiUQJfkqBtQ
GI-489 | 42e77df5-b553-40d1-a83d-c88293302454 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment type |  |  |  |  | MOT - Simulate Pressure Drop The alarm name on the BMS "Leak detection" does not match the "Pressurization unit in operation" status. The alarm was received on the BMS after a delay of 90 minutes plus expansion tanks dropping below 20% Ã¢â‚¬â€ this is a significant time delay to receive the alarm on the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627387&prj=263&rqi=G6rzW5GioldjHsdwdPGYi3Atr9
GI-471 | 2737dec1-fdf7-4181-bd3d-3a106d9392a9 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | MOT - Testing at the generator panel for loss of power to supply motorized valve in day tank. No alarms received on the BMS when power was cut to the valves. Pumps were shown as unavailable on the FCP panel HMI, which is incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627365&prj=263&rqi=IWHs4HkpH6gWkzIPdDg5nZ79SD
GI-486 | 2dab81f8-eea8-466a-b7e5-3a5039d83255 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | AER - Aermec |  | Design Correction Needed | Design | [7 empty] | MOT - Refrigerant leak detection system (centralized system) testing Ã¢â‚¬â€ Refer to schematic drawing "48 points system" page 11. Opening the closed contact on one relay connected to chiller from Relay Board 1. If the relay board is physically damaged, it will result in opening all normally closed contacts of all relays, leading to shutting down all chillers. Same risk: In case of wire damage from the panel (same cable tray) going out from the panel, this will lead to the same result. Note: On the relay board, each relay normally closed contact is connected to one chiller. Once the relay is energized, the normally closed contact opens, opening the wire loop to the chiller and triggering chiller shutdown. Any cause of opening these wires will lead to chillers shutting down. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627384&prj=263&rqi=uFeCaRZGl2eCoB82cj1KzAjNaz
GI-643 | 5f588176-2451-488d-8380-f2ae0fb5d7d7 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-30 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT â€“ CHWSTR â€“ PDT sensors in DH04 and DH05 were reading 0.0 during testing. This requires further investigation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627312&prj=263&rqi=VNbdj7kl5OqE6GmrMJAwpAub6P
GT1DCOS-276-001 | 8b03ae46-80e7-40e7-8ad0-e690b137af32 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS General Issue | DCOS |  | Electrical â€“ LV | equipment | 1DCOS_1_OAP_1 | CP - Control Panel (Max Cool Announcement) |  | SCH - Schneider | Disconnecting the hardwired connection between the OAP and ECP did not generate an ECP Panel Fault indication on the OAP. As stated in the MaxCool SOO, Section 4.0 â€“ OAP Panel Description (Page 9), the "ECP Panel Fault" shall indicate when "the connection between both panels has been disconnected." This behaviour was not observed and should be investigated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627078&prj=263&rqi=76ekKx9HqWdPqOFJ6fkaGMwrAA
GI-460 | 24ef1202-8672-452d-87af-bfdcb17076b8 | PA12x-1 | 263 | N-EMEA | Closed | Outstanding Paperwork/Documentation | markb@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation Not issued/ Required | Commissioning |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | MOT - Testing Fuel Control panels for communication cut between FCP and GCP There is no network schematic diagram for all the FCPs and GCPs. The fiber cables connected to FCP 1 are not labeled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627088&prj=263&rqi=rBpkSA9oJiPw3qGISVrtsqNipw
GT1DCOS-276-002 | 6f7f0120-3a6e-4384-a895-e5ef3af85047 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCOS General Issue | DCOS |  | Electrical â€“ LV | equipment | 1DCOS_1_OAP_1 | CP - Control Panel (Max Cool Announcement) |  | SCH - Schneider | During testing, the ECP panel power supply was switched off. The OAP correctly activated the audible alarm; however, the ECP Panel Fault red indicator did not illuminate and the blue beacon was not activated. As defined in the MaxCool SOO, Section 4.0 â€“ OAP Panel Description (Page 9), the OAP shall indicate an "ECP Panel Fault" when the ECP power supply is unavailable, and the blue strobe light and audible alarm are used to signal that an alarm is pending. This behaviour was not observed and should be investigated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627079&prj=263&rqi=k41zMg3BUznGuZimZVz0bqazFv
GI-459 | 6c37789e-2dd3-4137-9241-55ad5247dc37 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | markb@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | MOT - Testing Diesel pump for loss of communication from the PLC The way both FCPs are connected to both pump contactors differs between FCP 1 and FCP 2. Having identical systems each wired in a different way makes troubleshooting difficult. Only the Rehlko technician who installed the system is aware of the wiring differences. action to audit the two FCP's and ensure they are wired in the same way as per design intent and provide the as-built drawing (drawing not available on site during testing) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627086&prj=263&rqi=ngvUrZipRTpgtEzv8FObYrXt6e
GI-455 | c39e2931-1913-4cb3-8ab5-c46fc11476ca | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | LLT - The SWITCHBOARD LOCAL/REMOTE selector switch is not generating an alarm when the MVTB is placed in local mode on either the local HMI or BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627081&prj=263&rqi=8XdJDaC69QNKkFQGO43xDv1iLX
GI-461 | 7fbcada9-363e-4929-ad81-9d3aa77b3080 | PA12x-1 | 263 | N-EMEA | Closed | Outstanding Paperwork/Documentation | markb@straightlineconsulting.co.uk | 2026-06-26 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | MOT - Testing at the Fuel Control panel for double skin pipes fuel leak detection The names of pipe leak detection units on the FCP HMI do not match the SLD, making it impossible to identify where the units are located on-site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627089&prj=263&rqi=gWN29tKr8JA73slPKLOiq0EerR
GI-638 | c08007b2-0878-497e-ad71-1181ef14c15f | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-06-25 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall C | Data Hall Heat Load Test Phase 2 |  |  | HLT - Issue discovered during 25% heat load testing: The pressure sensor for 1CA_M1R1_47 was observed reading out of range, exceeding 100 Pa, while adjacent pressure sensors remained stable at â‰¤15 Pa. The sensor subsequently dropped to 0 Pa before recovering. As no similar behaviour was observed on neighbouring sensors, this indicates a likely fault with the pressure sensor or its associated signal/wiring rather than an actual pressure condition. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626862&prj=263&rqi=u88htLobdaPuHdlshGidp4Sf6h
GI-450 | 6716ba49-270b-4523-b89b-96f34eabebe5 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium DCOS | kostask@straightlineconsulting.co.uk | 2026-06-24 04:00:00.000 +0400 | AER - Aermec |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment type |  |  |  |  | Mechanical - The differential pressure sensor on the chiller evaporator is showing a negative value when there is no flow. The DCOS page indicates that the sensor has failed. The issue is probably be related to scaling on the DCOS side rather than a sensor fault. DCOS team to check and correct the scaling configuration for ALL the chiller evaporator DP sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626705&prj=263&rqi=VRS3e0Mji2JoJ8Q7qZV4OBpAro
GI-627 | c910234c-93f0-480d-8b65-a41b475766c1 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Component/Equipment Failure | Commissioning |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT 2 - Mechanical - 1RAS_04 - Status deviation alarm active | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626480&prj=263&rqi=fkjkM4e3qdaVUvgHokoXE3cRfG
GI-631 | 98932429-ebda-4f1c-b488-4e32a053c146 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Component/Equipment Failure | Commissioning |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical -both MAU - Major fault & shutdown | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626484&prj=263&rqi=1wyIKvMNXHDmFG4ZmqT6jMf2wX
GI-630 | b5f20535-1d9d-4e2d-b01a-eea179e732e8 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | AER - Aermec |  | DCOS General Issue | DCOS |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CHWSTR_M2R1_2_CH_1 - Low evaporator alarm active | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626483&prj=263&rqi=Pg7y9KoMtvyzUqXC7dP8qIsp4h
GI-633 | f1e14952-7347-49e3-b6ff-e916c417bbf7 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1RAS_04 - High high alarm active - 2.3 bar reached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626486&prj=263&rqi=jAI3BDhMGcdDPV7ueWHbgpU7rA
GI-634 | a4b9d318-1ba6-48c5-a5bd-311a4529fdef | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CHWSTR_5_RAS_3 - Input value 3 in alarm - negative reading | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626487&prj=263&rqi=NIgUQwerDFkRzr6tbDvyjatgRz
GI-628 | dd5c0409-3117-454f-9d55-2d69ad8eaddf | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Component/Equipment Failure | Commissioning |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1PSER_M2R1_1 - Leak alarm active | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626481&prj=263&rqi=B34UvpF0c4dm3zEM1R2bEMie8P
GI-635 | 513da467-60d7-4fbd-a62d-51211b95c055 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CHWSTR_5_RAS_2 - Input value 3 in alarm - negative reading | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626489&prj=263&rqi=cYeeDXKZ6fO0Z1Nl0zar1WOiRj
GI-637 | bac2ba17-1ba4-445e-8853-ee58da690a02 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | DCOS General Issue | DCOS |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CHWSTR Strings 1,3,5,6,7 RAS deviation Alarms | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626492&prj=263&rqi=ItcG29wvHKNGEp9ItKmouTOAAi
GI-449 | 8dd0b874-7290-41ad-8a47-a7ed4115dd2e | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning |  | HVAC | system | CHW System |  |  |  | HLT - Cool array corridors build up in large amounts of water from pipe condensation. - Data hall 5 & 6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626499&prj=263&rqi=xt3fCngZkFW37pvZD4CTzXspuw | https://equinix.facilitygrid.co.uk/x/project/263/system/9233
GI-632 | ed803459-af26-41fb-8ab3-b9f8b0487c99 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1CHWSTR_3_RAS_3 - Input value 2 in alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626485&prj=263&rqi=cRuzFRbU0PBzDJib9puR4baEVf
GI-629 | 76331582-d4f8-4e90-ba61-9061a1294ef6 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - 1FCU_M1_54 - Alarm active | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626482&prj=263&rqi=VEHcjj4gQhTp0ALeqOs7p4aA69
GI-448 | 8e4252ba-7eed-4edc-b2b3-d01133e7e0f7 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | Component/Equipment Failure | Commissioning |  |  | system | DCOS System |  |  |  | Heat load test - Full of E & F String in communication alarm. Impact to HLT & deadline for IST | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626496&prj=263&rqi=5hDUtBFoQysHNKyZADqB56KAou | https://equinix.facilitygrid.co.uk/x/project/263/system/10784
GI-636 | a55b5cf6-6141-4e5d-a99d-f72fda6eeca9 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-06-23 04:00:00.000 +0400 | General Contractor - Mechanical |  | General Design issue | Design |  | HVAC | equipment | Heat Load Test Hall B | Data Hall Heat Load Test Phase 2 |  |  | HLT - Mechanical - High humidity alarms - DH3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626491&prj=263&rqi=0gTKICQlQP4hcsjMsJcxQ2uIw8
IST-23-001 | 9647c411-1f78-42ad-9356-991fdfade262 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-06-19 04:00:00.000 +0400 | General Contractor - Electrical | L5 | Installation Not Correct | Commissioning |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | L4 C&E Testing: 1MVHR_M1R1_01_IHM not confirmed if shutdown was achieved (Mech needed) Lift 3 not connected for shutdown, shown on Matrix. removed from Matrix, agreed by PPA Ground Floor fire curtains not fully closing Event log for Genset testing to be sent to SLC | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626226&prj=263&rqi=9zwPJRX7b8jOwMsbWKfKZ80Ufr
IST-24-001 | 8e2079c6-1ce5-4723-943e-6a66b1173a48 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-06-19 04:00:00.000 +0400 | General Contractor - Electrical | L5 | General Design issue | Design |  |  | equipment | Fire Alarm Cause and Effect | Fire Alarm Cause and Effect |  |  | Fire Alarm - Following issues found on Testing 17/06/2026. Smoke extract dampers in following Zones failed to operated after manual trigger for Phase 1.1 ZDA104 ZDA105 ZDA106 ZDA130 No event log from testing was able to be downloaded from Racks to to internal issue. all areas tested to be re-tested. ZDA001, ZDM039, ZDA106, ZDM049, ZDA101, ZDA104, ZDA108, ZDA105, ZDA112, ZDA130, ZDA121. DH1 HA+CA, DH2 HA+CA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626229&prj=263&rqi=CmkO0oCRnf1i9KNeJUDPIBvI1c
GI-441 | 4dfe17f5-eacf-4c58-88f2-46267cbd9214 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-06-18 04:00:00.000 +0400 | SCH - Schneider MV |  | Installation Not Correct | Commissioning | [7 empty] | #LLT Issue on the MVTB R2 (Test performed on the 17/06/2026) during the LLT test when we switch off the breaker energizing the P5 of the loop 2 and when we switch back on this breaker who feeding this P5 The MVTB R2 calling the Gen start | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625856&prj=263&rqi=sp8L0Ycw76fYnesNeNniCDBS55
GI-440 | 2903bdfb-c677-47a1-921d-2582e0faafbf | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-06-16 04:00:00.000 +0400 | SCH - Schneider MV |  | DCOS Comms Issue/Fault | DCOS | [7 empty] | LLT issue comms failure we lost all the coms of the site during the test of the BTU A (losing power source ) DCOS server crashing many times after trying to restart DCOS on engineer laptop ( issue need to be resolved asap) please see [picture attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625501&prj=263&rqi=RuwgcVRfZp6tdx5jzJptnDdx9Q
GT1FD-80-001 | 3133860f-49d2-4952-8d12-4c1877a67880 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-06-16 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Cleaning | Commissioning |  | Fire Detection | equipment | SSI_RACK_1 | FACP - Fire Alarm Control Panel |  |  | Cleaning: of Fibre connection /DCOS rack before C&E testing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625421&prj=263&rqi=bSfbYOLMpxi9WtlP3qOPE3V5ik
GT1FD-80-003 | 36e22ef2-71ab-4ec3-94d8-6a32b895bb7a | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-06-16 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Cleaning | Commissioning |  | Fire Detection | equipment type | FACP - Fire Alarm Control Panel | FACP - Fire Alarm Control Panel |  |  | Cleaning: All EAE units require deep cleaning. EAE_1-23 ALL EAE Units to be cleaned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625422&prj=263&rqi=zIjGhID5BfRGCW7vnYzujsMCKw
GI-422 | 820be720-9dc5-4481-9de3-e7d3c5ae9adb | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-03 04:00:00.000 +0400 | AER - Aermec |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment type |  |  |  |  | IST1 - CHILLER LEAK DETECTION â€“ NO COMMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623770&prj=263&rqi=K5KBeq58DGJDdgx4hFLy9xBYI7
GI-429 | ba9e9028-d675-430f-bf81-b72979ca8607 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-03 04:00:00.000 +0400 | REH - Rehlko Gens |  | Commissioning Issue | Commissioning |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | IST1 - LEAKAGE PIPING LDT ALARMS PRESENT FOLLOWING IST TEST 1.0 SWITCHING | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623777&prj=263&rqi=I1VPBRn1S8bCy4oZ4QY7yl2ulr
GI-428 | 877a88c3-65a0-45e2-b92a-a5dcbd82554c | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | markb@straightlineconsulting.co.uk | 2026-06-03 04:00:00.000 +0400 | REH - Rehlko Gens |  | General Design issue | Design |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | IST1 - FCP01 FUEL PUMP FAIL ALARM ON DCOS WHEN COMPLETING M1/R1 SWITCHING ON IST TEST 1.0 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623776&prj=263&rqi=269sgu9YZSUumbFRlXlc0lxHAk
GI-418 | d578c08c-e6a5-4f6e-94d7-e89253e2af44 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-06-03 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Damage | Commissioning | [7 empty] | #IST ## CRAH M1R1_10 Elec Switch need to be replace | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623758&prj=263&rqi=OpNbAhihGJJ8Lb1t4DCEVPddXJ
GI-417 | c85849ea-a82f-4699-aac1-52a34ab39879 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-06-02 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Installation Damage | Commissioning | [7 empty] | IST# Masterpack Q03 FEEDER TO 1COP_AR1_1 cover protection broken need to be replace please see picture attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623645&prj=263&rqi=zYGsItx5OvXt18QiEjTjHLdqTx
GI-626 | 29e83e06-9551-45d8-b2db-2257a47c5e78 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low DCOS | joshw@straightlineconsulting.co.uk | 2026-05-30 04:00:00.000 +0400 | AER - Aermec |  | DCOS General Issue | DCOS |  | HVAC | equipment | Heat Load Test Hall D | Data Hall Heat Load Test |  |  | HLT - During fire Test 29.05.25, Multiple communication alarms on CHW Pumps / Chillers. Still gave command feedback/ feedback as correct - DCOS to investigate further whilst remained in purple alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623493&prj=263&rqi=fMl58ZZXggTv08DLoJYuQiOrMY
GI-415 | d4ffddbc-0dd9-4df6-81f6-961b689d9141 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-05-27 04:00:00.000 +0400 | General Contractor - Commissioning |  | Cleaning | Commissioning |  |  | equipment type |  |  |  |  | Mechanical - All condenser coils of the chillers require cleaning. The dirt in the coils will effect chillers performance. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623216&prj=263&rqi=zPUu8Yz5zLjnt1k3xrDedy6e1x
GI-414 | 69e5a5d2-ceea-4858-b8b9-c932467231a5 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-05-22 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning |  |  | equipment type |  |  |  |  | All Bone tags on All CRAH's Phase 1 have been amended with permanent marker, all incorrect, BYES to change to all correct permanent tags on CRAH ATS Cables both supplies | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622776&prj=263&rqi=YzOMd51iRjwYu6JZRvOvG8rGh9
GI-413 | 78228aba-4858-40ea-85f9-106f4fbd3a5c | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-05-19 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design | [7 empty] | Mechanical/Safety - Data hall pressure causing entrance Doors to data halls & Cool array corridors to slam and potential injure someone entering or leaving. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622243&prj=263&rqi=iIghAPGp50m5qTxU5g3ZMB2ISj
GI-625 | 29803af8-eb22-4a4a-ad37-0c3eb2857978 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | Mechanical - TEST 7.10 HLT - Valve actuator communication alarm - when re instated the temperature increased above SLA - Suspected Valve closing during communication failure | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621805&prj=263&rqi=yYy5aixzi6gb5B6LBJDD8PB6db
BT1MECH-529-045 | c1d0d029-ad2c-4b89-8052-fc0dfc9516f3 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | Mechanical - RAS04 - Point 17&18 reading -0.34 Installed but not programmed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621831&prj=263&rqi=nEeAmIfnP2QKuJJfVYBa4eks0t
BT1MECH-532-046 | d46163a0-bf56-4183-a680-5b83bdbc709a | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall D | Data Hall Heat Load Test |  |  | Mechanical - 1CA_M1R1_08 - White space 5 temperature to be corrected. 1.3 degrees out and coming into alarm reading 28.3 all others are reading approx 27 in same area | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621827&prj=263&rqi=hTExGjhptVdIgEj5I1cgEl5oLW
BT1MECH-529-043 | acad7973-e992-461d-aeed-94290b402285 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low DCOS | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | Mechanical - Data hall temperature & humidity sensors go into communication alarm when rising above 50 degrees | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621812&prj=263&rqi=h1DQ6AWuIlFi3bsvoyox1euZjH
GI-624 | 5433ae06-e167-43c7-8ea5-785a63bb0213 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low DCOS | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS |  | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | Mechanical - HLT Test - Fan fault on cool arrays not latching. changes to a Fan communication alarm due to fan spinning in reverse. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621803&prj=263&rqi=LHD5y44PAVJ3z6D3UiB4MnVFW4
BT1MECH-529-041 | 5bd06b0e-4267-4623-8fcb-6bdc3064b17d | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Component/Equipment Failure | Commissioning |  | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | 1GEN_M3 â€“ A sensor fault caused an M3 Generator trip. Kohler will investigate the issue and replace the sensor if required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621804&prj=263&rqi=pYHp2UkOuwDboQiGkIIozJm6sl
BT1MECH-529-044 | 6804c31b-a84f-443b-a9aa-aaa0da44f220 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | General Contractor - Mechanical | L4 | Design Correction Needed | Design |  | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | MECHANICAL - Both MAU'S major fault - to be investigated - Planned commissioning/investigation on 20.05.26 Alarming as low temperature under 15 degrees. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621823&prj=263&rqi=JpbbupdB4vgND4ewshbRF6XXzQ
BT1MECH-529-038 | 001d4f10-02ae-4f09-bcd9-048d0b91e4b1 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | General Contractor - Mechanical | L4 | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | 1CHWSTR_1_RAS_2 - Temperature sensor not reading correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621760&prj=263&rqi=7lZqw7lHhiOK8HiKxcxmStLiSD
BT1MECH-529-037 | 4af5629b-c9bc-4c88-80b0-b44c26eb25da | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | Commissioning Issue | Commissioning |  | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | 1CHWSTR_M2R1_2_CH_2 - Experienced intermittent issues that recurred throughout the day | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621759&prj=263&rqi=0zzMOGuxiIBMTRDl6sTXdHZ340
BT1MECH-529-039 | 5910cde8-9be1-4e21-8f8f-b3c41f19a5b2 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-05-14 04:00:00.000 +0400 | General Contractor - Mechanical | L4 | Component/Equipment Failure | Commissioning |  | HVAC | equipment | Heat Load Test Hall A | Data Hall Heat Load Test |  |  | 1CHWSTR_5_RAS_2 - Temperature sensor not reading correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621766&prj=263&rqi=5oC3JVDD3ut6UdACdv4eZEV7fA
GI-411 | 6d97e5ef-7ae4-4267-9261-4523451a77b9 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | jayb@straightlineconsulting.co.uk | 2026-05-07 04:00:00.000 +0400 | Design Professional |  | General Design issue | Design |  | HVAC | equipment | MSB_R2 -Room - CRAH | CRAH Switch Room Redundancy Test |  |  | when UPS is on full load the room temp exceeds higher UPS temp limit causing UPs R2 to inhibit battery charging and derating of UPS output occurs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620657&prj=263&rqi=KmHYl1XJTIGn4TawtXhAYrjqSE
YT1DCOS-226-001 | 384277a7-785c-4666-86dd-97db92d6e715 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-29 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Not Correct | Commissioning |  | DCIM/DCOS | equipment | 1DCOS_1_HMI_24 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - no main earth from HMI panel to containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619885&prj=263&rqi=Pr9nx1e6H97yYrf1Dl2smH55Uv
YT1DCOS-274-001 | c2c4ee73-0052-48ad-93e3-40494687626e | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-29 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Not Correct | Commissioning |  | DCIM/DCOS | equipment | 1DCOS_1_HMI_55 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - CYT. Phase 2 asset fed from Phase 1. Temp cable installed for energisation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619886&prj=263&rqi=2BAvZK0arLkVP2Oxk8TgL9DCW1
YT1DCOS-223-001 | afd9ee93-fb0f-421c-9a5f-d99eceabcf7f | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-29 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Not Correct | Commissioning |  | DCIM/DCOS | equipment | 1DCOS_1_HMI_21 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - no main earth from HMI panel to containment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619895&prj=263&rqi=VBT7HIgJXgZxcPBUR8UpAzzpRB
YT1MECH-648-731 | a4a38213-03d2-46a3-8be1-060bcc845afb | PA12x-1 | 263 | N-EMEA | Closed | Outstanding Paperwork/Documentation | emanuelp@straightlineconsulting.co.uk | 2026-04-28 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Documentation Not issued/ Required | Commissioning |  | Plumbing | equipment | 1PSET_A_03 | CHWP - Cold Water Booster Pump |  | LOW - Lowara-xylem | Mechanical - earthing report missing and permanent cable report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619711&prj=263&rqi=jLOFIarJxA5gYuOIZumuORObPR
GT1MECH-724-001 | c6fde2b7-a022-4d9a-95a4-c76966aae430 | PA12x-1 | 263 | N-EMEA | Closed | Outstanding Paperwork/Documentation | emanuelp@straightlineconsulting.co.uk | 2026-04-28 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Documentation Not issued/ Required | Commissioning |  | Plumbing | equipment | 1PSET_A_03 | CHWP - Cold Water Booster Pump |  | LOW - Lowara-xylem | MECHANICAL - live cable test report required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619710&prj=263&rqi=bnNRQ93bdpZHo27SkxGY6Utad6
GI-404 | 6d085649-0c45-4c96-931c-ca7386eb79b1 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | aarond@straightlineconsulting.co.uk | 2026-04-16 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | During testing of the Vertiv cooling arrays in Data Hall 01 (PA12), the DP to DT changeover time was observed at 40â€“80 seconds, which differs from the 120 seconds specified in the Sequence of Operations. This issue is related to all CRAY units in the Data Hall 1. 1CA_M1R1_01 / 03 / 05 / 07 / 09 / 11 / 13 / 15 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618331&prj=263&rqi=pRxm56L5pNnKTzr0Fa9efkoPNO
GI-403 | 0ab3df74-8b3c-40fe-a6ef-d5dd4f37d8a1 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | joshw@straightlineconsulting.co.uk | 2026-04-15 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | Mechanical - CRAH's D string - When failing Return sensor, Fans Do not ramp up as per SOO. Vertiv engineer had to simulate by settings after to increase fan speed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618284&prj=263&rqi=apF5GWUe4K8f1bcLLFYmb2to7j
GI-400 | 3723dc93-54bb-418c-9d4d-33ce9cf7a71c | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-04-13 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | Damaged folder holder for documents/drawings to be repaired and secured in place. M1R1_15 M1R1_15 Extension M1R1_01 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617923&prj=263&rqi=yHuIuz4mX0wyCIzSehB0eKNBnd
GI-402 | a30da8cb-6fed-4f32-a253-e811858d61af | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-04-13 04:00:00.000 +0400 | SCH - Schneider DCOS |  | Installation Not Complete | Commissioning | [7 empty] | The layout drawing for Data Hall 2 is incorrect. The CRAY units (shown in red) are positioned on the wrong side of the room, and the DP sensors (shown in blue) are also incorrectly located. Reference to the drawing: PA12-SC-IC-6140-ZZ-DC-BGMS-SCH (R06) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617961&prj=263&rqi=mQwru0WSeKx0NJvURDDjGWy5MH
GI-396 | 5c406281-7ad2-439f-b965-964b4f1e4f80 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | aarond@straightlineconsulting.co.uk | 2026-04-13 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | Missing Valve Tags on the CW flexible hoses 1CA_M1R1_02 1CA_M1R1_04 1CA_M1R1_06 1CA_M1R1_08 1CA_M1R1_10 1CA_M1R1_14 1CA_M1R1_16 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617919&prj=263&rqi=ZUMmmVMHKKIvczKlyWctpMPPMd
GI-393 | 0c0f5dc9-35ff-457b-a946-8c9b7a700057 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-11 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning |  | Fire Detection | system | Fire Detection |  |  |  | Electrical - Hellerman sleeve not used on cables in the following connection boxes ZDA090 ZDA084 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617868&prj=263&rqi=bIsXrZYnRT3Qr9LBEWBKrrIEzN | https://equinix.facilitygrid.co.uk/x/project/263/system/14098
GI-394 | 9bb95f9c-81ac-415b-882d-d24c9ebf377e | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-11 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning |  | Fire Detection | system | Fire Detection |  |  |  | Electrical - Hellerman sleeve not used on cables in the following connection boxes ZDA074 ZDA075 ZDA076 ZDA077 ZDA078 ZDA089 ZDA081 ZDA073 ZDA072 ZDA071 ZDA066 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617869&prj=263&rqi=pnKC59dyL8sySaQBzBvSIO9hDF | https://equinix.facilitygrid.co.uk/x/project/263/system/14098
RT1FD-181-001 | e0f9e846-7215-4db6-aaf8-b8722ce3cbb4 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-04-11 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Installation Not Correct | Commissioning |  | Fire Detection | equipment | ZDA121/12150 | ASDP - Aspirating Smoke Detection Panel |  |  | Electrical - ZDA121. No hellerman sleeve used in vesda or connection box. Silver pipes covered in paint. Trunking lid doesn't fit properly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617870&prj=263&rqi=EAk1YtUMnUF0UV17n0NwQV1aEl
YT1DCOS-273-001 | 5208a04e-2310-4131-a3f4-2959321f05ab | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | mirceag@straightlineconsulting.co.uk | 2026-04-11 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Damage | Commissioning |  | DCIM/DCOS | equipment | 1DCOS_1_HMI_54 | DCOS - HMI Panels |  | SCH - Schneider | Small paint chips and minor surface damage observed on the panel door exterior. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617836&prj=263&rqi=wtvnLawNUGCfzNEwYCGbluFkV7
GI-395 | bded3b48-4ef2-4fdd-a590-e6121182d130 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | gregb@straightlineconsulting.co.uk | 2026-04-11 04:00:00.000 +0400 | General Contractor - Electrical |  | Cleaning | Commissioning |  |  | equipment type |  |  |  |  | Electrical - All Vesda pipes to be cleaned. most are covered in paint | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617873&prj=263&rqi=bRPnBfUy5eErTUm4n5cK5DaMfq
SOR-2412-002 | 4df72c17-cdd3-2364-935c-3b69cf41e884 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation Not issued/ Required | Commissioning | [7 empty] | no drawing present in the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617674&prj=263&rqi=EA5dOtaVHNbrVkuvj6Nzwjm8s7
SOR-2412-001 | c29eab54-ee16-c820-6c7c-b1e1ec301c31 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [7 empty] | no labelling on the main power supply | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617673&prj=263&rqi=tZrGM2GPQppu11Pr4uduh59Kym
SOR-2410-001 | 58fc3f68-9af7-2a19-f6a0-2592268e37a6 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | tayebb@straightlineconsulting.co.uk | 2026-04-09 04:00:00.000 +0400 | General Contractor - Electrical |  | Commissioning Issue | Commissioning | [7 empty] | earthing cable not terminated need to be reviewed by electrical vendor | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617672&prj=263&rqi=NWcmmW4WbOQm3Rk7WYImdkZzs2
GI-390 | 49f2df46-ae5c-45ef-a1da-5d8aa53017e1 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-27 04:00:00.000 +0400 | General Contractor - Electrical |  | DCOS Installation Not Complete | DCOS |  |  | equipment type |  |  |  |  | Electrical - No earth torque marks on DCOS_1_HMI panels between HMI and Door THIS ISSUE APPLIES TO ALL DCOS_1_HMI PANELS 1-50 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616649&prj=263&rqi=fgwRUKPLICoQJSgKfvOMRxoK0N
GI-388 | bcd926a7-de66-4771-8f87-710f376b401b | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | stephenturner@sygna-emea.com | 2026-03-24 04:00:00.000 +0400 | Equinix Project Manager |  | Installation Not Correct | Commissioning | [7 empty] | the cables powering up the load banks in data hall 2 are passing through an open door into the data hall, these door are not forced open the door could close on the cables and damage the cables. the data hall is live and multiple door are open on the data hall letting dirt into the hall. this is also a safety issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616287&prj=263&rqi=4KIy5SnqaBSPHXt3VNLSUyCFLb
BT1MECH-428-036 | 07b0f0cd-fce1-4f63-a62f-acedf9870371 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-03-20 04:00:00.000 +0400 | General Contractor - BMS | L4 | Component/Equipment Failure | Commissioning |  | HVAC | equipment | UPS R1 Room - CRAH | CRAH Switch Room Redundancy Test |  |  | Mechanical - Whilst testing CRAH Redundancy testing, TT01 sensors were not working correctly. DCOS confirmed they changed parts with phase 2 panels but scaling from 40-50 are different. All TT01 / dcos panels linking to temperature sensors need all retesting and calibrating with a data logger. for this test we will have to rely on Data loggers. if BYES Fail to supply data logger trends a retest under full load will be required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616069&prj=263&rqi=cRFSPoffLrcBqNTHPLcB3PQiWb
BT1MECH-428-035 | 5783bea0-e847-4eff-845e-91ee3422d0a7 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | joshw@straightlineconsulting.co.uk | 2026-03-20 04:00:00.000 +0400 | Design Professional | L4 | General Design issue | Design |  | HVAC | equipment | UPS R1 Room - CRAH | CRAH Switch Room Redundancy Test |  |  | Mechanical - CRAH Redundancy testing, Whilst CRAH 8 is failed and running on CRAH 7, With the distance between the UPS & CRAH, the heat coming off the UPS is not reaching back to the return temperature on CRAH 7 and putting demand on. Temperatures on UPS reached in over temperature alarm at 36-37 degrees. No further increase as temperature values but clear indication the circulation in the Ventilation getting back to 'load' the CRAH. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616060&prj=263&rqi=tTioXWYqVuXKkIr85wkCcQU3aU
RT1DCOS-272-001 | 010e16ff-d562-48c4-aee7-61d3d673d417 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-19 04:00:00.000 +0400 | General Contractor - Electrical | L2 | Installation Damage | Commissioning |  | DCIM/DCOS | equipment | 1DCOS_1_HMI_20 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Damaged Perspex screen | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616033&prj=263&rqi=YZr9ZOXgObFbzHEmFkLjaY7Mjt
RT1DCOS-265-001 | 592a1c53-a709-47ca-afea-5ea4b9b61c52 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-19 04:00:00.000 +0400 | General Contractor - Electrical | L2 | Installation Damage | Commissioning |  | DCIM/DCOS | equipment | 1DCOS_1_HMI_13 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Damaged Perspex screen and damaged internal plastic trunking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616032&prj=263&rqi=Us5OcjMHgYVlgZpPvfK9KKgmHP
RT1FS-302-010 | a2b55a5a-a983-6d0f-95d7-2b1d3f340762 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-03-18 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Installation Not Complete | Commissioning |  | Fire Suppression | system | Fire Dampers - Ground Floor |  |  |  | Mechanical- 1SD_NC_0031 - cabling / Conduit to be fixed correctly after floor resin laying | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616371&prj=263&rqi=lTIrRSn4DT0Qvzs2ABo9GkpEJW | https://equinix.facilitygrid.co.uk/x/project/263/system/11600
GI-386 | bf23fb96-7e68-4de4-9257-ee068453b3ab | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | stephenturner@sygna-emea.com | 2026-03-18 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | on Facility grid on a weekly basis the numbers change for the Total Activities. these changes for each level of tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615969&prj=263&rqi=mUxnWspG7AP2NsRCVhMhh7leBH
GI-389 | 3dc97341-f937-1b1f-cf79-3ee83d3e3054 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-03-18 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [7 empty] | Mechanical- conduit to be re connected correctly after floor resin install | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616372&prj=263&rqi=c0Z5TShy8fi4VXOpmBrcOnJ7Mz
SOR-2326-001 | 8faf7675-5b61-ed5e-acd8-03e42718e876 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | [7 empty] | Poste 6 ID tag missing Cable needs proper support Bone tags missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615842&prj=263&rqi=ZV6K63VnWfFRhXp9viieXWytI4
GI-379 | 852b740a-3b42-4032-bfd7-76616f80034a | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Incomplete Connections | Commissioning | [7 empty] | 1DB_M1R1_7_1 Conditional - Conditional yellow tag applied to unit - Issue will ONLY be closed once permanent supplies are installed and all documentation issued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615788&prj=263&rqi=af5E9L31H8nON4mkfyq37AjcXf
GI-380 | 0e82432c-0ec5-408a-bb27-9e7cea41cf30 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Incomplete Connections | Commissioning | [7 empty] | CYT 1DB_M1R1_8_1 Conditional - Conditional yellow tag applied to unit - Issue will ONLY be closed once permanent supplies are installed and all documentation issued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615789&prj=263&rqi=ESUaUmPP3vi1y9kVHaZCjGQ3pY
SOR-2329-001 | 7843a420-8164-c997-7163-53e430411c49 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [7 empty] | Mechanical: Poste 5 Bone tag missing proper support for the cables ID to be visible | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615845&prj=263&rqi=AZdOTDd4D6LUJNg6f77hoGb53U
SOR-2320-001 | 5f59f2ed-9615-0392-bc7a-f39f042484a3 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [7 empty] | 1FCU_R2_157 Bone tag missing The label on the drainage is missing Torque mark missing on the isolator Cleaning needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615805&prj=263&rqi=0qKF5vdFDznq7zXRWP9NaUU3Aq
GI-382 | 042c3b46-5725-4dfe-a091-bc765ac01ebd | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [7 empty] | CYT 1DB_M1R1_13_1 Conditional - Conditional yellow tag applied to unit - Issue will ONLY be closed once permanent supplies are installed and all documentation issued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615791&prj=263&rqi=svjEVyoxHmUIItXNxH10e17pPB
SOR-2323-001 | 14670112-6e7d-dbe5-a1cc-d9fc3b5a4188 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [7 empty] | 1FCU_M4_156 Torque marks are missing on the torque and the insulator Cleaning needed Bone tags missing ID is missing on the drainage and flow direction | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615808&prj=263&rqi=95glCsja056lIHhgNa1z1ISzAI
SOR-2327-001 | 4a92951e-91c3-7234-0e81-a9ce90c71e95 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [7 empty] | Poste 1 Bone tag missing ID not attached to the pipework | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615843&prj=263&rqi=UixmbxqUFGhfheeH27xhZIZKFi
SOR-2319-001 | e339256d-30a7-0c0b-5ba2-a9a3007731a2 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [7 empty] | Mechanical 1FCU_M6_159 Drainage not terminated Bone tag Missing Earthlings missing Cleaning needed Drip tray missing Torque mark missing on the Isolator Labels are missing on the income to the isolator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615804&prj=263&rqi=S8O4Mhx9yEJMFOkfKl4vYb2QSd
GI-383 | 2f949746-7448-9401-a07e-78c528abc90b | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [7 empty] | Mechanical 1FCU_M5_160 Drainage not terminated Bone tag missing Earthlings missing Cleaning needed Torque mark missing on the Isolator Labels are missing on the income to the isolator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615803&prj=263&rqi=2Ctf2MhZFkUcPmnkBaynSMgoep
SOR-2328-001 | 83959176-1b96-bdea-0fe8-11abec354cbf | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [7 empty] | Poste 4 Bone tag missing ID not attached to the pipe | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615844&prj=263&rqi=Im70q6JhB0BDe0W3vu860pkwh0
SOR-2317-001 | f73e1629-fff8-994a-ab18-4ebcee699d7e | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [7 empty] | Mechanical 1FCU_M6_158 Drainage not completed Bone tag missing Earthlings missing Cleaning needed Drip tray missing Torque mark missing on the Isolator Labels are missing on the income | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615802&prj=263&rqi=z2qLQSwbNm8gnw26e0SoTMnQ7L
SOR-2316-001 | e1c03854-5d61-5c00-44f0-6c54cf72a941 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [7 empty] | Mechanical 1FCU_R2_161 Drainage not completed Bone tag missing Earthlings missing Cleaning needed Drip tray missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615801&prj=263&rqi=19LQFseuOyO5WHoH00glGxrXQo
SOR-2321-001 | 618acd11-358c-0dc7-1166-0cdd41f0ebd8 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [7 empty] | 1FCU_M6_155 Torquin is missing on the isolator Labels are missing on the wiring Labels are missing on the drainage Cleaning needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615806&prj=263&rqi=QMbbfGSgLOVLMjnkYjNZ9POvlw
SOR-2322-001 | 9e042aff-2c03-a8b0-29cf-a36eb3529e54 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [7 empty] | 1FCU_M6_155 Torquin is missing on the isolator Labels are missing on the wiring Labels are missing on the drainage Cleaning needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615807&prj=263&rqi=1u0d9FPWHyBTbGt1OW0S3pPlYd
GI-381 | 5e40d674-1479-4c79-95f4-3ecb25abea26 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-03-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Incomplete Connections | Commissioning | [7 empty] | CYT 1DB_M1R1_8_1 Conditional - Conditional yellow tag applied to unit - Issue will ONLY be closed once permanent supplies are installed and all documentation issued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615790&prj=263&rqi=hIs2zNvMMoBX5ASxkEGzOxIMjj
RT1DCOS-229-001 | 36aacef2-02ee-42d5-8439-b0a344307585 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Electrical | L2 | Installation Damage | Commissioning |  | DCIM/DCOS | equipment | 1DCOS_1_HMI_27 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Perspex screen broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615722&prj=263&rqi=05E7oFURmoDgKe8GkCbADkHNhK
RT1DCOS-224-001 | 777b0ce4-f3b0-48db-adfd-d23ca7022525 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Electrical | L2 | Installation Damage | Commissioning |  | DCIM/DCOS | equipment | 1DCOS_1_HMI_22 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Perspex screen broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615721&prj=263&rqi=0aULJdBVV9SueKT41mAxMEkoDX
YT1DCOS-237-001 | fde40757-5c23-4507-91e8-c9d85bb94aa5 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Not Correct | Commissioning |  | DCIM/DCOS | equipment | 1DCOS_1_HMI_35 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Earth Cable sharing same entry gland as CAT6 cable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615724&prj=263&rqi=1xmqXpaeCT4yDtImoz5sgEqdTu
GI-378 | ce5a551e-2136-4c3b-b308-1bf99c7487df | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Complete | Commissioning | [7 empty] | MECHANICAL: The bolts on the CHWSTR system are loose, and an extra bolt should be added. Please remove the delivery brakes from the chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615720&prj=263&rqi=ACQqp5bYIbi2AJtthZ2GTCE6tk
GI-377 | d6cbf45e-f082-4c5b-a0a6-ece19e5d2fb7 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Correct | Commissioning |  |  | equipment type |  |  |  |  | Mechanical: Bolts are loose on the CHWSTR. Remove the shipping brackets from the chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615719&prj=263&rqi=8wQxXD92qfbDYZnjGyDOZ5JpZ4
YT1DCOS-228-001 | c4cd2c82-c6b9-4080-ba98-786187c957af | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | gregb@straightlineconsulting.co.uk | 2026-03-16 04:00:00.000 +0400 | General Contractor - Electrical | L2B | Installation Damage | Commissioning |  | DCIM/DCOS | equipment | 1DCOS_1_HMI_26 | DCOS - HMI Panels |  | SCH - Schneider | Electrical - Earth bonding incomplete | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615710&prj=263&rqi=oFsZcSfslPL9iTeWMISM8S5Ai1
GI-376 | 25c78881-102e-b387-d8e8-ebdbde5b43e4 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-03-13 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS Graphics Issue | DCOS | [7 empty] | Mechanical- scaling on graphic to be amended 20l/s difference between flow meter and graphic | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615515&prj=263&rqi=vQy71NrByspxIYftsyH81Kk2Af
BT1MECH-402-030 | fd718b8d-ac48-429a-ac53-a402759058c0 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-12 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Installation Not Complete | Commissioning |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Mobile gent set pipework requires a plug/end cap on the valve. The cables and the terminal boxes to be tidied up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615452&prj=263&rqi=cYRKIAFBWMUP0Ov3Uz7svULfhn
GI-375 | c093c89f-28ac-45c7-ab51-cc53c35bc237 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | stephenturner@sygna-emea.com | 2026-03-11 04:00:00.000 +0400 | Commissioning Authority |  | Installation Not Complete | Commissioning | [7 empty] | During the L4 Fuel testing, on the fuel system HMI Phase 2 equipment is visible and in Fault, at this moment in time works are unfinished in phase 2. this must be noted in the L4 script and rechecked when phase 2 is undergoing L4 testing . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615343&prj=263&rqi=YJOi42r3d5Epb7PtCwEAHaWZUw
BT1MECH-402-029 | 69096cdd-be52-4aed-9671-70f0f2908047 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-11 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Component/Equipment Failure | Commissioning |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - The HMI is freezing during L4, KOHLER team is fully aware about the issue but they cannot provide a solution. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615340&prj=263&rqi=3ixuZsYpsWrxhEyxj62qCdBOBJ
BT1MECH-402-026 | e966ee05-e819-435f-b773-6ad3f813cb0a | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-10 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | DCOS Graphics Issue | DCOS |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Police valve on HMI appears as Fire Valve Daily Tank --> Gen Set Pompier Valve Â appears on HMI as Fire Valve No1 Tank and Â No2 TankÂ The DCOS has the correct labellingÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615264&prj=263&rqi=R9YWUrgAuVOAabNC3xxgvUDybE
BT1MECH-402-028 | b354df4f-8f74-42d9-af30-72a766e7cfca | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-10 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | DCOS Graphics Issue | DCOS |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - HMI Graphics to be adjusted with correct labelling. Alarms description should be specific to the equipment: i.e. Alarm Police Valve GS M1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615297&prj=263&rqi=DVheFVozbYyV5BTfPjafZLAq2P
BT1MECH-402-025 | eea75b0d-2724-4f30-aa8e-ff84d9583655 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-10 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Cleaning | Commissioning |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - All bulk tanks require cleaning. Bulk tank 1 is used as a storage and bulk tank 2 is flooded from rain water. See attached pictures. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615259&prj=263&rqi=FOlVvcJe7lgHB00Amg748pX4Gy
BT1MECH-402-027 | ca08a409-b860-44dd-a8ee-150eb71ab321 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-10 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | DCOS Graphics Issue | DCOS |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - No Â alarm on HMI for pompier valve. There is Pompier Alarm on DCOS. Â Graphics issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615266&prj=263&rqi=lAlNKegPSMNHfxJCS6dnFdTVtp
BT1MECH-402-024 | 65e3e6da-b694-cc9b-a7a9-e292d99acf89 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-10 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Component/Equipment Failure | Commissioning |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Bulk tank 3, solenoid valves not responding on manual and close request. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615222&prj=263&rqi=r8QD2CAUHw40uT9hnGf5gLxO2Z
BT1MECH-402-023 | 5f22597c-4e12-e0b1-bc03-619d7537cafa | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-09 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Component/Equipment Failure | Commissioning |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - HMI not responding, issue with time response of HMI between tabs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615143&prj=263&rqi=GdNHxEnJm5LLiFFDrLwDTbdUls
SOR-2284-001 | 5ff57684-00e1-986a-b7f3-ece60a40c046 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-03-06 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Installation Not Correct | Commissioning | [7 empty] | scratch on the front panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614903&prj=263&rqi=Fzy1Wg4gpD1pZlOt91QAzh9b7Z
SOR-2283-001 | e54190ff-4196-8f0f-a2c6-0c26d89eec02 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-03-06 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Commissioning Issue | Commissioning | [7 empty] | scratch on the panel inside | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614902&prj=263&rqi=BWmah0GmX6fVSnHCrl3RJ2Ebwp
GI-374 | 7067fce6-5aae-438f-876d-7a6954e4b955 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium DCOS | joshw@straightlineconsulting.co.uk | 2026-03-05 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | DCOS/MECHANCIAL - TT01 in UPS Room M1 seems to be reading way off actual temperature off the room BYES/DCOS Team to provide document showing all TT's in phase 1 + calibrations commissioning is complete. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614799&prj=263&rqi=9jxryhtKcC0OEqpzOTVjblGf2o
BT1MECH-402-022 | 9aa54015-06d5-ff61-f6dd-a4e756ba40f7 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-03-04 04:00:00.000 +0400 | REH - Rehlko Gens | L4 | Design not as Specified | Design |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Fuel bulk tank set points are not matching the SOO. There is not enough fuel and have been adjusted to allow available tanks during the L4 test. Kohler to revert set points | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614707&prj=263&rqi=AZfhQjxJ5HAH4WuQlBokBWX7Ws
GT1MECH-729-062 | ba31dbb4-e26d-9ef4-22df-0d584a1205b7 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-03-03 04:00:00.000 +0400 | REH - Rehlko Gens | L3 | Installation Not Complete | Commissioning |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Ad Blu manifold Flow Sensor Missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614610&prj=263&rqi=SFSKXfAW7UhVOYjYUzDqDxOVNW
GI-372 | 398fea6c-d275-d8eb-dbbb-d8b00ea84252 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-26 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Damage | Commissioning | [7 empty] | Scratches on the pump 1CHWP_M1R1_02 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352221&prj=263&rqi=8vBmsYRlp5HZV8WN3TDKYtJhM3
GI-373 | c6bc39db-5b1c-4671-72e4-efc5980e33ce | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | emanuelp@straightlineconsulting.co.uk | 2026-02-26 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | [7 empty] | 1CHWP_M1R1 01 Mechanical earthing not terminated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352222&prj=263&rqi=pqsBXmIlNYc89493BXW4gehx6z
SOR-2258-002 | 2bd9e89c-79b7-ca66-eca7-98847c5fefc2 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | tayebb@straightlineconsulting.co.uk | 2026-02-25 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | drawing is not up to date as per checks on site picture attached should be Version 6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=212868&prj=263&rqi=nTWackFygvnXfdRXvYqK7T5DH6
SOR-2351-004 | a5140fda-61a3-f23c-ccf1-99e4cc9992f4 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | grantw@straightlineconsulting.co.uk | 2026-02-24 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning |  | Fire Detection | equipment | EAE_11 | EAE Fire Panels |  |  | Damage to panel Bent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615999&prj=263&rqi=GdvoTqY6Y4OI18kAb8pz94nKEs
SOR-2354-004 | ba18a04d-fb6f-3023-a027-43f25e1fd763 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-24 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning |  | Fire Detection | equipment | EAE_22 | EAE Fire Panels |  |  | No bone tags on Cables | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616000&prj=263&rqi=88704kAsQZ5ZnBrIuPgHc6scdE
GI-371 | 2985e76f-4080-4c17-ad11-523b8ade47aa | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | grantw@straightlineconsulting.co.uk | 2026-02-23 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation Not issued/ Required | Commissioning | [7 empty] | ELECTRICAL L3 LIVE Cable test reports missing for the following cables\\\\\\\; CBL-1UMDSB_M1R2-01 CBL-1UMDSB_M1R2-02 CBL-1UMDSB_M1R2-03 CBL-1UMDSB_M1R2-04 CBL-1UMDSB_M1R2-05 CBL-1UMDSB_M1R2-06 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199773&prj=263&rqi=b64jiw6KS3wqIrcys9ihUg8Dic
GI-387 | 32345d85-ab11-d94b-e4c6-99a3811c28c3 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-18 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning |  | Fire Detection | equipment | EAE_18 | EAE Fire Panels |  |  | panel has damage to paintwork | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615997&prj=263&rqi=l8c4R1dw9HD83Jz7RgyqhFxMyA
SOR-2340-005 | d8bc7f06-e4a0-1d8c-7591-1b467a6284bf | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-18 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning |  | Fire Detection | equipment | EAE_19 | EAE Fire Panels |  |  | Paintwork damage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615998&prj=263&rqi=knxwHHxYugF7tc2r7aKz6Dlgip
RT1ELEC-634-393 | 4d72af0c-b6f8-a541-8ccc-0d9f95b9230f | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-17 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Installation Not Complete | Commissioning |  | Electrical â€“ LV | equipment | 1DCOS_1_OAP_1 | CP - Control Panel (Max Cool Announcement) |  | SCH - Schneider | 1DCOS_1_OAP_1 Mechanical: End Caps missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199345&prj=263&rqi=yGWIK5jTE5oW3SQ4JoLZrRyHYn
GI-370 | e09bbd38-39ee-60c6-fccc-12da0b4c60cc | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | adamb@straightlineconsulting.co.uk | 2026-02-16 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [7 empty] | Mechanical- flow meter from CHWP 5-2 Incorrect showing 30 l/s with pump running at approx 25 Hz when pump delivering approx 65l/s and running at 50 Hz | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199328&prj=263&rqi=biRHSl6aWb3Sjbr4qONslpKPf5
GT1MECH-729-058 | 44d56036-062b-b7d0-68b3-9df042e24f01 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-11 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Commissioning Issue | Commissioning |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Urea filling request on the HMI remains off during filling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199061&prj=263&rqi=vHf68fKUVvHIQWFVmOO1s4Hpkt
GT1MECH-729-061 | b52f9298-1f15-4ae2-a4c1-d7c26fa3d7b2 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-11 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Documentation Not issued/ Required | Commissioning |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Urea SOO L3 carried out based on R05 SOO, the R06 is for review Â at the moment and KOHLER advised that revision 7 (R07) will be the last oneÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199064&prj=263&rqi=RMvs5oBUIZFz2nnjCfYF11Eeyl
GT1MECH-729-060 | 26bf88f2-fd88-3d47-fcae-0ee5181e08d4 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-11 04:00:00.000 +0400 | REH - Rehlko Gens | L3 | Installation Not Correct | Commissioning |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - Urea pump 1 - flexible hose stretch. To be replaced with the correct size | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199063&prj=263&rqi=nYtYSrG8fej7QBMoSCT9JQuM0n
GT1MECH-729-059 | 0163590c-7c7b-01b2-ea64-9b3d6d4dedb6 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-11 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Commissioning Issue | Commissioning |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - fuel level on alarm at 47% and 2minutes later the alarm disappears still at 47% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199062&prj=263&rqi=kLnTdHfnXeWS6tuusnfHDg4gBd
SOR-2199-002 | ad50be0f-31e1-b4cf-026c-fa0e32544a2a | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical |  | Torque required | Commissioning |  | Fire Suppression | system | Sprinkler System |  |  |  | Sprinkler System Poste 12 Cx L2A 10/02/26 EP torque missing End caps missing Painting | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198926&prj=263&rqi=gHWSwmOHJR1z76GyoEmam8Cjzs | https://equinix.facilitygrid.co.uk/x/project/263/system/10985
SOR-2196-001 | 4800fe9f-067a-5c0c-c386-21d4c34d0268 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1CHWSTR_M3R1_8_ELC_1 | CP - Control Panel |  |  | Income power needs to be torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198882&prj=263&rqi=0Qzz4IsgSe4GVOtYebr8UQLI0c
GT1MECH-729-057 | b1e2b4bf-d7bd-e7c0-eb87-2c1ef728f62e | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Commissioning Issue | Commissioning |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - graphics in hmi not matching with SOO and Equinix standards | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198928&prj=263&rqi=ocf6y3uTzSWBzOXwWIGDuYN1zl
GT1MECH-729-056 | 5624186f-2e68-9147-5878-3eebaa72c177 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical | L3 | Commissioning Issue | Commissioning |  | Plumbing | equipment | Fuel System | Fuel - Fuel System |  |  | Mechanical - fuel low level alarm in SOO R06 is not matching with HMI setpoints. There is not enough fuel in bulk tanks to be able to have low level alarm at 50% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198927&prj=263&rqi=FvxzJdYWIwBynnEk5KAtzaTt00
SOR-2199-001 | 9af67dc5-df49-b967-3c61-458d7075f20e | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning |  | Fire Suppression | system | Sprinkler System |  |  |  | Sprinler fittings need touch-up painting Poste 28 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198925&prj=263&rqi=PWIZuFkcjioj68sFGoxF7bLTln | https://equinix.facilitygrid.co.uk/x/project/263/system/10985
GI-360 | 72f3b146-7d9f-c8b2-ab53-56142fe9c50e | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical |  | Torque required | Commissioning |  | Fire Suppression | system | Sprinkler System |  |  |  | Bolts not torqued Poste 28 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198923&prj=263&rqi=IJhhsncvtg5ALTEzjvRQei3a3v | https://equinix.facilitygrid.co.uk/x/project/263/system/10985
GI-361 | d8635a9f-b61f-6a88-fdac-9e404ebd3c08 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning |  | Fire Suppression | system | Sprinkler System |  |  |  | Extra support needed and end caps on the bar Poste 28 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198924&prj=263&rqi=sZe9RvEWtvQn2UtA48ABnrAGB4 | https://equinix.facilitygrid.co.uk/x/project/263/system/10985
RT1FS-301-003 | 88abecb3-6bac-69b2-8f42-c7181db24840 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-02-04 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Incomplete Connections | Commissioning |  | Fire Suppression | system | Smoke Dampers - First Floor |  |  |  | Electrical - 1SD_NC_0025 - exposed wire to be wagoed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198633&prj=263&rqi=Et1qkQ3wwNdmnYgu3XJbBwNORG | https://equinix.facilitygrid.co.uk/x/project/263/system/11603
SOR-2150-006 | 5765995b-77d5-05fe-7285-974bfbf3a530 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning |  | Fire Detection | equipment | EAE _06 | EAE Fire Panels |  |  | Electrical no End caps in Trunking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198256&prj=263&rqi=qx6QEkYCVARD6GD1qLh6Hz3J6a
RT1FS-301-002 | 4322f5c6-9e60-a588-d176-ea4a7a2af905 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Incomplete Connections | Commissioning |  | Fire Suppression | system | Smoke Dampers - First Floor |  |  |  | electrical_earth not connected or protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198249&prj=263&rqi=StkSegzJznnnLiAIVp2aPGwZCq | https://equinix.facilitygrid.co.uk/x/project/263/system/11603
SOR-2149-004 | 31f18115-351a-1377-4a66-3694935d3520 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning |  | Fire Detection | equipment | EAE _05 | EAE Fire Panels |  |  | Electrical no End caps in trunking | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198251&prj=263&rqi=2fkGjHUIb8ZaFAc9Stavjgh45Y
SOR-2149-005 | 248e7d30-4e60-ff0e-41f6-131b810148cf | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | Fire Detection | equipment | EAE _05 | EAE Fire Panels |  |  | Electrical No Asset ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198252&prj=263&rqi=hMX4nkuKG6JRV49JZDSnZDSW4a
RT1FS-301-001 | 8b354e24-36a8-2373-56c8-6525a1662d82 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | emanuelp@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Mechanical | L2A | Incomplete Connections | Commissioning |  | Fire Suppression | system | Smoke Dampers - First Floor |  |  |  | Electrical- earthing cable cut and not protected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198248&prj=263&rqi=tS3GJx5JcuCtNPt9WB4Yu7ZdCM | https://equinix.facilitygrid.co.uk/x/project/263/system/11603
SOR-2150-005 | 1e17e645-9d93-ee5c-d5f1-b21b92dfa6c7 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  | Fire Detection | equipment | EAE _06 | EAE Fire Panels |  |  | Electrical No Asset ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198255&prj=263&rqi=clZUst8GXgjS31R1wGrUjLg45V
SOR-2150-004 | 311c0ea5-05b6-827f-8237-2249432964cd | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | Fire Detection | equipment | EAE _06 | EAE Fire Panels |  |  | Electrical i Cable ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198253&prj=263&rqi=iLeHnWWPASObFW56waAVb4oVG5
SOR-2149-006 | d1c23cb1-ec85-718a-f3a1-4305af8143a1 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  | Fire Detection | equipment | EAE _05 | EAE Fire Panels |  |  | Electrical No Cable ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198254&prj=263&rqi=nhlXfRm2CGqjyrk3AiJCDTg4WM
GI-357 | 1b6b53a4-ce2f-4226-9d95-b2199f0564a6 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | stephenturner@sygna-emea.com | 2026-02-03 04:00:00.000 +0400 | Equinix Project Manager |  | Installation Not Correct | Commissioning | [7 empty] | Earthing cable next to the transformer to be fixed in a better position see photo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198247&prj=263&rqi=k2cciOi9c2nMrZSOGpnBDtT3NW
GI-356 | 66eafbd9-65d8-4d22-b9d0-829a494844eb | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | stephenturner@sygna-emea.com | 2026-02-03 04:00:00.000 +0400 | Equinix Commissioning Manager |  | Commissioning Issue | Commissioning | [7 empty] | in all data halls permanent light must be on before energisation for PDCs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198246&prj=263&rqi=Tog2Ox4ryueqQrYoMuEaxGKahU
GI-353 | dfa105fa-17a5-47c6-90eb-c873c22d758a | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | stephenturner@sygna-emea.com | 2026-01-29 04:00:00.000 +0400 | Equinix Project Manager |  | Installation Not Correct | Commissioning | [7 empty] | On all MVTB'S the MV cables have noÂ glandes, this will effect the IP rating and it seams that foreign objects will can enter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197940&prj=263&rqi=IQmZiOFJI66ehP3qtepKxbhE50
GI-352 | 813747e1-8b74-4e3d-80a2-02f64261090c | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | stephenturner@sygna-emea.com | 2026-01-29 04:00:00.000 +0400 | Equinix Project Manager |  | Installation Not Complete | Commissioning | [7 empty] | It is imperative that permanent lighting be installed in all data halls when electrical equipment is energized. Unfortunately, this is not currently the case in Data Halls 3, 4, and 5, and this issue requires immediate attention. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197937&prj=263&rqi=FXYjKC2x6gHNo0a89grchVia4i
GI-354 | 40ab92ad-c429-447a-aae5-34cbd4be6960 | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | stephenturner@sygna-emea.com | 2026-01-29 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | [7 empty] | on all transformers the earth cable is only connected with a cable tie this can fail in the future. there are only 1 torque mark on each tightened bolt 2 marks are needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197941&prj=263&rqi=XcWvWfeMTwbL3o1CtfjXz1Rmt4
GI-355 | 6a41c70b-fae1-4cdd-80e2-6a6f4bff9ac2 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | stephenturner@sygna-emea.com | 2026-01-29 04:00:00.000 +0400 | Equinix Project Manager |  | Cleaning | Commissioning | [7 empty] | energised data hall are no condition to be energised due to poor house keeping planks of wood and other objects need removing and dust is also an issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197944&prj=263&rqi=5sGJRil3r3U1ISb1yZoicHWwUB
GI-349 | 991c611b-a86a-2b91-b8c8-a5ce0043007c | PA12x-1 | 263 | N-EMEA | Closed | P2 Medium CX | kostask@straightlineconsulting.co.uk | 2026-01-28 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Correct | Commissioning | [7 empty] | Mechanical - exposed copper on secondary power supply L1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197800&prj=263&rqi=Q3FLKr8doIFxXjKE74v1foPdmk
SOR-2126-002 | be21d123-6e2a-217a-8f1e-870aea9d99fc | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-28 04:00:00.000 +0400 | General Contractor - Electrical |  | Cleaning | Commissioning | [7 empty] | Electrical BB requires cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197796&prj=263&rqi=V5GDHx2k3O4gXiQB3CFHebxg4b
GI-351 | 2b8228f2-700a-455d-311d-f16c332f1a38 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-01-28 04:00:00.000 +0400 | General Contractor - Mechanical |  | Torque required | Commissioning | [7 empty] | Mechanical - earthing torque marks required in all three panels | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197802&prj=263&rqi=CLsSU4iCKtbBtgFeNRU6atNuie
GI-350 | 3e69e3b0-5b68-197b-0539-5135f32e4c6c | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-01-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation Not Correct | Commissioning | [7 empty] | Mechanical - glands not in use to be capped off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197801&prj=263&rqi=aLWPtflum0ulvl1eKr6NdCuvkr
GI-346 | e1a187dc-0248-3efc-35c5-06825f742aae | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Damage | Commissioning | [7 empty] | Mechanical- Coil Fins to be combed prior to energisation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197674&prj=263&rqi=XN4YaQ90sdOQxOGE5M1kLslOCw
GI-345 | ad083c8d-aeb4-1a9c-ae96-ea42760dfdcf | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation Not Correct | Commissioning | [7 empty] | Electrical- Conduit to be fitted correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197673&prj=263&rqi=YBYtc7hMMpZT0YXsYrZBLkW6fd
GI-344 | 4db44add-276d-73c9-a320-179a34a5340a | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [7 empty] | Electrical- No Bone Tag Fitted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197672&prj=263&rqi=5kShiFALZHbZreuaDNOQtbLT2n
SOR-2105-005 | 7627dc9d-05a6-1ba4-da20-c8409387d399 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [7 empty] | Electrical- Fire cable to be supported by cable tray and conduit to be made good | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197666&prj=263&rqi=nPM2o5MMeCpb4AvEC9hchcYT91
GI-347 | 7bcfe51d-25c6-bc60-16b4-462b16e949a4 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [7 empty] | Electrical- No Bone Tag fitted and Conduit to be made good (1CU_M1R1_29) Gen Building Roof | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197676&prj=263&rqi=Ov9PpZ1b22qqlQJNZRegNf51xl
YT1FS-303-001 | 20de5fd3-f464-4fe9-bd24-5682d0c1c4d0 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-22 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Cleaning | Commissioning |  | Fire Suppression | system | Smoke Dampers - Ground Floor |  |  |  | Mechanical - All Data Hall 1 & 2 Low level ductwork behind dampers to be cleaned and to be free of dust and debris before Fan start up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197445&prj=263&rqi=mUEwFKPzpkW83AvEG9F3LLMghL | https://equinix.facilitygrid.co.uk/x/project/263/system/11604
SOR-2076-004 | d302b6ae-ab64-388b-14ae-6c457c1b0e9b | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-22 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | [7 empty] | Electrical - containment to be re routed to gain access to Fire damper Acuator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197464&prj=263&rqi=NNRRPuaawEwzqu0iz0Kmd06Rvv
SOR-2074-004 | 8b1fc1e3-1bd4-b297-37ce-72796da623e6 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-22 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [7 empty] | Electrical- Containment to be extended for Fire Cables | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197462&prj=263&rqi=Q1g8CUxl2pZsZEHr6mtVJkyrA5
YT1FS-305-001 | b7eed687-6537-4c78-8013-7a8a2a5147a8 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-21 04:00:00.000 +0400 | General Contractor - Mechanical | L2B | Labelling | Commissioning |  | Fire Suppression | system | Smoke Dampers - Second Floor |  |  |  | Electrical - All Bone Tags to have correct reference in Data Hall5 & Data Hall 6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197352&prj=263&rqi=OFxEkyrfZHv17pTX3ZGFNtoGFe | https://equinix.facilitygrid.co.uk/x/project/263/system/11605
RT1FS-304-023 | b8f54145-57f1-b830-adcb-3acd1270e5bb | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | adamb@straightlineconsulting.co.uk | 2026-01-20 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning |  | Fire Suppression | system | Fire Dampers - Second Floor |  |  |  | Electrical - All bone Tags to Low Level Smoke Dampers in Data Hall 5 have incorrect reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197303&prj=263&rqi=lElOfzOuRAa1IawTwswqZ58zQQ | https://equinix.facilitygrid.co.uk/x/project/263/system/11602
SOR-2083-005 | 8f3311a9-a36a-aa96-db53-86d616c4cef0 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-20 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [7 empty] | Life Safety No Asset ID | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197468&prj=263&rqi=5fKSgKUT8akLlmvYeCEqCaY2Zi
GI-342 | 127d9fc1-f9bc-cb72-0292-4cf2f2029b0a | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-19 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [7 empty] | Electrical Holding down bolt for Rear compartment Section 2 the thread is worn/ Criss threaded | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197191&prj=263&rqi=p33h6efqd4LXIRDFpFIgLxml7x
SOR-2049-005 | e3262cfc-cbd4-17e7-dc64-237a60a8d571 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Documentation Not issued/ Required | Commissioning | [7 empty] | Electrical Drawings need to be updated as | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197014&prj=263&rqi=10jTNHLYKfXO0UmPt2QCIhZAgE
GI-340 | 2f256a28-6581-135f-46ba-3f6627b1d7c5 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-15 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Correct | Commissioning | [7 empty] | Electrical No Ferrels on Earth cables | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197016&prj=263&rqi=QjPyChcyMtA6hk5BmaNU70XLCn
SOR-2049-006 | 415d853a-0b86-8a23-f04f-6d22439de60a | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Cleaning | Commissioning | [7 empty] | Electrical Panel requires repaint/ Cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197015&prj=263&rqi=OTlDkXMWFUdqmjNLGQTDuZpjZe
SOR-2032-002 | fc1bd48f-c4d0-e416-2865-d2780a04328c | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | Electrical No Red Tag QR code for Yellow tag to be placed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196808&prj=263&rqi=M22Lh4FMQdWit1Y25VuVxQUEJL
GI-339 | 9bdf1be4-b364-561f-c55d-4a265bfab585 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | grantw@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning | [7 empty] | ELECTRICAL Torque on BB messy need to be cleaned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196805&prj=263&rqi=zUhpL3ZicbXjGotRLeYDRnj7H8
GI-338 | fe8ec42f-9cb9-2dfe-decf-07ec7aca42c3 | PA12x-1 | 263 | N-EMEA | Closed | P3 Low CX | kostask@straightlineconsulting.co.uk | 2026-01-07 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Not Complete | Commissioning | [7 empty] | Mechanical - cable tray earthing missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196486&prj=263&rqi=K5DnoEyRIUUB13X5aIwb96AwP9
FPT-765-001 | 5c614710-1fdf-4c67-8756-baa52bcf248e | PA13x-2 | 406 | N-EMEA | Closed | Outstanding Paperwork/Documentation | gregm@straightlineconsulting.co.uk | 2026-04-14 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation Not issued/ Required | Commissioning |  | Mechanical â€“ Water | system | PA13.2 Post Sec Chilled Water System Integration Verification Test Script |  |  |  | Mechanical - MER /KES to issue the results from the on site water analysis test taken 18/3/26 of the Sec CHW system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618095&prj=406&rqi=97mN6r5oRb0hnvWEXCbWXmPP2S | https://equinix.facilitygrid.co.uk/x/project/406/system/14161
GT1MECH-450-001 | f98641ec-e589-4ff6-a1b0-77c341431adc | PA13x-2 | 406 | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-03-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS Installation Not Complete | DCOS |  |  | equipment | 1-MVHR-M5-1 |  |  |  | 1-MVHR-M5-1 DCOS and temp checks not carried out by DCOS team and Temperatures to be taken,. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616192&prj=406&rqi=6medUHygYUUjrnNLLkeivWOd62
DCIML4-1-001 | d15625dd-de7a-4d2a-9b36-c1bff261fe00 | PA13x-2 | 406 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-18 04:00:00.000 +0400 | SCH - Schneider DCOS | L4 | DCIM Cooling Zone issue | DCIM |  | Controls | system | DCIM |  |  |  | Location Vectors missing for Leak detection phase 2 assets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615974&prj=406&rqi=2yDFQyvzqnZPSNwPljZZ3TuHdp | https://equinix.facilitygrid.co.uk/x/project/406/system/11776
DCIML3-1-001 | f279acf7-bcdd-4aaf-be1f-10f1c554192f | PA13x-2 | 406 | N-EMEA | Closed | P3 Low DCOS | Cyril.Sabara@eu.equinix.com | 2026-03-18 04:00:00.000 +0400 | SCH - Schneider DCOS | L3 | DCIM Sync service Issue | DCIM |  | Controls | system | DCIM |  |  |  | Template Valve not upserted on DCIM | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615972&prj=406&rqi=6zkC6h4zQ0E4gjkPx2rqvkAOHD | https://equinix.facilitygrid.co.uk/x/project/406/system/11776
FPT-763-001 | 04db2bbf-ffc4-4a48-afe4-2dc1214bd6e6 | PA13x-2 | 406 | N-EMEA | Closed | Outstanding Paperwork/Documentation | gregm@straightlineconsulting.co.uk | 2026-03-05 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation Not issued/ Required | Commissioning |  | Mechanical â€“ Water | equipment | Cooling String 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12 String Failure | Cooling String 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12 String |  |  | Cooling String 1, 2, 3, 4, 5, 6, 7, 8, 9, 10, 11, 12 String Failure test - As left settings still to be issued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614794&prj=406&rqi=dPpTQFWK62ZPeiFgaOXmCYAKIx
FPT-762-001 | 492f82e6-5b44-4a7c-a389-7aa8c405f916 | PA13x-2 | 406 | N-EMEA | Open | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-02-23 04:00:00.000 +0400 | General Contractor - Commissioning |  | DCOS General Issue | DCOS |  |  | system | Fuel System |  |  |  | Fuel system Â Pressure switches on fuel pumps are sticking and need to be adjusted Pump 2 was alarming momentarily. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199774&prj=406&rqi=W8QybGIjuvdBKm2KLHZLFDThbB | https://equinix.facilitygrid.co.uk/x/project/406/system/7699
GI-282 | 8c0920b7-5deb-46c4-9cff-9cddcbb17e24 | PA13x-2 | 406 | N-EMEA | Closed | P2 Medium CX | michaeld@straightlineconsulting.co.uk | 2026-01-27 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Component/Equipment Failure | Commissioning |  |  | equipment | 1-ATS-JR2-1 |  |  |  | Electrical - During IST J it was noticed that ATS-JR2-1 was in alarm and not switching to redundant source. A thorough investigation is required by ITEC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197670&prj=406&rqi=bGa7RO7CFqlWE5exe1lBDFOKtw
WTIST-15-004 | 8b69ed5e-3067-4686-9e8d-f2e90ccb98ca | PA13x-2 | 406 | N-EMEA | Closed | P2 Medium CX | seanh@straightlineconsulting.co.uk | 2026-01-13 04:00:00.000 +0400 | SCH - Schneider Electric |  | Commissioning Issue | Commissioning |  |  | equipment | IST Phase 2A Hall I | Intergrated System Test Phase 2B I |  |  | Electrical - Failure of Utility (Test 1) during transfer to Gen after the Generator start signal was confirmed however the generator breaker failed to remain closed on 2 occasions. 51N was the ansicode that was received at the time of failure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196784&prj=406&rqi=xX6Is9EWPBj5AlOLzjxrawrJCH
L3-13-002 | b455c018-3c72-4d99-9164-0110be86a2cf | PA13x-2 Mickey | 554 | N-EMEA | Open | P3 Low CX | richardw@straightlineconsulting.co.uk | 2026-07-30 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Documentation Not issued/ Required | Commissioning |  |  | system | FIRE - Fire detection / Alarm system |  |  |  | Documentation - Latest documentation related to the tests performed for the DH. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631412&prj=554&rqi=o106pFCnJQgQYoAXkczQ7gJzCT | https://equinix.facilitygrid.co.uk/x/project/554/system/13897
YT1MECH-439-002 | 3215d565-dba2-4e0b-a2f9-dd7ea91b79b7 | PA13x-2 Mickey | 554 | N-EMEA | Open | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation Not issued/ Required | Commissioning |  | Fire Suppression | equipment | Fit Out - MFD-3131 | FD - Fire Damper |  |  | MFD-3031 - Chubb Cable test docs missing for MFD | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627578&prj=554&rqi=LNZPN0YnjJ9l88nvOhNyyeWgNQ
YT1MECH-439-001 | d833781a-c992-4a19-8f0e-01525065603c | PA13x-2 Mickey | 554 | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Correct | Commissioning |  | Fire Suppression | equipment | Fit Out - MFD-3131 | FD - Fire Damper |  |  | Fire Suppression - MFD-3031 fire damper access panel in Mickey office badly cut in to ductwork sharp edges - CUT risk | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627572&prj=554&rqi=mOyzK4NbQ01cyVOvQtF5bjy3YK
RT1MECH-424-001 | 604adb8a-2ba8-43a4-851b-9dfd3473c1e1 | PA13x-2 Mickey | 554 | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning |  | Fire Suppression | equipment | Fit Out - MFD-3131 | FD - Fire Damper |  |  | Fire suppression Â MFD-3031 Damper label required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627576&prj=554&rqi=WBYjY6WIBzyTBpm4T2jREnuUO4
YT1MECH-438-002 | 48675291-0868-4432-a3f2-a24d8a11d2a1 | PA13x-2 Mickey | 554 | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-07-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation Not issued/ Required | Commissioning |  | Fire Suppression | equipment | Fit Out - MFD-3130 | FD - Fire Damper |  |  | Fire Suppression MFD-3130 GC YT checklist missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627581&prj=554&rqi=GM9Qfz0o6ZPcRQvi7lvSlYXXRM
RT1MECH-423-002 | 473e0a27-ea87-4e63-9015-802fb677f487 | PA13x-2 Mickey | 554 | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Installation Not Complete | Commissioning |  | Fire Suppression | equipment | Fit Out - MFD-3130 | FD - Fire Damper |  |  | Fire Suppression - MFD-3030 fire damper access panel in Mickey office badly cut in to ductwork sharp edges - CUT risk | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626710&prj=554&rqi=fe2bwyTSxSgKHNaJuqEnr8TzqV
RT1MECH-423-001 | 11cba920-523f-4e98-a607-9b3bb746d274 | PA13x-2 Mickey | 554 | N-EMEA | Closed | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-06-24 04:00:00.000 +0400 | General Contractor - Commissioning |  | Labelling | Commissioning |  | Fire Suppression | equipment | Fit Out - MFD-3130 | FD - Fire Damper |  |  | Fire Suppression - MFD-3030 ID label missing from actuator | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626707&prj=554&rqi=DExCQyqXLMknuZqTZBa2kTsbke
YT1MECH-438-001 | b336b28d-153e-4fe8-951b-870a2f1c6a7f | PA13x-2 Mickey | 554 | N-EMEA | Open | P3 Low CX | gregm@straightlineconsulting.co.uk | 2026-06-15 04:00:00.000 +0400 | General Contractor - Commissioning |  | Documentation Not issued/ Required | Commissioning |  | Fire Suppression | equipment | Fit Out - MFD-3130 | FD - Fire Damper |  |  | Fire Supression MFD-3130 Chubb cable test doc required | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625340&prj=554&rqi=76cVPIXxNcbDxxMvYlk8r76GXv
L3-10-001 | 5c493f38-a0fb-43bc-9dfb-f1a04ece2741 | PA13x-2 Mickey | 554 | N-EMEA | Closed | P3 Low CX | richardw@straightlineconsulting.co.uk | 2026-06-11 04:00:00.000 +0400 | General Contractor - Commissioning | L3 | Documentation Not issued/ Required | Commissioning |  |  | equipment | 3-PA-11 |  |  |  | Mechanical - 3-PA-11 Missing documents ( Updated drawing, System) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624919&prj=554&rqi=FgONTGJzvO6LgscsEgKt9Hlu6D
GI-236 | 8017ac2b-f6e2-4880-b3e2-7c9bd713325b | PA13x-2 Mickey | 554 | N-EMEA | Closed | P3 Low CX | richardw@straightlineconsulting.co.uk | 2026-06-10 04:00:00.000 +0400 | General Contractor - Electrical |  | Commissioning Issue | Commissioning | [7 empty] | Electrical - Missing Arc Flash label for DB, STS and UDP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624754&prj=554&rqi=a8g8DDp2pPtyaTot6ZpyzTk61t
GT1ELEC-510-001 | 3537467a-23fc-4cd1-abe6-feace7d2f9e5 | PA13x-2 Mickey | 554 | N-EMEA | Open | P3 Low CX | richardw@straightlineconsulting.co.uk | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning |  | Electrical | equipment | Fit Out - Lighting / Emergency Lighting | LITE - Lighting Control |  |  | Electrical - Confirm all associated distribution panels for lighting controls and power have been level 3 commissioned and signed off accordingly. DALI system needs to be reviewed and handed to OPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622449&prj=554&rqi=AyvLAHtH4RgaspFNm2dQjBXzFW
GT1ELEC-510-002 | 39dcc0ec-79eb-4c06-b576-39ece5ae935d | PA13x-2 Mickey | 554 | N-EMEA | Open | P2 Medium CX | richardw@straightlineconsulting.co.uk | 2026-05-20 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning |  | Electrical | equipment | Fit Out - Lighting / Emergency Lighting | LITE - Lighting Control |  |  | Electrical - Confirm LUX levels have been checked against global standards (normal lighting). Lux levels not achieved - Minimum 500 lux | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622452&prj=554&rqi=gsU06KDbDgbbbtpxDrUxZYQoWU
L3-13-001 | 441b78e2-d648-4a81-967e-7ea6a4144b34 | PA13x-2 Mickey | 554 | N-EMEA | Open | P2 Medium CX | richardw@straightlineconsulting.co.uk | 2026-05-19 04:00:00.000 +0400 | Equinix Commissioning Manager | L3 | Commissioning Issue | Commissioning |  |  | system | FIRE - Fire detection / Alarm system |  |  |  | Confirm that battery back-up autonomy meets specification (isolate mains supply for â€˜24â€™ hours then operate fire detection and ensure sounders operate for specified time) Battery needs to be replaced and test needs to be re-done | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622265&prj=554&rqi=YQ5bNWQUGZ60Rt87Q32rvF4CAm | https://equinix.facilitygrid.co.uk/x/project/554/system/13897
GI-235 | 82d3625a-c025-411d-92f7-918f88ffc1ce | PA13x-2 Mickey | 554 | N-EMEA | Closed | P3 Low CX | richardw@straightlineconsulting.co.uk | 2026-05-01 04:00:00.000 +0400 | General Contractor - Commissioning |  | Commissioning Issue | Commissioning | [7 empty] | Electrical - Missing labels on all busbars | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620116&prj=554&rqi=kp0YZzoT50Uub7T9S2pKBEq0Vb
GI-021 | 7c9926c3-37ff-424d-a61b-f6567bd75bb3 | PA13x-SWGR | 526 | N-EMEA | Closed | P2 Medium CX | Iuliant@straightlineconsulting.co.uk | 2026-02-10 04:00:00.000 +0400 | VER - Vertiv Electrical |  | Comms Issue/Fault | DCOS |  | Electrical | equipment | 1-COP-D2 | COP - Customer Operating Panel |  |  | Circuit breakers B12;C2;C3;C4 show issues/fault on DCOS trip status . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198862&prj=526&rqi=hS3joZBIydWS90l63GRqQPXe9W
SOR-72-004 | 25366127-ac66-4e08-bc93-52f065a60fda | PA13x-SWGR | 526 | N-EMEA | Closed | P3 Low CX | Iuliant@straightlineconsulting.co.uk | 2026-01-09 04:00:00.000 +0400 | VER - Vertiv Electrical |  | Labelling | Commissioning |  | Electrical | equipment | MSB-D | MSB- Main Input Switchboard |  |  | MSB-D Bus-bar Phase Sequence Label | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196647&prj=526&rqi=1HENVRkC5how3P0AiDhYUDvqd2
SOR-52-003 | b788ac45-e98e-430c-aeb3-a685b402e124 | PA13x-SWGR | 526 | N-EMEA | Open | P3 Low CX | Iuliant@straightlineconsulting.co.uk | 2026-01-09 04:00:00.000 +0400 | SCH - Schneider DCOS |  | DCOS not Complete | DCOS |  | Electrical | equipment | 1-COP-D1 | COP - Customer Operating Panel |  |  | Confirmation is required regarding the current status of the MCB for COP-D1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196646&prj=526&rqi=QjJBMS5YvdP3catCACkBaIdbxd
SOR-413-001 | 544173ac-a78f-4649-aa45-91402da822b9 | PA14-1 | 553 | N-EMEA | Open | P2 Medium CX | emanuelp@straightlineconsulting.co.uk | 2026-09-17 04:00:00.000 +0400 | General Contractor - Mechanical |  | Installation not complete | Commissioning | [7 empty] | AFIRE_A_01_DMP_03 Hoses were routed through the damper, preventing verification that it could close fully and operate correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638494&prj=553&rqi=Fw8oVgfnReKsslmOt62KqSHzqv
L2L3 Sun-166-001 | c01460af-8e42-960f-b808-6c64cd5bdd8f | PA14-1 | 553 | N-EMEA | Open | P3 Low CX | steved@straightlineconsulting.co.uk | 2026-08-14 04:00:00.000 +0400 | General Contractor - Electrical |  | Incomplete Connections | Commissioning |  | Electrical â€“ MV | equipment | 1HMTX_1 | HMTX - Primary Substation Transformers |  |  | Thermal Relay fed by temporary power, needs a permanent supply, and has a temporary label, plus has a few scratches on the door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633621&prj=553&rqi=Rgm7gj6kp39eVu8T1PYCw0C5Ct
GI-018 | 0ddee08e-89e2-4417-80e4-983c772500fb | PA14-1 | 553 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [7 empty] | 1PCP_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625302&prj=553&rqi=JHDX6Sl3PHL9AczlvoVqNouGZ6
GI-019 | 12fa8da9-ef26-4c67-b891-708495b1e253 | PA14-1 | 553 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [7 empty] | 1PCP_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625303&prj=553&rqi=u1hXjtAZM6VIm60GDsbjyHAeEF
GI-017 | bfca1929-4bb2-452c-b9a6-2501c7cc734e | PA14-1 | 553 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [7 empty] | 1PCP_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625301&prj=553&rqi=DoKJ7tARdxSpCxOjrLLD5eMzMl
GI-016 | 552563ad-e20f-4440-87f7-dbea3a11bbc6 | PA14-1 | 553 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-15 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [7 empty] | 1PCP_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625300&prj=553&rqi=R3lECsmujlKTyQDlyOpXktc41c
GI-015 | 3e024975-df85-417b-a526-86e1cca86a40 | PA14-1 | 553 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-14 04:00:00.000 +0400 | General Contractor - Mechanical |  | Commissioning Issue | Commissioning | [7 empty] | 1PCP_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625293&prj=553&rqi=XTbVnghJqdS4HjkcQnM7DXQKXo
GI-012 | f572925d-de29-4ee9-91aa-3550fd651cc6 | PA14-1 | 553 | N-EMEA | Closed | P3 Low CX | hajar.banan@spie.com | 2026-06-09 04:00:00.000 +0400 | ITEC - ITEC Groupe |  | Commissioning Issue | Commissioning | [7 empty] | 1UDP_C2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624695&prj=553&rqi=qTWOqYB72EJ8uxTraeAdSk7Fd1
GI-011 | 86853b5c-e00a-1455-3bf9-f16b78209dfe | PA14-1 | 553 | N-EMEA | Open | P3 Low CX | hajar.banan@spie.com | 2026-06-04 04:00:00.000 +0400 | SOC - Socomec |  | Commissioning Issue | Commissioning | [7 empty] | 1STS_C2R_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623938&prj=553&rqi=fDlCE84nxS0yAshynBpxtNh9lV
RT1ELEC-12-001 | 99d89c66-3102-ff6a-f931-ecdbe8611738 | PA14-1 | 553 | N-EMEA | Closed | P3 Low CX | steved@straightlineconsulting.co.uk | 2026-06-02 04:00:00.000 +0400 | SCH - Schneider MV | L2A | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1GRMU_B | GRMU - Generator Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme. Missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623599&prj=553&rqi=dMEGRmABzXFNClMw7PpoEXSK0G
RT1ELEC-11-001 | 889b430e-c4a1-34ed-5a71-b7486791fc20 | PA14-1 | 553 | N-EMEA | Closed | P3 Low CX | steved@straightlineconsulting.co.uk | 2026-05-26 04:00:00.000 +0400 | SCH - Schneider MV | L2A | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1GRMU_A | GRMU - Generator Ring Main Unit |  |  | Verify permanent equipment labels are fixed, proper label language and colour scheme, labels missing for breakers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623136&prj=553&rqi=6EaNG6ANjTGZpz6Frosd3cf1MK
RT1ELEC-11-002 | 5d9237af-f116-4773-b584-d75e3e652dbb | PA14-1 | 553 | N-EMEA | Open | P3 Low CX | steved@straightlineconsulting.co.uk | 2026-05-26 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning |  | Electrical â€“ MV | equipment | 1GRMU_A | GRMU - Generator Ring Main Unit |  |  | Verify the switchgear tool board is secured to a wall. Missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623137&prj=553&rqi=nlx5jmBMKbRxzieLIBDLylLdHd
GI-010 | 8e49efed-c66d-4daf-b3c0-c146075fde21 | PA14-1 | 553 | N-EMEA | Closed | P2 Medium CX | simonm@straightlineconsulting.co.uk | 2026-03-26 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  |  | system | CWTR |  |  |  | Installation in progress without approved test packs/QA process in place. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616658&prj=553&rqi=9s0VoWa9jiEqAAIxe1sG7N05QY | https://equinix.facilitygrid.co.uk/x/project/553/system/12491
GI-008 | 74118d5b-8a79-4186-9f61-1fa5934fe63e | PA14-1 | 553 | N-EMEA | Open | P3 Low CX | simonm@straightlineconsulting.co.uk | 2026-02-25 04:00:00.000 +0400 | Project Manager |  | Design not as specified | Design | [7 empty] | Mechanical - Technical Submittal of TW240. The approved tech sub has a statement on page 13 stating that the CHW return temperature must be reduced to from 28Deg C to 27.4Deg C, achieved by increasing the flow through the balancing valves. And on page 15 the return air temperature to be increased from 37Deg C to 37.5Deg C This means that all the assets withing the CHW system will need to have recalculated specification to accommodate this, but there doesn't seem to be addressed anywhere. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221135&prj=553&rqi=DEyBkfr6kTClNLi2BJBaObpMAJ
GI-002 | 5a829f94-d452-47a1-9e83-828217ca589c | PA14-1 | 553 | N-EMEA | Open | P3 Low CX | steved@straightlineconsulting.co.uk | 2026-01-19 04:00:00.000 +0400 | SCH - Schneider MV |  | Documentation not issued/ Required | Commissioning | [7 empty] | Electrical - Issue found during FWT of PUSP Panel :- â€¢ Schneider: To update the nameplate of each cubicle according to SPIE instructions and Equipment naming to be added to each panel like : 1PUSP_1 / 1PUSP_2 â€¢ Schneider: To add the cell serial number to the PUSP schematics to avoid errors during assembly â€¢ Schneider: Key number: R1T to be differentiated between the 2 stations according to SPIE's instructions (R1T_1 / R1T_2) â€¢ Schneider must provide the connection recommendations (Cable heads, etc.) â€¢ Schneider: Place a warning label on the emergency stop button of each PUSP panel. â€¢ Schneider: To update the schematics by taking into account the various issues raised. â€¢ Schneider: must submit to SPIE a control/monitoring cable schedule (eg. P643 cabinetâ€¦) following the same method implemented by Schneider MCE. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197156&prj=553&rqi=yqtJbjCC3tC0SgWoDQUUQoAAkO
BT1MECH-1-006 | 9030a48f-d79d-4f27-b247-28bc3139e388 | PA3-DH7 Liquid Cooling | 676 | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-30 04:00:00.000 +0400 | Equinix Project Manager | L4 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | EPIVE 07,02,06 - Glycol Concentration 60% compared to other valves at 24% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616876&prj=676&rqi=dIq8dfBuJ6Pu4AEckuBIJywdWT | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
BT1MECH-1-005 | e087bc3c-a7b1-45f2-9544-4c092dcc75a4 | PA3-DH7 Liquid Cooling | 676 | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-29 04:00:00.000 +0400 | Equinix Project Manager | L4 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | CDU status not changing to 'Tank filling' during pump fill process. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616804&prj=676&rqi=8WXLBfyUZ6SG3uGi6RpJ8i8JsQ | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
BT1MECH-1-004 | d0dbee97-c66c-5a03-97b4-b6754ae985dc | PA3-DH7 Liquid Cooling | 676 | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-27 04:00:00.000 +0400 | Equinix Project Manager | L4 | Labelling | Commissioning |  | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | All valves to be labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616705&prj=676&rqi=EU2bu1ljBeyFa30j8v6hzvLUdj | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
BT1MECH-1-002 | 35ec537a-06e4-cb00-2a66-0a886337ebb0 | PA3-DH7 Liquid Cooling | 676 | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-27 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | CDU-01 HMI not responding to some setpoint changes. Changes are reverting back to original settings after a few seconds. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616661&prj=676&rqi=UUqmzVXXET9O7kU4NwweJE2XcQ | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
BT1MECH-1-003 | 97df6b19-fdb9-5d2b-1f09-2e7901a6117b | PA3-DH7 Liquid Cooling | 676 | N-EMEA | Open | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-27 04:00:00.000 +0400 | Equinix Project Manager | L4 | Installation not correct | Commissioning |  | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | PTFE tape and brass/galvanised steel connections used on temporary connections to Manifold. All materials used must comply with wetted materials list and a suitable anaerobic sealant used instead of PTFE tape. PTFE tape can disintegrate and contaminate TCS/SFN causing blockages to filters and equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616663&prj=676&rqi=idTwGgjmWz4IKeLYNYZeupN7ks | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
BT1MECH-1-001 | 73da2fda-f51c-2e97-84e7-4545c7a851c7 | PA3-DH7 Liquid Cooling | 676 | N-EMEA | Closed | P3 Low CX | chrish@straightlineconsulting.co.uk | 2026-03-27 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Installation not correct | Commissioning |  | Mechanical â€“ Water | system | Liquid Cooling Heat Load Test |  |  |  | All CDU airvents installed with PTFE tape, some o-rings appear damaged/mishapen and some airvent caps are missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616660&prj=676&rqi=Ib1lM72mFW2nnrtzwQhEW4wxzX | https://equinix.facilitygrid.co.uk/x/project/676/system/13954
GI-026 | f52a7667-9158-4834-a085-25fd2d7046c8 | RJ03-2 | 651 | AMER | Open | P3 Low CX | jesse.oliveira@b2dc.com | 2026-09-18 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning | [7 empty] | The equipment's project tag was not identified | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638756&prj=651&rqi=2xPWGD0mAIJIeBryUTCdWcLBqs
GI-024 | 5947791a-53f1-45fc-8f42-6ee73b671e40 | RJ03-2 | 651 | AMER | Open | P3 Low CX | jesse.oliveira@b2dc.com | 2026-09-15 04:00:00.000 +0400 | Subcontractor |  | Installation not complete | Commissioning | [7 empty] | missing the support for the hydraulic line | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638234&prj=651&rqi=SE4ryTianbRLt7q13odCqikdV7
GI-025 | d293e59b-5c91-4074-ad11-6b0d04eee5a4 | RJ03-2 | 651 | AMER | Open | P3 Low CX | jesse.oliveira@b2dc.com | 2026-09-15 04:00:00.000 +0400 | Subcontractor |  | Installation not complete | Commissioning | [7 empty] | missing teamwork | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638235&prj=651&rqi=MNdkAaYzTpbbSdgEqJnWBbwaoi
GI-023 | 28d6da24-6d8a-4347-bac6-8290818ed6ea | RJ03-2 | 651 | AMER | Open | P3 Low CX | jesse.oliveira@b2dc.com | 2026-09-15 04:00:00.000 +0400 | Subcontractor |  | Missing Components | Commissioning | [7 empty] | Conduit box without cover | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638233&prj=651&rqi=YgeGPPVCY5cpdnv9tE3Of8L0a2
GI-022 | b1568d90-325f-4d9a-b072-58349b4102dc | RJ03-2 | 651 | AMER | Open | P3 Low CX | jesse.oliveira@b2dc.com | 2026-09-10 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning | [7 empty] | The arc flash sticker was not found on the equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637624&prj=651&rqi=dCBSIXwVRySNxpH5ZUsD5DsU7N
GI-017 | 44554309-cdd8-41a0-ae24-020c88284dbd | RJ03-2 | 651 | AMER | Open | P2 Medium CX | mt.uchoa.eng@gmail.com | 2026-08-22 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Vesdas VEU-15 and VEU-16 installed in previous Phase 1: Existing pipes have not been removed. New pipes in circulation have not been installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634808&prj=651&rqi=jTJ1CuDXssZZ30XjFCtzZzcJlv
GI-018 | 9a9a90ff-0887-450b-8451-7037fa44b1e1 | RJ03-2 | 651 | AMER | Open | P2 Medium CX | mt.uchoa.eng@gmail.com | 2026-08-22 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | VESDAs - Asbuilted and approved ASPIRE hydraulic calculation and isometrics not delivered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634809&prj=651&rqi=pmkrkllRrSlZoW2Ij3NjoSlsG5
GI-015 | aba179bb-c0e9-4c79-b6d4-d2578f66da87 | RJ03-2 | 651 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-22 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | Drawings are out of date within panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634805&prj=651&rqi=4D2zEKpteV1RH2iAlX8S8ziZJw
GI-016 | b9487618-d6a7-42bb-afe0-6beab66d9c5f | RJ03-2 | 651 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-22 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | Drawings are out of date within panels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634807&prj=651&rqi=ynVdV3JsoUgQaaTKhQVY5izX5F
GI-007 | 32aefb94-7460-4fe0-a710-6f6f1cfa4c2a | RJ03-2 | 651 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-20 04:00:00.000 +0400 | General Contractor |  | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | There are some loose clamps in sampling pipes - VES-03; VES-014; VEU-07; VEU-08; VEU-09; VEU-17 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634534&prj=651&rqi=ScDExoyGssKaTfDOLNrHCuWW9Q
GI-008 | d86b261b-6589-4633-bc61-08616b458a76 | RJ03-2 | 651 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-20 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | VESDAs - L2A GC checklist signed-off not presented. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634535&prj=651&rqi=q6vnmJa2dpJMUBDGX6ZUe7jJ8w
GI-012 | 10abeb2f-1648-420b-bc51-0d3ca61e33d0 | RJ03-2 | 651 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-20 04:00:00.000 +0400 | General Contractor |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | VESDAS Model VES - Quick connect benchmark fiiting specified in design are not installed in endpoints. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634541&prj=651&rqi=2GRrKA2BOdQyLDl7PZQ0TGDaw8
GI-013 | 74b0aac0-12a3-45c3-9a0e-7a317bd91ddf | RJ03-2 | 651 | AMER | Closed | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-20 04:00:00.000 +0400 | General Contractor |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | VESDAs - Quick connect benchmark fittings specified in design are not installed in testpoints. -- Issue closed (repeated) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634542&prj=651&rqi=AYcpTIhP59QaiT8iCOWTPUh5p5
GI-006 | 2784ce37-2d29-440f-8db4-5f9b31e77456 | RJ03-2 | 651 | AMER | Open | P3 Low CX | mt.uchoa.eng@gmail.com | 2026-08-20 04:00:00.000 +0400 | General Contractor |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | VESDAs - Batteries not installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634527&prj=651&rqi=RSROleh8C1lnJkefI1saOboso4
GI-004 | f54b0fad-b064-4c79-8f9e-890c7d662771 | RJ03-2 | 651 | AMER | Ready for Verification | P3 Low CX | Julio@b2dc.com | 2026-08-15 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [7 empty] | The LOTO procedure complete with organogram structure are not available on Sharepoint The LOTO procedure posted on SharePoint does not mention the equipment in Blocks B and C or how to lock them out | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633851&prj=651&rqi=NNMHtu8NL3tWXJzGlta8BY17hF
YT1ELEC-163-001 | 5c713b5c-f225-49e0-9f45-1ad0a210077e | RJ03-2 | 651 | AMER | Closed | P2 Medium CX | Julio@b2dc.com | 2026-07-30 04:00:00.000 +0400 | General Contractor | L2B | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment type | TX - 480v-208/120 Transformer | TX - 480v-208/120 Transformer |  |  | The L2B documentation is not available on SharePoint for analysis and inspection of the equipment | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631615&prj=651&rqi=TqU2CTIAeGMvX0fVb4NXnLhzeo
GI-002 | 89f0b796-7d10-4753-bad8-8ffe42a18d7b | RJ03-2 | 651 | AMER | Open | P3 Low CX | cassiano.ferreira@b2dc.com | 2026-07-24 04:00:00.000 +0400 | SCH - Schneider Electric |  | Documentation not issued/ Required | Commissioning | [7 empty] | An analysis of the available documentation was conducted, and it was found that the documents listed below were missing, MSB, UDP e RMU-BTU. The torque wrench calibration certificate was not found on Asite The approved technical documentation (description) was not found on the Project Portal MCE was unable to find the electrical panel installation and operation manual on the Project Portal | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630749&prj=651&rqi=i37Qo1Cvh9VVyjhpQVXA0urKgw
GI-001 | c5809c8a-76ca-4ff0-906d-69484ea9a791 | RJ03-2 | 651 | AMER | Ready for Verification | P3 Low CX | bruno@b2dc.com | 2026-05-22 04:00:00.000 +0400 | VER - Vertiv |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | Actual Submittal evaluated from projects ""PW161 (AAN).pdf"" to CRAH Vertiv equipment requires additional specification described below: 1) Specification of the CRAH outlet air deflectors. This issue requires the aprooval from design for the specification of the air deflectors to be closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622830&prj=651&rqi=BydYlmnxWmmfcvH3yNQz62JXbb
L2L3 Sun-238-001 | e95a9115-0e5d-4951-8206-89a06d271afd | SG03-P4 | 615 | APAC | Open | P2 Medium CX | MarcusGoh@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | UPS-R-CPR2-5 | CPR2 - UPS |  |  | HMI OS and APP version for UPS-R-CPR2-5 differs from the approved setting list. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636549&prj=615&rqi=Dca97ZIlySM91DnAAvYJy3nHIs
GI-042 | 54b1879f-3ae5-4e62-a8d5-f581258534e1 | SG03-P4 | 615 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-31 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Electrical | equipment | DB MP-R-CPR2-02 | CPR2 - Mech DB |  |  | [Power Meter Test with PQMS]: During the test, the power factor readings for power meters F01 and F02 were displayed incorrectly on PQMS. In addition, the THD-V and THD-I readings for F02 were also not displayed correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636080&prj=615&rqi=EStb0RdqTw1vFGz1b9BLd5IiM3
GI-035 | 78f784de-e606-472c-8c3f-de2b58d6ba89 | SG03-P4 | 615 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | The UPS has separate Overload and Output Overload alarms. When the Output Overload alarm was triggered, the corresponding Output Overload alarm was correctly received by the BMS. However, when the Overload alarm was triggered, the BMS continued to display Output Overload instead of the corresponding Overload alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633597&prj=615&rqi=DLmecP184GBxcDk1zVdm9WGcBg
GI-037 | 3d2a5e97-8d46-4eea-80f0-5659e0edf87d | SG03-P4 | 615 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | Redundant alarm notifications were observed in the BMS alarm log. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633599&prj=615&rqi=iBBQeuzWMXb5yZAiUtyOI9gGS7
GI-038 | ff08fa66-2d95-4f42-a1c7-36a19f8b54f5 | SG03-P4 | 615 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | During the battery discharge test, the BMS received a Low Battery alarm; however, the corresponding Low Battery alarm was not displayed on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633600&prj=615&rqi=Aq9NhWQMyhdC0sRd14uUO7ChcY
GI-036 | 2999a0ec-415d-4253-80ef-53cfad5005c0 | SG03-P4 | 615 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | Battery remaining runtime was not displayed on the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633598&prj=615&rqi=0b2xkpxjb20XmeX8yWdmL4sit7
GI-034 | e0ce462b-ef0b-4011-bbd8-e11495e57d19 | SG03-P4 | 615 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | Upon simulating high-level communication loss by disconnecting the CAT6 communication cable, no SMS notification was generated to AlertOps. As a result, Operations may not be aware of the communication loss. However, the BMS interface at the respective UPS displayed â€œ?â€ indicators against the affected AI points, indicating the loss of communication. BMS vendor to configure SMS notification as an alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633592&prj=615&rqi=gJtM1gsXfUyl8isevVSUZiMNuP
GI-041 | 74dfd292-9a4a-442c-97fc-b00b6941afa4 | SG03-P4 | 615 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | No approved UPS setting list was available at the time of testing. Testing was initially conducted based on the UPS settings proposed by Eaton. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633603&prj=615&rqi=DiuRXEv22wdt4vuI82I0jXcr36
GI-040 | 6773a634-c982-4759-93d9-f0d789c8aa61 | SG03-P4 | 615 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | SMS notification to AlertOps was not ready for testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633602&prj=615&rqi=gd0mOjNsyUWOuJOta1Jbhn8YsA
GI-039 | 78ae4fa0-1f76-4023-94c3-06c57a7d954e | SG03-P4 | 615 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | UPS-R-CPR2-7 | CPR2 - UPS |  |  | During Overload Stage 1 (110%â€“125% load), the inverter transferred to Static Bypass after 7 minutes 40 seconds instead of the required 10 minutes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633601&prj=615&rqi=vEXC809qqnQ5kiuxWHvqAFYAFj
GI-032 | 06a01e9e-115c-4659-a923-343d7a2a1138 | SG03-P4 | 615 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | [CHSB Breaker Modification Works]: The BMS team shall update the GUI (SLD) in accordance with the approved naming convention and SLD. It was observed that CHSB CPR2 still shows an outgoing feeder to CP-CHWP. Therefore, the team shall ensure that the BMS SLD is updated prior to conducting the CHSB breaker modification works. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630921&prj=615&rqi=OjOPQGOyrly2waZTZivohYYuj3
GI-033 | 2368eff4-6899-4e51-9fb7-a320248d7d01 | SG03-P4 | 615 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-07-27 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | PLC-R-CPR2-01 | CPR2 - BMS |  |  | Revealed during Cx3 FCU with BMS: It was observed that the BMS graphics only display the FCU tag/name without indicating the corresponding room layout or the specific room served by each FCU. As the approved GUI was not available during the inspection, the BMS team shall update the graphics to include the room location served by each FCU. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630924&prj=615&rqi=oDM41rTdct8NFxnve6J78xQGge
GI-030 | 897d55b5-2a3f-42a6-9979-cf4352fb35c2 | SG03-P4 | 615 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Electrical | equipment | CP-FCU-R-CPR2-04 | CPR2 - FCU CP |  |  | There was no approved setting for overload thermal relay for both MV fans and FCU visible during inspection. WL to confirm with design consultant/LEW. This issue applicable to all 12 nos of FCU and 12 nos of MV Fan at CPR2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624675&prj=615&rqi=M4qgIScX9jufMDAOTy6yHabANS
GI-029 | cc166e6f-7fcf-4644-90a0-17f054429e95 | SG03-P4 | 615 | APAC | Closed | P3 Low CX | harizdaniel@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | PLC-R-CPR2-01 | CPR2 - BMS |  |  | Few issues revealed during Cx2A for PLC panel: 1) Vendor to provide and submit the SLD/control diagram drawing for design consultant's approval. This drawing was not visible during inspection. 2) To update GA drawing as per built on-site. 3) There were two different MCB type installed for both PLC panels. One panel was equipped with Type B 6A while another one was equipped with Type C 6A MCB. To confirm with design consultant. 4) To install earth bonding between panel door and panel 5) To put component's sticker labelling for clarity | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623900&prj=615&rqi=5jUSzGUMi5P1NZYviKtxo5ep2G
FPT-16-002 | 1626095a-f3d1-4c61-a1f7-25b9dce7f418 | SG04-4A | 663 | APAC | Closed | P2 Medium CX | MarcusGoh@commtechasia.com | 2026-08-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | After the CRAC unit restarted following a power failure, the EBIV failed to open to Vmax as specified in the SoO. Instead, the valve returned to 0% open and resumed modulating based on the Supply Air Temperature (SAT) control logic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632816&prj=663&rqi=i1WGia29h5ohCKg9CwnIlKvsBG
FPT-49-001 | 9391393d-85ab-4887-8ad0-e74aaf52c1d7 | SG04-4A | 663 | APAC | Closed | P2 Medium CX | MarcusGoh@commtechasia.com | 2026-08-09 04:00:00.000 +0400 | General Contractor | L4 | Installation not correct | Commissioning |  | Multi-Discipline | system | Heat Load Test (DH 5-2) |  |  |  | DH5-2 cold aisle temperature increased to 26.8Â°C at RLE Sensors 11 and 18 when the CHW ring valves between CRAC Units 9 and 10 were closed. It was also observed that one of the CHW ring valves between CRAC Units 8 and 9 was not fully opened. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632815&prj=663&rqi=SJrEImpsQci19AiPrmQ1GqsjX1 | https://equinix.facilitygrid.co.uk/x/project/663/system/14481
GI-048 | 0bccb82a-726c-4d8c-9079-3a763f1f6950 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | 1. There are questions mark on top of all the faceplate in granular control overview page.Granular control 2. PLC connection status on graphic not ready, to be configured. 3. Existing Prosoft Gateway for RLE manger keeps showing alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629920&prj=663&rqi=tw9fMErvAU4ekmSO37fU8R2J0S
GI-049 | 552828cb-abc8-4f54-bd85-9efcd46dc467 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-19 04:00:00.000 +0400 | General Contractor |  | Component/ Equipment Failure | Commissioning | [7 empty] | RLE-24 temperature and humidity readings different with other sensors. The sensor was unable to recover back after RLE Wing Manager power failure test. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629921&prj=663&rqi=jmnfuiqpwww3QMnMpB9W7z1Qn4
GI-050 | 3198eddf-2e84-41fb-ac98-3d2d7c1f0aad | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | CRAC did not fall back to local unit SAT setpoint when signal from Granular Control is lost. CRAC will be running based on last SAT setpoint commanded by Granular System. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629922&prj=663&rqi=JjTXicsYMjhgU2h8YUeSdtNs56
GI-047 | 27b5f309-90db-47ba-b240-c327c36a628f | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Comms Issue/ Fault | DCOS |  |  | equipment type |  |  |  |  | When CU loss of power and communication loss with DCOS, there is no loss comm alarm at DCOS. Parameters loss comm but communication alarm still show inactive. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628312&prj=663&rqi=yjjtzhb48TwkudHUJFpGW5f0W3
GI-045 | 2afc28c9-4049-46ca-b85a-e28ca50d7676 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | DCOS summary and face plate naming need to be changed from 5_BATTR_A_1_PREACT to 1-GSCP BATTR 5A and 1-GSCP BATTR 5B. Applicable for all gas suppression panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628310&prj=663&rqi=K0HyokeU85uOM9uo3UkQj7FCrF
GI-046 | 2a45fb5c-868b-427b-8e6b-75a757f10f15 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-07 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | Fire Mimic panel needs to reflect the latest battery room layout 5A and 5B. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628311&prj=663&rqi=gXZmi1ejgfj2vrTQelDoCTyOYO
GI-044 | 6a066533-fcc3-40f9-9455-76f883d69be2 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-07-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | To provide LEW endorsed drawing and place inside the LCP. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628136&prj=663&rqi=QsFI8uYXjmfBzIP9GYfjDrbPf5
GI-042 | 693e3925-68c7-4fd1-bc14-7b8233a7d53f | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | 1. Rockwell is required to check whether the RLE sensor will still be included in the calculation when it is placed in maintenance mode. 2. Rockwell is required to check the meaning of the triangle with a question mark symbol shown on the RLE sensor graphic. 3. Two parameters are missing from the Machine Learning faceplate. Rockwell is required to add these parameters. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627195&prj=663&rqi=TgIOJJClm3pMpLmisTO8wQvNMZ
GI-038 | 8bd0240e-14ec-4f74-9d0e-b31d4de24f10 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | 1. The layout of the ProSoft and FiberTek communication gateways differs from the drawing. 2. The labeling of the ProSoft gateway does not match the drawing. 3. The quantity of the TB-24V1 fuses does not tally with the drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627098&prj=663&rqi=eWHcXd33LVTGDIwkR2GTjB8zka
GI-035 | 9057ccc9-a575-4c43-bc15-33642487c74c | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | There is no labeling for smoke detector signal cables inside the unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626875&prj=663&rqi=PgG6KVDim1oKUDjkV76lZqrJg2
GI-031 | 00b60cd2-cdeb-4231-a7eb-9de3c855f968 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-21 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | 1. The installed manual release and abort switch for GSS are different with approved layout. 2. The installed Pre-action pipe and sprinkler head quantity/location are different with approved layout. 3. Location of pre-action sprinkler pipe drain point are different with approved layout. 4. The location of fireman intercom panel is different with approved layout. 5. There is no drawing placed inside the GSS panel. 6. The height of GSS panel installed is different with approved drawing. 7. There is no breathing apparatus installed outside the battery room. 8. There is no zone chart installed. 9. The painting of trunking and conduit need to touch up. 10. There is no zone chart installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626329&prj=663&rqi=m8JGKef84kMB59AdvIgBorHlCH
GI-032 | f83d7eac-38d2-44aa-b6ea-74b0d68e87f0 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-21 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | 1. External fire modules are not labeled. 2. There is no labeling of all the cables inside the GSS panel. 3. There is no labeling of all pipes, conduit and trunking. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626330&prj=663&rqi=kZUBAO7fRxSaASNZSt7iD335Tf
GI-028 | 961e9e23-ca27-4c55-9b8c-92fe14a22a6a | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-21 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | 1. Table of primary and secondary source need to be updated in LCP SLD as per site installation. 2. Battery room 5A equipment layout is different with the drawing. 3. The rating of fuse for LCP cooling fan is not tally with SLD, update in SLD is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626313&prj=663&rqi=gKYcz66Xf6I1tgZVnAbERTAcYu
GI-029 | eab5ce99-f34d-4993-9674-cdb594662145 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-21 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | 1. The name of LCP need to reflect actual room name "5A" and "5B". 2. MCB for damper, control and 230V XFMR inside the LCP are not labeled. 3. Fuse for cooling fan and power sensing "NSF", "ESF" are not labeled. 4. To provide labeling for incoming power cables. 5. Labeling of LCP trunking and conduit are inadequate and some are not labeled. 6. The fan isolators, hydrogen and methane sensor are not labeled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626314&prj=663&rqi=dfcl30EiHV8Wubhzz9wWeqyyGD
GI-023 | f95d5158-77bd-4be7-80aa-d9ddd5402708 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | 1. There is no equipment labeling for condenser unit. 2. There is no circuit labeling for power isolator. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625562&prj=663&rqi=qfAxqJytkcUykzTKrAUfqei3Qg
GI-024 | 8382306f-e565-487a-8ce7-fae9c151f955 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-06-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | 1. The gradient of condensate drain pipe has been lift up by power conduit, to rectify. 2. The condensate drain pipe armaflex insulation is incomplete and not properly sealed. 3. There is no equipment labeling on DxFCU and its thermostat. 4. There is no labeling on condensate drain pipe and trunking. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625566&prj=663&rqi=HslBHrqBcRXQIdBPTULyCsm5iP
GI-022 | 8db2b960-070e-48bf-a4fe-9311372f04ab | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-05-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | 1. All the labeling of outgoing cables terminal blocks are not tally with the circuit number. 2. The labeling of relay is not tally with the outgoing circuit. Refer to the photo attached. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621850&prj=663&rqi=UphvqaQlKDIPFa02d936CoOV7Q
DCOS-1-002 | 10265f87-2e8a-43bf-8d0b-0c82b6cafd61 | SG04-4A | 663 | APAC | Closed | P2 Medium DCOS | MarcusGoh@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L1 | DCOS Template Issue | DCOS | [7 empty] | ERCS/QA required to raise RFI regarding the alarm severity that is not stated in SPL â€‚â€‚â€‚ UPS: - Blower fan failure 850 - Emergency power off 850 CRAC: - Loss of air flow 450 - Loss of power 650 - Supply air RH high / low 650 - Return air RH high / low 650 - Return air temp high / low 650 - SAT sensor failure 650 - RAT sensor failure 650 - RH sensor failure 650 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621310&prj=663&rqi=UzsESppq5YoEGwGXR1rjBbkASr
DCOS-1-001 | cd29bc96-8e08-42bf-a8c1-72ce039a2276 | SG04-4A | 663 | APAC | Closed | P2 Medium DCOS | MarcusGoh@commtechasia.com | 2026-05-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L1 | DCOS Graphics Issue | DCOS | [7 empty] | DCOS SFAT Issues and Observations: 1. UPS "load on bypass" and "low battery alarm" alarm severity to change from critical 950 to urgent 850 as per SPL 1.0. 2. The summary page of UPS did not show any alarm when the alarm was triggered. 3. Static text for UPS tagging needs to be corrected and the text â€œtemplateâ€ shall be removed. 4. UPS high limit and low limit alarm thresholds shall be user-editable. 5. All equipment Maximo IDs have already been provided by ERCS. DCOS is required to deploy and update the IDs in the graphics. 6. ERCS is required to request the location vector from EQIX and provide it to DCOS for updating. 7. Equipment naming in DCOS shall follow the UIUX naming format. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621309&prj=663&rqi=dBE1AV63x3NuKxNfuHZIRHtOH3
GI-017 | 6e3accc3-fd69-42ac-b855-d8078fdc2201 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-05-07 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | Kindly provide sticker labeling for the breaker settings, in accordance with the approved discrimination study, for all new SUDP and PDU. Including Arc Flash sticker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620702&prj=663&rqi=E7tAsXRtWg8rMzBG59X30YTnuo
GI-014 | e79f9cbe-eb67-4422-90f9-8405fee8c563 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | To provide drawing pocket and attach LEW endorsed drawings for SUDP and PDU. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619994&prj=663&rqi=9vXBcyC1XgCCMmxpbmou4Fhtpp
GI-015 | 6f916f47-47a1-4bab-a834-f6038064516f | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | 1. Missing cable labeling for CAT6 cables as per photo attached. 2. To provide drawing pocket and attach LEW endorsed drawings for SUDP. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619995&prj=663&rqi=8T9XtYph9gx8RgQV9fO4v5rRMA
GI-013 | b3468e05-5402-4c3b-992b-8b0ef741dff7 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | When the unit stops due to loss of air flow, there is no loss of air flow alarm showing at the unit HMI. The unit only shows fan failure alarm, Stulz to check and clarify. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619992&prj=663&rqi=CJr7FZq8OZ4kLGAbRV5Ql9EMpu
GI-009 | 6e662d7e-b28c-4116-a9e8-9a1118905da1 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | To provide labelling for signal cables at E2 controller terminals J14. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619397&prj=663&rqi=bi2j0jaqFEbguZrzBPlV7QnkIc
GI-008 | c821e00a-217f-4af6-928e-40a87321297e | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | To standardize the SAT sensors under the raised floor to face toward the CRAC units, except where obstructed by other services. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617417&prj=663&rqi=xYFfQivfww0PX4vlAKKXQWZKID
GI-002 | 0c4c1847-0a51-4ff2-b388-d6eaa4814e8d | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Torque required | Commissioning |  |  | equipment type |  |  |  |  | To provide torque markings on all earth cable terminations. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617411&prj=663&rqi=3ge4F5Iq7UBn4dBaVw4YXUsOnd
GI-006 | b56d6018-1191-4a10-908f-25a7d52fe1df | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | The Armaflex insulation for CHW pipes inside the units is not properly wrapped and has come loose, to rectify accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617415&prj=663&rqi=LNM74xjgd3QiUn8nGK5Emko45w
GI-005 | 43453877-c25c-450e-b0ed-1f9dd821c2b1 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | To cap off the cooling coil drain point. Applicable to all CRAC units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617414&prj=663&rqi=4vIbCDZWODYtXmDyQdlqCa0bHM
GI-004 | dd5822a7-3d50-4445-935d-026dd6353bf6 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | 1. The fuse F02 rating of "6A" does not tally with the approved drawing, which specifies "4A". To update the drawing. 2. The overload contactor F31 range of "26Aâ€“32A" does not tally with the approved drawing, which specifies "2.5Aâ€“32A". To update the drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617413&prj=663&rqi=9ZT2iDGI7RiioMz6iDptSnOeBV
GI-007 | b01dedcd-ce89-4d1f-a08c-23b7785e1168 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | Condensate drain pipes after passing through the units are not properly secured, to secure accordingly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617416&prj=663&rqi=zkt0LhLPNrI0V9nn7EWInkN5VX
GI-003 | 3ddc218e-1474-473c-b929-8a004ee69ae0 | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | To provide labelling for signal cables at E2 controller terminals J10 and J4. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617412&prj=663&rqi=2RAz6R0v8tTgZjIskCj16qjqk8
GI-001 | a9dcb3e5-b9b6-413e-8428-c7ed9deebffc | SG04-4A | 663 | APAC | Closed | P3 Low CX | MarcusGoh@commtechasia.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | All the CAT 6 cables connecting between Adapter Board and MCMS Port are not labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617001&prj=663&rqi=c2WOhAvm0H3xpSIFqHrZj2UxN5
GT1SEC-2-005 | 768d9cf4-7ce1-4b1a-9241-06e9c50144f0 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-11-09 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not complete | Commissioning |  | Security | system | Security - CCTV System |  |  |  | Cx3: Level 5 : D137 no BG D153 no KCU D147 cannot test door cannot close D152 cannot test door cannot close D148 cannot test door cannot close | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637847&prj=618&rqi=bEzazUudJZOFDuBd9OWwLQuP4N | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GT1SEC-1-003 | 73c81012-f400-4f19-9957-d05fb97ce253 | SG06-1 | 618 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-09-16 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Commissioning Issue | Commissioning |  | Security | system | Security - Card Access System |  |  |  | L8 CX Issues - D224 DC always open - D222 DC always open | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638425&prj=618&rqi=uvd0w0Han8QsFpSyk6PvDsz3WJ | https://equinix.facilitygrid.co.uk/x/project/618/system/14513
GT1DCOS-13-001 | 3ae44e1c-e1b2-49bd-9d39-7e9272346573 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-09-16 04:00:00.000 +0400 | General Contractor - BMS | L3 | General Design Issue | Design |  | Controls | equipment | 1CPOS_RIO_01 | DCOS - Control Panels |  |  | It was observed that the Power Supply Common Alarm refers to the PSU failure alarm. During the simulation of Primary Source and Secondary Source failures individually, no alarm was triggered to provide notification. (Apply to all CPOS Panels) Based on the control wiring, the two sources are combined to supply the two PSUs. Therefore, a failure of only Source 1 or Source 2 will not trigger the PSU failure alarm. The PSU alarm will only be triggered when both the primary and secondary sources fail, resulting in a loss of supply to the PSUs. Kindly clarify with the EoR to confirm the design intent and verify whether the current alarm logic is in accordance with the approved design. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638239&prj=618&rqi=EygAsmeEFvZrlzzs59SWw1NjAY
GT1SEC-1-002 | 8155d8ed-1f96-492d-a72c-b574d414f680 | SG06-1 | 618 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-09-15 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Commissioning Issue | Commissioning |  | Security | system | Security - Card Access System |  |  |  | L7 CX - D197 DC always open - D211 DC always close - D212 EL no power - D210 no BG - D208 DC always open | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638424&prj=618&rqi=QJztzkWAQPqPYFSvqTy1hT7KhU | https://equinix.facilitygrid.co.uk/x/project/618/system/14513
RT1ELEC-552-001 | cbdcb41d-e39d-4de6-92b6-5d9ec5520e7d | SG06-1 | 618 | APAC | Open | P3 Low CX | KeeLeongLee@commtechasia.com | 2026-09-14 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Labelling | Commissioning |  | Electrical â€“ LV | system | IT Busduct System |  |  |  | For Level 8 IT busduct, please rectify the following: 1. To replace label for J-21,56,67, 2. To ensure the joint label is installed properly for J-043 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637901&prj=618&rqi=Rqp6JXqigqsHEhlO2UdBvuszwk | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GT1SEC-2-006 | 9de21375-fc25-4e88-b737-777e7622fb84 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-09-14 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not complete | Commissioning |  | Security | system | Security - CCTV System |  |  |  | L6 CX3 Issues - D172 DC always close - D173 EL Issue - D169 no BG - D714 EL Issue - DR181 no BG - D184 DC always close - D184 no BG - D180 DC always close | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637903&prj=618&rqi=tRRwpfH0lrYuGUsqIvGzUZFWdL | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GT1SEC-2-004 | e74e71d5-e600-461c-aede-5cce45d2db2a | SG06-1 | 618 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-09-10 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not correct | Commissioning |  | Security | system | Security - CCTV System |  |  |  | Cx3: Level 4 Issues D108 No REX MC1 No Siren D119 No REX D121 DC always open MC3 No Siren | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637587&prj=618&rqi=lykB4VxsJQtyT3fkU3ser521qf | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GT1SEC-2-002 | 1dfe1c90-65d9-47a9-98a5-5b24c6202cbd | SG06-1 | 618 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not correct | Commissioning |  | Security | system | Security - CCTV System |  |  |  | Cx3: CCTV CX3 : Cam 153 : View is partially obstructed by the exit light | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637399&prj=618&rqi=Ht73BvxSGnk4TFCJbQAzmsRkWm | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GT1SEC-1-001 | 3f6a100e-b421-4658-ba64-575e55d316c1 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not complete | Commissioning |  | Security | system | Security - CCTV System |  |  |  | L3 CX Issues - D85 DC always closed - D81 DC always open - D94 DC always closed - D96 open without scanning card | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637450&prj=618&rqi=lhssmkNJrGx49wgExXOrr7u9gu | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GT1SEC-2-003 | e6b02481-693f-4eb8-888f-e871729f7c00 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-09-09 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not correct | Commissioning |  | Security | system | Security - CCTV System |  |  |  | Cx3: Level 2 to 9: 1.Fire fighting lobby 2A to ext corridoor biometric reader need to shift 2. Level 2 TER Room A door access have issues 3. E wall A door access have issue 4. Door 65 Cool spine 1 has issues Camera: 1. L1 to L9 (Staircase 1 to 4) CCTV is removed as per SCDf comments , thus the view of the respective cameras is blanked out during the CX3 test | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637400&prj=618&rqi=f6Pu9iQ7DdoXTPGleNdknJ6stw | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-500 | cc4ae275-deb8-4bee-a2c6-b9c3b0fc7eb1 | SG06-1 | 618 | APAC | Open | P2 Medium CX | jessyong@commtechasia.com | 2026-09-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General Design Issue | Design |  |  | equipment type |  |  |  |  | Observed incorrect voltage readings and negative kw readings at the ACB micrologic for STSSB. Socomec to rectify for all STSSB. Dcos has feedback when load test with s2, no negative values observed and voltage readings are normal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637058&prj=618&rqi=JaFt03K4n62kVh3qmMo9ipRy8R
GT1SEC-2-001 | a5084461-3580-475e-8fea-9b27ec5f1fc2 | SG06-1 | 618 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-09-02 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L3 | Installation not complete | Commissioning |  | Security | system | Security - CCTV System |  |  |  | Cx3 : L1 to L9 (Staircase 1 to 4) CCTV is removed as per SCDf comments , awaiting waiver from scdf if it would be reinstalled | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636413&prj=618&rqi=NCyPjR5ACPHa7hEyCHEoHxEkYO | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
RT1ELEC-553-001 | a970335f-e198-4eb9-bd38-9500773df7d4 | SG06-1 | 618 | APAC | Open | P3 Low CX | RyanWu@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Component/Equipment Failure | Commissioning |  | Electrical â€“ LV | system | Mechanical Busduct System |  |  |  | To replace torn off tags for: Lvl 2 joint 20 Lvl 5 joint 14 Lvl 8 joint 64 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636226&prj=618&rqi=vVE5ltCU5UthGORC3QDI6NoFiX | https://equinix.facilitygrid.co.uk/x/project/618/system/14864
GT1DCOS-19-007 | 76c47879-11cd-4270-87c7-a1c7f13f4651 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-31 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning |  | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | Observed that CWP 4 starts running before CT 4 FCV-01 valve opens during the stage-up sequence. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636036&prj=618&rqi=0HWXN7rGOmICxkCbucuWvvzgpX
GT1DCOS-16-001 | 3acbc1a5-4756-4a76-927c-a544b7da577f | SG06-1 | 618 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-31 04:00:00.000 +0400 | General Contractor - BMS | L3 | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1CPOS_RIO_04 | DCOS - Control Panels |  |  | Observed that when the operating string fails, the next available string is automatically called to run. However, the failed string is commanded to stop immediately, and the pumps will stop after a 60-second time delay based on the current timer settings. This occurs before the next available string has successfully started and achieved a proven run status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636037&prj=618&rqi=dnyJau2mwlV2VDr1rAj6vA7z0L
GT1DCOS-17-003 | 4b765771-f3f4-46df-81b2-6a6d63957b57 | SG06-1 | 618 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-31 04:00:00.000 +0400 | General Contractor - BMS | L3 | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1CPOS_RIO_05 | DCOS - Control Panels |  |  | Requires fine-tuning of the CHWP PID settings, bypass valve opening, and timer. When both CHWP are running, the system repeatedly triggers a CHW low-flow alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636035&prj=618&rqi=jNnNx3N5D2kSp1YppmgRcQXxrC
GT1DCOS-19-006 | cfa027f9-6876-42d3-af61-e9807119a5c8 | SG06-1 | 618 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-31 04:00:00.000 +0400 | General Contractor - BMS | L3 | General Design Issue | Design |  | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | Observed that only one CT is running to support two CWPs during string rotation. Kindly confirm with the design consultant/EoR the design intent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636034&prj=618&rqi=a4pnaz9fmaFbyZIl9Z7bGHs8oV
RT1ELEC-553-002 | aa4d2399-ca43-4750-a7ce-3974d7bc1f04 | SG06-1 | 618 | APAC | Ready for Verification | P2 Medium CX | RyanWu@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | system | Mechanical Busduct System |  |  |  | To move the unistruts and obstructions away from the joints of the mechanical busducts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635241&prj=618&rqi=wO20ALEqAESiIEjCjjodyYFDFe | https://equinix.facilitygrid.co.uk/x/project/618/system/14864
GT1DCOS-17-002 | a75be695-d6c8-4c25-ac33-5d276a679058 | SG06-1 | 618 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning |  | Controls | equipment | 1CPOS_RIO_05 | DCOS - Control Panels |  |  | Observed that during string rotation, while CH was still in VSD precharge, CPOS considered String 2 as already run and stopped String 4. Kindly check with the JCI chiller team whether the system can take the chiller run status as the run point signal to CPOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635216&prj=618&rqi=al19IxeXXBHqAWiaDigpJTIx90
GT1DCOS-19-005 | 607f71ee-e6d7-410c-abae-c4b959b55904 | SG06-1 | 618 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor - BMS | L3 | General Design Issue | Design |  | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | As per SoO, initial chiller start sequence, one cooling tower will run . Observed that chiller string still able to stage in although after sequentially reset the faulted latching alarms and attempt to start the towers one at a time for three times maximum and "insufficient devices available to run" activated. Kindly confirm with the design consultant/EoR the design intent | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635218&prj=618&rqi=3OJuxhZXhgkASEhsDfjK8zE0wS
RT1ELEC-555-003 | 1e5e7cd9-9ada-44a7-b827-bf232e06cb89 | SG06-1 | 618 | APAC | Ready for Verification | P2 Medium CX | RyanWu@commtechasia.com | 2026-08-26 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | system | IT Busduct System |  |  |  | To move unistruts and other obstructions away from the joints of the IT busducts as shown in the screenshots | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635236&prj=618&rqi=wKDslcnfsoIO5fWoSulaKIrEks | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-462 | 512f3f0c-94ae-449d-9d6f-55f08dc79526 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-08-17 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | To update submittal 6211 lv schematic diagram z swing, to include secondary circuit to 1mdsb_z2 source 2 from 1mdsb_r1_2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633910&prj=618&rqi=HwTTxGgqsNMglNrYDbr4MwXgIM
GI-459 | 0364ffd8-6dc0-4329-ba51-0e38b11937b1 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-08-14 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not correct | Commissioning |  | Electrical â€“ LV | system | IT Busduct System |  |  |  | BUSDT cx2A observation 1.GA dwg to update, sld to upload in FG(incorrect dwg indicating the placement of the components) 2. earth bond to install at panel door 3. to install labels on equipment as per approved maximo list 4. Missing otdr passing critieria in mos and testing wavelength. (vendor mentioned is 850nm and less than 3db/km) 5. To install labels the incoming source to the thermal monitoring panel on the power socket 6. Unable to find patching panel in equipment layout | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633586&prj=618&rqi=HLw4eWPXpsz6NvrZfxrmyVDwIg | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-458 | b31e03fa-baa1-467b-a761-d6af911229a4 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-08-13 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Observed signs of possible water/moisture ingress and including discoloration/rust-like staining within the loadbank enclosure. Engie to investigate the condition of the enclosure seals, joints, cable glands and other potential entry points, and implement the necessary corrective action to prevent recurrence | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633389&prj=618&rqi=dK42HlLW7Q46PAqI9t5mM7RXco
GT1DCOS-23-004 | ae6b6aba-dc1e-4c9c-a8bd-2d44eeb601ae | SG06-1 | 618 | APAC | Closed | P2 Medium CX | hemendrrajeganathan@commtechasia.com | 2026-08-12 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning |  | Controls | equipment | 2CPOS_RIO_04 | DCOS - Control Panels |  |  | Cx3 2CPOS_RIO_04 Temperature readings during sensor verification and current status are out of range. To check the condition of temperature sensors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633145&prj=618&rqi=xbxrgtDCqUgm3A4iWQUuomb214
GT1DCOS-23-002 | cbd89c44-8736-4fa6-ad6e-0cb364adf58b | SG06-1 | 618 | APAC | Open | P3 Low CX | siakhongneogh@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS |  | Controls | equipment | 2CPOS_RIO_04 | DCOS - Control Panels |  |  | Vendor to cross-check and ensure all alarm shall reflect corresponding alarms correctly on the CPOS HMI. Apply to all strings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632972&prj=618&rqi=eW2mW9KszUQbeP9mM7a4Y9qZQc
GT1DCOS-23-001 | ba2f331d-e77a-48ae-b0e5-b46143fb44cc | SG06-1 | 618 | APAC | Open | P3 Low DCOS | siakhongneogh@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS |  | Controls | equipment | 2CPOS_RIO_04 | DCOS - Control Panels |  |  | Vendor to cross-check all alarm names and alarm descriptions to ensure they accurately reflect the corresponding alarms. Apply to all strings. Including Bypass valves and Temperature/DP/ flow sensors in Chiller Plant Room 2 (South), all indicated wrong location in faceplate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632971&prj=618&rqi=AajY4jXAWenKUwcMZu4QAvpUzb
GT1DCOS-23-003 | eaced495-266d-4cb7-a31e-27204d8d3cdb | SG06-1 | 618 | APAC | Open | P3 Low CX | siakhongneogh@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS |  | Controls | equipment | 2CPOS_RIO_04 | DCOS - Control Panels |  |  | Observed that was a command of 30% speed command during DCOS manually override to command run. Vendor to investigate and cross check the logic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632973&prj=618&rqi=2E0hFJItlBdD8N84QReqUsM8sT
GT1DCOS-18-001 | 8d691e78-a4f4-45b4-bff8-e294e53cbd82 | SG06-1 | 618 | APAC | Open | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-08-11 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS |  | Controls | equipment | 1CPOS_RIO_06 | DCOS - Control Panels |  |  | Observed that FCV01 will automatically open when Cooling tower and Valve Control Panel are in Auto mode, while the VFD is manually commanded to run via DCOS. Kindly confirm with the EoR the intended design philosophy and sequence of operation during manual override. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632958&prj=618&rqi=0CasVbzOgFVB9sDbctMfSz3ukf
GT1DCOS-26-001 | 26beccf2-fc5b-44e3-8c1c-0e398adacbe2 | SG06-1 | 618 | APAC | Closed | P3 Low CX | hemendrrajeganathan@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning |  | Controls | equipment | 2CPOS_RIO_05 | DCOS - Control Panels |  |  | Cx3 2CPOS_RIO_05 TT-14 sensor is out of tolerance limit (more than 12 deg difference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632399&prj=618&rqi=6fd4dGCBRffyknrPWUtR1w6TWz
GT1DCOS-17-001 | f38d5dc1-8612-40a4-a10c-9d3a409b1747 | SG06-1 | 618 | APAC | Closed | P3 Low CX | hemendrrajeganathan@commtechasia.com | 2026-08-06 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning |  | Controls | equipment | 1CPOS_RIO_05 | DCOS - Control Panels |  |  | Cx3 1CPOS_RIO_05 TT-17 sensor is out of tolerance limit (more than 12 deg difference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632401&prj=618&rqi=qP8imI1rRdjaZ02sdKpHDyIvQR
GT1DCOS-19-008 | 001c7bdb-83d6-4784-ad84-440f27078f0e | SG06-1 | 618 | APAC | Open | P3 Low CX | jasontan@commtechasia.com | 2026-08-04 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS |  | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | Cx3: Level 9 : Temperature Sensor HMI and DCOS / Sensor While performing the sensor verifications of the temperature sensors , the following below was observed : Sensor 1 reading is out by 1 degrees Celsius Sensor 8 Reading is out by 0.57degrees Celsius Sensor 15 reading is out by 0.5 Degrees Celsius Sensor 14 reading is out by 0.6 Degrees Celsius Sensor 7 reading is out by 3.5 Degrees Celsius The allowed tolerance is +/- 0.5 degrees Celsius Please refer to the table attached to this Issue for your reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632158&prj=618&rqi=JW470jTk7xRxdDfQQS7yjKyPlI
GI-422 | 4596849a-e897-4830-8dba-f80011e8ccc5 | SG06-1 | 618 | APAC | Open | P3 Low CX | jessyong@commtechasia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | To install labels as per approved maximo list and/or sld. Observed at 1RMU_A, Q01 and Q02 installed labels do not align with approved mv sld. ABB to rectify and attach photos of all RMU and BTU showing correct labels installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631119&prj=618&rqi=78azinUBk4FIzAzpSOjzZJsuai
GI-424 | 6cea80eb-212d-4833-86fe-b5f27dc17b70 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | To update ATS settings for 3914 and 3904 voltage imbalance only able to set minimum at 0.02s instead of 0s. To resubmit the revise settings to EOR for review and approval. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631122&prj=618&rqi=thdB3tTz8CoRYTKSB0qKV4KqoF
GI-423 | 20aee5da-20cf-4177-9b68-de8a430f0a12 | SG06-1 | 618 | APAC | Ready for Verification | P2 Medium CX | jessyong@commtechasia.com | 2026-07-29 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | To update mech ATS/socomec settings and SOO and submit to EOR for review and approval, unable to set as per approved settings during cx3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631121&prj=618&rqi=ADlAqjLxKPHPTXxP8tbAFKMT42
GT1DCOS-19-003 | 616ce062-a226-4e50-ba64-3b9e8d2a4222 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | General Contractor - BMS | L3 | Commissioning Issue | Commissioning |  | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | The CHWP and CWP cannot be ramped up or down from the CPOS HMI. To investigate and enable this functionality. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630639&prj=618&rqi=0gQtPzlIdAjKByM8pcBBgQZCCT
GT1DCOS-19-004 | 551496fb-d99c-48d6-bca4-0994b2cb410e | SG06-1 | 618 | APAC | Closed | P3 Low DCOS | siakhongneogh@commtechasia.com | 2026-07-24 04:00:00.000 +0400 | General Contractor - BMS | L3 | Labelling | Commissioning |  | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | On the CH DCOS faceplate, the refrigerant temperature displayed refers to the saturation temperature. To confirm that this is correctly labeled or revise the display if necessary to avoid misinterpretation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630640&prj=618&rqi=Y6ZGjkvIWxumXTgC38hjFnb373
GI-413 | 0267e5f9-2e65-45d6-bef6-5878a7b132d4 | SG06-1 | 618 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: To upload the compile picture file for hard to access joint for level 2 for MECH, IT and LB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630048&prj=618&rqi=OglAuQqkI7SunI8eBTMt28TV4S | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GT1DCOS-19-001 | e8efed54-b62e-4549-8dd4-a3013edfc3b2 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS |  | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | DCOS is unable to execute manual ramp-up and ramp-down commands for the CWP and CHWP because the control is being overridden/ affected by CPOS although HMI in Remote mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630045&prj=618&rqi=fULj3tBXr4HoxKZN1dua70sRd7
GI-414 | 59876f3d-a3ea-46a4-80b3-3942484727d9 | SG06-1 | 618 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: To upload the compile picture file for hard to access joint for level 5 for MECH, IT and LB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630049&prj=618&rqi=MPcmRBfuc9zE4Qo1YSXLKHVPnx | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-416 | acb561b5-1ed9-4f86-8ec5-c972bc712881 | SG06-1 | 618 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: To upload the compile picture file for hard to access joint for level 8 for MECH, IT and LB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630051&prj=618&rqi=ZWTlOj1tymJ4B22NTvqa5oiSz0 | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
RT1SEC-2-005 | a39e422a-b96a-453d-8879-15090bab9a72 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L2A | Installation not correct | Commissioning |  | Security | system | Security - CCTV System |  |  |  | Cx2a: Level 9 : DR216: FIRE FIGHTING LOBBY 1 BIOMETRIC SCANNER IS DISLODGED | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630112&prj=618&rqi=mUG47UM2VdMxAduJKtjbJzZa13 | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GT1DCOS-19-002 | 4f61f153-83e4-439d-9844-47d08f479192 | SG06-1 | 618 | APAC | Open | P3 Low CX | siakhongneogh@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - BMS | L3 | DCOS General Issue | DCOS |  | Controls | equipment | 1CPOS_RIO_07 | DCOS - Control Panels |  |  | The CPOS HMI and DCOS are unable to identify or indicate which system currently has manual control overriden. There is no clear status or indication to distinguish whether the equipment is in CPOS Manual Mode or DCOS Manual Mode, resulting in ambiguity over the active control source. Attached D2SD screenshot was during Local panel in Auto mode, CPOS HMI in Local mode and DCOS in auto mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630046&prj=618&rqi=BZzDzl0T25JYxbogqXjqTmDLJl
GI-417 | 65b6b0f8-b25a-4446-a7ff-169a90e8ddb7 | SG06-1 | 618 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: To upload the compile picture file for hard to access joint for level 9 for MECH, IT and LB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630052&prj=618&rqi=txhMZ2050FHZjEmT5qDchjdjBl | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
YT1DCOS-18-001 | 7e6f9e94-8908-45bf-998b-ae5bb87362d8 | SG06-1 | 618 | APAC | Open | P3 Low CX | hemendrrajeganathan@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - BMS | L2B | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1CPOS_RIO_06 | DCOS - Control Panels |  |  | Cx2B 1CPOS_RIO_06 To revise schematic and panel drawing and upload into checklist once completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630058&prj=618&rqi=GZzAeGgG8EOQI29USg14ohnaZV
GI-415 | f187d7bd-36a0-4fcf-8d78-cb21d8ef0e58 | SG06-1 | 618 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: To upload the compile picture file for hard to access joint for level 7 for MECH, IT and LB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630050&prj=618&rqi=xg5uj92gZZmKX0EnvuVMuJvd1u | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
RT1ELEC-554-002 | ba32f4b0-ab88-45a1-b72e-151f42d71844 | SG06-1 | 618 | APAC | Ready for Verification | P3 Low CX | alifasyraf@commtechasia.com | 2026-07-18 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: Load Bank busduct During inspection it was found that some busduct is unaligned and the jointing was block but Unistrut support. To rectify and upload proof of rectification Unaligned joints - LB-L5-J-028, LB-L5-J-027, LB-L5-J-026, LB-L5-J-020, LB-L5-J-019. Blocked by Unistrut - LB-L5-J-018, LB-L5-J-007, LB-L5-J-003 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629894&prj=618&rqi=CRhmnCmAS7mZCzY7oT3rXf2huP | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
RT1ELEC-554-001 | 878a2e87-8fec-4372-9bb4-04b967657046 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | alifasyraf@commtechasia.com | 2026-07-18 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | system | IT Busduct System |  |  |  | Cx2A: Load bank busduct At Level 9 the joints of LB-L9-008 was not installed to rectify and upload the proof of works | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629893&prj=618&rqi=egvQR6mjyO6MdOsvmFnE1qsOMf | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
GI-407 | f58a98ef-cf0b-44fd-8f47-1fadac9647ab | SG06-1 | 618 | APAC | Open | P3 Low CX | jessyong@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | To update the hv power study for the curve characteristic for RMU Z, C, A, R1, M1 and D hi set settings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629351&prj=618&rqi=FtTXhonFU1a4LWoNKK81RlxuXJ
GI-406 | b4948ddc-087a-4629-a66d-8ce7c98fbb7b | SG06-1 | 618 | APAC | Closed | P3 Low CX | RyanWu@commtechasia.com | 2026-07-15 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | system | IT Busduct System |  |  |  | To update routing of bus ductors on drawing where necessary, as there are changes to the locations to some of the panels where the ductors are supposed to go | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629350&prj=618&rqi=SjfX9T7DFdFmY5Amof7jUCDqa6 | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
RT1ELEC-555-002 | f57dbc74-e149-4c2a-883b-3376159cc174 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | RyanWu@commtechasia.com | 2026-07-14 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | system | IT Busduct System |  |  |  | Observed misalignment in the IT busduct installed in the STS RM D, from joint IT-L5-J-72 to IT-L5-J-77. Engie to rectify and call for reinspection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629134&prj=618&rqi=gBuCEgi5lgicGsWrtpk1TPAf6C | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
RT1ELEC-555-001 | da3d04e4-d1db-4fdd-b344-350e66151c60 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | RyanWu@commtechasia.com | 2026-07-14 04:00:00.000 +0400 | General Contractor - Electrical | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | system | IT Busduct System |  |  |  | Observed misalignment in the IT busduct installed in sts room 2A from joint IT-L2-J008 to J009. Engie to rectify and recall for reinspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629133&prj=618&rqi=Fe2NKQHk21jF9NqHCPAKH74SvC | https://equinix.facilitygrid.co.uk/x/project/618/system/14737
RT1SEC-1-001 | 73b3ce5a-5b17-44f0-92b9-50c07d343b41 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-07-11 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L2A | Labelling | Commissioning |  | Security | system | Security - CCTV System |  |  |  | C2A: Level 5 Security System Labels wrong for some security camera in E- wall room A side need to be rectified Some camera alignment appears to be slanted and needs to be rectified | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628769&prj=618&rqi=kgriUQG9C4wSt0xShYQo2nqKHe | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-371 | 1244eb23-b1d4-4617-a749-5b63350e22c9 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-06-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | Observed the lamp test at the gen annunciator, does not light up the low coolant level alarm. Rehlko to rectify | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626882&prj=618&rqi=xMOCqS5k0ssU33O7WCp7Yd4Qt5
RT1DCOS-1-002 | 22a4aea7-d8c0-426d-a478-aa831cace7b8 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-24 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning |  | Controls | equipment type |  | DCOS - Control Panels |  |  | Cx2B: 1DCOS CP 01 cable not terminated due to a module needs replacement 1DCOS CP 02 Drawing holder did not stick on the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626929&prj=618&rqi=2QNPzIJQqGja4KJu2UEHXUVHWm
RT1DCOS-13-002 | b1380fab-3271-40ac-804b-74913daf8fb8 | SG06-1 | 618 | APAC | Open | P3 Low CX | Weihaolim@commtechasia.com | 2026-06-22 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1CPOS_RIO_01 | DCOS - Control Panels |  |  | During the Cx2A inspection, the following observations were noted (apply to all PCP and RIO panels): To update network architecture and earthing connection diagram, connection on site don't tally with drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626336&prj=618&rqi=7gtiNXFE9116VmsP5PY9zHguxB
RT1SEC-2-004 | babd1092-9e30-4539-ab0b-0cb23ce71ba0 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-06-13 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Security | system | Security - CCTV System |  |  |  | Cx2A: L7 Card Access Panel ACP-13 and ACP-14 L8 Card Access Panel ACP-15 and ACP-16 L4 Card Access Panel ACP-07 and ACP-08 L6 Card Access Panel ACP-11 and ACP-12 1. PSU needs to be labeled to show where /what devices it is connected to 2. Battery needs to be labelled (Installation / Start using date) 3. Earth cable within the PSU units need to be attached / installed 4. Panel earth needs to be installed on the door 5. Internal wiring needs to be terminated with proper labelling 6. Applicable to all ACP units 7. There needs to be a GA drawing of the main ACP unit so that people can identify the components within 8. In the drawing , label the PSU units 01- 07 as shown on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625189&prj=618&rqi=ubmECS2FIiyDTbsCqKCDt1cTa7 | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
RT1DCOS-28-002 | c51ce8f0-6c59-4986-a741-7f5efb4fc9d6 | SG06-1 | 618 | APAC | Closed | P3 Low CX | siakhongneogh@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 2CPOS_GWP_01 | DCOS - Control Panels |  |  | During the Cx2A inspection, the following observations were noted (apply to 1CPOS_GWP-01 and 2CPOS_GWP-01): 1. The equipment layout plan / setting-out drawings have not been updated to reflect the current site conditions. 2. General housekeeping and cleaning works are required. 3. To install flexible conduit/ trunking for the incoming cables 4. Pending power earthing details explanation 5. Drawings to be in place 6. Permanent labelling shall be properly installed for incoming cables and screw terminal 7. To retighten and torque as per manufacturers guildelines | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624889&prj=618&rqi=MEObYj4BppRBlrZKD1J1nIyzh6
RT1DCOS-28-001 | 5f8a0794-01b7-45df-8504-df80f73c40e7 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - BMS | L2A | Installation not correct | Commissioning |  | Controls | equipment | 2CPOS_GWP_01 | DCOS - Control Panels |  |  | Onsite 1Q2 , 1Q3 and 1Q4 MCB model was not tally with the bill of materials. Onsite was model A9F84110, however BOM indicate A9F84106 (apply to 1CPOS_GWP-01 and 2CPOS_GWP-01) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624885&prj=618&rqi=1SqwCFSk3gCzrlv6vaofnDICH7
RT1DCOS-28-003 | b2eaa6f1-0b4b-4363-af2c-2414c1b79c2a | SG06-1 | 618 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-06-11 04:00:00.000 +0400 | General Contractor - BMS | L2A | Installation not correct | Commissioning |  | Controls | equipment | 2CPOS_GWP_01 | DCOS - Control Panels |  |  | Onsite the input card/ multiplexer quantity was not tally with the bill of materials. Onsite was only 1 set of input card and secrew terminal, however BOM indicated 2 sets | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624890&prj=618&rqi=o3QMRh2q61Z4KMABK2CxY1RAs8
GI-332 | 1357979f-3f79-401e-a4f6-ff49f3d0e8e8 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | General Contractor - Mechanical |  | General Design Issue | Design |  |  | equipment type |  |  |  |  | FCU Cx3: Observations: 1. SOO states that when FCU in shut down or off mode the PICV valve should return to close state (0% position) 2. When tested on site the FCU shuts down or go into Off mode , in local / Auto / The PICV valve remains as open 3. Accesstech to confirm if the valve should remain open / close when the unit is shut down 4. Dirty Filter alarm , when it is in local mode , it stays on , but when its in auto mode , it switches off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624516&prj=618&rqi=7pxmCqQnHMUkZGvxyJGA6fB6AA
RT1SEC-2-003 | 96096da5-bdc1-4cfd-a0ce-146a1654313b | SG06-1 | 618 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-06-09 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Security | system | Security - CCTV System |  |  |  | Cx2a: L4 Card Access Panel ACP-07 L4 Card Access Panel ACP-08 L6 Card Access Panel ACP-11 L6 Card Access Panel ACP-12 1. PSU needs to be labeled to show where /what devices it is connected to 2. Battery needs to be labelled (Installation / Start using date) 3. Earth cable within the PSU units need to be attached / installed 4. Panel earth needs to be installed on the door 5. Internal wiring needs to be terminated with proper labelling 6. Applicable to all ACP units 7. There needs to be a GA drawing of the main ACP unit so that people can identify the components within 8. In the drawing , label the PSU units 01- 07 as shown on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624520&prj=618&rqi=JpcPZaCV0Ct8xyufyupNNcQepx | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
RT1SEC-2-002 | 3969c56c-9175-4837-863e-5eadb79ffcac | SG06-1 | 618 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Security | system | Security - CCTV System |  |  |  | Cx2A: L2 Card Access Panel ACP-03 L2 Card Access Panel ACP-04 L3 Card Access Panel ACP-05 L3 Card Access Panel ACP-06 1. PSU needs to be labeled to show where /what devices it is connected to 2. Battery needs to be labelled (Installation / Start using date) 3. Earth cable within the PSU units need to be attached / installed 4. Panel earth needs to be installed on the door 5. Internal wiring needs to be terminated with proper labelling 6. Applicable to all ACP units 7. There needs to be a GA drawing of the main ACP unit so that people can identify the components within 7. In the drawing , label the PSU units 01- 07 as shown on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624008&prj=618&rqi=I1uUW0XjOLoUBwpcUM3fLxrjgm | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
GI-330 | 1972a2dc-2140-470e-b259-95349bbb357c | SG06-1 | 618 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-06-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | To update the approved settings to include the change in the PT100 sensor setpoints change and excitation current limit change from 23% to 40%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624010&prj=618&rqi=qQo5ExzRn0SZkBn5MudJbp710Z
RT1SEC-2-001 | 82f4fb27-6aae-4a78-baa7-15c4ac3d4814 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | jasontan@commtechasia.com | 2026-05-29 04:00:00.000 +0400 | Electronic Safety and Security Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Security | system | Security - CCTV System |  |  |  | Cx2A: ACP_1 and ACP_2 ACP_9 and ACP_10 1. PSU needs to be labeled to show where /what devices it is connected to 2. Battery needs to be labelled (Installation / Start using date) 3. Earth cable within the PSU units need to be attached / installed 4. Panel earth needs to be installed on the door 5. Internal wiring needs to be terminated with proper labelling 6. Applicable to all ACP units 7. There needs to be a GA drawing of the main ACP unit so that people can identify the components within 7. In the drawing , label the PSU units 01- 07 as shown on site | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623494&prj=618&rqi=1uEjdL34ZHSYzCZiZGu8aJxRMp | https://equinix.facilitygrid.co.uk/x/project/618/system/14514
RT1DCOS-9-001 | 16900ac2-664b-47bd-a375-71d942e9199d | SG06-1 | 618 | APAC | Closed | P2 Medium CX | siakhongneogh@commtechasia.com | 2026-05-29 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1CPOS_PCP_1_CPU | DCOS - Control Panels |  |  | Onsite PCP Prosoft model was not tally with the drawing. Onsite was PLX31-EIP-MBTCP, however Drawing indicate PLX32-EIP-MBTCP (apply to all PCP panels) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623462&prj=618&rqi=GIi9VH2BOYcQ4kAxaoDrZydjAT
GI-316 | d944d32a-014e-4b19-881a-166364ad1263 | SG06-1 | 618 | APAC | Open | P3 Low CX | jessyong@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | SMBE to ensure all DPM settings are set as per approved DPM alarm setpoints. Observed all levels DPM during DCOS cx3 inspection alarm setpoints are not as per approved settings. Please submit the approved settings DPM, crompton relay settings, sync check relay settings, UOVR in procore for EOR review and approval | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622957&prj=618&rqi=mLeSmr5hI5a04gTZJPOF7Byuf4
GI-317 | a68b421d-dec4-419c-bd9d-3273cb242c0d | SG06-1 | 618 | APAC | Ready for Verification | P3 Low CX | jessyong@commtechasia.com | 2026-05-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | SMBE to ensure all labels installed are as per the revised approved dwg and in addition breaker ratings AT/AF should follow as per approved studies. Please ensure the dwg indicated breaker ratings follows the approved power studies. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622958&prj=618&rqi=QHkSwQzGgX8G9vw83z7IyFvMjn
GI-311 | 3e13bdc5-4cf4-40ed-86bd-c236453a8599 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | ericchong@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | Cx2A: 2CHWSTR_M1R1_CTSF_2 1CHWSTR_M1R1_CTSF_1 1CHWSTR_M1R1_CTSF_2 1CHWSTR_M1R1_CTSF_3 1CHWSTR_M1R1_CTSF_4 1CHWSTR_M1R1_CTSF_8 1CHWSTR_M1R1_CTSF_9 1. SLD & Panel GA to be amended to reflect the correct set up. ACT to call for reinspection upon drawings approval. 2. Vessel to be cleaned prior to sand filling. 3. Missing equipment labels. 4. Typo on control panel indications 5. Missing isolation valves before the skid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622615&prj=618&rqi=dQktCyxakXDOAgc6xWEfqBm5iP
RT1DCOS-13-001 | 0311b72e-2d9e-4478-b686-31ffe695d8bc | SG06-1 | 618 | APAC | Closed | P3 Low CX | siakhongneogh@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1CPOS_RIO_01 | DCOS - Control Panels |  |  | During the Cx2A inspection, the following observations were noted (apply to all panels): 1. The equipment layout plan / setting-out drawings have not been updated to reflect the current site conditions. 2. General housekeeping and cleaning works are required. 3. To install flexible conduit/ trunking for the incoming cables 4. Pending incoming feed earth stud to loop on earth bar 5. Drawings to be in place 6. Permanent labelling shall be properly installed for incoming cables 7. To retighten and torque as per manufacturers guildelines | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622407&prj=618&rqi=yDnndPf2mvD5kwwcUrzfmdSbJp
RT1DCOS-17-001 | 5d68d317-d631-441a-8275-17ab807c4b1e | SG06-1 | 618 | APAC | Open | P3 Low CX | siakhongneogh@commtechasia.com | 2026-05-20 04:00:00.000 +0400 | General Contractor - BMS | L2A | Installation Damage | Commissioning |  | Controls | equipment | 1CPOS_RIO_05 | DCOS - Control Panels |  |  | Observed that the HMI has been scratched. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622408&prj=618&rqi=BTNSUQc8KV328ysaoHTkt9r8Ai
GI-284 | 4cc76626-4a0c-431a-9f89-ad48ff004ae6 | SG06-1 | 618 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-04-28 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | CX2A: 1FCU_Z_75, 1FCU_M1_13, 1MAU_C_2, 1MAU_M1_07, 1MAU_D_2 & 1MAU_M1_08 In the General Lay out drawing , the position of the relays do not follow as per the as GA drawings , please check and update the position of the relay in the GA drawings , as per what that is in the panel Please also trace and check the wiring of the fuse before updating the drawings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619677&prj=618&rqi=VSguuouk3hBAOeKPMV756WX45T
RT1DCOS-7-001 | 4aeb0369-fe95-435f-ad3c-972a748fee18 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | RyanWu@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor - BMS | L2A | Installation not complete | Commissioning |  | Controls | equipment | 1DCOS_CP_7 | DCOS - Control Panels |  |  | put a missing 50mA fuse at compartment 13 for 2x1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618995&prj=618&rqi=qk2RL4lSZejABjWM6YQL6Il0NV
RT1DCOS-3-001 | 7bc3a0f5-be41-40e8-bfcc-caeccaecd6d8 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_CP_3 | DCOS - Control Panels |  |  | To provide updated dwg in panel pocket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618321&prj=618&rqi=3933uzMs1bCTD5vODAmdRdMrDP
RT1DCOS-4-001 | 4acd5325-ad41-4205-b613-2aabaa0031a0 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_CP_4 | DCOS - Control Panels |  |  | To provide updated dwg in panel pocket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618323&prj=618&rqi=Z5qAkNvZeNn4itjUNKQdpbEjU5
RT1DCOS-5-001 | 507ac735-1e94-43d0-8585-5f56b66aacd5 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_CP_5 | DCOS - Control Panels |  |  | To provide updated dwg in panel pocket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618324&prj=618&rqi=m7I2iAYZTjkgtzya6pbfFiRQEZ
RT1DCOS-6-001 | 37b101d9-39c2-477d-a021-9553bece9b20 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-16 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_CP_6 | DCOS - Control Panels |  |  | To provide updated dwg in panel pocket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618325&prj=618&rqi=6DSYSKUXjkD0VNlRNE00nyEyn6
GI-264 | 6dde5137-c0e0-43ef-980f-b40c63821aab | SG06-1 | 618 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | General Contractor - BMS |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | CX2A visual inspection conducted for 1DCOS_CP_3,4,5,6, observed the following issues 1. Cable sheath to reinstall at enclosure, not at gland plate once trunking is installed 2. Missing danger sign 3. Missing engraved sign for PE and TH1 4. Incorrect PLC part number in dwg 5. To update dwg on IE grounding 6. Provide additional 50mA fuse within the panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618201&prj=618&rqi=kUmYnlBSqA5abFUfpnbRyKNFim
RT1FD-2-001 | 05a75184-e4a8-4a7f-8643-158257d0e871 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | Cx2A : MAP : 1. MAP drawing , needs to be updated , please insert and resubmit the drawings for review 2. Batteries need to be installed in the PACP / SAP/ MAP , with the date of installation affixed to the battery 3. Permanent labels to be installed PACP : 1. PACP GA drawing , needs to be updated , as total power failure module is not included in the GA drawing , please insert and resubmit the drawings for review 2. PACP GA drawing : Patent CP - the module needs to be named in the GA drawing 3. Permanent labels to be installed PACP / SAP: 1. Batteries need to be installed in the PACP / SAP , with the date of installation affixed to the battery This general defect is applicable to all PACP / SAP panels MAP / SAP / RP / Mimic Panels 1. Please ensure that the incoming power cables are terminated prior to CX2B inspections 2. Permanent labels to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618261&prj=618&rqi=2HifGadLopx5AHFQyYYL8vpQUR
GI-263 | 994834dd-3235-4e31-87dd-aac6b708131c | SG06-1 | 618 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | General Design Issue | Design |  |  | equipment type |  |  |  |  | LVSB SOO to include transferring system to maintenance bypass procedures and the panels involved in the transfer process, including but not limited to ups system, udp/umdsb/or any associated panels and MSBs. Update soo to submit to procore for EOR review and approval. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618105&prj=618&rqi=xErMg74ZVclXWBLtewKUoHff3r
GI-243 | da570d90-e4a0-4c43-8dc1-0a8f92c69fcb | SG06-1 | 618 | APAC | Closed | P2 Medium CX | RyanWu@commtechasia.com | 2026-04-08 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | Replace the earth cable "FROM MFEB ELEC RISER 5B-2" at level 5 FEB STS 5B as insulation is scratched to the point can see copper inside | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617515&prj=618&rqi=sdLLEbM1eB4oIQztRfhjNKEeCa
RT1DCOS-2-001 | dbbfaff4-c928-4831-9834-3cdb58fa1c98 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-02 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_CP_2 | DCOS - Control Panels |  |  | Cx2A : DCOS_CP_02: 1. Cable entry edge needs to be protected by a rubber sleeve to prevent the sharp edge from cutting / damaging the cable 2. Light needs to be indicated in the GA drawing 3. the door panel earth needs to be checked its the approved type 4. Danger stickers to be affixed to panel before energization 5. Document pocket needs to be affixed to panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617168&prj=618&rqi=HXCMpu7Hr4CO8BFxmIwwopyUNC
RT1DCOS-1-001 | fc5d0033-728e-479c-aaef-cea1f22254cb | SG06-1 | 618 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-04-02 04:00:00.000 +0400 | General Contractor - BMS | L2A | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_CP_1 | DCOS - Control Panels |  |  | Cx2A : DCOS_CP_01: 1. Cable entry edge needs to be protected by a rubber sleeve to prevent the sharp edge from cutting / damaging the cable 2. Light needs to be indicated in the GA drawing 3. The door panel earth needs to be checked its the approved type 4. Danger stickers to be affixed to panel before energization 5. Document pocket needs to be affixed to panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617166&prj=618&rqi=9jWFCzxWDqa7VkeR1IvG8r7Sjz
GI-234 | aec591f3-aba3-432e-8074-745d361806d4 | SG06-1 | 618 | APAC | Closed | P3 Low CX | KeeLeongLee@commtechasia.com | 2026-03-27 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | Observed during Cx2B earthing inspection, all the earth bar is not labelled. Affected earth bar as below: 1. MFEB ELEC RISER 9A-2 2. FEB-1-E-WALL-9A 3. FEB-2-E-WALL-9A 4. FEB UG MUWP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616629&prj=618&rqi=pNKZUif68Evw709BqFIki4wxpH
GI-229 | e0e481e8-5f98-484a-9528-9e3e999d3d07 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-03-23 04:00:00.000 +0400 | General Contractor - Electrical |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | CxL2a: LV MFEB B for LV to MFEB ELEC RISER 5B-2 Drawing needs to be updated on the position if the Note one ( Cable Tray Earth) , as well as the position of the Incomming earth wire from LV MFEB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616167&prj=618&rqi=e7srKvrHiOd0HlUPDUVy4S3EOs
GI-200 | bdfbcddf-0f07-482f-befd-ed83dbbd534b | SG06-1 | 618 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | General Contractor - Mechanical |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | CX2A MV Fan: 1EF_Z_4 1EF_Z_5 1. Missing label on the ducting. 2. Debris to clean. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615048&prj=618&rqi=OEn5uUuBNybQsf9PNeVzj9sUO7
GI-193 | d201e3f2-0eb6-46bb-98e9-950c5078ece1 | SG06-1 | 618 | APAC | Ready for Verification | P3 Low CX | jasontan@commtechasia.com | 2026-03-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | Earthing Cx2A Earthing from MV FEB B / A to CSS ( RMU ) 12 way Earth bar type and dimensions installed on site in the RMU differ from type / dimension shown in the drawing The 12 way EB shown in the drawing is split into two and has a test link connected to it where else on site the bar is just straight, without a test link and is different from the one that is installed Please check and advise on the dimensions on which one is correct | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614805&prj=618&rqi=lX9HxR6adoLqZAw1gL07fIrmP0
GI-192 | 827735eb-d15d-49f5-9463-4867787abd38 | SG06-1 | 618 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | CX2A Buffer tank: 1. 2CHWSTR_2_CHWBT_1 has damaged insulation and dented. 2. All three Buffer Tanks 1CHWSTR_01_CHWBT_1, 2CHWSTR_2_CHWBT_1 & 1CHWSTR_02_CHWBT_1 leg insulation below the base is incomplete and not fully covered. 3. Issue with 1CHWSTR_02_CHWBT_1 and 1CHWSTR_04_CHWBT_1, on the approved drawing 1CHWSTR02_CHWBT_1, have "1CHWSTR_04_CHWBT_1" on its name plate and 1CHWSTR_04_CHWBT_1 have "1CHWSTR02_CHWBT_1". AccessTech to check approved drawings and change name plates. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614789&prj=618&rqi=r5IqeOcMysOMpaZIcJKMGnXVb3
GI-190 | 88255c6a-74de-421a-aca9-c1d0a57f7811 | SG06-1 | 618 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | Cx2A Issues FCU_M56 & FCU_Z27 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Only FCU Panels have labels, No Labelling for the FCU itself. 3. Temperature Thermostat to be installed in all FCU rooms. 4. Approved drawing, general arrangement discrepancy of components. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. PSU 50W is also in the incorrect area. Drawing to be updated and approved. 5. Incoming Terminal for FCU Panel, termination is incomplete 6. Dirty Filter Alarm Status, X1.3 & X1.4, drawing indicates 1B & 13/A, on site shows 13/A & 14A. 7. Fan Speed Command, X3.18, drawing indicates 6/B, on site shows 2/B. 8. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 9. Drawing Pocket to be installed in FCU panel 10. Not able to tally FCU S/N due to inaccessibility. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614690&prj=618&rqi=3y7hSAA4BwHylv51rdaXgmbH3o
GI-189 | a2af66c1-5699-4e9e-8534-52ecd1518518 | SG06-1 | 618 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | CX2A Issue FCU_M40 & FCU_Z60 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Only FCU Panels have labels, No Labelling for FCU itself. 3. Temperature Thermostat to be installed in all FCU rooms. 4. Approved drawing, general arrangement discrepancy of components. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. PSU 50W is also in the incorrect area. Drawing to be updated and approved. 5. Incoming Terminal for FCU Panel, termination is incomplete 6. Dirty Filter Alarm Status, X1.3 & X1.4, drawing indicates 1B & 13/A, on site shows 13/A & 14A. 7. Fan Speed Command, X3.18, drawing indicates 6/B, on site shows 2/B. 8. Control Circuit Diagram 1 Drawing indicates OL1 LRD16 (9 ~ 13), onsite shows LRD08 (2.5 ~ 4) 9. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 10. Drawing Pocket to be installed in FCU panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614688&prj=618&rqi=vcqiBCy3DgMf4FyWcRWkw6qA7x
GI-188 | f86bdeee-5b71-42df-ba59-118c0dfb07e0 | SG06-1 | 618 | APAC | Closed | P3 Low CX | KianFuiTain@commtechasia.com | 2026-03-03 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | CX2A Issues FCU_Z53, FCU_Z54 & FCU_Z55 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Only FCU Panels have labels, No Labelling for the FCU itself. 3. Temperature Thermostat to be installed in all FCU rooms. 4. Approved drawing, general arrangement discrepancy of components. Magnetic Contactor (MC1) and Overload (OL) Relay is in the incorrect area. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. TS Relay to be remove in drawing. Drawing to be updated and approved. 5. Incoming Terminal for FCU Panel, termination is incomplete 6. Dirty Filter Alarm Status, X1.3 & X1.4, drawing indicates L1B & 13/A, on site shows 13/A & 14A. 7. Fan Speed Command, X3.18, drawing indicates 6/B, on site shows 2/B. 8. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 9. Drawing pocket for panel to be installed 10. FCU_Z53 location to be update in the floor plan layout 11. FCU_Z54 cable pulling test failed. 1FCU_Z_54_CP_LCP_UI1 cable is broken during the cable pull test. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614687&prj=618&rqi=ifWtg3MopNVcb9nlxWDDPxAk0j
GI-185 | 394e9b73-5491-4fc2-8ba5-8537a4079e92 | SG06-1 | 618 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | Cx2A Issue 1FCU_M1_33, 1FCU_C_12, 1FCU_M1_34, 1FCU_D_13 in STS ROOM A & STS ROOM B 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Only FCU Panels have labels, No Labelling for the FCU itself. 3. Temperature Thermostat to be installed in all FCU rooms. 4. Approved drawing, general arrangement discrepancy of components. Magnetic Contactor (MC1) and Overload (OL) Relay is in the incorrect area. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. PSU 50W is also in the incorrect area. Drawing to be updated and approved. 5. Incoming Terminal for FCU Panel, termination is incomplete 6. Dirty Filter Alarm Status, X1.3 & X1.4, drawing indicates 1B & 13/A, on site shows 13/A & 14A. 7. Auto Mode & Common Alarm, drawing indicates U12 & COM respectively, on site it is swapped COM & U12. 8. Fan Speed Command, X3.18, drawing indicates 6/B, on site shows 2/B. 9. Control Circuit Diagram 1 Drawing indicates OL1 LRD16 (9 ~ 13), onsite shows LRD10 (4 ~ 6) 10. STS ROOM A & B, unable to check the S/N of FCU Units 11. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 12. Drawing Pocket to be installed in FCU panel 13. Not able to tally FCU S/N due to inaccessibility. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483507&prj=618&rqi=3AekIbFXsEIcreYY6JkHQVM2QK
GI-186 | c3a76316-7b45-4d6e-bd43-74c18b76de86 | SG06-1 | 618 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | Cx2A Issue 1FCU_C_11, 1FCU_D_11 & 1FCU_D_12 in TER 5A & TER 5B2 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Only FCU Panels have labels, No Labelling for the FCU itself. 3. Temperature Thermostat to be installed in all FCU rooms. 4. Approved drawing, general arrangement discrepancy of components. Magnetic Contactor (MC1) and Overload (OL) Relay is in the incorrect area. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. TS Relay is missing in drawing. Drawing to be updated and approved. 5. Incoming Terminal for FCU Panel, termination is incomplete 6. Dirty Filter Alarm Status, X1.3 & X1.4, drawing indicates L1B & 13/A, on site shows 13/A & 14A. 7. Fan Speed Command, X3.18, drawing indicates 6/B, on site shows 2/B. 8. Control Circuit Diagram 1 Drawing does not indicate OL1 Model and Range 9. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 10. Drawing pocket for panel to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483508&prj=618&rqi=XT57diJRewxvVKDX19d9FrFdN9
GI-187 | d18d7acf-0498-44f6-bec2-b9d3a6b214a9 | SG06-1 | 618 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | Cx2A Issues 1FCU_M1_55_CP & 1FCU_Z_26_CP 1. No second Labelling above Run(G)/Stop(R)/Trip(Y) LED lights on panel 2. Temperature Thermostat to be installed in all FCU rooms. 3. Approved drawing, general arrangement discrepancy of components. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. Drawing to be updated and approved. 4. Dust & Foreign Debris to be cleared from all FCU Units and Panels before Cx3 5. Drawing Pocket to be installed 6. For 1FCU_M1_55_CP, earth cable is not terminated to the panel earth bar. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483511&prj=618&rqi=0YMObAaHUbVXP4hnGnZN9bBdKK
GI-217 | 46304e4e-dcae-49aa-9519-7f360f75370e | SG06-1 | 618 | APAC | Closed | P3 Low CX | ericchong@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - BMS |  | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_CP_7 | DCOS - Control Panels |  |  | Cx1 FWT: 1DCOS_CP_07: 1. Danger sign not pasted during FWT. RVS to paste on site after confirming the sign design. 2. Incoming/outgoing cable management to be done onsite. 3. To add label on trunking lid adjacent to respective terminal block. Missing label are GWP_01, 1XO and 2XO. 4. To change the wire tagging of DI terminal blocks connected to Extension PLC module, to tally with latest as-built drawing. 5. Drawing: DO relays (1XO, 2XO) to be updated in the drawing, tally with existing panel. 6. Drawing: To change the incoming cable labelling to â€œTBX:L / TBX:Nâ€, tally with existing wire tagging. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615696&prj=618&rqi=UUe9KmfqFj9LaFXFT0hoR9UaHF
GI-216 | d3a1c381-0614-4aa2-83a4-c1d0e517c239 | SG06-1 | 618 | APAC | Closed | P3 Low CX | ericchong@commtechasia.com | 2026-02-27 04:00:00.000 +0400 | General Contractor - BMS |  | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1DCOS_CP_3 | DCOS - Control Panels |  |  | Cx1 FWT: 1DCOS_CP_03, 1DCOS_CP_04, 1DCOS_CP_05, 1DCOS_CP_06 1. Danger sign not pasted during FWT. RVS to paste on site after confirming the sign design. 2. Incoming/outgoing cable management to be done onsite. 3. Drawing: DO relays (1XO, 2XO) to be updated in the drawing, tally with existing panel. 4. Drawing: To change the incoming cable labelling to â€œTBX:L / TBX:Nâ€, tally with existing wire tagging | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615692&prj=618&rqi=u013uAdXXTTyr7EddZXVBDL2sC
GI-184 | 2ac99944-3c20-4f8a-9c0a-28e0daae9ba1 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-02-26 04:00:00.000 +0400 | General Contractor - Electrical |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | As per HDR comment, for OPSFLEX Rm, STS Rm and Ewall Rm to install 50x6mm2 earth bar. Engie to rectify as per HDR comment and submit the revise dwg to procore for official approval. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483397&prj=618&rqi=YMvOhy5o9XaviyK7hka6jprVl0
GI-183 | 236359b3-ef10-4dd6-9a65-8c94a47bbe38 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | Engie to update the following, 1. Earthing overall SLD to update FEB EWALL 2A-1 and 2 cables connection, including incorrect location installed as per the approved layout, submittal 1502. 2. MFEB elec riser 2A to update in overall SLD, current earthing cables connection does not align with the approved SLD 3. Missing main label for all earthing bar 4. Observed earthing cable sleeve installed at cable tray. Engie to replace. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483396&prj=618&rqi=rQSpVftxZMixM6CgDrpfO514Wn
GI-181 | 70bd857a-dd7c-4fc1-b2f2-bd2cf15d06f2 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-02-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Incorrect heater watt installed for all LVSB panels. As per dwg is 55W. 1UDP_C1, 1UDP_C2, 1UDP_D1, 1UDP_D2, 1MDSB_C, 1UMDSB_C, 1UMDSB_D, 1MDSB_Z2, 1MDSB_Z3, 1MDSB_R1_2, 1MSB_Z 1LBSB_ZR1_2, 1MDSB_M1_1_1_5, 1UDP_Z, 1 MDSB_Z1, 1LBSB_ZR1_1, 1LBSB_ZR1_2 To update for all LVSB panels and insert the updated approved dwg in the panel pocket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199750&prj=618&rqi=yCwxaHPIWbOCDt3LTVIQE1hSnI
GI-182 | e3f45599-9580-4571-b55e-26a604ca1605 | SG06-1 | 618 | APAC | Closed | P3 Low CX | jessyong@commtechasia.com | 2026-02-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | Observed incorrect cable size installed for all UMDSB panels. Drawing indicated internal power cables size as 50 sqmm but on site/actual installation measured 35sqmm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199753&prj=618&rqi=AbQDBohKq0B8a1sAlwW1jhNH2t
GI-173 | 1215e04c-8506-4a65-bddc-597d6139ddad | SG06-1 | 618 | APAC | Closed | P3 Low CX | jasontan@commtechasia.com | 2026-02-12 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | Cx L2A - General Issues for FCU / EF / SF 1. Please ensure that there are permanent labels affixed to the Equipment / Control Panels 2. Ensure that there is a document pocket affixed to the control panel 3. FCU - Ensure that permanent labels are affixed to the thermostats of the FCU when they are installed 4. FCU name plate is installed on to the Control panel as per GA drawing 5. Ensure that the earthing cable (Trunking) is terminated 6. Unit strut needs to be shortened with end caps installed on them 7. The Ducting needs to have label applied to them | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199135&prj=618&rqi=kfNW409wWqdns9mu49bUiNZSkX
GI-171 | 2451f6ad-9125-4157-b477-88b91b94b302 | SG06-1 | 618 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-02-11 04:00:00.000 +0400 | General Contractor - Mechanical |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | Cx2A General Issues for all FCUs 1. Thermostat for FCU only installed in Rooms FER B-2 and TER B-2 for mockup, before Cx2B testing all thermostat to be installed -CLOSED 2. Only FCU Panels have labels, the FCUs itself do not have labelling, all FCUs to have labels before Cx2B. -CLOSED 3. Unable to check the fan coils and identify the sensors/components inside the FCU due to either inaccessibility or already joint with duct, arrangement to be made to verify condition of coil and any components such as sensors or dampers (if applicable). -CLOSED 4. 1FCU_Z_65, 1FCU_Z_66, 1FCU_Z_67, 1FCU_Z_72, 1FCU_M1_45, 1FCU_C_13, 1FCU_M1_35 signaling and power cable not terminated, unable to do Cx2A. -CLOSED 5. 1FCU_Z_05 Unable to do Cx2A, because FER ROOM 1B-2 not accessible. -CLOSED 6. 1FCU_Z_06_CP, 1FCU_M1_54_CP, 1FCU_Z_48_CP, 1FCU_M1_50_CP, Typical panels. Approved drawing, general arrangement discrepancy of components. Magnetic Contactor (MC1) and Thermal Overload Relay is in the incorrect area. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. PSU 50W is also in the incorrect area. Drawing to be updated and approved 7. 1FCU_Z_03_CP, 1FCU_Z_04_CP, 1FCU_Z_40_CP, 1FCU_Z_41_CP, 1FCU_Z_42_CP Typical Panels. Approved drawing, general arrangement discrepancy of components. Magnetic Contactor (MC1) and Thermal Overload Relay is in the incorrect area. Relays DFR1 and THR1 are swapped. Fuses are in the incorrect area and F5 fuse is missing from the drawing. TS Relay is not shown in the approved drawing but is present inside the panel on site. Drawing to be updated and approved. 8. Second Labelling above the R/S/T Light on panel missing, However GA Drawing shows Labelling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199127&prj=618&rqi=KqQ8VkOA7d6NN3qZ5Mk0AbfluS
GI-138 | b333b676-6f8d-416e-a532-b2f9601ee130 | SG06-1 | 618 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | For ALL STSSB observed the following issues 1. Incorrect fuse installed at F18, instead of 20A, 10A was installed instead - CLOSED 2. no fuse rating label install for F18, 18A, 18B, 18C, 18D - CLOSED 3. install label for MOXA - CLOSED 4. Missing terminal numbering on 1X2, to include control drawing for 1X2 circuit in drawing - CLOSED 5. Missing phase label indication on busbar - CLOSED 6. Missing busbar mimic label on panel - CLOSED | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198099&prj=618&rqi=eV12hZgOfxjhJaOS5X4yfaOk1I
GI-139 | 2869b51a-8de4-44ec-949f-c62e26a7b8fd | SG06-1 | 618 | APAC | Closed | P3 Low CX | tunlinnay@commtechasia.com | 2026-02-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | For All STS panels Observed the following issues 1. IP21, however there is no cover at the bottom of the panel 2. No GA, no fuse breaker/rating, no PCBs (QB540S1/2, QB120.4, QB102.1, QB102S1/2, ST630 S1/2 etc) labels indicated in approved drawing. 3. Incorrect fuse numbering on approved dwg 3. no phase labels installed at busbar 4. to install on/off label at isolator Q51 5. missing label for key exchange box and key lock 6. to check if busbar mimic label can be installed on panel door 7. Poor adhesion observed on heatshrink(bubbling on heat shrink tubing) 8. socomec to check as per IEC on the minimum distance between phase busbar and ensure design comply Socomec to rectify before Cx2B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198100&prj=618&rqi=DCWpTWQ8esSe2ybVmACrGAJ7dD
GI-068 | d37f34e1-6f4c-4ced-bb5d-49244d918a67 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | ericchong@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | Cx1 DCOS SFAT2 (19-20 Jan) Refer to issue tracker in attachment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197213&prj=618&rqi=p00MreLmRkGttm8ZFzTJFjGjTv
GI-067 | 4d0180e3-aefc-4050-ac99-0e88920b7cf9 | SG06-1 | 618 | APAC | Closed | P1 High DCOS | ericchong@commtechasia.com | 2026-01-20 04:00:00.000 +0400 | General Contractor - BMS |  | Documentation not issued/ Required | Commissioning |  | Controls | equipment | 1CPOS_PCP_1_CPU | DCOS - Control Panels |  |  | Cx1 CPOS SFAT (19-Jan): Refer to issue tracker in attachment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197212&prj=618&rqi=aS2oViSOLuf2zrqTBkaVM8I5Se
GI-064 | 26abda62-dcba-4090-b75f-2d56dba9be7a | SG06-1 | 618 | APAC | Closed | P3 Low CX | YenBinChai@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor - Electrical |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | Equipment: 1UMDSB_R1_7, 1UMDSB_M1_2_1, 1DB_Z2_1_01, 1DB_Z2_2, 1DB_Z1_1, 1DB_Z2_2_03 Issue: The outgoing label is currently missing because the existing SLD does not indicate any outgoing feeders. It will be finalized based on the approved naming convention and updated SLD. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196922&prj=618&rqi=hK7QlQfXEGdcNg2vvRuWKHh9XE
GI-061 | 1864a0d0-89b0-4bcf-99f3-d77364b4faf0 | SG06-1 | 618 | APAC | Closed | P2 Medium CX | jessyong@commtechasia.com | 2026-01-09 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | CxL1 Rehlko KD-3500-E FWT DCOS Issues DCOS(Action from DCOS Team, to update the deviation in the elec points list and coordinate with WH to submit for approval) â€¢ Incorrect Genset command status in faceplate â€¢ Incorrect gen operating status(status remained in gen fault) in faceplate â€¢ Incorrect gen run status(running emergency service/running non-emergency service) in faceplate â€¢ Alarm severity not as per dcos elec points list rev.4 â€¢ Incorrect load capacity % status on summary page â€¢ SMS/Alertops to test during Cx2/3 (not available during FWT) â€¢ Load current, kVAR shown out of limits range during load test with DCOS â€¢ To enquire low coolant level alarm on alarms page. (As per Rehlko, GEN only has low coolant level shutdown) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196654&prj=618&rqi=yT5QphbZQcCg69PrqraOidcTYT
WTELEC-3-002 | 6dd7801f-7ee6-4370-86a8-f61b4121dc83 | SL02x-2 | 450 | APAC | Closed | P3 Low CX | youngjinkim@commtechasia.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Multi-Discipline | system | Electrical system |  |  |  | (Cx-Elec-L5) 1ATS_M3R2_75 common alarm observed during M3 block's dead bus test. During the ATS transfer for VRFOD, a common alarm was observed temporarily. While the ATS transfered successfully, the feedback received by ATS controller was otherwise, leading to the common alarm. The alarm normalized automatically in a few min. Please check the ATS condition on site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615742&prj=450&rqi=xnhyfc8FBnZrEXSXKOj5od9zKd | https://equinix.facilitygrid.co.uk/x/project/450/system/13552
WTMECH-9-002 | 9eac916b-8955-4c27-90b2-1e5f81d2951f | SL02x-2 | 450 | APAC | Closed | P3 Low CX | donghunsong@commtechasia.com | 2026-03-08 04:00:00.000 +0400 | General Contractor | L5 | Missing Components | Commissioning |  | Multi-Discipline | system | Mechanical system |  |  |  | ( CxA-L5-MECH IST(4F)) During the UPS Room N-condition test, one SLA temperature in the UPS room exceeded 35Â°C. Therefore, the airflow limit of the relevant CRAH was increased from 80% to 100%, after which the UPS room temperature was maintained at or below 35Â°C. Confirmation from the design team is considered necessary regarding this temperature exceedance. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615105&prj=450&rqi=nmO0w6HMNBdz3qbxKy1HbNEBUj | https://equinix.facilitygrid.co.uk/x/project/450/system/13553
WTELEC-2-001 | a7d043de-e9bd-45f8-99b8-7c2fa9c86670 | SL02x-2 | 450 | APAC | Closed | P3 Low DCOS | junghohan@commtechasia.com | 2026-01-22 04:00:00.000 +0400 | Subcontractor |  | DCOS General Issue | DCOS |  | Multi-Discipline | system | Electrical system |  |  |  | (L5-CxA-DCOS) PUE and total IT load cannot be monitored on the DCOS dashboard graphics. The Tranche 2 IT load is not combined with the Tranche 1 value. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197512&prj=450&rqi=l9nm475l5t2up6dhOMuuaEPKlI | https://equinix.facilitygrid.co.uk/x/project/450/system/13552
GI-103 | 44ca6421-1c7d-47e3-9880-aa6255c531fb | SL02x-2 | 450 | APAC | Closed | P3 Low DCOS | youngtaekkim@commtechasia.com | 2026-01-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | (L4-CxA-MECH) During the ICOM failure test process, a Temperature High-High alarm is being triggered due to a fault value, although it should not occur under this test condition. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196628&prj=450&rqi=iglAPaYw90v9Ap6b0JTjO8yOEb
GI-102 | b7a455a8-8ce3-4e8b-997a-5835e3fae06c | SL02x-2 | 450 | APAC | Closed | P3 Low DCOS | seungdeokseo@commtechasia.com | 2026-01-04 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | (L4-CxA-Elec) The circuit breaker status is not displayed correctly after server integration during LIB test During the Battery L4 discharge test conducted after server integration, it was observed that the UDP_E2_OUT_3 circuit breaker was closed and supplying load, but its status was not displayed correctly. After correction, it appears necessary to perform the test again to verify proper operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196320&prj=450&rqi=tiX0Kjj9cEAlxVCciT7U1r7bjy
GI-050 | 60ede99b-8889-44a0-ad8f-c078d2667d70 | SL2x-F2 | 509 | APAC | Closed | P3 Low CX | youngtaekkim@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | (CxA-MECH-L3) The 4F STS RM text on DCOS is hidden by overlapping SIM text, making it unreadable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196415&prj=509&rqi=8SG7xIz2q0GEbx94ixgOWTSlfS
RT1ELEC-35-001 | d152bc24-87ce-4d0e-843b-4748f042afa9 | SP03-P2 | 693 | AMER | Open | Outstanding Paperwork/Documentation | celso.okuyama@lzaengenharia.com.br | 2026-08-26 04:00:00.000 +0400 | General Contractor | L2A | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | TX-PG-AUX-1.1 | TX - 480v-208/120 Transformer |  |  | GC Inspection checklist is approved on Project Portal and appended to the document section of this checklist | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635335&prj=693&rqi=KDefw87rrnGr7xf7v9g5IVHLTX
SOR-4-001 | ad6f3d10-4f37-4949-b1d7-ce082b9751a3 | SV11-P2 | 624 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-03-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Design Issue | DCOS |  |  | equipment type |  |  |  |  | (All Delta CRAHs BMS) Fan status not working correctly at the BMS. Confirmed by Delta that the Modbus point for Fan Status (Binary) is not functioning correctly. Will need to be resolved and potentially applied to new projects as a software / firmware update. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615862&prj=624&rqi=xHMvZVCLMnLGhOvd9Vivg5LcOz
GI-134 | 034afe05-31f9-4c88-87e4-49df71cffd0c | SV11-P2 | 624 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Incomplete Connections | Commissioning | [7 empty] | UDP-C-1 breakers C-4, 5, 6 Micrologic screens are not energized. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614729&prj=624&rqi=NUjNpaOyVCB5KbwqpPc98LNBUH
GI-135 | be2c2ac2-4a4f-4a9f-8bc4-17e9be2040fa | SV11-P2 | 624 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-03-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Incomplete Connections | Commissioning | [7 empty] | UDP-C-2 breakers C-4, 5, 6 Micrologic screens are not energized. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614731&prj=624&rqi=SE5s0NxOJo5QY9CVJvyj4ehdxz
GI-129 | 209bdde5-97a5-468f-864f-e7116e561527 | SV11-P2 | 624 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-02-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | (All Delta CRAHs BMS) L4 Fan status not working correctly at the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352245&prj=624&rqi=38PQNduNKJN7v9uoQ9L9rbDRej
GI-128 | 0ee6b747-ae3b-46f7-9829-500a4712cac9 | SV11-P2 | 624 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-02-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | (All Delta CRAHs BMS) L4 CHWV mismatch alarm not working correctly at the BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352244&prj=624&rqi=VGGDG1GUqbpfnAZUspGooRxx2S
GI-132 | dc72eb55-292c-4330-b830-1057864467cf | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-26 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | (Both Chillers C-04 and D-05 BMS) L4 Cooling Tower Bypass does not properly increment open when it's setpoint is not met. Timer counts down but the valve never get's the incremented command. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352250&prj=624&rqi=B6H7tRySMUM2lrEdFuMHhuE2Ca
GI-130 | 972df981-ed1c-4df3-b3df-b1eec6dacd29 | SV11-P2 | 624 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-26 04:00:00.000 +0400 | Design Professional |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | (Both Chillers C-04 and D-05) L4 If the JCI Chillers go into "Cycling Shutdown" due to leaving liquid low temperature - Full Free Cooling, while the Skid is in the process of proving, the proving process will get interrupted and the Skid will "Fail to Start". JCI Chillers always start when receiving an enable (regardless of current CHW temps), and will shut down if their CHW supply is low. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352248&prj=624&rqi=6D3fj04S01pBCk20hebsSVUhjw
GI-127 | 9179e5a8-b2c1-4974-b988-25889bd4b148 | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-25 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | (Both Chiller Skids BMS) L5 No communication alarm comes in when comms are lost to the JCI Chiller control panel (or the Chiller is completely de-energized) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221117&prj=624&rqi=4fOdYRN6DNP2RTsNha3YvY0rPU
GI-125 | ceb8e79e-4ab6-4e39-a724-6a5635a15f99 | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-25 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | (All Chiller Skid BMS) Remove the following points at the chiller skid module on the "Chiller" layout screen on the BMS: - CHWDP - Chiller Cap | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221112&prj=624&rqi=GEmxNN8gowDA1ot1NIfb7aVoYB
GI-126 | bf8e8acd-a72f-49e7-ae71-5025cd3367d4 | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-25 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | (BMS general) L5 Trending graphs for Chiller Skid sensors and Delta CRAHs do not track to the specified value, no data appears. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=221115&prj=624&rqi=3ZJDh02wk4OX6xfUq1oF8OUO7s
GI-122 | 8553f217-5786-4585-95b0-63535b656d13 | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-24 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | (All Chillers BMS) When accessing the Chiller faceplate in the skid pop up from the Chiller layout button, it shows updated information. However, when accessing the skid pop up from anywhere else (Equipment control, roof layout, etc), there is information missing (DT value) and several points not matched/updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199969&prj=624&rqi=eD1fxaYNeOjXx0mEj0FZmD7VHh
GI-121 | 4fc9cd17-f84b-47ed-8091-5ed72188f3d8 | SV11-P2 | 624 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-02-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | (All Chiller Skids) CWP VFD would fault on overcurrent during fast restart. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199968&prj=624&rqi=Vv7oh67wVRfJO3cw7NJMwXOCDi
GI-114 | 61251391-c2d6-40f6-ae0e-dd4a3cafbbd2 | SV11-P2 | 624 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-21 04:00:00.000 +0400 | Design Professional |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | (Both Chiller Skids C-04 and D-05) L4 The categorization of multiple abnormal conditions as "Cycling Shutdowns" (0 on HOA, 0 on hardwired fault, 1 on hardwired cycling shutdown) by the JCI Chillers causes various system PLC integration issues in the following scenarios: Full Free Cooling: - Full free cooling is not available, will remove Skid from rotation - Unless loss of HOA is supplemented by the "Cycling Shutdown" bit Any other "Cycling Shutdown" condition, including loss of suction pressure transducer, loss of condenser flow, and loss of evaporator flow: - Will stay in Cycling shutdown indefinitely and not be removed from rotation - If loss of HOA is supplemented by the "Cycling Shutdown" bit to allow for full free cooling | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199717&prj=624&rqi=OC53sNfmTTWTFZPdI0v3p70ldU
GI-107 | d93d81bb-ea73-42ac-b3cc-a024788b4291 | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | alec.dughi@veolia.com | 2026-02-20 04:00:00.000 +0400 | Design Professional |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | (All Chiller Skids) L4 TST mode change center point does not track Chiller supply temperature setpoint. Currently acts based on a hard coded value written in each PLC (inaccessible). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199702&prj=624&rqi=4tIPr1f94Zxn5Xp5UKqDTCWyv4
GI-112 | 3fc12dda-0e3f-4d5c-a52c-805d8fdedae2 | SV11-P2 | 624 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-20 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | (Both Chiller Skids C-04 and D-05 BMS) L4 Faulting a running Chiller does not create the proper latching fault status in the BMS to allow for it to be successfully rotated off of. Causes the Skid enable to be constantly opened and closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199710&prj=624&rqi=zEqzxvKAQvaDetKR0VKX0oKl2g
GI-105 | e97322c3-f66c-438d-bc4b-7bd7bf4ca451 | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-20 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | (All Chillers CH-C-04 and D-05 BMS) L4 Chiller block graphics on the BMS display a nuisance "Warning" message even when the Chiller does not present any warnings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199686&prj=624&rqi=KSKdjBGHIZ07ylJ0PRHm4shYzw
GI-109 | e77f508d-68d5-43c4-ac30-437f05738bbd | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-20 04:00:00.000 +0400 | Design Professional |  | DCOS Design Issue | DCOS |  |  | equipment type |  |  |  |  | (Both Chiller Skids C-04 and D-05 BMS) L4 The System bypass valve will continue to climb open when flow through the skids is below minimum in the following states: - There is no run status from the CHWP - The Skid is performing an initial start-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199706&prj=624&rqi=YfGVfCsvquqQqn1XYtOzat8u4p
GI-110 | aa831763-d954-45a4-a42d-4babd4528ab3 | SV11-P2 | 624 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-20 04:00:00.000 +0400 | Design Professional |  | DCOS Design Issue | DCOS |  |  | equipment type |  |  |  |  | (Both Chiller Skids C-04 and D-05) L4 Failing the CHWP on a running JCI Chiller Skid will not cause a hardwired fault status from the Chiller, so the Chiller Skid will not be faulted and removed from the rotation until the debounce timers count down (3 min total, 1 min for CHWP, 2 min for Skid). During this time, the System Bypass Valve will continue to open, eventually reaching 100% with N-1 pumps running, causing an unrecoverable building DP crash. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199707&prj=624&rqi=VmePO9qWPFR7i2WAvlyKYJRVqK
GI-108 | 0ef65dd8-1d69-486b-906a-007b25c69275 | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | alec.dughi@veolia.com | 2026-02-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | (All Chillers C-04 and D-05) L4 When values become negative (ex. evaporator / condenser approach temps) the Modbus data from Chiller to BMS goes high >6000F even though the Chiller HMI correctly displays the negative value (ex. -0.5 deg F) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199705&prj=624&rqi=xj2j2MtHI3KrHnvdgubPI8fXF4
GI-104 | 11e54449-7f18-48da-90b2-cdd074b99618 | SV11-P2 | 624 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-20 04:00:00.000 +0400 | Design Professional |  | General Design Issue | Design |  |  | equipment type |  |  |  |  | (All Chillers C-04 and D-05) L4 Allowing the Chiller to cycle off of it's compressor for the purpose of full free cooling (Cycling Shutdown) does not send the expected signals (HOA status) to the BMS to allow it to stay in the CHW plant rotation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199684&prj=624&rqi=9ALeFWipobiQTd7DJeAPGgT9nh
GI-102 | 79633a63-00c2-420f-8a5a-82c78783de6a | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-19 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | (All Delta CRAHs) L3 Valve mismatch alarm is missing from alarm summary page | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199624&prj=624&rqi=5USrdQFQ74iJe2kveK1ZLM0Kko
GI-100 | e7cdf64a-4af2-442c-b87d-bbe66320ecd5 | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-18 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | (Both Chiller Skids BMS) L3 Cooling Tower Bypass needs it's setpoint adjust added to front end BMS graphics. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199497&prj=624&rqi=taWPmZ9Y0GIfmmsKLn5PcRCjB6
GI-099 | c6518684-33b3-c779-afdb-22778c4d5c73 | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | (All Chiller Skid BMS) CV-02 and CV-07 graphically are colored green indicating that the valves are open but physically they are not. Those should be grey on the Chiller Skid graphics. See attached. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199383&prj=624&rqi=YWSAQKLinHCLcyLpq3ac3gftYE
GI-098 | 799727a2-7650-0ee7-00cd-6cd2a43446ed | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-12 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | (All Chiller Skids BMS) Current (Amps) value for CWP and CHWP display as off by a factor of 10. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199145&prj=624&rqi=0VR3sY30I9paSGFRdOUYbImyRQ
GI-095 | 347f1510-cafa-4b2e-80a8-0f8746c084b0 | SV11-P2 | 624 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-02-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Design not as specified | Design |  |  | equipment type |  |  |  |  | (All Chillers C-04 and D-05) L4 Chillers are throttled due to over amperage when at 90-100% load. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199097&prj=624&rqi=29kDKJIuCWed4U8yg4vUeicxEd
GI-091 | 21d2f990-6560-48f6-9708-b67fe1e4c625 | SV11-P2 | 624 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-11 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | (All Chiller Skids BMS) L3 When the entire Skid has it's enable removed, the Cooling Tower enable stays activated and it continues to run, even when all other components have shut off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199093&prj=624&rqi=YHvB4eNHO3lqOSgkr1umgaRRYu
GI-093 | 39e59ce9-a187-4b9a-8f3f-3f365c3f4778 | SV11-P2 | 624 | AMER | Closed | P2 Medium DCOS | nick.shawger@veolia.com | 2026-02-11 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | (All Chiller Skids BMS) L3 The Chiller cycling off it's compressor due to low CHWST is treated as a hard fault by the BMS, which will remove it from the rotation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199095&prj=624&rqi=nwYRWR7T6nxddqbXHGRiVqgsq2
GI-090 | 995b8323-341c-413d-b480-3c21226edbd7 | SV11-P2 | 624 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-02-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [7 empty] | (MSB-C) MSB-C did not have appropriate UL certification stickers installed on any of the switchboard panels. Issue was identified during an external inspection and not noted during Cx testing *LESSON LEARNED* | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198935&prj=624&rqi=b1tbCvyLMz1L3q09c3eWEDvJgb
GI-081 | 04d1410a-ec71-4bc0-898c-c431a783baef | SV11-P2 | 624 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | (All Chillers) L3 Modbus data unable to be received from JCI control panel. BMS communication established, but no register data able to be pulled in. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198713&prj=624&rqi=XICEKQlFlfHky9Vt2ViJpZAcID
GI-083 | 0f6c2e81-8a65-47df-b7cd-a4e0394e44b0 | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | (All Chiller Skids BMS) L3 BMS graphics show blank (% open) boxes for two-position valves. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198715&prj=624&rqi=297NvE6f4088B1HGcR2ofrDBVT
GI-080 | 40fe7ebe-df38-407c-acb5-cd6d6644ab9d | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS |  |  | equipment type |  |  |  |  | (All Delta CRAHs) L3 Re-arrange required to alarm summary page graphics, should neatly represent reduced quantity of alarms that are available from the Delta CRAHs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198711&prj=624&rqi=ej9xRuqvEPuiD0hsDpep1f7rmL
GI-084 | d614c8bf-efdc-4bb1-a6f3-b85d66fdfad9 | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | (All Chiller Skids BMS) L3 Graphics and control for CV-03 do not function from the BMS, works from local HMI | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198716&prj=624&rqi=ITyOb1BsE0pl26rujfAF9qsZUX
GI-085 | 8a075153-ad27-46c2-815c-1911c2ad77ea | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | (All Chiller Skids BMS) L3 CV-09 (CHWP isolation) has associated graphics even though it does not exist as a control valve | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198717&prj=624&rqi=LyjQycmXSuvgalwhNZjqxCnU3i
GI-082 | 0a366213-b7e2-46e6-bd4b-e77048942727 | SV11-P2 | 624 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-02-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Design correction needed | Design |  |  | equipment type |  |  |  |  | (All Chillers) L3 Head pressure control not functioning, signal sent to valves from JCI panel does not correspond to minimum open percentage setpoint during Chiller operation, unit always faults on "No Condenser Flow". | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198714&prj=624&rqi=NUSxR5phfm9PuiDFhqmqAP0uUS
GI-075 | 8d5dc486-dd81-4dc9-a7aa-58b9f06123dc | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | alec.dughi@veolia.com | 2026-02-03 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | (All Delta CRAHs) (BMS) L3 Chilled water valve mismatch alarm is missing from Alarms page on BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198260&prj=624&rqi=gLerZVVUITN1vFZV5izyGUNQWm
GI-074 | 86582a75-11a5-436e-bc89-0d43d84b01d1 | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | alec.dughi@veolia.com | 2026-02-03 04:00:00.000 +0400 | Controls Contractor |  | DCOS Template Issue | DCOS |  |  | equipment type |  |  |  |  | (All Delta CRAHs BMS) L3 Entering water temperature and leaving water temperature are switched in BMS faceplate. Leaving water temperature on BMS seems to be monitoring entering water temp of the CRAH (70F). Entering water temp on BMS seems to be tracking supply air temperature of the CRAH. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198259&prj=624&rqi=L7O1HBEupp97ZYCr7KZLlzV2Bu
GI-069 | ae15e19c-7b83-0c39-6352-592517b08bf7 | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | (All Delta CRAHs) L3 Return Temp and Supply Temp in BMS seem to be tracking Return and Supply humidity of the actual CRAH, respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198153&prj=624&rqi=RXauZxxTTcI24mXWefEiU4bZ4T
GI-071 | 82e9e444-67a4-f4d7-df96-f0a59fae46ec | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | (All Delta CRAHs) L3 Data Points to add: - Supply fan command (%) - Supply fan feedback (yes/no) Alarm Points to add: - Communication alarm - CHW Valve mismatch alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198155&prj=624&rqi=qcWKLLfXdMf0XUuCnbXtwm7h0w
GI-068 | 22c6fd57-166d-5344-b2e6-77b2b5b755c3 | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS Template Issue | DCOS |  |  | equipment type |  |  |  |  | (All Delta CRAHs) L3 Duct static pressure is not needed on CRAH faceplate. (+scaled incorrectly and incorrect units) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198152&prj=624&rqi=yjqoqrkAKjrv3s3xbLdOuj4FOR
GI-070 | 1fd97bbb-fcd0-a290-2968-17854cf7d779 | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-02-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | (All Delta CRAHs) Graphics for Chilled Water Valve command are monitoring Fan Speed command. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198154&prj=624&rqi=jMheZpetFCG1serrV0WjnNa2Lp
GI-065 | 64a41366-8bf6-4460-8f9a-cb6dfdc6136f | SV11-P2 | 624 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-01-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | (Chiller Skid C-04 and D-05) L2B Wires terminated between load side A and B phase lugs do not allow 1" clearance over air and no barrier is present. Per UL580A c 10.2, 1" clearance over air is required for 480V applications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197700&prj=624&rqi=QM9XRnVnAZ08rSBoq7vSPFQNnT
GI-063 | 1ef72fe3-ac13-42f4-e742-05e98f102afd | SV11-P2 | 624 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-01-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning | [7 empty] | (CH-C-04) Refrigerant monitor exterior alert light bracket has broken off. Replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197590&prj=624&rqi=xdNvPOL0fcnbWd3kCdhyrWpdoe
GI-062 | a6283d58-94b6-45e6-b2a2-f65b838b8299 | SV11-P2 | 624 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Component/Equipment Failure | Commissioning | [7 empty] | (Electrical SKID-C) A badge reader has been knocked off its housing and is dangling by a small clip and some wires. The badge reader needs to be reinstalled correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196897&prj=624&rqi=SitqPziAq15MrBXtzvV2UYZ5GI
GI-060 | fc2663a3-302c-4e05-b3fd-599915725345 | SV11-P2 | 624 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-01-13 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | (All Delta CRAH's) Delta CRAHs do not have grouping mode. Please remove the following from the BMS faceplate graphic: Lead unit status, grouping mode status, grouping unitary demand status, group hot aisle SP, group hot aisle temp, group A/M slider. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196818&prj=624&rqi=3fxQZjbPMS9nVvqc8jjz57lxVS
GI-056 | b7f97b0d-175a-6838-c636-29ceeb948e65 | SV11-P2 | 624 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-01-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | (All Chiller Skids) L3 Permant labels for CHWP breaker is currently labeled as spare. New permanent label is needed to depict the new termination. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196664&prj=624&rqi=4gXRDKD2ofB2kQnO9s4nOXkZqh
SOR-273-001 | 8e290a55-73fa-46d3-bc56-ed172573c5ae | SV18-1 | 479 | AMER | Open | P1 High CX | jordan_dubose@fsttechnical.com | 2026-09-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [7 empty] | The top hat in 1MSB_C section 6 is missing the cover to the termination out to 1UDP_C1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638759&prj=479&rqi=GOANPz8K8ZAxUu7TeihfNSpCR5
SOR-272-001 | 28a9a178-988b-4dda-b2ba-9cada62c6b68 | SV18-1 | 479 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | 1MAU_R1_01 & 1MAU_B_02 CMS investigated the issue with the previously reported low flow to the Heating cooling and Dehumidifiers Hx's, found both units locked out on cooling and dehumidification modes, due to Low Pressure switch activation on the DX system, opened the liquid solenoid and checked the saturated refrigerant pressure against the pressure temperature chart using ambient temperature and the charges are found to be low in both units. CMS to schedule a resource to leak test and repair the leaks and top up the refrigerant levels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638418&prj=479&rqi=6miP570exObN5ChbBVaPQCDhAF
SOR-271-001 | 02f021c9-825e-4092-935c-38f232641e8a | SV18-1 | 479 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-09-14 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | MEGA CRAH Automatic Transfer Switch Timers If the Reserve S2 fails and the utility power is available on S1 ... Currently sequence is Immediate Design requirement is a 3 second delay switching back from Reserve S2 to Utility Power S1, aligned with the intention of a minimum of 3 second break before make timer, can this be achieved with a late break auxiliary contact on a contactor, if deemed acceptable? Applies to all 36 units | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638018&prj=479&rqi=TDpZoWsU0VdlshIfXzg7FxyAgq
SOR-271-003 | 4a0770cc-5717-437a-a250-2f06bc1c3a2f | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | After adding the control wires, the Maintenance bypass breaker on the mimic for UPS_A3/B3/C3/D3/E3/F3/R1_3 should be added. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638021&prj=479&rqi=Cuvo1bYsxMx32ZEwo97OFNH4Cp
SOR-270-005 | 4c9ade9b-c3da-4dc5-82c0-2118f4b1c2bf | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-09-10 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [7 empty] | To provide cap for all exposed terminal for power supply 24VDC at MDSB to prevent shorting and trip the control breaker. Note: Applicable for all MDSB at Skid A/E/F/B/C/D | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637589&prj=479&rqi=0VNNJRec3bMJTM0kIYp2oYR4Tr
SOR-270-001 | bafe9796-0dc2-460d-addd-68d82f26204e | SV18-1 | 479 | AMER | Open | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-09-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | To upgrade the STS, 800AMPS firmware for UM1 Control card to V7.0 as per the Equinix approved Firmware release Aug. 26. Applicable for block A/B/C/D/E/F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637285&prj=479&rqi=QA8DsoHUpnoulgdf9AnrHqEEHm
SOR-269-001 | 983569d7-8823-4061-adfa-c60a00d5c62e | SV18-1 | 479 | AMER | Ready for Verification | P1 High CX | jordan_dubose@fsttechnical.com | 2026-09-02 04:00:00.000 +0400 | Controls Contractor |  | DCIM BCM Issue | DCIM |  |  | equipment type |  |  |  |  | Equinix Operations is not able to see the programmed 44 (A/E/F) 1RPP_X2s on Level 2. This prevents FST from starting the primary injection testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636628&prj=479&rqi=4nSXVSmSljrcISEIBQeCoMAHvX
SOR-267-001 | 2e764b9f-e6d5-4558-9749-c18582f6718b | SV18-1 | 479 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | Vertiv Control Panel wiring needs to be cleaned up the large coils of wiring is putting strain on the points of connection, which will lead to component failure. This has already manifested itself on 1CRAH_D_07 HMI THIS APPLIES TO ALL 36 UNITS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635881&prj=479&rqi=cK1KD1TAt0DL6GqLCFhqOw1aKF
SOR-267-002 | 12367160-e9eb-4175-b400-f4d798a22f11 | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-08-28 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | FST observed that the 1RPP panels in Data Hall B & Data Hall F are in different locations than what is in the E130.2A & E130.2B drawings. 1RPP_F2_1_3 1RPP_F2_2_3 1RPP_F2_1_4 1RPP_F2_2_4 1RPP_F2_1_6 1RPP_F2_2_6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635912&prj=479&rqi=NLw1HcK6F6FaSaMTH6MgupF8Am
SOR-266-001 | e7149faf-fa7d-4d51-989b-d85fbfa1eb44 | SV18-1 | 479 | AMER | Ready for Verification | P1 High DCOS | jordan_dubose@fsttechnical.com | 2026-08-27 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS |  |  | equipment type |  |  |  |  | The breaker frame sizes in the all the blocks (A-Z and also the 2nd phase) MSB One-Lines were changed to all be 4000A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635745&prj=479&rqi=LFhjWVBz2zRCP7lz2oAd2cipv5
SOR-264-004 | 3bf55f8d-5ba3-4d16-9a35-26a348ea66c9 | SV18-1 | 479 | AMER | Open | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | The SCR at Gen A was found faulted and didn't run when the GEN A was running with 1.4MW load. The fuse 4Amps at the control panel is randomly busted during the lost of utility and transfer to Generator source. Note: This is happening on Gen E and F. Cummins to revisit the size of the fuse if that is the correct size. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635098&prj=479&rqi=QyjuAf4lpsICGqjcqH3JB0DRkU
SOR-264-003 | 00979cd5-06a3-4f07-816d-ff25067eec7a | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-08-24 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS |  |  | equipment type |  |  |  |  | The labeling of the 1STS_A2's are incorrect in Oneline_A_UDP_PDU as it should go 1STS_A2_1, 1STS_A2_2, 1STS_A2_3, and 1STS_A2_4 from left to right to match E603.05 Drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634979&prj=479&rqi=csReqmuqdzYeNGfF1LpXvkKDbE
SOR-263-005 | 004a1aa1-543f-4250-8868-f7cf12ef95e1 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | Align all Vertiv MEGA CRAH - Transfer Time from S2 to S1 per agreement, reference Matrix attached | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634826&prj=479&rqi=SNIEs5kkuRkbrjH72nFBVoMO6C
SOR-263-001 | 46e926f1-079f-4496-8ca6-36ad19833262 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Vertiv MEGA CRAHs not transferring back from S2 to S1 when utility power is reinstated, thus applies to the following units 1CRAH_C_06 1CRAH_D_08 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634822&prj=479&rqi=dAR23TZ4B6BQd1BN3FG995HWNG
SOR-263-004 | 6f46ee83-bd7a-4654-9133-1a3e024e1f6b | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | As found condition - buzzer active no alarms on HMI, this issue applies to units: 1CRAH_B_07 1CRAH_B_09 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634825&prj=479&rqi=IH3NvlKWA5CJR7f2JUVpMMmxJV
SOR-263-007 | 07c31b3c-f7f7-4e61-8bbe-3cdd9abef118 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | The 30 second-time delay is not deployed for the loss of utility power S1, transfer to reserve power S2, it needs to be to protect the fan motors. This applies to all Vertiv CRAH units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634847&prj=479&rqi=hpvuJgVXb6cgw22XZ2LnJpzwGa
SOR-263-002 | f02737dd-87a5-4a15-aa4b-0a0b46cc8569 | SV18-1 | 479 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | Air Flow Sensor - not alarming when tubes are disconnected, this applies to the following units: 1CRAH_B_01 1CRAH_C_01 1CRAH_C_08 1CRAH_B_09 1CRAH_D_06 1CRAH_D_09 1CRAH_D_10 1CRAH_D_12 airflow sensor only works when one tube is connected. . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634823&prj=479&rqi=ArRIF7MwxhH402kH0Hn70dRt5G
SOR-263-003 | 77ee5523-6661-40e5-9f03-b065907d1916 | SV18-1 | 479 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-23 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | Fan rubbing noise coming from the fan section of the Vertiv MEGA CRAHs, this issue applies to: 1CRAH_C_06 1CRAH_C_10 1CRAH_D_12 THE FIX APPLIES TO ALL VERTIV CRAHs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634824&prj=479&rqi=TlZ2dKEc0ZMdIzOVNgaa5uJ47l
SOR-262-004 | 3b003155-5a98-4493-84c9-9b3c6c3c407f | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-21 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment type |  |  |  |  | Chiller 1ACC_A_03 & 1ACC_A_04, there is an issue with the auto alarm reset function, after three unsuccessful try's the loop goes into a lock down scenario. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634679&prj=479&rqi=FqzYJKBEdOI1Oy1G1IK0UqCGEH
SOR-262-003 | 8a4934da-cd08-468e-8984-bab72900ccfb | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-21 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning | [7 empty] | The following Flow transmitters are generating repeater status deviation alarms on flow CWR_FT_C1 CWR_FT_C5 CWR_FT_C10 Thais needs to be investigated to determine root cause. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634673&prj=479&rqi=BtlPUP8h14EwqyGAKFBThFpaUY
SOR-261-003 | ac5e6f26-1812-417a-9f5a-4835c44a2139 | SV18-1 | 479 | AMER | Open | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Investigate the ON and OFF battery low alarm in the UPS_X3 Note: Applicable for 1UPS_A3/E3/F3/D3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634438&prj=479&rqi=j9XT3YIjvKwP1I21r4wqca6KIq
SOR-261-001 | e6e827ed-b333-46bf-b7f1-2c14f1ba37e7 | SV18-1 | 479 | AMER | Open | P3 Low DCOS | jordan_dubose@fsttechnical.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | The 1STSs are missing a general alarm in DCOS. This was shown when 1STS_E2_4 had abnormal fan alarm locally but not in DCOS detailed in Issue 1092. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634295&prj=479&rqi=jPgnEFEkzx644sSaepmXUqVzzJ
SOR-260-001 | 694a3831-fc6f-418b-ac6b-b866f4a82397 | SV18-1 | 479 | AMER | Open | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-18 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [7 empty] | During the event, the 20 A breaker (1UPNL_E3, L1#1) feeding the secondary source of the DMARC was found in a tripped condition. At the same time, the primary source was unavailable due to the loss of 1MSB_A during the pre-IST condition, resulting in a complete loss of communications for all equipment associated with Skid A, including MLTX_A, GEN A, and 1RMU_A. Need to re-evaluate the proper size of the breaker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634163&prj=479&rqi=OXzRRkkAbPeyTlRgHHa6u9Phcj
GI-104 | 889d285f-8970-4bdb-b86f-daf794e7ffd3 | SV18-1 | 479 | AMER | Open | P2 Medium CX | daniel_chavez@fsttechnical.com | 2026-08-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | UPS_X3 (Mechanical UPS's) for the below skids require an expansion card in order for the MSB interface to be integrated. UPS_B_3 UPS_C_3 UPS_D_3 UPS_R1_3 UPS_A3 UPS_E3 UPS_F3 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634136&prj=479&rqi=qIL1MxB6uLhXBQqQgfHxrNhkWH
SOR-257-003 | 60c0e82e-4a4f-482b-ac47-fe81181de07e | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Investigate/troubleshoot and rectify the On and Off low battery alarm for 1UPS_F3 that is showing at DCOS. The actual battery readings at HMI are normal and not showing low battery alarm at the UPS unit. However, in the DCOS is showing battery alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633723&prj=479&rqi=TSNCK89NHjm2rVQcrnNY8TsKcw
SOR-258-001 | 62c370c5-b948-433d-804d-c09742173f15 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [7 empty] | The MAUs Roof FOH, 1MAU_R1_1 & 1MAU_B_2 have had numerous alarms on low chilled water flow, inhibiting the dehumidification and heating modes of operation, Suspect the chilled water strainer to units is blocked. Issue Raised on Facility Grid to investigate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633741&prj=479&rqi=XLhR6ATKAGU8uFw67Z2JZb2KYV
SOR-257-001 | 43f0c7db-6776-4e3b-a656-153d85e753b3 | SV18-1 | 479 | AMER | Open | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Investigate the missing battery voltage readings at DCOS. The reason might be the modbus register from the UPS wasn't the same with the DCOS. Note: The issue is also the same with 1UPS_A3/E3/F3/D3.- Delta needs to resolve the issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633434&prj=479&rqi=uH4kGStCGwfMmN8wuOCBz4Z4P7
SOR-257-002 | 1ff19429-7271-48c4-98cc-d111266493b4 | SV18-1 | 479 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-08-13 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [7 empty] | Hanley to provide the missing terminal block for breaker auxiliary contact for 1UPS_X3 Breaker input at 1MDSB_X. The breaker auxiliary contact will provide information to the UPS_X3. The missing terminal block is applicable for 1MDSB_R1/B/C/D | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633580&prj=479&rqi=796BwMOUcvgYUNJaIo5Hzrmiov
SOR-255-007 | 5ba5e1d8-d6b1-4556-9482-e1e76754ae04 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-08-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | The modification you rightly completed to the units to avoid drawing in FOG into the OSA air section, since this air is heated in the first section with an electric heater. The eliminator (photo for clarity is attached) is now clogging up with air borne dust. Can you please have one of your guys tidy this up so the filter can be easily removed for cleaning and/or replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632365&prj=479&rqi=d6KanBb8AS8Xcl7OcfDrzoKHBK
SOR-255-006 | 724b7ff6-071a-481b-92f2-7a5a9f1e7e60 | SV18-1 | 479 | AMER | Ready for Verification | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-31 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | CMS humidifier has been attributed to High water consumption, please review the current design with a view to improve water consumption. This applies to all units | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631845&prj=479&rqi=vcLp9ThhhZa2Nk9aBbV60lnRLE
SOR-255-004 | d8b83496-dd32-447a-8e23-5024a61c1bc1 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-31 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [7 empty] | Missing Auto/Manual label at the HMI for the following. 1. 1MSB_Z 2. 1MSB_A 3. 1MSB_E Replace the phenolic label that will include the missing Auto/Manual. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631734&prj=479&rqi=zI9FflG8gZ0Roe1NP36npyQ7Wm
SOR-255-005 | 7569f6d6-e699-4a0b-8696-32c101d79453 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-31 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [7 empty] | Replace the defective Phase sequence relay at 1MSB_F | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631735&prj=479&rqi=dDZCXkV4nexb5XEFpXJUTIdrch
SOR-255-003 | c1c16f33-e3f2-4dbb-8916-5c6e8ab11020 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-31 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [7 empty] | Check the loss of PM3 PQM communication with the DCOS in 1MSB_F | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631730&prj=479&rqi=HPcsRwaey5ABp3URqzX9vvY0kY
SOR-255-002 | 4703bd9c-0858-447d-a8cf-5bf18d5480e6 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-31 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [7 empty] | The maintenance mode illuminated selector switch doesn't work at IOB breaker for 1UPS_A2 and Q09 OUT TO 1LBSB at 1MSB_A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631729&prj=479&rqi=k6k8ZraMmKXAHT4zen8uKw5NDu
SOR-254-004 | 02d5f842-55a2-40a8-ad32-6e943339fde6 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Jessie_Salita@fsttechnical.com | 2026-07-29 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Side cover canâ€™t fix at 1UDP_A1_1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631336&prj=479&rqi=UbH4YA6CCRoaD9pN8748VDxH0k
SOR-250-004 | b5a5fce1-017f-4e5d-9f69-eae0ef116add | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | All of the TRANE heat pumps Condensate Pumps in areas A, E & F , condensate pumps discharge connection leaked on start-up- Therma repaired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630601&prj=479&rqi=KS3SOU3laJSy49382OsIwcS5LU
SOR-249-001 | 29bba75c-39f8-4f98-9d75-f2bc4718442d | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-21 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [7 empty] | Request of information on missing indication at DCOS for input, output and MBB breaker status for 1UPS_X3. Applicable for all 1UPS_A3/E3/F3. Note: Phase 1 doesn't have also the Breaker status at 1UPS_X. It might also, apply as well. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630209&prj=479&rqi=zpvIKHN4QxKXLD4jrWGYmDBJ9v
SOR-248-002 | 609cb69b-cba5-49ba-8601-e8303d5e745d | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [7 empty] | Powerhouse A "VESDA system" the UPS side of the PH: the orifice on the sniffer Pipe EOL is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630040&prj=479&rqi=hz5afalpEdYiiGfIoF9UDmIGUN
SOR-246-004 | 6cda2dd0-a299-478f-ab92-84ac093cc546 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-16 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | PDU voltage monitoring to be changed: From: Phase to Neutral To: Phase to Phase. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629796&prj=479&rqi=b9xHXZAWqnIEOcP9tcZOKnVBXO
SOR-246-005 | 12564ecb-48d6-460c-9016-cd27cffcc5ad | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-07-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [7 empty] | The cover 1RPP_E1_2_5 are the incorrect size resulting in the exposure of the breakers for the branch circuits 69 and 71. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629799&prj=479&rqi=KpjKGr0vzd0GUsklf7Egw5rsBe
SOR-242-007 | fd4420ae-80a6-4f9d-91dd-9c4cb81ea3bf | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-12 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [7 empty] | In MPS interconnection wiring between 1MSB_X and 1UPS_X3, there was a control cable for input to PLC for 1MBB signal for 1UPS_X3. The 1MBB breakers are located in 1MDSB and 1UMDSB_X. There's no cabling between these two switchboards to 1UPS_X3 for 1MBB indication to UPS. Please advise how we can get the 1MBB input signal to PLC. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628790&prj=479&rqi=fGsxqYJnYljO6Y5jMnok3OvRVv
SOR-242-006 | 3545aecd-c65d-47e9-a07b-28fd72b4d157 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-12 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [7 empty] | 1MTS_Z2_C was added recently at 1MDSB_C. In order to accommodate 1MTS_Z2_C breaker required which is 250AT, Redwood took the 250AT from 1MAU_C_3 and used to 1MTS_Z2_C. The 1MAU_C_3 transferred to 150AT breaker which was spare breaker before. It satisfies the Overload settings for 1MAU_C_3 but the short circuit and Instantaneous canâ€™t set to 2500AT which is the required setting. The minimum setting is 1500Amps only. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628783&prj=479&rqi=CBKItPn1EyPJMclNj3I84qUroY
SOR-242-003 | e274be9c-306b-444f-ab7e-6bd71ff52d12 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [7 empty] | 1MTS_Z2B breaker at 1MDSB_B can't set the Overload protection to 225Amps as per Protection Coordination. The trip unit was 600AT and the minimum to set the Overload protection was 240Amps. We might replace the trip unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628780&prj=479&rqi=utMfZu019Xp0Yx6otTM2ZK0Htz
SOR-242-004 | e7bcf0d7-31a7-4e3d-ac98-6e41fa10f33f | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [7 empty] | The 1MAU_Z_01, Q11 at 1MDSB_Z1 breaker can't set the Overload Protection, to 60Amps per the Protection coordination study. The breaker was 250Amps and the minimum to set was 100Amps. Need to replace the CB to 150Amps. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628781&prj=479&rqi=75BIWZdoXKVUjBxoQ4UZPZF8HM
SOR-242-001 | 1dd525c0-a85a-4e87-aac0-02aaa12a501f | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | Generators All Generators vibration isolators - the bushings are damaged and needs replacing on the guide associated with this assembly. Cummins have agreed to replace all of them. Issue raised to trace to closure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628773&prj=479&rqi=PY28jLCuWE4xanJiUhASOLpplf
SOR-241-001 | 38073039-0067-4e74-b5ee-ab8df611fa3a | SV18-1 | 479 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Replace the failed rectifier for 1UPS_A2 that was found during the load banking. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628756&prj=479&rqi=yEpZxoac2gdx8ghNW98E9zTsp6
SOR-239-001 | a4680f03-f18e-49e4-8d9e-3e0ffcd9fabe | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  |  | equipment | Fire Alarm |  |  |  | 1. VESDA unit started and air flow-maintained constant, but unit did not normalize- programming required. 2. Install of VESDA piping at PH door diagonal to VESDA equipment is incomplete, variety of deficiencies noted: a. Pipe not glued to valve, b. Missing air cap, c. Missing valve, There is a deadline of 7/17 for the completion of this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628435&prj=479&rqi=KNlS2df8vuvCnkzYlIWe8VYMTu
SOR-239-002 | 2b0c82ff-2de0-439a-b11b-b0ebed7a51a1 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  |  | equipment | Fire Alarm |  |  |  | 1. VESDA unit started and air flow-maintained constant, but unit did not normalize- programming required. 2. Install of VESDA piping at PH door diagonal to VESDA equipment is incomplete, variety of deficiencies noted: a. Pipe not glued to valve, b. Missing air cap, c. Missing valve, There is a deadline of 7/17 for the completion of this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628438&prj=479&rqi=zMBZjaG5w8VvxZB8zgoZkUBPUK
SOR-239-003 | f91e8b61-cbc3-4282-9f30-6ed288d1cfc0 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-07-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  |  | equipment | Fire Alarm |  |  |  | 1. VESDA unit started and air flow-maintained constant, but unit did not normalize- programming required. 2. Install of VESDA piping at PH door diagonal to VESDA equipment is incomplete, variety of deficiencies noted: a. Pipe not glued to valve, b. Missing air cap, c. Missing valve, There is a deadline of 7/17 for the completion of this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628440&prj=479&rqi=BhOPShorwCF5bRzoeDbZEnsfeG
SOR-238-001 | a893dbe7-377b-40d4-8c54-63e00b3c9d24 | SV18-1 | 479 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Investigate and rectify the SCR abnormal fault alarm. Note: Applicable for the following. 1. 1STS_A2_1 2. 1STS_A2_2 3. 1STS_A2_3 4. 1STS_A2_4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628205&prj=479&rqi=BxGkkfaVq6OQ3UYYFsIzk1iwbN
SOR-236-004 | 79cef703-a371-4717-acf1-fd326524e42c | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | The motherboards in the A2/E2/F2 RPP panels on Level 2 have screws of incorrect lengths. The screws in the 44 1RPP_X2_X _X blocks below have this issue A Block: 22 E Block: 2 F Block: 20 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627627&prj=479&rqi=AEh5NyKZGNDYzTyzAeXuGQ7SiF
SOR-236-003 | 3facb9c0-9de1-4aed-8e5c-d2aefa544a47 | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | The labels for phases are incorrect and will need to be replaced for RPP's. The labels should show A-B-C from left to right. Note: This issue is applicable to the additional 28 RPP panels added after Bulletin 1. 18 in Block C 10 in Block F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627616&prj=479&rqi=8FipSj92wncTMUGVuKHDTnvN2a
SOR-235-002 | 620c24a1-5388-42fb-89ab-3dcdca399317 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | To transfer the cables from 1MSB_X external status of the RIB breaker to 1MDSB for 1UPS_A3/E3/F3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627571&prj=479&rqi=hKs0fw3ytdtGvJefeczVJvXGlB
SOR-235-001 | 1eb6a94b-3f6e-40b0-bc6a-81afa88e4434 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Current at Phase A is not showing readings while Ig showing current which is not correct.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627455&prj=479&rqi=nNESo2AZWczOqGLUitVK6b8uGY
SOR-233-002 | a04cb4a8-22cc-4931-a0ec-26b33ffb75a9 | SV18-1 | 479 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-28 04:00:00.000 +0400 | TRN - Trane |  | Installation not complete | Commissioning | [7 empty] | Warning sticker missing from heat trace j-Box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627185&prj=479&rqi=sJz6y12UmsDcJWrkbhlzBgjqhP
SOR-233-001 | 80d8a305-baf8-4ffa-ae1d-de2cb2072a8f | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-27 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [7 empty] | Chiller 1ACC_A_04 Chiller Pump Non-Drive Bearing noise, and today when we ran it at low RPM, we realized it has deteriorated to a point where the bearing will need to be replaced. Trane have taken to bearing details from the pump nameplate and have ordered a replacement. The work to change the bearing can be completed with the pump in situ. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627184&prj=479&rqi=LM9EZezp8b6ycND7waGELQ87d5
SOR-230-003 | 386d99c7-f1ee-4b6d-8c24-2375ce179a73 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Breaker status at DCOS is not changing when breaker is Open or Closed. Note: Applicable for Gen A & E. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626834&prj=479&rqi=Mv2ZeuBcpEjiJNhx2Xb6wI1mfX
SOR-229-005 | 583bdbf8-7d97-4736-9e05-219aae409de3 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-24 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | When simulating Emergency Stop, the Phase Overcurrent alarm & Shutdown alarm are also initiated and should not be the case. Note: Applicable for Gen A & E. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626836&prj=479&rqi=kVywu5oOHYTYzWG7uF3SNcEjNH
SOR-230-004 | 77e14a00-9f08-4e56-948f-37628b0ede78 | SV18-1 | 479 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-24 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | When simulating the Emergency Stop, the Phase Overcurrent alarm & Shutdown alarm were also initiated, and those alarms shouldn't be activated. We expect Emergency Stop to be activated. Note: Applicable for Gen A & E | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626837&prj=479&rqi=8BQAz0wEJg7L1Y1QvuR2bD1IG3
SOR-229-002 | b6303c98-d1b1-4623-89c8-9a291d64407d | SV18-1 | 479 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Replace the defective CT for Phase A in 1UPS_F1. Note: The defective CT was originally found in 1UPS_A1. The replacement was taken from 1UPS_F1 and installed to 1UPS_A1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626629&prj=479&rqi=h3LioKlyRo3auZj9WkHL8MoK54
SOR-228-001 | f9f34796-8418-46c7-aec7-59cc425ff662 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-23 04:00:00.000 +0400 | Design Professional |  | General Design Issue | Design | [7 empty] | Potential issue with the Chilled water make-up station: The check valve resides on the discharge after the bypass line on the chilled water make-up station, if it did stick closed situation may be difficult to recover. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626547&prj=479&rqi=qJPYspBiE92Rp1fvKMVoC5cswA
SOR-225-003 | 61d30bd4-95ec-4d84-9a4b-3c08222f68e5 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [7 empty] | Investigate the fluctuating voltage reading from 476V to 482V from 1UDPR_C2 breaker which should be stable voltage from 1UPS_R1_01 & R1_02. The breaker voltage sensor might be an issue. The voltage IOB from 1UPS_R1_1 & 1UPS_R1_2 are stable with voltage reading of 479VAC and the voltage should be the same with 1UDPR_C2. The voltage reading at 1UDPR_C1 is the same with 1UPS_R1_1 & R1_2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625695&prj=479&rqi=1H8aD9G3mqg1255NL4omB9b7w3
SOR-225-004 | d8c02dcd-0556-46f6-9426-1af4f2bd56cd | SV18-1 | 479 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Replace the defective MCU card for 1UPS_A2. In order to troubleshoot and rectify the issue. Delta took MCU card the 1UPS_F2 and installed in 1UPS_A2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625698&prj=479&rqi=96oiBIrCL9zNBs5I5rQuYcS7SQ
SOR-222-004 | 2b8ca445-35e1-49ec-be3c-ed5171debec4 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-13 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | This week we had to split the chilled water system to facilitate chiller load bank testing. Part of the test we had to valve the headers feeding the 1CRAH_D_01 THRU 1CRAH_D_12. Since it's an open space, we left the units running to help cool down the areas. When we reinstated the chilled water system back to normal configuration, the Vertiv CRAH alarm for "loss of Cooling" alarm had to be manually reset before the units returned to normal cooling operation mode. FST think this alarm should be an auto reset. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625201&prj=479&rqi=AaL5te6fpsAdot5H33kBZ4xoRw
SOR-222-003 | 08fe9639-ab5b-4d2e-9b57-934698568c93 | SV18-1 | 479 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Troubleshoot and rectify the SCR 1 SRC OVER TEMP WARNING during load banking and the load is around 780amp at 1STS_D1_4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625198&prj=479&rqi=8domWhBB9AV9nsQRRDKfRfcYPQ
SOR-221-007 | d507b2b7-e745-4580-a9d5-3acb481e85ec | SV18-1 | 479 | AMER | Open | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-06-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [7 empty] | 1STS_A2_1, 1STS_A2_2, 1STS_A2_3 are missing knobs on top of the A2 sets in the top hats and 1STS_ E2_3 has the missing hardware detailed below. -13 screws missing meant to secure back cover. - 8 top hats knobs either missing entirely or is missing the screw that mounts it inside the knob. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625173&prj=479&rqi=Ha2CQT9wURjCCjBFsPLzHZpDUo
SOR-220-001 | e0c6982e-f5c2-4819-b8f6-20244809c43b | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Replace the breaker from 20AT to 15AT for Heat Pump at 1PNL_R1_1_H1 feeding HP_A , E and F according to the manufacturer recommendations. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625039&prj=479&rqi=7P9vSuKTbiBVwSuq8rCwbcT1xB
SOR-217-003 | 716cbc47-952d-4b89-9268-60586bc74fc7 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Provide missing power two (2) units module for 400KW for 1UPS_A3, 1UPS_E3 and F3. The installed modules are good for 300KW. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624353&prj=479&rqi=aIgqYMP0PUiRsSH3RP2AIYb6gG
SOR-215-003 | 50e41bec-f7e1-4119-bde1-6e4ca6b542ef | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | To find the missing wire for SKRU release signal. The wire 2015 & 2016 are terminated at 1MSB but on UPS terminal, the wires can't be found. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624192&prj=479&rqi=aMq21xehw8erYhS77aQjDSjX9Z
GI-102 | c598fc47-7a5e-452c-a0bd-28e1ebd0158c | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-05 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [7 empty] | p3E-Tech surveyed leak Detection tape located in PHs A, E, F: MPS-installed leak tape is missing the EOL (â€œEnd of Lineâ€) terminators for all of the sense lines in these PHs. Issue raised on facility Grid to Track to completion. E-Tech can install when parts are received from MPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624162&prj=479&rqi=3pgD1d8Ji96fhO1OOaGVhAPHCT
SOR-214-001 | f08d6230-67af-48d6-9b18-6eca7b6a7ad6 | SV18-1 | 479 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-06-04 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [7 empty] | The LTD settings of the PRX10 LSI trip units in the Eaton breakers in 1UDP_A1_1., 1UDP_A1_2, 1UDP_E1_1, 1UDP_E1_2, 1UDP_F1_1, and 1UDP_F1_2 are fixed and cannot be adjusted. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623970&prj=479&rqi=NP4ZrsU6YbxXtH4UcKw53Ft8lM
SOR-213-002 | b49bd804-1424-4840-9df7-382f6ed05951 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-04 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [7 empty] | Provide missing settings for 1UDP's_A1_1/2; 1UDP_E1_1/2; 1UDP_F1_1/2.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623877&prj=479&rqi=YU6z8iofACrGP4A9liB7JNsuTf
SOR-213-001 | af7b0d1a-1a27-4055-9959-ed3cd19f4d6e | SV18-1 | 479 | AMER | Closed | P2 Medium CX | jordan_dubose@fsttechnical.com | 2026-06-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1RPP_F2_1_2 | RPP - Remote Power Panel |  | RPP-208-250-60 | The 1RPP_F2_1_2 is missing the lug cover. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623861&prj=479&rqi=IwROUCJVdzkTItDn3nBl5gixsL
SOR-211-006 | 873b6ec5-dde1-4463-9335-1d6028b57091 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-02 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [7 empty] | Replace the defective CAT6 cable for gateway 2 to switch at 1MSB_A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623581&prj=479&rqi=a3BFnQbpbbXvCeBzzQHmwZQ1By
SOR-212-001 | ed26c05d-c5f3-48d5-ad00-a541a091e6a2 | SV18-1 | 479 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [7 empty] | The door is difficult to open at skid R1 front left door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623713&prj=479&rqi=XD4XVYv2SgYhclGU2nP98Hsg4v
SOR-211-001 | cd7aad6e-e1b9-4ca7-90a6-27178fa81e6b | SV18-1 | 479 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [7 empty] | The door is difficult to open at skid D front left door. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623554&prj=479&rqi=SoFSJ6gyWGh0hGpzg4g6QXyzKd
SOR-211-003 | 45aa454b-c8d7-48ba-b2b6-1a304dbb0c39 | SV18-1 | 479 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-06-01 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Engine hours at the local HMI are not the same with the DCOS. Information for both should match. This is applicable for the following. 1. GEN B 2. GEN C 3. GEN D 4. GEN R1 5. GEN Z | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623572&prj=479&rqi=ikxlKD3xlYQoaris38ZRgDwYdx
SOR-256-002 | 3fcbefd4-08fd-4e7f-a068-1d76a5a8607d | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-01 04:00:00.000 +0400 | TRN - Trane |  | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | Minor damage to Armaflex Insulation Damage, Needs Patched. Applies to Chillers 1ACC_E_19 1ACC_E_20 1ACC_F_22 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623540&prj=479&rqi=dxYS9TSP9GdRs7QDVgt6hITY19
SOR-211-002 | abb474cb-59f5-4588-99e2-39f0d3a74345 | SV18-1 | 479 | AMER | Open | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-06-01 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | The labelling for the Q#'s of 1MSB_A/E/F is different in the SV18-2 submittal than in the engineering drawings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623567&prj=479&rqi=FHFeBZc5NYsLVFKpzBpTJYvPt8
SOR-211-004 | 4c3bfd10-dc25-4f3d-92de-5fb043964495 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-06-01 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [7 empty] | Powerhouse F: 1CRAH_F_15 SV18.1RLEM_F_LEAK_15 Leak Detected - Leak detection in alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623577&prj=479&rqi=PFCE2IcWFljg0YGcD8kVKw2WAi
SOR-210-001 | c4251d78-5ee1-4a79-82b8-db2b1038cea7 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Provide the connecting bar for Transformer tap 4-5 to compensate the voltage drop on Transformer output. Provide- 48 pieces. 1PDU_B2_4 1PDU_C1_4 1PDU_D1_4 1PDU_D2_4 1PDU_E1_1 1PDU_E1_2 1PDU_E1_3 1PDU_E1_4 1PDU_F1_1 1PDU_F1_2 1PDU_F1_3 1PDU_F1_4 1PDU_A1_1 1PDU_A1_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623488&prj=479&rqi=snwdLPFeNnxhhkIIbdHOU1i7Vg
SOR-209-001 | acca22d9-d560-45e2-877f-ef599e15c78c | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Provide the missing Ethernet cable for the following. 1. 1HP_A_1 and 2 2. 1HP_E_1 and 2 3. 1HP_F_1 and 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623393&prj=479&rqi=tKrWuNVeF8GwX4BRXlFu24nrmj
SOR-208-001 | 594c027d-7350-4583-a345-8f240a2f5196 | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-05-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1RPP_C2_2_2 | RPP - Remote Power Panel |  | RPP-208-250-60 | There is a damaged door in RPP_C2_2_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623240&prj=479&rqi=ggD3aqVZG0e9JCVyobgf3oBw4Y
SOR-207-001 | 906e3565-2adc-4f95-9742-9ce656daecf1 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | The clearance of 1â€ phase to phase wasn't maintain for B & C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623150&prj=479&rqi=u2aAA930kBlgKcf0QOwD6gEwST
SOR-206-003 | 74fe5ad3-e067-4356-b5c1-d9a3052eb8c1 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-25 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [7 empty] | To provide new updated setting to reflect the breaker model Square D instead of ABB for the following PDU's 1. 1PDU_A1_1. 2. 1PDU_ A1_2, 3. 1PDU_A1_3 4. 1PDU_ A1_4. 5. 1PDU_E1_1 6. 1PDU_E1_2 7. 1PDU_E1_3 8. 1PDU_E1_4 9. 1PDU_F1_3 10. 1PDU_F1_4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623058&prj=479&rqi=zN2WKetYzVrTEUDPkpiXj5JIla
SOR-206-001 | 7f718152-eeb9-4ec2-a004-2d61c57d1360 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-22 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [7 empty] | Provide missing protection settings for the following. 1PDU_B2_4 1STS_B2_4 1STS_C1_4 1PDU_C1_4 1STS_D1_4 1PDU_D1_4 1STS_D2_4 1PDU_D2_4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622857&prj=479&rqi=QzE4jDJlZarppruii1wzOc8nKd
SOR-206-002 | cbaa4798-f71e-4d0a-88f2-89eb9d03928e | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-22 04:00:00.000 +0400 | Design Professional |  | Commissioning Issue | Commissioning | [7 empty] | Provide missing protection settings for the following. 1UTX-F3-L1 1UTX_A3_L1 1UTX_E3_L1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622879&prj=479&rqi=HQFhwgZGVBPuhtvFvDFEkXASFv
SOR-201-002 | 5937f90c-23c2-45ff-8f4f-56c765934465 | SV18-1 | 479 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-05-16 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  |  | system | CHW System |  |  |  | The following Chilled Water Riser, Onicon flowmeters need to be replaced FT401 FT601 FT903 As they are reading outside of the 10% range. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622028&prj=479&rqi=wDyq1tzNi48lZ72E7OwdXb54rG | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-200-001 | 89e27bd6-fceb-414d-96cb-cfdcc3b4eb46 | SV18-1 | 479 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-14 04:00:00.000 +0400 | Equinix Ops |  | DCIM BCM Issue | DCIM | [7 empty] | Tested all the CTs (100% with 72 CT's) for each panel and found sensor 37 to 42 doesn't show current readings in BCM. This is consistent to all 18 panels. Completed as follow's 1RPP_B1_1_1 1RPP_B1_1_2 1RPP_B1_1_3 1RPP_B1_1_5 1RPP_B1_1_6 1RPP_B1_1_7 1RPP_B1_2_1 1RPP_B1_2_2 1RPP_B1_2_3 1RPP_B1_2_4 1RPP_B1_2_5 1RPP_B1_2_6 1RPP_B1_2_7 1RPP_B1_3_1 1RPP_B1_3_2 1RPP_B1_3_3 1RPP_B1_3_5 1RPP_B1_3_6 1RPP_B1_3_7 1RPP_C2_1_1 1RPP_C2_1_2 1RPP_C2_1_3 1RPP_C2_1_4 1RPP_C2_1_5 1RPP_C2_1_6 1RPP_C2_2_1 1RPP_C2_2_2 1RPP_C2_2_3 1RPP_C2_2_4 1RPP_C2_2_5 1RPP_C2_2_6 1RPP_C2_3_1 1RPP_C2_3_2 1RPP_C2_3_3 1RPP_C2_3_4 1RPP_C2_3_5 1RPP_C2_3_6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621917&prj=479&rqi=Anpp0StJ0dkeVo8oCYqLnxwUpS
SOR-195-001 | c17fc6ce-654f-4347-b65b-c0e86d90ab6f | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-05-08 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [7 empty] | Replace the breaker 2/0 to 350 lugs to 14 to 1/0 lugs to fit the 2AWG that was pulled for 1UTX load at 1UMDSB_A3/E3/F3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621010&prj=479&rqi=G9UDVXAd7RDsNa37daepBUQCCl
SOR-193-002 | 5778f4fb-6fee-48d1-90d9-494a8a51eae3 | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-05-06 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | FST observed that they are several screws in the different 1PDUs that are stripped. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620627&prj=479&rqi=BIHfgfPKHm8NqmmbNpuadd6dDk
GI-094 | 60db3cd4-ea82-407c-87b2-6881561f7b9d | SV18-1 | 479 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-04-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [7 empty] | Generator Output Breaker is missing the K1 kirk key and cylinder. K1 Serial Number is 64393. This is applicable to GEN_A, GEN_E, & GEN_F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619964&prj=479&rqi=fRXE6d3YAuIJKSirKzgaRBMvmj
SOR-187-004 | 2284976f-3649-402b-977f-f1b61b606db2 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Incomplete Connections | Commissioning |  |  | equipment type |  |  |  |  | Perform neutral connection modifications to all STS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619816&prj=479&rqi=YaKs1zCVrMSF8b0TKOnuOZTimt
SOR-187-001 | 48203245-bd03-4410-896f-2fcc1e11d3c1 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Provide missing parts for breaker key interlock. 1. Missing TABS for breaker drum kirk key Gen A/E/F 2. To provide whole set of kirk key for Gen A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619793&prj=479&rqi=qiKq8tvgrxCDIgr5CyGsakvjqx
SOR-187-002 | 5d1fa015-008b-4dc5-85f2-c7f6dd237154 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-28 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Bolts missing on the following units: 1CRAH_D_12 1CRAH_D_10 1CRAH_D_09 1CRAH_D_05 1CRAH_D_04 1CRAH_D_02 1CRAH_C_10 1CRAH_C_09 1CRAH_C_08 1CRAH_C_07 1CRAH_C_04 1CRAH_C_03 1CRAH_B_01 1CRAH_B_02 1CRAH_B_03 1CRAH_B_04 1CRAH_B_07 1CRAH_B_08 1CRAH_B_09 1CRAH_B_10 1CRAH_B_11 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619805&prj=479&rqi=FeGbWN4665bKTfglYgabeinatG
SOR-186-002 | 70baf896-eca0-4ec5-bce4-753211013617 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-27 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Power Houses A, E & F - Trane Heat Pumps Trane representative reviewed the panel wiring and discovered the units have been set up for BACnet so they will need a gateway to change the protocol, issue raised in facility grid to track this to closure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619646&prj=479&rqi=8och30ozajevYGTAWkX2VpNxYa
SOR-186-003 | 448fa63f-641b-4940-b9f5-e0cee869171c | SV18-1 | 479 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | To perform the neutral modification for STS to meet Equinix standard. Applicable for all STS for Block A/E/F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619661&prj=479&rqi=VXHmSKghi8SfgI75qAiTpsbn0z
SOR-186-001 | babf8f44-0b35-429b-bbdf-4e9301b90b0a | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Power Houses A, E & F Heat Pump - Smoke Detector Circuit: The power wire at the smoke detectors at the Trane WSHPs has not been pulled. Currently they have only pulled the control wiring that shuts the units down. See Attached Photo's for clarity | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619586&prj=479&rqi=41L8BRJjESln8PZJIEBhD5xbgs
SOR-183-002 | ed32e159-d3e7-48c9-b098-cb11916a74ea | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [7 empty] | Two ceiling junction boxes in Skid K are incomplete and/or not labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619421&prj=479&rqi=uVzEaS7CkeBtFPQuiMAwvI5WHx
SOR-183-001 | 6b1357c8-e99b-4557-9311-66db2ac0c51c | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [7 empty] | In 1MSB_K there are missing bonding cables to ground the top hats in the sections 05A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619372&prj=479&rqi=0znhbSVN5fLTqoC8tmiVHUWY7R
SOR-181-001 | 155221b9-72ce-4703-87ec-414361bd4122 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1RPP_C2_3_2 | RPP - Remote Power Panel |  | RPP-208-250-60 | To provide the missing bar and bolts connecting to the main incoming cable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619258&prj=479&rqi=SserRxd7IFQo5Y280nxpFD7IW7
SOR-182-002 | 34988c65-6a2f-478c-a7b1-fdce68408efc | SV18-1 | 479 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-23 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not complete | Commissioning | [7 empty] | In 1UDP_K2 the lugs for the termination to 1STS_K2_3 in BKR#4 are incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619277&prj=479&rqi=Qb7wNgiNm3GlUN2ixj5EstOYuj
SOR-182-001 | 2757d90c-f792-4ede-b2d8-4d718373813b | SV18-1 | 479 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-23 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning | [7 empty] | In 1MDSB_K the lugs are not correct for the 1PNL_K_HP_BKR & 1UPS_K3_BKR terminations. Hanley to send (3) lugs for #1/0awg to support the 1PNL_K_HP_BKR and (6) lugs for 3 #500kcmil to support the 1UPS_K3_BKR | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619274&prj=479&rqi=mtXAfihB8FKCD7792Ctqy12rh5
SOR-180-003 | 07a7fef0-a2d9-4935-a4a4-7f414e1c382a | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-22 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [7 empty] | Provide missing SKRU key (K3) at 1UMDSB_A3/E3/F3 for UPS_A3/E3/F3. K3 Serial Number is 6440 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619148&prj=479&rqi=CkNsVwz3LwWHV3xaIZHvhS5HuW
GI-091 | 005d0d9b-c98e-4bd8-b3a1-851d0eda4135 | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-04-22 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS | [7 empty] | aalogmonitor is still showing errors and warnings in the platform | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619141&prj=479&rqi=us6rdIcEoJKkc5qYTOrN3G6pvu
GI-092 | f20067d5-43d1-4a58-bb9b-5d4a837d7a5a | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-04-22 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS | [7 empty] | topserver is reflecting several errors & warnings & hundreds of connections | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619142&prj=479&rqi=kRl0z77tbIPd53m0mX0ybbOPDD
SOR-180-001 | d23aa271-e319-4e10-945a-923bd8d8c11e | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-22 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [7 empty] | Provide missing SKRU key (K7 & K8) for 1MSB_A for 1UPS's. 1. 1UPS_A1- 3 pieces 2. 1UPS_A2- 3 pieces K7 Serial Number is 64155. K8 Serial Number is 64156. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619146&prj=479&rqi=AQPzMHuQbsTv38tTFq8HsNpKLG
GI-088 | 65b50e8a-dd99-48ed-8d02-df76d897c3bb | SV18-1 | 479 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | On Powerhouse Skid A; Door B does not fully close/latch. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618917&prj=479&rqi=tCMnxcDScnQGGuJLnrJz9INCrL
GI-089 | 0a9c6960-560a-43b3-8252-3b42dfe79020 | SV18-1 | 479 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | On Powerhouse Skid A; Door D does not fully close/latch. Furthermore, the door is not level. The door contact was removed to prevent further damage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618918&prj=479&rqi=3cT6iBBJ6bebXBV25XWJyuzLYM
GI-090 | f256d32b-046c-4438-9065-f333629b7d0e | SV18-1 | 479 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | On Power Skid E; the Mortise/Cassette has a short/blown security panel fuse. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618919&prj=479&rqi=sVAfAJW8MuXZK67R0UWwJ0Fm4n
SOR-179-002 | 56af1710-734d-44ce-96de-d821062fefda | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-21 04:00:00.000 +0400 | TRN - Trane |  | Installation Damage | Commissioning | [7 empty] | Armaflex insultation on chiller pumps, needs protection from UV light, it would need to be covered/Jacketed or painted. see attached photo the damage is already occurring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618915&prj=479&rqi=gHIMKlfpLtJ2KhF5umg8NK6mV6
SOR-179-001 | 2a5905db-b234-4a67-babf-04b4d33a078d | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-21 04:00:00.000 +0400 | TRN - Trane |  | Installation not complete | Commissioning | [7 empty] | Chiller ball valve plugs missing issue raised on Facility Grid. Chiller C_12 Supply BV Drain Plug Missing. Chiller D_18 _ 2 X Pump & Suction Diffuser drain Plugs. Chiller R1_01 Suction Diffuser Drain Plug Missing. Chiller R1_01 Supply BV Drain Plug Missing. Chiller R1_02 Supply BV Drain Plug Missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618913&prj=479&rqi=fa6YE4Mlryyxfj1t80sLikJ3kh
SOR-178-003 | 44389618-c29b-4d5c-a5e8-3fc69f126494 | SV18-1 | 479 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning | [7 empty] | The mechanical lugs for 1UMDSB_X3 terminations to Q09 in the 1MDSB_X are incorrect in skids A, E, & F. Six (6) lugs are for the (2) #500kcmil wiring. Six (6) lugs are for the needed for (2) #2/0 ground. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618778&prj=479&rqi=zkbwRpX8fA9fsuQKiJ9J11gton
SOR-178-005 | 0e4894dd-4f72-42c9-8969-dcf588cf1682 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [7 empty] | Chiller 1ACC_C_12 failed following UPS power loss testing. Both control fuses located in the harmonic filter housing and fuses feed the main controls circuit; they blew with the inrush current. there are two sets in series 15 amps in the harmonic filter & 10amp in the power panel. TRANE have agreed to upgrade the 10-amp fuses to 15amp. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618780&prj=479&rqi=8kZD5juQGeUzbypUyLMvctsZl5
SOR-178-004 | 8dd84b13-d3d0-4f8a-90e6-0083f57403f6 | SV18-1 | 479 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | [7 empty] | The current 1PNL_X_HP_BKR in the 1MDSBs in Blocks A, E & F has only LSG ground protection and not the LSIG ground protection required in both the Hanley submittal and engineering drawings. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618779&prj=479&rqi=grP2BU3fzTEvkdwdsk1XRfi197
SOR-178-002 | 0132d646-663c-40e6-8d92-a58905df9125 | SV18-1 | 479 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning | [7 empty] | The mechanical lugs for 1PNL_GEN_X terminations to Q04 in the 1MDSB_X are incorrect in skids A, E, & F. Nine (9) lugs are needed for the #4 wiring. Three (3) lugs are needed to support the #8 ground. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618777&prj=479&rqi=AWbiTouzeAcc9tlmxxQnx3HzRb
SOR-178-001 | e2104719-e3a6-4437-957e-94399f445c86 | SV18-1 | 479 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Missing Components | Commissioning | [7 empty] | 1UMDSB_A3 has mismatching lugs as they have 3/0 - 350kcmil lugs installed but need lugs to support 3 #2 & 1 #8G, 1-1/4"C wiring for the 1UMDSB_A3 to the 1UTX_A3_L1 breaker. Three (3) lugs are needed for the #2 wiring. One (1) lug is needed for the #8 ground. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618776&prj=479&rqi=HvAVbdF5xXjIcNc3MhGxq3edle
SOR-178-006 | f72fa5cf-b490-4513-841f-fbffc066f771 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-20 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [7 empty] | Chiller 1ACC_D_18 Chiller failed on phase loss during IST. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618781&prj=479&rqi=Lukp16jMD9sTQpOQ7CLFwocc1g
SOR-170-004 | a5d3eac6-2948-423a-99d7-40fd5de333d7 | SV18-1 | 479 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-04-19 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | To remove the "Heat Traced" alarm from the General alarm through the hardwire from Chiller control to RIO panel. This is preventing the Chiller lockout every time there was a momentarily loss of supply voltage to the "Heat Traced" circuit which is non-UPS source. Separate the Heat Traced alarm by pulling new cable from Chiller control panel to I/O input at the RIO panel. Etech will program the additional input for DCOS. Note: Applicable for all Chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618674&prj=479&rqi=xS4tuV006eDpw9nkGw8C8rtOky
SOR-176-013 | 99ff0a36-42a8-4e5a-a735-7e6d85886c28 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [7 empty] | MV-1 & MV-2 Power Houses - Air conditioning units Graphic need to be deployed. This issue applies to the following units: 1SUDB3_AC_1: MV-1 North Yard. 1SUDB3_AC_1: MV-1 North Yard. 1SUDB1_AC_1: MV-2 South Yard. 1SUDB1_AC_2: MV-2 South Yard. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618615&prj=479&rqi=gbEIkEkyq39R2qLXYsB6I8a67M
SOR-176-012 | a51d5e29-1072-42c9-9e5f-9da470bb47b4 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | James_Kenny@fsttechnical.com | 2026-04-18 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | This one applies to all TRANE chillers The location of the Thermal Dispersion is not ideal as these switches respond better to laminar flow as opposed to turbulent flow. Chiller manufacturers use Tube Grooving to Improve Heat Transfer The use of grooved copper tubes in chiller systems is a method to enhance heat transfer efficiency. Grooves can induce a swirling motion in the fluid, which helps to displace the fluid and increase the heat transfer rate. This technique is effective when the Reynolds number is between 500 and 5000, as it can lead to a significant increase in heat transfer capacity. The grooved design is particularly beneficial in heat exchangers where the goal is to maximize thermal energy transfer between fluids. The thermal dispersion switch is installed right at the end of the tube bundle, this switch is sensitive the turbulence, please review. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618604&prj=479&rqi=gz0eX1Bj2FUAKmC5K1aeOcZyoB
SOR-174-003 | 84515290-e45b-4767-8bff-a383affea7ac | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | To investigate the current harmonic on B-phase of Rectifier input is high in comparison with phase A & C. The 9.09% current harmonic in phase B is the total for two units of UPS. Phase A & C have almost the same harmonic value of 1.5% average. Take note that we applied 1100KW each UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618587&prj=479&rqi=6BXaHCf33c6abnxeNm4nDeLTfn
SOR-176-009 | 9fc0871a-8dd5-4a41-bf40-e66443abc773 | SV18-1 | 479 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-04-17 04:00:00.000 +0400 | SCH - Schneider MV |  | Commissioning Issue | Commissioning | [7 empty] | The SF6 alarms for Breakers and other compartment wasn't able to get the alarms in DCOS at 1SUDB_2. Schneider will need to verify the Modbus register to match with DCOS. The SF6 alarms is assumed to be the same issue in 1SUDB_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618599&prj=479&rqi=6i3Izzinh7LM8qCaA3c1dkLSz2
SOR-176-010 | b715666b-ea7f-4c0e-8953-3995714453f9 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-17 04:00:00.000 +0400 | Subcontractor |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | MPS to resolve why Skid D Heat Pumps are not responding to their corresponding room thermostats | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618601&prj=479&rqi=DPeFJraPfJJDiaGPUW5wszjh63
SOR-176-011 | e80d8c3f-8ee4-4561-b364-ff92cc98d7c4 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | MAU_D_4 Smoke detection alarm test | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618603&prj=479&rqi=RrNncOZl7KWw88eeZpFhFWxl4R
GI-087 | 763123c0-b312-43f4-a21d-cd0886ad6184 | SV18-1 | 479 | AMER | Closed | P1 High CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | Provide the materials the was taken from STS _F2_1 for the replacement of damaged components for 1STS_D2_3. As follow's. 1. Control cables. 2. Set of control breakers strip. 3. Electronic Modules (Oumar from Delta knows the model. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618602&prj=479&rqi=QOGuvYSyJWpciztOPiiLc2VC3q
SOR-174-002 | 38126590-6ebc-4afd-994e-61d17bceb900 | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | The humidifier sump has gone numerous times into drain down mode, since these units are fed by softened water so the conductivity probe may not be readying reliably, please have your technician check this out to verify the proper functionality. This applies to MAU_R1_01, MAU_B_2, MAU_C_3, & MAU_D_4. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618293&prj=479&rqi=xIokWixw9yUhhLRDCkBFzKPvNV
SOR-173-002 | 4d8a15ff-5aec-44eb-bdbc-b82518d1ff65 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Commissioning Issue | Commissioning | [7 empty] | Investigate the tripped occurred on the breaker 60AT feeding 1TX_R1_2_R1 at SKID R1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618265&prj=479&rqi=bz1cIpHkuho7ZlIlSttOz8dt5j
SOR-173-001 | 552ca08f-e9f1-4c90-b97b-f33107a30d2e | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-14 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [7 empty] | 1ACC_R1_02 Compressor 3 Fault - Compressor failed The compressor failed the bearing levitation recalibration tests. The chiller sub cooler circuit the liquid solenoid valve & EXV were creating a lot of noise/hammer, it was found the chillers number 3 compressor was running with the suction isolation valve closed, due to an actuator fault. Tech support asked the Trane service engineer to isolate the compressor for troubleshooting tomorrow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618182&prj=479&rqi=Jef5RuBnfpAGVoyy1Px1w0iLdm
SOR-172-004 | 9d432cea-1ecf-45ad-b608-584a7580e705 | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning | [7 empty] | Skid D Heat Pumps are not responding to the thermostats. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618007&prj=479&rqi=IdcILuKFz0kg4rjVZ6NPsKB9uW
GI-086 | 327d6bc6-1d0e-40f3-8a22-017bbd1264c0 | SV18-1 | 479 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-04-11 04:00:00.000 +0400 | Ver - Vertiv HVAC |  | Component/Equipment Failure | Commissioning | [7 empty] | Control board was taken from one of the 1st floor MEGA CRAH units. Note that the asset nomenclature has not yet been identified for this unit, but the serial number for this unit is T26C006449. This was to resolve Issue #762. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617874&prj=479&rqi=hK354pbVVQuoulLycxiIZoti66
SOR-170-001 | 7bf7edf0-303c-4c83-b109-1c7d3abb8043 | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-10 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS | [7 empty] | In DCOS the "Electrical" screen cuts off the kW values for the PDUs on the right side of the screen. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617828&prj=479&rqi=ErdX4vML41boy8HjM5lvLvTjVZ
SOR-169-003 | 92ad1537-dac2-4cde-afb7-a35d63372380 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | James_Kenny@fsttechnical.com | 2026-04-10 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | A T3C A78 General Heaters Protection Alarm notification associated with loss of Heat Trace activated during power transfers for the following units: ACC_B_07 ACC_D_17 ACC_R1_01 ACC_R1_02 If the chiller is in idle mode, this alarm caused the chillers to lock out on DCOS. To avoid a reoccurrence of this issue this point need to be changed to a monitored point. TRANE to provide information on how they recommend the points to be managed, this is required for the associated RFI | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617786&prj=479&rqi=90HADpqgtP34OC3nowGRRmApja
SOR-168-006 | 20e9556e-2fe8-4383-8420-9fe0fa285cd0 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-09 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [7 empty] | PRE-IST TESTING CHILLER 1ACC_C_11 FAILED ON LOW FLOW | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617631&prj=479&rqi=QqxUO5Oj2yVqZTDZ9OK28eXE6M
SOR-168-007 | 29fde6c2-5a05-4e9e-82c7-e574d327ff49 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-09 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [7 empty] | PRE-IST 1ACC_R1_02 FAILED ON MOTOR BEARING ALARM | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617632&prj=479&rqi=3wPHwa8vKxg2pc75btVzFjIHaR
SOR-166-010 | 24934c21-9d37-4567-ba6d-2e98036eb38c | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | MAU's depict wrongly 2 supply fans There is one supply and one return Fan | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617564&prj=479&rqi=JmPWVLFIZY8CJdTIodz147r5TI
SOR-166-006 | 3fc34a2f-8b4e-44d9-8593-7f387297365e | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [7 empty] | PRE IST TESTING Chiller 1ACC_B_08 FAILED ON LOW FLOW THROUGH NORMAL OPERATION | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617525&prj=479&rqi=4N9Z63DKSWdUQHUJOQxQ1HoXDp
SOR-166-008 | c80e3393-8738-4997-ab68-90d4894a7ffa | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [7 empty] | PRE IST TESTING Chiller 1ACC_B_08 FAILED ON LOW FLOW FOLLOWING BEING RESET AND RESTARTED & THROUGH BEING SEQUENCED ONLINE | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617527&prj=479&rqi=uRQmyZn1KqpKkHkl6xbVMcu8RG
SOR-166-003 | c311c4b6-8546-494f-bcb9-2602ca640e65 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [7 empty] | PRE-IST TESTING Chiller 1ACC_R1_02 FAILED ON LOW FLOW DURING BLOCK R UTILITY POWER TRANSFER TO GENERATOR | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617522&prj=479&rqi=jxGJnMKG5xbmOflG0QZobYNvOH
SOR-166-009 | 847b5281-0424-4cd5-b2b1-d0ae5f22df31 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | PRE-IST TESTING Chiller plant manager dialed up to the sequencer all 18 chillers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617528&prj=479&rqi=xBBzinDVhlRvV0oYitEV7w6M1L
SOR-166-005 | 1b9e4a91-4cd2-46ab-a7cc-367323aabcba | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | TRN - Trane |  | Commissioning Issue | Commissioning | [7 empty] | PRE IST TESTING Chiller 1ACC_C_12 FAILED ON LOW FLOW THROUGH BEING SEQUENCED ONLINE | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617524&prj=479&rqi=CrCATWK3Z6SVpqw6iuljiGAf7t
SOR-166-007 | 01ba1a5e-bffe-4840-8493-4ae5bf951edc | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | Controls Contractor |  | Component/Equipment Failure | Commissioning | [7 empty] | PRE IST TESTING Chiller 1ACC_B_08 CHILLER PLANT MANAGER DIDNT RESET IT | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617526&prj=479&rqi=0pIuyRSViaQmemtUvgaWE07tmx
SOR-166-004 | 16a444f8-d614-48a8-b9e1-29860cb888c0 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-08 04:00:00.000 +0400 | TRN - Trane |  | Component/Equipment Failure | Commissioning | [7 empty] | PRE IST TESTING Chiller 1ACC_C_11 FAILED ON LOW FLOW THROUGH BEING SEQUENCED ONLINE | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617523&prj=479&rqi=QZ91N5YC8MUyVacQAWSMQ0IcqZ
SOR-166-002 | 2a428b8b-4f4b-4afc-bcb6-3218d1af204b | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Comms Issue/Fault | DCOS | [7 empty] | 1UPS_D3 is not communicating with the DCOS/BMS. Delta will need to investigate as E Tech confirmed they are not able to ping it. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617475&prj=479&rqi=wBOdHtc3au601hFDX5DNMwxsAw
GI-085 | 068947e5-5758-400c-b53f-664fbaf78b78 | SV18-1 | 479 | AMER | Closed | P1 High CX | daniel_chavez@fsttechnical.com | 2026-04-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1RPP_B1_2_5 | RPP - Remote Power Panel |  | RPP-208-250-60 | A hot spot was discovered during load bank testing on RPP_B1_2_5 panel bussing. Refer to attach photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617460&prj=479&rqi=kjxQ3NHquofH35NW0lUniiMacJ
SOR-165-006 | ac232e09-22bb-4cf7-88ec-1ac23545742d | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [7 empty] | Alarm Screen Shots for the Chilled Water System | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617386&prj=479&rqi=3ntXoxN1DFcXsv7qsqnMkQg3eB
SOR-165-008 | e05cf32d-747e-4146-8b75-06b1518859e1 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [7 empty] | Delta CRAHs - Powerhouse Issues | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617389&prj=479&rqi=Rk62fWs6gz62rZajgDNvygATOh
SOR-165-002 | e65b4852-d8e8-4924-8e5d-31bb52dfdd74 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [7 empty] | Alarm Screen shots for Data Hall B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617364&prj=479&rqi=6xL1oYX0DszHyc5Rzzd24tR0uc
SOR-165-005 | 8cdfbdcd-acac-4332-ab38-4889f4a5df36 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [7 empty] | Alarm screen shots for DATA HALL F + Mega CRAHs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617384&prj=479&rqi=9Zr12YTLaOgCRS631cfxsuX1Wl
SOR-165-004 | 5b4ae49b-ac9b-4582-84f6-daa72e956b00 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [7 empty] | Alarm Screen Shots for DH D and associated Mega CRAH units | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617383&prj=479&rqi=OlUTWV8561XgfHvD2SPcTjlmxF
SOR-165-007 | 5b97c17f-9145-48c8-a900-65388865ceed | SV18-1 | 479 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [7 empty] | The Block A, E, & F 1BATT cabinets are missing batteries. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617388&prj=479&rqi=zXVSkyrc2k5atyNjuP9SWtF57q
SOR-165-003 | c7e7a7ec-e375-4581-aefc-dd662369c578 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS | [7 empty] | Alarm Screen Shots for Data Hall H including Mega CRAHs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617382&prj=479&rqi=fxdyZDOiKddWGoEz4JlCaf58OS
SOR-163-002 | 5ac459fd-473b-42d1-806b-ef84c1aa016f | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | 1MAU_C_3 Alarm on Low Pressure Limit Switch | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617245&prj=479&rqi=Xj1WOw69vqYBDhm6Zs6vTwuB4Q
SOR-162-001 | 5a4c96fa-89a0-4721-b776-1b51fb3b6a26 | SV18-1 | 479 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-04-02 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Clear alarms for GEN R1, Z and B. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617157&prj=479&rqi=8kQB4uCNrVZJrcyS0K4znJQFSk
SOR-161-001 | d01f25e2-a792-447b-97cb-ce5878cecb21 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-04-01 04:00:00.000 +0400 | Design Professional |  | General Design Issue | Design | [7 empty] | There was no information where to get the UPS source for 1MSB_A/E/F feeding the controls as per Hanley submittal. DLB should provide direction what 1STS to use for feeding the 1MSB_A/E/F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617095&prj=479&rqi=a1ViEMMzeu02zylAiyw7d5Q8Vb
SOR-158-010 | 0f4063fe-bd18-41c3-99bc-89c685b6dd24 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-04-01 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [7 empty] | Freeze Protect valve on chiller 1ACC_R1_02, appeared to respond slower that the valves on the other chillers. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617099&prj=479&rqi=sXX6ITA62RR5hsixN0R18cex9z
SOR-158-004 | b6f2e010-e7a4-4b3c-904a-f6f79752cdcf | SV18-1 | 479 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS | [7 empty] | E-Tech to include the Bard Units in the DCOS at MV1 and MV2 for monitoring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616960&prj=479&rqi=h27SfqPKONbc9P9xtJtsgYQTFc
GI-081 | 3f207992-38e9-4497-82eb-94f2783f9d8f | SV18-1 | 479 | AMER | Closed | P1 High CX | daniel_chavez@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Washer discovered in MSB_A lineup, located in the 1BB_LB cabinet, far back against the bussing. Refer to attached photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616985&prj=479&rqi=XWKPONocron8Ic3P0zpGRjHA9D
SOR-158-003 | 5277be9e-1009-41f1-b7a4-902feddf50a8 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  |  | system | CHW System |  |  |  | Chiller Transfer from Utility Power to Generator Power testing 1ACC_R1_01 & 1ACC_R1_02 failed on DCOS as the plc did not capture the power loss event and apply the 30 seconds delay on the external chiller alarm for phase loss. Without phase loss event capture the plc thinks it's in normal mode and will alarm and latch any alarm from external source. Trane troubleshooted the issue with tech support and lessons learned from DC22, they found that the phase loss relay was wired incorrectly to the normally closed contact on the phase loss relay. Trane corrected this and set the voltage to 480V. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616914&prj=479&rqi=78RSNULBOhxPYqMoBx9boZXRTI | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-158-008 | cdb2958d-1432-4930-a693-937a796a2ae5 | SV18-1 | 479 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | All energized Equipment should have While Line background to indicate that were energized. This is applicable for all 1MSB's.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616973&prj=479&rqi=7mIOgIPN68cH5FED2jB3qlhQLc
SOR-158-007 | 2c77041e-2fcd-4f32-8c2d-bf787af5955d | SV18-1 | 479 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | I noticed that every day we are losing communication for all the equipment and come back in. Then your need to come back for each equipment's to clear the alarms. Could you please investigate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616971&prj=479&rqi=zSz8QMw6da6ZX0sra09BFmtY00
SOR-158-009 | 5ac731b9-d617-46a4-8fbf-203e3fe0ba81 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-03-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Leak Detector LD2100 RLE controller from MPS found not communicating to BMS/DCOS and needs to be replaced. Powerhouse D | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616984&prj=479&rqi=4rBmz7bealAFav5xAig1ZUGWiq
SOR-156-003 | 4985c99e-cab3-4eb8-8ca2-32f118b46c98 | SV18-1 | 479 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-03-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment type |  |  |  |  | The SCR Common Alarm is active on 1GEN_B, 1GEN_R1 & 1GEN_Z. E Tech is to troubleshoot and resolve. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616762&prj=479&rqi=Id8uVSY6dZ8EXTDGx5Me1xbim0
SOR-156-002 | e4490cc4-e2c6-44cb-a45c-7546adeab8f8 | SV18-1 | 479 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-03-28 04:00:00.000 +0400 | Subcontractor |  | Installation not correct | Commissioning | [7 empty] | Rectify the loss of communication for Leak Detection for the following. 2. Clear all the alarms. 3. Level 1 & 2 FOH | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616760&prj=479&rqi=CIHd0MBzhm2l5stYNOIipUj2v3
SOR-155-002 | c9da9e92-167d-4e9e-ab17-5078610f747b | SV18-1 | 479 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-03-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Duplicate of issues 661-677. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616632&prj=479&rqi=yoal2I9V9Wm71dBQuJZxyLy0ec
SOR-155-001 | 9069ea9b-d81f-466d-bceb-f29b08fb37c4 | SV18-1 | 479 | AMER | Open | P2 Medium CX | jordan_dubose@fsttechnical.com | 2026-03-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | The Carrier Heat Pumps natively speak BAC-NET communications to the BMS system at Equinixâ€™s SV18 facility. However these units will require BAC-NET gateways to allow proper communication to this BMS system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616631&prj=479&rqi=guGMKmekVDDLYafuK4lxdUd3IQ
SOR-154-004 | d305d000-86f4-44ba-9a4d-2377c0b94d03 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-03-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | The exhaust fan didn't energize, and damper didn't open during the simulation of battery temperature rise for UPS's for PH D and R1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616472&prj=479&rqi=oPaDeWzcuFT8kyh15JyQjSd1wn
SOR-151-002 | c0833f97-3e49-4a10-ad8b-5e164e19b8e6 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-24 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not correct | Commissioning |  |  | system | CHW System |  |  |  | Riser 4 and riser 9, when all other risers were closed, we had a no flow condition on the riser suggesting the bypass is closed, needs to be cracked open for corrosion protection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616272&prj=479&rqi=wmIHAFwD5iOxbU8drkqzNLQZBu | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-151-001 | 3279769c-22ab-4900-9d4d-e1b93a48d3f0 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-24 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not complete | Commissioning |  |  | system | CHW System |  |  |  | Riser 1 & 6 was using 600 gpm cooling; issue raised on facility grid to track to closure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616270&prj=479&rqi=phBvh6TJPyxPFe1n5guQPX0V8d | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-149-002 | 66f3fb87-5a34-4e4e-b2fa-e018eb4e0881 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | James_Kenny@fsttechnical.com | 2026-03-22 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning |  |  | system | CHW System |  |  |  | Chilled water - Chiller flowmeter to riser flowmeter alignment - CDU risers 1 & 6, 4 & 9 Pressure control valves, not available to view or operate on the DCOS graphic, | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616136&prj=479&rqi=gWLpJs1aeHZmWsezVJyeFDy7J5 | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-149-001 | fd3cdf38-37a2-4e59-a36c-40964f0c8cfc | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-21 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Issues with Utility Power Loss and transfer to generator for all Trane Chillers, Issue raised on facility Grid and Trane contacted in this regard. See attached report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616135&prj=479&rqi=y93bWnjaKBSNKT27yalkd44QRZ
SOR-148-003 | c49f6348-521a-48d7-a627-5ae6aea05c21 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Humidifier Piping, from pump to humidifier needs to be supported. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616058&prj=479&rqi=eTAofbkEWnlVz4TuonDZJpXZDK
SOR-147-001 | c15fc431-880e-4edf-8c75-f97e76c41aeb | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [7 empty] | Currently the chiller sequencer does not react appropriately staging down and there have been a number of chiller failures as a result. When the load on HVAC equipment associated with the chilled water distribution loop drops off the sequencer doesn't react quickly enough as the valve close so does the flow path the chillers run at minimum flow and fail when flow is reduced further. This issue can be resolved by implementing the low flow control strategy, where the recharge valve is brought online to maintain minimum flow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615992&prj=479&rqi=4VLfBnwpSGBZRoG5EW3Qh9UgO3
SOR-147-002 | f84d2f0d-0aa4-4fd8-a258-55e3d3c4bf84 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Equinix engineering and design team, need us to isolate one riser and one chiller at a time run the chiller into the riser, the reason for this exercise is to match the chiller flow to the riser flowmeter as it seems there is a very large error between the two. This procedure will take place when Leo is finished load banking. Detail to follow. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616013&prj=479&rqi=qp7IuGofHjdv8ukCLOqM1zZEfO
GI-077 | b57ffda1-aacb-4f80-8bc1-642cba10a5d5 | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | Buttons without filler color once they are selected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615774&prj=479&rqi=XNDjlZaLETwcY7zpb9O62tkKRF
GI-078 | fe14b4f2-dda1-4228-b6a6-4b67f3e8cc0f | SV18-1 | 479 | AMER | Closed | P3 Low CX | Rangsiya_Faihin@fsttechnical.com | 2026-03-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | The internal connection cable labeling for the battery cabinets is not consistent with the MPS.322 submittal. As shown on the attached page, the red boxes highlight the field-observed conditions. Please re-assign this item to the appropriate responsible party if needed. UPS_R2_2 & UPS_R2_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615834&prj=479&rqi=FPvCtkLu0XKk9ilZvRbXKYPLtR
SOR-139-003 | cb88fd4a-d444-4121-afba-d301bad12e06 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | All Make-up Air handling units need to have droplet eliminators installed after on the inlet air hood of the unit, to deal with ambient fog conditions outside. Applies to the following: 1MAU_R1_01 1MAU_B_02 1MAU_C_03 1MAU_D_04 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615320&prj=479&rqi=1sAPJ3DpUshqWhuNNjg2mQQq8E
SOR-138-005 | f35eeeca-2ebc-478e-9d47-a81b79ac66a0 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Carrier Heat Pumps: The TCV within the unit is limited to 2.5 to 13 GPM, design flow for this unit is 18 GPM, this applies to the following units: HP_R1_01, HP_R1_02, HP_B_01, HP_B_02, HP_C_01, HP_C_02, HP_D_01, HP_D_02 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615178&prj=479&rqi=1eIuUIWztkbtqaPm3w0CLtchzB
SOR-138-006 | ddf439bc-f4da-4512-9bd7-08b0405f8659 | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-03-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | DCOS General Issue | DCOS |  |  | equipment type |  |  |  |  | The soft point "Logic Failure" per 2.16 DCOS Table of the Record - Delta STS 800A Submittal 480v V2 is not visible for the 1STSs to the customer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615190&prj=479&rqi=LWG3erLwt0fz4bIjLuVIhp5XLk
SOR-101-008 | 4cf66225-3df5-47ae-a42a-54c4dbde172d | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-09 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [7 empty] | RESULTS OF SURVEY CONDUCTED BY THERMA TAB ON ALL OF THE CHILLED WATER PRESSURE TRANSMITTERS THE FOLLOWING TRANSMITTERS WERE READING OUT OF RANGE: DCOS Input numbers 1, 2, 5, 6, 7 & 8. See attached Table for reference, pressure readings were taken with a calibrated meter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615145&prj=479&rqi=VkcmqdmsltCTsJlwLmYRJVwFn1
SOR-137-010 | 4dde0840-5561-48e4-be72-8fcaed05c1a7 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | VESDA CONTROLLER Units located in the Power house Skids & the MV-1 & 2 Power houses are in constant alarm. Relating to: R1, B, C, D, MV-1 & MV-2. WE NEED A REPRESENTATIVE FROM VESDA HERE ON SITE TO RECTIFY THE ISSUES WE ARE ENCOUNTERING. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614988&prj=479&rqi=biq1Zy941Z6mIZIU2EwcNdOSuk
SOR-137-007 | 55020a15-cc8f-450f-ae1b-8f50fcbc1230 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Delta CRAH Units located in the Powerhouse Skid: R1 A B C D E F Units do Not shut down on smoke detector activation when the units operate in manual. In automatic the units will only work when the Fire Shutdown is enabled "ON". This is not acceptable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614985&prj=479&rqi=aVAdTFTUYPAfSdI2txuQ6mpfRx
SOR-137-009 | b3d063b6-6394-4d76-a29e-86327766b6ff | SV18-1 | 479 | AMER | Closed | P1 High CX | James_Kenny@fsttechnical.com | 2026-03-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Delta CRAH units located in the Power house Skids, do not transfer back from Reserve power to Primary power following power reinstatement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614987&prj=479&rqi=8ae8WifXKxiWakRO8FPKFz66aN
SOR-137-008 | cb71f131-16e0-489a-88be-3c682f61c658 | SV18-1 | 479 | AMER | Closed | P1 High CX | James_Kenny@fsttechnical.com | 2026-03-07 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Condensate Pump not activating on Delta CRAH unit located in the Power House Skids | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614986&prj=479&rqi=wgNcqYWK1wCENikgw7vFsUsqFS
GI-076 | e8f175e7-30a6-4d93-a8ff-471ebd4e3a0b | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-06 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | PDUs are not reflecting the output CB in the onelines | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614921&prj=479&rqi=HQl4F0qPve54M0HqPucmXhjLNC
SOR-135-003 | 161767b8-35d0-4461-942a-e9831b1159d7 | SV18-1 | 479 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Smoke Detector is shutting the unit down locally but the unit's points integration to DCOS is not completed and this alarm needs to be verified once communications are established. This applies to the following units: HP_R1_2 Â HP_B_1 1HP_B_2 1HP_C_1 1HP_C_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614852&prj=479&rqi=IP1jacLZJx3qYnIGNhP2yDrDYA
SOR-135-004 | 5c69edde-53f8-433c-9a11-a1997d3edae0 | SV18-1 | 479 | AMER | Open | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Condensate Hi level switch interlock with the unit's compressor works but the unit's points integration to DCOS is not complete and this alarm needs to be verified once communications are established. This applies to the following units: make repairs necessary. 1HP_R1_1 1HP_R1_2 1HP_B_1 1HP_B_2 1HP_C_1 1HP_C_2 1HP_D_1 1HP_D_2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614853&prj=479&rqi=mbR2t8tD1Kz3IKrOjaHenkLF9U
GI-065 | ad1de7c0-3d4b-45ae-9566-a229117c8325 | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [7 empty] | Need confirmation whether these meters are the first monitoring point upstream of the SUSPs; if yes, Utility digital assets must be created per Appendix 7. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614734&prj=479&rqi=kF9gxUafPFALH1ab0NW1e1cvWL
GI-073 | 0ec920c5-90d7-48ec-be97-5d94ce6ba9d2 | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | Risers are displayed in the detail view but missing in the overall floor plan view. Riser labels do not show which data halls each riser supports (operational context is missing). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614742&prj=479&rqi=ywh88k0YRxwP7sxE5cZGRmBpjv
GI-072 | 85489bc5-2c54-408f-93f0-d50a1f443968 | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | Floorplan does not visually show which element is currently selected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614741&prj=479&rqi=0eKB0fNI2o7i9iIxVei4lDyWiE
GI-074 | bba232f8-047b-4766-8d7f-fc1e17717014 | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | Missing weblinks/deep links for assets (CRAHs, UPSs, etc.) from graphics to their detail/faceplate pages. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614743&prj=479&rqi=CGfWTkfVUe2dJjJZDqVKUD0xPM
GI-066 | 92250b42-cc4f-4cfe-bebd-bd98d106ae0f | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS | [7 empty] | SPARE and FUTUREâ€‘SPARE breakers must not be monitored or ingested. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614735&prj=479&rqi=sxZjNSVoAv9dsWfErBHcKhVL29
GI-070 | 8a4fb10b-22d2-4577-b89b-893a2cc4d373 | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | The UI does not highlight the selected item, making it unclear which item is currently active. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614739&prj=479&rqi=6QI48yIZOeKONPjaSXpH0MPG3b
GI-067 | d184d27c-4ddc-4bcc-94c2-a6880b1ea0d8 | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [7 empty] | PQM data shows incorrect voltage and PF due to negative incoming power; polarity must be corrected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614736&prj=479&rqi=U2ffRwhVm7FDAYM7OfBmlGUEFs
SOR-134-002 | 72db3dad-760c-4a5b-affa-7f3bc7cf377b | SV18-1 | 479 | AMER | Closed | Outstanding Paperwork/Documentation | jordan_dubose@fsttechnical.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | Documentation not issued/ Required | Commissioning | [7 empty] | Missing BMS/ ENMS signed documentation (Point to point check sheet and fibre results) for SV18-1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614722&prj=479&rqi=tBmASVOhERGNMqrD1p9VWsIKWI
GI-064 | fc5164f2-3b11-48ff-a7e8-8eb98b006b31 | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS | [7 empty] | 1. Chiller Flow Low Alarm Logic Incorrect Category: DCOS Design Issue (Alarm logic implemented incorrectly â†’ design/config logic error) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614733&prj=479&rqi=ZIiFXkX8BaY2dRApGS1pzZADjj
GI-069 | 68309ba0-89b6-48a3-a951-cdfceaad299d | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | The CRAHs overviews are not setup yet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614738&prj=479&rqi=f91Stu8erfcedxVjrZqyDSnn9u
GI-075 | 45817d0b-a911-4d58-b9c6-d1bc9d704ef5 | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS | [7 empty] | Battery Time Remaining is missing for all UPSs on the graphics/monitoring views. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614744&prj=479&rqi=k9TaNPv6tlgwbBHOx0VC1TTmJX
GI-068 | 5af5accd-5d80-42ad-9b1f-76b0be2c6ede | SV18-1 | 479 | AMER | Closed | P2 Medium DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS | [7 empty] | DP sensors are reading a wide variety of numbers, suggesting are missing scaling or not reading well | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614737&prj=479&rqi=k1VrdBj7K23taqKfXvIYIwbhab
GI-071 | 49601d6b-0538-46df-8fda-58db781ad37c | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-04 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | Hot/cold aisle selection is reversed; cold selects hot and viceâ€‘versa. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614740&prj=479&rqi=4mcV1vTHj21Pk5iEU1BXsy7gjd
SOR-132-006 | 54fbfda3-ff76-483c-935a-3949e40d84ef | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Some DCOS issues uncovered during our Powerhouse Skid CRAHs -Smoke detection testing. Skid B 1CRAH_B_13 - Successful Test - Not Depicted on the unit's faceplate in DCOS - E-Tech notified Skid C 1CRAH_C_13 - Successful Test - Not Depicted on the unit's faceplate in DCOS - E-Tech notified. 1CRAH_C_15 - Successful Test - Not Depicted on the unit's faceplate in DCOS - E-Tech notified. Skid D 1CRAH_D_14 - Successful Test - Not Depicted on the unit's faceplate in DCOS - E-Tech notified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614632&prj=479&rqi=5aGS239dPj2GyoRRNSMacnTSgf
SOR-132-007 | 5f9150f0-dbe3-4d18-84e1-0933152c883b | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Skid C & D CRAH fan speed control All units were placed in automatic during testing, chillers and associated pumps were started and rooms cooled down to temperature set point. All fans continued to run at full speed, the expectation is the fan speed reduces as the temperature comes within range of setpoint. Suspect issue with the CRAHs Units remote temperature transmitter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614633&prj=479&rqi=G4aow4QEVucdhXcgruUWAmn12q
SOR-133-003 | bbec10af-e95e-4498-9185-c823f9f2debb | SV18-1 | 479 | AMER | Closed | P1 High CX | daniel_chavez@fsttechnical.com | 2026-03-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | The transformer for the VESDA system on Power House Skid B doesn't provide output voltage on the secondary side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614659&prj=479&rqi=EFdBPpn1vb2TCehNz0IgYK9Olm
SOR-132-005 | 64af67af-b194-4a16-a5c0-34f32dcc8e6a | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | PID pop-up settings are not working well: -scale is bad -name on buttons is wrong - EU range is wrong In GENERAL all pop-up settings | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483499&prj=479&rqi=3U6VGWD7onFnAGem1rxLQJZPOz
SOR-132-004 | 51ab5959-15e2-4786-b1c2-bc0d0deefc10 | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-03-02 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS |  |  | equipment type |  |  |  |  | Gateways for the RPPs (BCM) connection can be move 2-3 Us above the current position so the cables won't be curved like now, which will affect the comms in the future | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483495&prj=479&rqi=hOrqxbpNH9FcWZSJSNpeHDnmYa
SOR-117-005 | 333f88a5-2f2c-4bb1-a07e-b65dc9bb7c1b | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-27 04:00:00.000 +0400 | Owner |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | 1ACC_R1_01 - rode through the test and alarms reset thereafter, all UPS circuits were healthy during the test. 1ACC_R1_02 - House 120V UPS power was removed and the alarms didn't reset. The reason it didn't ride through is the Trane UPS in their control panel is programmed to provide power for a 3 second drop in power An extension of this timer from 3 seconds to 12 seconds would get us through the transition to Gen power. Trane Panel UPS is an Emerson Sola-HD 300w and backs up the chiller controller only. During test of the generator back up circuits on Saturday, Chillers 1ACC_B_07 & Chillers 1ACC_B_07 Phase Loss alarm activated and latched. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483373&prj=479&rqi=9cmTYgsQHLhFwX6pTwZyTmy6Hd
SOR-127-005 | 4242ba8d-391a-4e83-8c26-ceffd7b11137 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-27 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Discharge Valve oriented, there is a risk with the operation of the valve the mechanism may loosen up, and the handle would drop and disengaged from the actuator in its current position | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483372&prj=479&rqi=f081saJeFhDncu0K2xQp8E9L4x
SOR-130-003 | c5e3a70f-7bb2-4f4d-a0f9-afe3b67aaeb3 | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1RPP_B1_3_1 | RPP - Remote Power Panel |  | RPP-208-250-60 | During the PEI FST found a CT Senser had been damage possibly from installation on 1RPP_B1_3_1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352261&prj=479&rqi=foTQfGhHOU4BeqE75IWACDESR2
SOR-130-004 | 6d098479-3949-423d-aa23-aae057f80074 | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1RPP_F2_2_6 | RPP - Remote Power Panel |  | RPP-208-250-60 | 1RPP_F2_2_6 is missing two CT sticks due to them being used to replace the damaged CTs in 1RPP_B1_3_1 and 1RPP_B1_3_6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352262&prj=479&rqi=u2y46Na6C2YJPEEYYVjh78jXut
SOR-131-003 | 0c520f5e-e402-4eb6-9458-3a6c37701dbe | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Component/Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | Fan spring isolators to be replaced on all units | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483382&prj=479&rqi=oOpcV2ToF2CL0zezPv9NLInNXz
SOR-130-001 | 0c09a85c-0602-4fca-8a19-3aeda7f0691b | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-26 04:00:00.000 +0400 | Electrical Contractor |  | Commissioning Issue | Commissioning | [7 empty] | CONDUIT CONNECTIONS Covers missing on the conduit leading to the field devices on TST_B_07, See attached Photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352246&prj=479&rqi=yrySkr5RRuYK8dbi1oPEd1DD4t
GI-060 | a953fd21-3f10-446d-9c2c-53d86f1ea742 | SV18-1 | 479 | AMER | Closed | P3 Low CX | adrian_brown@fsttechnical.com | 2026-02-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1RPP_B1_1_3 | RPP - Remote Power Panel |  | RPP-208-250-60 | During the PEI we found a missing cover for the small terminal under the main terminal | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352240&prj=479&rqi=ELk7nCFXJo2vW7md6KKL1xjxFX
GI-061 | 2899bda7-41f2-4b20-9adc-8548821487e7 | SV18-1 | 479 | AMER | Closed | P3 Low CX | adrian_brown@fsttechnical.com | 2026-02-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning |  | Electrical â€“ LV | equipment | 1RPP_B1_3_6 | RPP - Remote Power Panel |  | RPP-208-250-60 | During the PEI we found a CT Sencer had been damage possibly from installation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=352241&prj=479&rqi=Z9f4ynieQsza3v4JDYZ3hUoxiR
GI-059 | bceb9aab-0970-44a9-889e-48339cee452a | SV18-1 | 479 | AMER | Closed | P3 Low CX | daniel_chavez@fsttechnical.com | 2026-02-24 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | Dummy Issue for JTM requested by Pat. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204066&prj=479&rqi=2tCtt5DzilWKPXkd3J1qaI7ro1
SOR-122-017 | c389705a-0a38-4e41-8f2f-1dcb20615c9b | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | [7 empty] | The mechanical lugs for 1PNL_X_HP terminations to Q06 in the 1MDSB_X are incorrect in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199681&prj=479&rqi=p2s1tEBLLYehrdV4vOITFCEVSU
SOR-122-005 | b8dd2102-07df-4014-819a-16bd44154f93 | SV18-1 | 479 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [7 empty] | The three pulling gutters shown in MPS.301 were not installed in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199637&prj=479&rqi=mr72ONbGB0GPau8x9ofWzApdla
SOR-122-007 | 8508c6af-d633-42ae-af5d-b41285a5be8a | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | [7 empty] | The mechanical lugs for 1UPS_X_3 terminations to Q07 in the 1MDSB_X are incorrect in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199639&prj=479&rqi=LOE3MVEEbljjVvfD7SZjEn656F
SOR-122-011 | 932cfe87-5e45-406f-a1bb-f17340dee6bd | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [7 empty] | The ball valve is missing from the section 2 VESDA conduit in front of 1CRAH_A3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199643&prj=479&rqi=8ukhda4URig2sUGi2iNaNForXg
SOR-122-002 | 424a24db-4e92-4c2c-b938-b7b4c273ded5 | SV18-1 | 479 | AMER | Open | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Design correction needed | Design | [7 empty] | 1MDSB_X Q01 in SV18-2 Hanley Submittal should be Spare. Refer to DLB Engineering Drawing Single Line Drawings E602.05, E602.009 & E602.10. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199633&prj=479&rqi=321sFjiFfzgj4muD7FLyEwQGM2
SOR-122-004 | 27ae3947-9e7b-410f-acb7-18ca31ac4079 | SV18-1 | 479 | AMER | Closed | P2 Medium CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [7 empty] | The external small green stub in between the condensate piping and the light shown in MPS.000 is not installed in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199636&prj=479&rqi=TcVW1GRbZr5IvgaJecguB9pdSc
SOR-122-016 | 9c80b1ae-432d-4af8-a435-06b3cdbaabea | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [7 empty] | The ball valve is missing from the section 2 VESDA conduit in front of 1CRAH_E3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199648&prj=479&rqi=5mBJPNubSeEoTNzyZ9iYl3RKMs
SOR-122-001 | 855f3e09-df1d-4f44-bf15-cf58ba8ce94b | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design | [7 empty] | The positions of 1WSHP_X_1 & 1WSHP_X_2 in skids A, E and F in E403 are different from latest approved MPS submittal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199627&prj=479&rqi=JqLJJZSIENs6uuq7iF5iJZoGy7
SOR-122-008 | 324347c8-b332-4759-9088-4361512078bb | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Mechanical Contractor |  | Missing Components | Commissioning | [7 empty] | The 1WSHPs in skids A, E, & F are missing drain pans underneath them per the request of Equinix. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199640&prj=479&rqi=ktJiU0n4ssVzL9buDyjYO24RmF
SOR-122-015 | 6e2e13d6-a242-4eca-a13b-7654a64c6329 | SV18-1 | 479 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning | [7 empty] | 1MSB_E sections 5, 6, 11, 12, and 13 each had a screw that was screwed into the ground bus bar. MPS successfully removed the screws in the 5 sections of 1MSB_E. This has resulted in the ground bus bar plates in the 1MSB_E sections 5, 6, 11, 12, and 13 each having a hole in them. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199647&prj=479&rqi=eK9M6tscjnVqKZHHNavS4z2SDb
SOR-122-006 | 7432f0fc-4cf5-4c97-8862-6bfd62890365 | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [7 empty] | The ethernet connection from 1UPS_X_3 to DMARK shown in MPS.521 were not installed in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199638&prj=479&rqi=EMPKJRXpYiyQvDce8tcScv2xJ0
SOR-122-003 | ab02c2da-2fd8-4246-9d4b-cba790c2aeb7 | SV18-1 | 479 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning | [7 empty] | The top external tabs shown in MPS.000 are not installed in skids A, E, & F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199635&prj=479&rqi=wFMVIBHb00KFKmBCneYI49Bgqx
SOR-122-009 | 23532c7f-7e24-43f4-9280-1ea5806fb1ed | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [7 empty] | FST observed that a third branch junction box above the 1BTUs in skids A, E, & F shown in MPS.400 was not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199641&prj=479&rqi=JKpUCZaF7ZcaIRfMfbV0sYxxts
SOR-117-004 | 16b43101-3695-41ba-a6b3-d7468b57b304 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-18 04:00:00.000 +0400 | Owner |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | Soft Points that are not available from the chiller: Flow switch COP Condenser Fan Fault Condenser Fan Summary Fault Evap. Approach Temperature Evap. DP Sensor. TXV 1 TXV 2 Free Cooling mode enable Free Cooling valve % Hot Gas 1 Hot Gas 2 Liquid Level 1 Liquid Level 2 Liquid Refrigerant Temperature Ambient Temperature Lockout. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199503&prj=479&rqi=OchoIHMb8WEeWrh6iIySfNwXfY
SOR-119-004 | 260363ed-7673-4f7f-a4ae-6aa3bcd70962 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-18 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning | [7 empty] | Chilled water make-up skid - Pressure transmitter needs to be wired and represented on the DCOS graphic. The flow switch is not on the graphics either, this needs to be tested to ensure an alarm is posted to the DCOS alarm page. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199502&prj=479&rqi=xd9jKzTXJSXNjhcHUL7lMV6X0a
GI-056 | 28865b00-67cd-44cc-86dd-1f9bb62b82ed | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | The alarm border is overlapping the objects in different dashboards. The objects need more spacing between them to show correctly the alarm border | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199401&prj=479&rqi=jNszjgZ1IY0jK5LD8nddbR3ic8
GI-057 | da0b47fb-d461-4939-81c5-aa8a81352b2b | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | STS faceplate issues with : - power factor not communicating - overview content not available - lines in the hierarchy are not showing the right flow, you can see on source one there is a piece of line at the top right corner that is not white. - The voltage in the table is not showing all the values as per the object (kwh, Vab, Vbc are different) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199402&prj=479&rqi=cfXNo2bEkf6uA9uspch4bMnsZM
GI-054 | b29c15a9-c8a9-45a2-a9e6-f76317a07729 | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Installation not complete | DCOS | [7 empty] | The statistics alarms app is not properly configured, furthermore, not working | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199399&prj=479&rqi=fYgcGbTc2ucLVDNOyfnUmIcgms
GI-055 | c175bdc9-fcd0-4263-a06f-5ba2b1f17f76 | SV18-1 | 479 | AMER | Closed | P3 Low CX | manuel.gomez@eu.equinix.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | The Alarm border overlaps multiple objects. The objects need more spacing between them so they can be reflected correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199400&prj=479&rqi=XuOPvB8obzNk6T1EqRoBzkGbM4
SOR-118-002 | c15c1419-2c2e-4b16-8355-4725e8222efb | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Clean debris and rust off all generator roofs | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199379&prj=479&rqi=sY9gTBzVbhLFtVYpfjtrHTn73D
SOR-118-001 | 22957183-325a-4b96-8ff2-285e3e8f9501 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Remove lifting eyes from all Generators on site: | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199378&prj=479&rqi=T95UqK2pr0o8Swx0tKAe6w6V2S
GI-053 | 53a754c5-a0c1-413e-a846-65047370a1ec | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | manuel.gomez@eu.equinix.com | 2026-02-17 04:00:00.000 +0400 | Controls Contractor |  | DCOS General Issue | DCOS | [7 empty] | Autolunch of OMI app is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199397&prj=479&rqi=xlkzZ9OhRChvUbQUyFg2DYHPJG
GI-050 | 54b3f69d-947d-4335-b83f-6dd70d6c3c0c | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Template Issue | DCOS | [7 empty] | Fire in the footer are not clickable, so we can not go to the respective faceplace/object page | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199281&prj=479&rqi=79LvmrTKFpvyKfMPttcRQxtbHP
GI-051 | e6edcf85-a29b-4e97-9e14-f1fe1d8b109a | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | I understand the previous apps bring the oversize for the "csv export," but let's standardize now across the alarm apps | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199282&prj=479&rqi=7eBYYOfwO9BSFvGpE0s7styE1l
GI-049 | 83e9c4c4-6523-4093-848c-84ad5575e61f | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | The Overviews for each MSB are inconsistent, leading to a graphical issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199280&prj=479&rqi=NL6meptR9ABCUZjkQZimLEcoh7
GI-048 | 6cb8ceba-8bec-4d72-8f62-13beb476ab07 | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | On the Data Hall Overviews, there is not a trace for the Leak Detection, this is against the DCOS configuration guide. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199279&prj=479&rqi=tAZwfaRk3xjPs3AVlNtkm87Zh9
GI-046 | ac5c5656-b29e-4653-8e78-7fccff33d493 | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | Chilled water overview graphics have several issues as the sensors are misplaced or not located with dashes or pipping leads to nothing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199277&prj=479&rqi=NDQkfUqn37R6BTc5RGu5W7oB3q
GI-044 | fc2ac9eb-dab2-4e90-b4c2-1fd276a19a79 | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | On Chiller ACC Overview the headers are repeated on each row, per DCOS Configuration Guide this is not acceptable. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199275&prj=479&rqi=aqAmC77ViD1YNcZ4gHI5GScn5U
GI-052 | 972b912f-87ea-4fd3-bd33-9ffc2fa17473 | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | Missing name of the data halls (floorplan and tooltip) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199283&prj=479&rqi=70H80Nc2FWwm5lXG4ePibIj01P
GI-045 | 1c2a82c3-48b0-4a9d-8cc8-d47944ee557a | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | The CWST screen appears to have overlapping issues; this screen needs to be revisited once we have more value. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199276&prj=479&rqi=YXuqKmpilYe7QeKpqbMY9DxI9v
GI-047 | ac81d72d-23d2-4322-b9c9-79592fb88069 | SV18-1 | 479 | AMER | Closed | P3 Low DCOS | andgarcia@equinix.com | 2026-02-16 04:00:00.000 +0400 | Controls Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | Chiller Overview has no arrows, and the pump is not in the right direction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199278&prj=479&rqi=zMHkGpyo9jXBCuyVhJXhTYGBI2
GI-043 | 22ad0d92-07db-46d5-885d-2649b7ac212a | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-02-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning | [7 empty] | This is a dummy issue to confirm that JTM is receiving email notifications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199223&prj=479&rqi=Qto9i4DE3GEwDPrI9HYLQTDzts
SOR-110-002 | 758e678c-ac0d-44de-855e-e1cd21862b8b | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-09 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning |  |  | system | CHW System |  |  |  | Issues with the Chiller RIO Panel wiring to be addressed, applies to the following RIO Cabinets: CHILLER-RIO-01 CHILLER-RIO-02 CHILLER-RIO-07 CHILLER-RIO-08 CHILLER-RIO-11 CHILLER-RIO-12 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198827&prj=479&rqi=zdTNt09uivMdkOaeiVJLvMI4V3 | https://equinix.facilitygrid.co.uk/x/project/479/system/10140
SOR-110-001 | 5a79e8b6-c4f6-48bf-bd9a-07f956b44958 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-02-09 04:00:00.000 +0400 | Controls Contractor |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | Scaling to be addressed on all Chillers & Pumps, this applies to the following chillers: 1ACC_R1_01 1ACC_R1_02 1ACC_B_07 1ACC_B_08 1ACC_C_11 1ACC_C_12 1ACC_D_17 1ACC_D_18 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198826&prj=479&rqi=gGfrOHPEuOhfOX3ZGw5R1mWFaF
SOR-109-002 | 096f7c31-6580-4ae0-b0d9-822b6d950deb | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-02-09 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | 1RMU_R1/B/C/D/Z are not communicating with DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198754&prj=479&rqi=WuqzeiQuiYgWMN4x1dYQtp1F0q
SOR-109-003 | a9bebdd5-6553-4d51-be6e-e574d37cc0fe | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-02-09 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | 1MSB_Z is not communicating with the DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198755&prj=479&rqi=5icLIRJi7HLMR2y7UYX9zp1JF1
SOR-109-001 | d4f72055-1faa-4b48-90af-ca9427b22351 | SV18-1 | 479 | AMER | Closed | P2 Medium DCOS | Leonito_Macasaddug@fsttechnical.com | 2026-02-09 04:00:00.000 +0400 | Controls Contractor |  | Commissioning Issue | Commissioning | [7 empty] | 1SUDB 1 & 2 are not communicating at DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198753&prj=479&rqi=iXetvNnWhQ6kbuw6x20T18EXuu
SOR-108-002 | ee640a29-961a-439c-9c96-abe8375413b5 | SV18-1 | 479 | AMER | Closed | P1 High DCOS | jordan_dubose@fsttechnical.com | 2026-02-07 04:00:00.000 +0400 | Controls Contractor |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment type |  |  |  |  | During 1UPS's battery drain testing FST observed that the "Low Battery Alarm" did not turn on in DCOS system. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198728&prj=479&rqi=oDI9uYpd3JlT1GLbzQMLz0YV7v
SOR-108-003 | c2cde1ae-b562-4687-87a1-dd4c133a173d | SV18-1 | 479 | AMER | Closed | P1 High CX | jordan_dubose@fsttechnical.com | 2026-02-07 04:00:00.000 +0400 | Controls Contractor |  | DCOS Design Issue | DCOS |  |  | equipment type |  |  |  |  | FST observed during testing that Soft Points listed below requested by Equinix are not available in the DCOS system for the different 1UPS's. -Battery Cycle Buffer Full -Battery Time Remaining Status -Battery Time Remaining -Control Power Failure -DC Bus Voltage -DC Cap Fuse -Emergency Power Off -Input Current Unbalance -Output Voltage AN -Output Voltage BN -Output Voltage CN -Rectifier Fuse -Static Switch Disable -kWh | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198729&prj=479&rqi=J6RTJFhnY2PgVrAMqd3zaEuDtD
GI-038 | c0ffe150-307f-4a71-971b-f4fb134da760 | SV18-1 | 479 | AMER | Closed | P3 Low CX | adrian_brown@fsttechnical.com | 2026-02-05 04:00:00.000 +0400 | General Contractor |  | Installation Damage | Commissioning | [7 empty] | Mega CRAH cosmetic issues Observed Issues / Damage: â€¢ CRAH C-06: Front grille is discolored with visible damage. Deep scratches were observed on the left-side panel. â€¢ CRAH C-04: Front grille shows visible damage, discoloration, and scratches. â€¢ CRAH C-03: Front grille has similar damage and discoloration as C-04, though less severe. â€¢ CRAH C-12: Front grille is damaged and discolored. â€¢ CRAH C-10: Significant dent and scratches on the front panel, consistent with possible impact from a lift. â€¢ CRAH C-11: T2 sensor wiring is damaged and stripped. Therma has been notified of this issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198645&prj=479&rqi=1cu7x2dmjGzUiJjxHmGhuylUIt
SOR-104-003 | 32092b1a-e218-4d97-a1ff-a25409a8307e | SV18-1 | 479 | AMER | Closed | P2 Medium CX | Leonito_Macasaddug@fsttechnical.com | 2026-02-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issue | Commissioning | [7 empty] | Incomplete leak detection cable installation for all Skids. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198185&prj=479&rqi=w2OzIGrD5zVENso3kFbh1FpXPf
SOR-102-006 | f6855482-18a4-4530-8012-dff52e96d589 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Power to the Smoke detectors is not installed from the Fire Alarm panel to the smoke detector, in this case the Carrier representative could not complete his scheduled start-up for the equipment. 1WSHP_C_01 1WSHP_C_02 1WSHP_D_01 1WSHP_D_02 Inline plugs for fans and pressure switches found unplugged in the unit, increasing the time troubleshooting. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198072&prj=479&rqi=3R6G1b6EktkqtXjM3HnHWiddQV
GI-035 | 1f6b6f4e-de44-4e9e-a485-6b0db5a90f52 | SV18-1 | 479 | AMER | Closed | P3 Low CX | baron_brown@fsttechnical.com | 2026-01-31 04:00:00.000 +0400 | Owner |  | Commissioning Issue | Commissioning | [7 empty] | Verify interfaces and interlocks with EMS / Generator control / HV & LV switches Confirm alarms and indicators are operable Confirm CxA Level 4 (Blue Tag) Functional Performance test script available and approved Complete DCOS/ ENMS signed documentation is attached as a document to this checklist. (Point to point check sheet) DCOS Point to Point check complete 100% DCOS status/ alarming verified to ENMS workstation DCOS Point to Point check complete. 100% DCOS status/ alarming verified to DCOS workstation. 100% SCADA status/ alarming verified to DCOS workstation Local Alarms/ statuses are proven to HMI 1HMI SCADA 1MSB Input checklist these items are open and checked NO at this time. FST will verify during Level 4 Testing . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198071&prj=479&rqi=tDU0mLQ229IcMVT4KTSoqKVe5v
SOR-102-002 | bdafcce4-9c84-4714-b5d3-63aa76f1a62f | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Missing Components | Commissioning |  |  | equipment type |  |  |  |  | 3 x Supply air sensors are missing from the Powerhouse Skid CRAHs. Delta is swapping the sensors to enable their commissioning process. Parts on order. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198059&prj=479&rqi=wM5UfSraJJKN704WuSyYlMY9CS
SOR-102-001 | 138a1e6a-7806-457b-a68e-e2feefb04f44 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning |  |  | equipment type |  |  |  |  | Powerhouse Skids CRAH's All panels appear to have been tightened up with a cordless drill and the captive nut broken from its anchor, or threads have been damaged, this has caused significant delay on the commissioning of the Equipment. MPS to better manage the QA Process in their shop, issue raised on Facility Grid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198058&prj=479&rqi=NbwUcDhvh7EVWPckL5I1gCkOhi
SOR-101-002 | 881c4eeb-20b9-41e2-892a-37fcf76e86fd | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-29 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design |  |  | equipment type |  |  |  |  | FST observed that labeling of the Skid Heat Pumps in the field, engineering drawings and approved MPS submittals did not match. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197956&prj=479&rqi=LTE7h01HOaDdTWimZoL38O5x6P
SOR-101-006 | 06a31460-876c-439b-9039-935e23786751 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [7 empty] | Raceway ran in the way of access panels for the Air filter section on 1CRAH_ C_14, needs to be moved. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197961&prj=479&rqi=mlPKy91s9MQ7wChZOjwI8wfK9t
SOR-101-004 | 03cb017d-02ef-4b5c-9c0e-54e297b2edfa | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | FST observed that the labeling of conduits and junction boxes for the panel sources of the Heat Pumps in Skid R1 are not accurate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197959&prj=479&rqi=igpihB5F9MxgOZSTkA5VuZFCCP
SOR-101-003 | f07754d9-d574-4e36-9cf2-e6283e8de954 | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-29 04:00:00.000 +0400 | Design Professional |  | Design not as specified | Design |  |  | equipment type |  |  |  |  | FST observed that source of the Skid Heat Pumps in the field, and engineering drawings did not match. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197957&prj=479&rqi=rfGpLdglzmTzDBOM5Kbls1MmxC
SOR-101-005 | ab06cb57-c22a-4c54-b9f8-93528ad0c4ea | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | FST observed that the labeling of conduits and junction boxes for the panel sources of the Heat Pumps in Skid B are not accurate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197960&prj=479&rqi=N03FaJcR6t1MCmTJTImEZc8iIu
SOR-97-002 | a1ba6102-6cef-4200-a12f-6b67650afa83 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-24 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | IP addresses to be uploaded into the chiller Pumps, Danfoss VFD: 1ACC_R1_01 1ACC_R1_02 1ACC_B_07 1ACC_B_08 To be done following start-up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197545&prj=479&rqi=mMCRn6ImXFEMe67IaLdJC8lChy
SOR-96-011 | 988415e1-3530-4712-b7c0-84f32eab47b3 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-24 04:00:00.000 +0400 | Mechanical Contractor |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | In the absence of reliable Chiller flowmeters, Cx & Trane representative made the call to install Pete's plugs on the inlet and outlet of the chiller evaporator. This way Trane can connect a pressure differential meter to the petes plugs and determine the actual differential using the manufacturers chart for the evaporator Flow plotted against differential pressure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197542&prj=479&rqi=iCh62fvvauejnLjyjo38OemJNq
SOR-95-008 | 65d8b5f5-f2ef-4c08-ac70-4d9bde3e4271 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-23 04:00:00.000 +0400 | Controls Contractor |  | Installation not correct | Commissioning | [7 empty] | Chiller Return flowmeter was not operating - screen was not illuminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197527&prj=479&rqi=Y9PIOjHp9CSL6coRmz79eQo4su
SOR-96-003 | aed844b5-d240-40e8-93b6-910af55bc622 | SV18-1 | 479 | AMER | Closed | P3 Low CX | James_Kenny@fsttechnical.com | 2026-01-23 04:00:00.000 +0400 | TRN - Trane |  | Installation not correct | Commissioning | [7 empty] | Chiller condenser fan junction boxes had water ingress, blew fuses on start-up on chiller circuit 3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197530&prj=479&rqi=OLKvWcAZ5qmtloDfjt8jJuNl0r
SOR-91-009 | 75011e72-0bb2-4a1e-8ccd-62b31562d891 | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-20 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1-EGB-Z-2-2 | BUS - Busbar |  |  | FST observed on 1TGB-Z-2-2 that the cables for connections to 1TBG-Z-2-3 and the ladder rack are thin wires instead of #4/0 AWG CU identified in E604.01-SINGLE-LINE-DIAGRAMS---GROUNDING-Rev.7. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197269&prj=479&rqi=zrPwTpGElOysbCz8qAeNNhYvzi
SOR-91-002 | 8d44475c-fdbf-4471-beae-14c49b4368c8 | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-16 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design | [7 empty] | In the latest R3 coordination study, E709 panel schedule and in the field both 1UPNL_B1_H1 & 1UPNL_C1_4_H1 have one 125A and three 80A circuit breakers but those panels have one 125A and three 100A breakers in the E603.06 & E603.07 UPS_DISTRIBUTION Single Lines from Bulletin 2 & 3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197068&prj=479&rqi=k6K78ES4ms5y7CvhRuuchmEIud
SOR-86-001 | 9efdb60f-a722-4ec3-bc15-3dd232428cdd | SV18-1 | 479 | AMER | Closed | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-01-10 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design | [7 empty] | FST observed that the E602.03-E602.14 Single Line Block Diagrams incorrectly state that only the 1MSB_Xs, 1MSB_X Remote HMIs, 1UPS_X1s, 1UPS_X2s, 1BATT_UPS_X1s, and 1BATT_UPS_X2s are pre-wired by the skid Manufacturer as it also lists the 1MDSB_Xs, 1UPS_X3s, and 1BATT_UPS_X3s as well. Attached are the Single Line Block Diagrams for blocks installed in the current phase but is applicable to every block. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196677&prj=479&rqi=xohEaLnb49nk7S7b7rPllkkDLD
SOR-83-004 | 5d5298de-9150-4d49-bc22-f8c400d047e1 | SV18-1 | 479 | AMER | Closed | P3 Low CX | Leonito_Macasaddug@fsttechnical.com | 2026-01-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [7 empty] | Missing communication ethernet cable for 1MSB_D at Dmark. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196537&prj=479&rqi=0TRk1asCrMC9RiySUb8SUB3R4d
BT1MECH-2-003 | dc0dfd44-ae71-44bf-90de-43905da4cfad | SV18-2 | 684 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-09-18 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Template Issue | DCOS |  | Mechanical â€“ Water | equipment | 1ACC_R2_05 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers) L4 Supply air temperature SP command is scaled incorrectly. Trane programming is set to accept a value between 60 and 76F (from 4-20mA). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638695&prj=684&rqi=i13Dk4L7HGQGb9NFExsFNBxV3z
BT1MECH-6-002 | 46528acf-e8e9-44fc-813e-9e3686a56fd8 | SV18-2 | 684 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-09-18 04:00:00.000 +0400 | Controls Contractor | L4 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1ACC_H_14 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_H_14) L4 Digital input card was taken from H_14 and given to R2_06. New digital input card is needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638728&prj=684&rqi=bL31oyEAr11CeYkiuhv1U0jRxu
BT1MECH-6-001 | 75061848-8188-4a7b-81de-2e9a2544c034 | SV18-2 | 684 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-09-17 04:00:00.000 +0400 | TRN - Trane | L4 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1ACC_H_14 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_H_14) L4 Compressor 3 constant fault | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638626&prj=684&rqi=a39bs8sk1ewMVcMpnvP4b5y0yB
BT1MECH-3-001 | e6a1d579-0d17-b832-fee4-194c6ecae85d | SV18-2 | 684 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-09-17 04:00:00.000 +0400 | TRN - Trane | L4 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | equipment | 1ACC_R2_06 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_R2_06) L4 Modbus communication is showing all 0's. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638622&prj=684&rqi=8a5FBq1NxOaxYV2uXJBe0J4fdN
BT1MECH-15-005 | 2bc73d60-3a44-4c06-a3e6-89f29806b702 | SV18-2 | 684 | AMER | Open | P2 Medium DCOS | nick.shawger@veolia.com | 2026-09-17 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS General Issue | DCOS |  | Mechanical â€“ Water | equipment | 1ACC_G_15 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers) Compressor Not Required (Low Load) does not have a robust implementation Details Current implementation of the â€œCompressor Not Required Bitâ€ does not allow a Chiller start and prove in the rotation under low load Only works to prevent a low load Chiller from â€œFaultingâ€ if it is already proven in the rotation before going to low load mode, also only if the debounce timer is set to > 120s Therefore CHW Plant stage-ups due to flow (as opposed to load) are unstable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638619&prj=684&rqi=kdELofSx2PWViEDWVBqQrZD9nw
BT1MECH-65-005 | 8e5dcc56-8fcf-4a8a-aa38-130471ce10b5 | SV18-2 | 684 | AMER | Open | P3 Low DCOS | nick.shawger@veolia.com | 2026-09-17 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS General Issue | DCOS |  | Mechanical â€“ Water | equipment | 1CRAH_G_13 | CRAH - Computer room air handler (Skid) |  |  | (All Skid CRAHs) Changing the SAT / DT Setpoint at the HMI doesnâ€™t update the value on the BMS faceplate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638620&prj=684&rqi=mJfr38XT4YjH9B3KMN7skpoJKl
BT1MECH-15-004 | 1cbf5ca1-fa6d-45f4-bf8b-7e1ed58a9d84 | SV18-2 | 684 | AMER | Closed | P3 Low DCOS | nick.shawger@veolia.com | 2026-09-17 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS General Issue | DCOS |  | Mechanical â€“ Water | equipment | 1ACC_G_15 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers) Setting the Chillerâ€™s setpoint from the BMS is currently not functional on all SV18-2 Chillers, scaling is way off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638618&prj=684&rqi=lgPpW3bG3FM0p2p8qrP80wQSV1
BT1MECH-15-002 | 515c3dc7-99f8-4c5d-8dd2-fb67c1257994 | SV18-2 | 684 | AMER | Open | P2 Medium CX | nick.shawger@veolia.com | 2026-09-17 04:00:00.000 +0400 | TRN - Trane | L4 | Design correction needed | Design |  | Mechanical â€“ Water | equipment | 1ACC_G_15 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers) Loss of minimum flow switch feedback will not â€œFaultâ€ the Chiller Details Chiller will shutdown HW fault signal will not be present Chiller will continuously attempt to restart â€œRunning Statusâ€ will flip back and forth Therefore debounce timer will never fully count down | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638615&prj=684&rqi=3qMW9fMxoyXceANHRo4MOxFrqQ
BT1MECH-2-002 | 6115c949-96d8-41de-b783-c5b689e3841f | SV18-2 | 684 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-09-17 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | equipment | 1ACC_R2_05 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_R2_05) L4 Constant Heat Trace warning alarm even though heat trace breaker is closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638625&prj=684&rqi=9Xupv5gRAyjytBfZSgpUcryP0i
BT1MECH-15-003 | c18fd242-b6b8-498f-aaa7-04b38fad5d51 | SV18-2 | 684 | AMER | Open | P2 Medium CX | nick.shawger@veolia.com | 2026-09-17 04:00:00.000 +0400 | TRN - Trane | L4 | General Design Issue | Design |  | Mechanical â€“ Water | equipment | 1ACC_G_15 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers) Failing the Chillerâ€™s main controller will not â€œFaultâ€ the Chiller Details Chiller will shutdown Values communicated to the BMS will â€œfreezeâ€ such that: HW fault signal will not be present â€œRunning Statusâ€ will remain ON Resolution Accept behavior and rely on Operator intervention OR code a patch to remove Chillerâ€™s from rotation due to not meeting setpoint | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638616&prj=684&rqi=NMY6n6LC2aRGuVBJtWo2vnJcNy
BT1MECH-2-001 | 4616bc09-0bad-d73c-36a4-296860867b89 | SV18-2 | 684 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-09-17 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | equipment | 1ACC_R2_05 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_R2_06) L4 Constant Heat Trace warning alarm even though heat trace breaker is closed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638623&prj=684&rqi=R6rMdLwf2LhaKbnpsuocqvTjuN
BT1MECH-15-001 | e12effd4-3e10-49a6-9e81-f05ea92c4216 | SV18-2 | 684 | AMER | Open | P2 Medium DCOS | nick.shawger@veolia.com | 2026-09-17 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS General Issue | DCOS |  | Mechanical â€“ Water | equipment | 1ACC_G_15 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers) Chillerâ€™s with miscellaneous alarms are not available to run in rotation Details Due to the above â€œFaultingâ€ sequence, Chillers that are physically available to run but have an alarm that triggers the HW fault signal will never prove in the CHW Plant sequence The combination of the HW fault signal and the initial lack of â€œRunning Statusâ€ will trigger a â€œFaultâ€ and removal from rotation | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638614&prj=684&rqi=K6WgoKONlVZ9zPz7OJIT4lfnUU
GT1ELEC-348-001 | dc0fd82d-9ffc-49d6-ae91-9a0bd945e932 | SV18-2 | 684 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_H_2 | UPS - Uninterrupted Power Supply |  |  | (1UPS_H2) HMI failed to turn on when energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638408&prj=684&rqi=hYRTpuHkXMJwxeiIm9zlOqHYLj
GT1ELEC-356-001 | 14cf5b16-1563-4c3b-bf91-d24de8bd8298 | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_R2_1 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_1) HMI on UPS failed to turn on upon energization.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638388&prj=684&rqi=RkAZvQMWp97UPA6HKqxSNzSfwe
GT1ELEC-350-001 | 805ee842-8d72-4a99-ad52-881879a80f1c | SV18-2 | 684 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_J_1 | UPS - Uninterrupted Power Supply |  |  | (1UPS_J1) HMI failed to turn on when energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638409&prj=684&rqi=zwLok3kVffUK87GSJXJJpxa8o0
GT1ELEC-357-001 | 0c76702f-ad51-49a1-b396-6af85ea5c7ae | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_R2_2 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_2)Â HMI on UPS failed to turn on when energizing.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638387&prj=684&rqi=eB2fmH5CuNBjl9i7zhRdvRGbht
GT1ELEC-347-001 | d4390485-abf4-4bf3-8d9c-1ca7c36afcc8 | SV18-2 | 684 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_H_1 | UPS - Uninterrupted Power Supply |  |  | (1UPS_H1) HMI failed to turn on when energized.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638407&prj=684&rqi=tRnCHp6WZNZFsJbmCwTK2BdTbv
GT1ELEC-344-001 | 4c6f3d89-75fb-4918-9c76-8cc32be8683d | SV18-2 | 684 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-09-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_G_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G1 L3 Several failed components identified during startup of the equipment. Issues include the inverter assembly, power supply module, and several cards. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638187&prj=684&rqi=OOaqtwuIvh3kAr6cXUCJsn7vl9
GT1ELEC-106-001 | 079e3b88-2e41-4673-b8b6-cb214ccd0d36 | SV18-2 | 684 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-09-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1PDU_G1_1 | PDU - Power Distribution Unit |  |  | Sub feed 4 has a communication alarm inÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638236&prj=684&rqi=ylsxABGEXYiRHhrb4RVeGihwKc
GT1ELEC-254-001 | d609d93b-1d52-4c5f-8256-b34afe7bdb0b | SV18-2 | 684 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-09-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1RPP_K1_2_6 | RPP - Remote Power Panel |  |  | Top hinge for door came off and door was falling out of placement | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638237&prj=684&rqi=REZIXL0Vy3ctNXCq0RwOmRCWTh
GT1ELEC-101-001 | 6c0991b7-e346-4874-a9aa-9b6b554b73a2 | SV18-2 | 684 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1PDU_E1_4 | PDU - Power Distribution Unit |  |  | (PDU E1_4): HMI failure. HMI is not showing subfeeds.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638005&prj=684&rqi=PvJDD7JiWXljo6nL5QJSLX0n93
GT1ELEC-126-002 | b9d09aa5-0f0a-4b62-b79c-bb9db85363b5 | SV18-2 | 684 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1PDU_J2_2 | PDU - Power Distribution Unit |  |  | Missing disconnect for HMI power supplyÂ | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638027&prj=684&rqi=9k48i5gFAttWgaYXjkR3WQllLW
GT1ELEC-126-001 | 757b4e52-972b-4772-8aa2-c8b14a80f019 | SV18-2 | 684 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1PDU_J2_2 | PDU - Power Distribution Unit |  |  | (1PDU_J2_2) HMI displays aux power fail.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638026&prj=684&rqi=4kDZiBJcOWAQvNwf0g1dfpikOa
GT1ELEC-183-001 | 439fe8be-eaf3-41e2-b784-f859670adc48 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-09-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1RPP_E1_2_2 | RPP - Remote Power Panel |  |  | 1RPP_E1_2_2 L4 During HLT, a thermal deficiency was noted and the equipment was shut off. After further inspection, a bolt on the bus bar was found not properly installed or torqued. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638038&prj=684&rqi=FvQPYW6wqpLCiiwvuF7TgL2rvW
BT1MECH-41-001 | a7a1b7a3-3045-40c9-972b-13ffcc14b193 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-09-11 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Comms Issue/ Fault | DCOS |  | Mechanical â€“ Water | equipment | 1CRAH_H_01 | CRAH - Computer room air handler |  |  | (All H-fed Data Hall CRAHs) L4 None of the H CRAHs are viewable on BMS, check if the MOH Network cabinet is up and working correctly? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637824&prj=684&rqi=e4MUkRGekS5RjA8sfALRgCnf20
BT1MECH-80-002 | 378479b8-fa0a-4e29-a52c-6f406e6e762f | SV18-2 | 684 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-09-11 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (HP_G_01) L4 BMS Graphic is switched in Aveva. HP-G-01 is showing data from HP-G-02 and vice versa. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637823&prj=684&rqi=hGFNZjBdZp9wfesXwgtTzgnXE7
BT1MECH-80-001 | e96320b1-1fb9-4a41-8f80-954fd60a06e7 | SV18-2 | 684 | AMER | Open | P2 Medium CX | alec.dughi@veolia.com | 2026-09-11 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Comms Issue/ Fault | DCOS |  | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (HP_G_1) L4 HP_G_ 1 port at network switch in D mark panel suspected to be bad. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637813&prj=684&rqi=iDrQYZe7TZ2RZC1ZJgUjT9ahTS
BT1MECH-56-002 | 86cedac1-a4bc-dcd6-6b7c-03e7e2e403ba | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-09 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_04 | CRAH - Computer room air handler |  |  | (1CRAH_K_04) L4 Unit produces significantly lower airflow than all other units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637509&prj=684&rqi=ojUsmXW7gH1hyjP2BoyR0mCguJ
BT1MECH-64-001 | baeaece7-da30-4033-b51a-5a5ffb9137ae | SV18-2 | 684 | AMER | Open | P2 Medium CX | ethan.hang@veolia.com | 2026-09-09 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_12 | CRAH - Computer room air handler |  |  | (1CRAH_K_12) L4 Two EC fans were taken and given to K_02 and K_04. New fans are needed for K_12. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637551&prj=684&rqi=qniYoLfkPEXKZvSF8xgbVeujmR
BT1MECH-56-001 | d2866469-63ea-4840-f6a2-88004d001121 | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | alec.dughi@veolia.com | 2026-09-08 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Incomplete Connections | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_04 | CRAH - Computer room air handler |  |  | (CRAH-K-04) L4 Condensate pump discharge copper piping has a leak at brass fitting that sprays water during pump operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637327&prj=684&rqi=OtDpUn07KGYR8XnVwPGFIC6qmh
BT1MECH-54-003 | 188dda5a-76a6-416c-1869-de5080abbc4a | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | alec.dughi@veolia.com | 2026-09-08 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (CRAH-K-02) L4 Condensate pump discharge copper piping has a leak that sprays water during pump operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637323&prj=684&rqi=ppPNDlDw3c2UnOyIgyOELsNgLl
GT1MECH-42-001 | 098361b9-e648-4de2-98d5-582d11adda2e | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-09-08 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | equipment | 1CRAH_G_01 | CRAH - Computer room air handler |  |  | (All K CRAHs) L3 At the BMS floor layout, all K CRAHs are labeled as J CRAHs. Etech relabeled to K. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637287&prj=684&rqi=1qfdVaJpbOesu7ch6aUBREyfcN
BT1MECH-55-002 | 2e9aa324-6110-0f1c-a5e6-a7ae118da4e4 | SV18-2 | 684 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-09-04 04:00:00.000 +0400 | Mechanical Contractor | L4 | Incomplete Connections | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_03 | CRAH - Computer room air handler |  |  | (CRAH-K-03) L4 Leak detection module is wired incorrectly. Not using the correct 2 out of 3 wires in both power and signal bundles going into the module itself. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636922&prj=684&rqi=ASNdAiJzXyOow1F8wB12lKo3G9
BT1MECH-37-002 | 8b3758f0-4b4b-cc34-7e22-773076aaecf4 | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | alec.dughi@veolia.com | 2026-09-03 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_09 | CRAH - Computer room air handler |  |  | (CRAH-G-09) L4 Condensate pump discharge copper piping has a leak that sprays water during pump operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636755&prj=684&rqi=GwmshKmED2ubW0qdctWxGLS71L
BT1MECH-36-001 | b0a92952-e62c-4074-b9c6-5ef3b2b40645 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_08 | CRAH - Computer room air handler |  |  | (1CRAH_G_08) L4 Failing RAT sensor does not make the fan speed go to 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636599&prj=684&rqi=3eUk34Mzry89cHltSbTixeo02j
BT1MECH-37-001 | c74a651f-3329-4292-bc9d-a6ebba8dd813 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_09 | CRAH - Computer room air handler |  |  | (1CRAH_G_09) L4 Failing RAT sensor does not make the fan speed go to 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636600&prj=684&rqi=A0rbLKiSn29OqPMt4vNlmYghgt
BT1MECH-54-002 | 869d8cc5-e9c7-958a-2b7c-2781fb5e901d | SV18-2 | 684 | AMER | Open | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (1CRAH_K_02) L4 K10 contactor is defective, preventing the correct operation of the ATS function. Replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636593&prj=684&rqi=KgsCBs1oG5fx3TQwWVrDxvZt0v
BT1MECH-54-001 | 1be775de-0a4d-684f-0d9c-5fdcbdde5304 | SV18-2 | 684 | AMER | Closed | P1 High CX | alec.dughi@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Incomplete Connections | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (1CRAH_K_02) L4 CHW valve 2 has no power. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636568&prj=684&rqi=SZiyUur9KWA6rK5D1UQFZcHaU4
BT1MECH-55-001 | f51f7ba3-1846-4608-aa08-0855ed44f75e | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_03 | CRAH - Computer room air handler |  |  | (1CRAH_K_03) L4 Failing RAT sensor does not make the fan speed go to 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636596&prj=684&rqi=1dxkTJHF5XORRfzvHsMAa3QcNR
BT1MECH-35-003 | 6cb6d2ca-3474-4302-a34b-7ffcb4bed0f4 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (1CRAH_G_07) L4 Failing RAT sensor does not make the fan speed go to 100% | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636597&prj=684&rqi=iNW8g2rbVkag4obmhrcnNtorVa
BT1MECH-57-001 | 1b870937-075e-cb23-12e1-09bebf7f6dcc | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-09-02 04:00:00.000 +0400 | Ver - Vertiv HVAC | L4 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_05 | CRAH - Computer room air handler |  |  | (1CRAH_K_05) L4 Failing RAT sensor does not make the fan speed go to 100%. EDIT 9.9.26: Hidden setting "Sensor Fail Fanspeed" found. Units require firmware update PA2.08.17R Build 20260303-185731 for this setting to be active. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636594&prj=684&rqi=NLI9ROG2C52kUVS1PiS6NyE9CH
YT1ELEC-155-001 | de2af298-b190-43f4-81c7-56a7cc384bb2 | SV18-2 | 684 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-09-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1RPP_A1_1_1 | RPP - Remote Power Panel |  |  | All RPPs L2B A single screw on all 4 corners of the panel board is too long and requires replacement. AMG is tracking this issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636356&prj=684&rqi=LXvub3fsrADWn1h3LyjI2FJbRT
BT1MECH-35-002 | 6809112f-cf55-7f16-9ecc-95094a224117 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-31 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (DH CRAH) L4 Supply fan speed command is not showing correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636165&prj=684&rqi=j9fzgfb3SATjUTWTQ8fi9fSjqs
BT1MECH-35-001 | 780c86eb-e6ca-22be-c12b-34a614e31c9a | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-31 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (DH CRAH) L4 Supply fan speed command is 1 input behind at the BMS. ex: default starts at 50%, inputting 60%, fans go to 60% but BMS stays at 50%, inputting 70%, fans go to 70% but BMS goes to 60%, etc | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636164&prj=684&rqi=fVIaXjYrR6vzXZ2zftt3msJB7H
GT1MECH-18-001 | ff6969f7-7f13-91d6-c121-eeef93cb9e3b | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-31 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_01 | CRAH - Computer room air handler |  |  | (1CRAH_G_1) L3 Source 2 50A fuse bracket was found to be broken during L3. Replacement bracket and fuse needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636119&prj=684&rqi=1txNMcRqPRiDXl3zZ8gfPI6KHr
YT1ELEC-355-002 | 5d8555da-aca9-4be3-9f74-71768c4902a8 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_J3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_J3 L2B Broken Dry Contact Card that requires replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635695&prj=684&rqi=AlXnw0Y7ilK2JKlAY0qR3EEqan
BT1MECH-61-001 | cdba36d5-b971-4088-8237-82dd1a606d18 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-27 04:00:00.000 +0400 | Controls Contractor | L4 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_09 | CRAH - Computer room air handler |  |  | (1CRAH_K_09) L3 Upper CAT6 port is not sending data to the Moxa switch for U2U communications. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635758&prj=684&rqi=n7IovP4ra2YrNjb1vCm7VFRYXi
GT1MECH-38-001 | 7dd39e31-a289-46ce-9509-f4b61378fcbd | SV18-2 | 684 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-08-27 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_09 | CRAH - Computer room air handler |  |  | (1CRAH_H_09) L3 Control board was donated to higher priority CRAH_K_04. CRAH_H_09 needs new control board. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635759&prj=684&rqi=kt9Zc9px3RcrYFB1fmkuHC8YJT
GT1ELEC-379-002 | 49c244b8-ffb8-4940-bc7b-899253e60890 | SV18-2 | 684 | AMER | Work Completed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | UPS_G3 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635474&prj=684&rqi=2SwkAZp1z5rRsvlvNbDo4C3JrP
GT1ELEC-93-002 | 0a28e72b-1957-4220-98dd-3aafced872a3 | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | UPS_R2_2 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635473&prj=684&rqi=lyvw3r8fBSOSY0oZEdkJPegTFt
GT1ELEC-380-001 | efe8b2bf-d0d5-4e72-8b78-07bac0c81f62 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_H3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | UPS_H3 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635475&prj=684&rqi=fVOthLR27sjXz7oL6ilFfg46iD
GT1ELEC-92-002 | b685a21b-f856-4793-9adf-43b5d74b265c | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | UPS_K_1 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635470&prj=684&rqi=oO7o9oVeZxofUQS9fFRH3BXfnv
GT1ELEC-91-001 | 8af9d846-17e9-4895-9900-dbbed2d6fcd2 | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | UPS_J_1 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635466&prj=684&rqi=JfvGaq5MxFSmgOlGiiiDWPZT0a
GT1ELEC-93-001 | deee7bac-24a6-49d8-9e6d-f7c0022af790 | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | UPS_R2_1 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635472&prj=684&rqi=yZPW1nZET506MeRXOgFggpRAWA
GT1ELEC-381-001 | 8b5c0227-4d4f-4070-b039-c42900d60945 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_J3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | UPS_J3 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635476&prj=684&rqi=ntjHn0jjmsrP7K08gxNz4SEdgE
YT1ELEC-237-001 | fc2624a0-1dcd-422d-b3ab-f8c1dc4b23f9 | SV18-2 | 684 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-08-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1RPP_H2_2_5 | RPP - Remote Power Panel |  |  | Found a broken/damaged connector piece during normal inspection of RPP | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635337&prj=684&rqi=Y7a90hvrb1z9TVU4Dyx8Zo9bs5
BT1MECH-65-004 | 960af819-e74e-4315-a1b3-3390ca8ba0ee | SV18-2 | 684 | AMER | Closed | P3 Low CX | abdul-qadeer.bilal@veolia.com | 2026-08-26 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS General Issue | DCOS |  | Mechanical â€“ Water | equipment | 1CRAH_G_13 | CRAH - Computer room air handler (Skid) |  |  | (All Skid CRAHs) L4 Supply air temperature on CRAH BMS faceplate is not actually tracking the SAT that the valve controls to. Please use address 0x0017 dec 23. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635452&prj=684&rqi=pAzteOhMPDPlmuQgt41GC8XRTa
GT1ELEC-89-002 | ac4d2230-611f-4652-9cad-ab5346b05e1c | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | UPS_G_2 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635462&prj=684&rqi=O0Rp43otYcnGCLUzb6kbBw5sJI
GT1ELEC-91-002 | 4d3083d9-14cb-4626-be92-6a7bf99bc708 | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | UPS_J_2 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635468&prj=684&rqi=BY5yBHyekYtHQDE3uNf9Wn9Bxp
GT1ELEC-89-001 | dfd9ef5f-b668-4781-a40e-0037b6914e2b | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | UPS_G_1 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635461&prj=684&rqi=qFy0xyOG8fvegxPccmFWUtxJmg
GT1ELEC-383-001 | b416c8a8-cd1e-494c-b744-a0c7e38db744 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_R2_3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | UPS_R2_3 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635478&prj=684&rqi=YLXTzGPHshlKOmE6C7w3nxLVqV
GT1ELEC-382-001 | aaa9a403-88bb-419e-8fcb-40c2d78948bf | SV18-2 | 684 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_K3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | UPS_K3 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635477&prj=684&rqi=4T8Gw3vqnPjWNbmMnPngKqEuRz
GT1ELEC-90-003 | aaaa62f1-fa72-4301-a8e5-64638387dfe1 | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | UPS_H_2 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635465&prj=684&rqi=6EyuuPt5FBEjuNEX4Rzmcp1CEC
GT1ELEC-90-002 | abf19b99-e433-47a5-8d22-3b2e277d07e6 | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | UPS_H_1 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635464&prj=684&rqi=1LpstRsMsjh83HLSruspOTYnaT
GT1ELEC-92-003 | 13ecb5f3-46a9-49cd-84ad-88ca6a172f89 | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | ian.tsurumoto@veolia.com | 2026-08-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | UPS_K_2 SKRU incorrectly wired | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635471&prj=684&rqi=dkELbBY2FKAhlw68sZza9DsAZ3
BT1MECH-65-003 | 610cfc9d-2b09-4b2a-bd0e-437408627495 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-25 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Comms Issue/ Fault | DCOS |  | Mechanical â€“ Water | equipment | 1CRAH_G_13 | CRAH - Computer room air handler (Skid) |  |  | (All Skid CRAHs) L4 Writing SAT and DT setpoint from the HMI does not update at the BMS. If a new number is then written from the BMS, it overrides the HMI as usual. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635131&prj=684&rqi=Xn4lhMENAajV69gN2dNLB8QNis
BT1MECH-73-001 | 81cb77bd-34c0-1043-bce0-fce45bccbc2c | SV18-2 | 684 | AMER | Closed | P3 Low DCOS | ethan.hang@veolia.com | 2026-08-25 04:00:00.000 +0400 | Controls Contractor | L4 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | equipment | 1CRAH_J_15 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_J_15) L4 Unit is mapped to J_13 on the floor layout, and J_13 is mapped to J_15 on the floor layout. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635191&prj=684&rqi=Jtlf8ZKL0t1LhsETROXtBJZJry
BT1MECH-65-001 | 096bdf90-be9c-4f81-8919-a750ce10b28e | SV18-2 | 684 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-08-21 04:00:00.000 +0400 | Owner | L4 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | equipment | 1CRAH_G_13 | CRAH - Computer room air handler (Skid) |  |  | (All Skid CRAH's) L4 Fan command to both supply fans is 1 signal. Separate supply fan commands for each fan exist on the BMS faceplate and 1 is always stuck at 0%. This prevents proper fan command mismatch alarming. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634681&prj=684&rqi=dTi69sxrvzTRfq27JIIgfRdJUf
GT1MECH-76-002 | d41c9b84-3b92-42c7-ac45-abf9d6f4efb0 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (HP-H-1) L3 Thermostat damaged during startup procedures, needs replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634443&prj=684&rqi=2tOvnXOilBDBXuwKKVkqsei8tH
GT1ELEC-346-001 | d5c55ba8-e8a5-47f4-aef9-13a02960fb63 | SV18-2 | 684 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_G3) L3: Battery breaker status on HMI is backwards. When breaker is shut, it indicates open.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634552&prj=684&rqi=IbvqnsJRC4RJagnA3XZc3GQkXL
GT1ELEC-379-001 | 2a65f0c8-b38e-4377-b2a5-c6953d8fb3cb | SV18-2 | 684 | AMER | Work Completed | P3 Low CX | chase.negich@veolia.com | 2026-08-20 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | (1UMDSB_G) L3: Kirk key interlock does not provide indication on UPS or UMDSB.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634554&prj=684&rqi=4GPf6N5aWE35ylL9y5eJxuM1yu
GT1MECH-82-002 | e2399f5d-718d-486b-a37e-74ab1909b183 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L3 Trane FSR found Bellimo Valve to not be functioning correctly. Trane has contacted MPS and they will work on getting a replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634485&prj=684&rqi=ZtXMdIUlVokIhGvoRd6DkIe03u
GT1ELEC-346-002 | 1fea6713-de8a-4b5a-8356-01c12a94869a | SV18-2 | 684 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_G3) L3: MBB does not indicate position on UPS HMI. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634553&prj=684&rqi=D0jit0av8jtV7yb9wzgrN2HaoD
YT1MECH-90-004 | d97dca4e-9082-660b-0596-02f03024021f | SV18-2 | 684 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-08-19 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (HP-R2-1) L2B Phenolic circuit labeling (circled in red) is incorrect (labels are swapped between HP-R2-1 and HP-R2-2). To clarify, east-most HPs are HP-X-1 and west-most units are HP-X-2. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634293&prj=684&rqi=a02Lqfb8gLT3jnGfS6Ms9vpUNG
GT1MECH-69-001 | 90463d2a-de25-47aa-b7d7-23857493caf3 | SV18-2 | 684 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-08-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“Air | equipment | 1EF_G_1 | EF - Exhaust Fan |  |  | (Skid Leak Detection) L3 Etech has found a bad leak detection cable section on the DMARK wall. New replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634236&prj=684&rqi=7wohsSmYg3OIS2xycgB1ENSOia
YT1ELEC-358-002 | 1606c7de-5831-45f3-a321-7fbb6df6a35b | SV18-2 | 684 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-08-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_K3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_K3 L2B:Â Torn door filter on cabinet panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634144&prj=684&rqi=4lJ1CzZXspUGxxcdW9mxBEW1jZ
BT1ELEC-4-001 | f52e6347-f299-4894-b982-c61278ffe3a2 | SV18-2 | 684 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_K | GENL - Generator (LV) |  |  | 1GEN_K L4 Failed pneumericator motherboard for 1GEN_K. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634012&prj=684&rqi=b42EuufHkZt5eTVKyQNodbRUBF
GT1MECH-75-001 | d00fe336-76b0-40b1-9741-a154b913679d | SV18-2 | 684 | AMER | Open | P3 Low CX | alec.dughi@veolia.com | 2026-08-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (HP_G_2) L3 Thermostat control wiring insulation is damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633996&prj=684&rqi=YSAA2YjSzVBZv6IWkf1ruBSB1S
BT1ELEC-3-001 | d1a55827-fe6c-4a27-b245-6b7e4b5ea283 | SV18-2 | 684 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L4 | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_J | GENL - Generator (LV) |  |  | 1GEN_J L4 Failed speed indication in 1GEN_J during testing. Warning came in early into testing labeled '689 ECM.C3 Crankshaft Speed Error'. This did not stop the test from completing but needs to be resolved. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634005&prj=684&rqi=MPeXajPmcqFDS3k7Dwplhj88MR
YT1ELEC-349-002 | 066574df-e3d6-4e5c-861a-48029b0015af | SV18-2 | 684 | AMER | Open | P3 Low CX | ismael.zapien@veolia.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G3 L2B Torn filter on UPS enclosure door | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633730&prj=684&rqi=HTBJf7L0g10y6LmX5uXz7urFn5
GT1MECH-83-001 | b2bb5842-9d75-46e7-8f7a-237de5351fb4 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-08-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (1HP_R2_2) L3 Trane FSR found Bellimo Valve to not be functioning correctly. Trane has contacted MPS and they will work on getting a replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633727&prj=684&rqi=IKvEubLEQ0Z6f6wGWT5IF8D6nK
GT1MECH-82-001 | f56be6a5-cefb-450c-a14c-3bcf18a1d309 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L3 BMS skid floor layout labelled incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633460&prj=684&rqi=sH1Ti7pYYawjep3U2wyLAg65tz
GT1MECH-76-001 | ecc2714a-3057-4ec7-acd5-ba0e74c1e2f3 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (1HP_H_1) L3 BMS skid floor layout labelled incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633456&prj=684&rqi=BYK4DTBiAhJZ2sMtDW3NGauKqc
YT1MECH-80-005 | 09509794-e772-2577-fbc6-61429f343ea1 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_K_1 | EF - Exhaust Fan |  |  | (Skid K leak detection) L3 CAT6 cable is too short to be terminated at the leak detection panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633532&prj=684&rqi=OrvQfJOWtVnsH6rjYMkCeqPohQ
GT1MECH-74-001 | e961d3ac-4696-44ca-abf0-98ac9fe24cfb | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (1HP_G_1) L3 HP_1 and HP_2 objects are flipped on the floor layout at the BMS. See attached electrical bulletin #2 for correct asset tags. Typical for all skids. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633453&prj=684&rqi=5APEFbdAZQJBG7fncSm40iCIbG
GT1MECH-80-001 | 8fdf9a77-b2ac-4dde-8447-5bb4b6b0baf3 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (1HP_K_1) L3 BMS skid floor layout labelled incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633458&prj=684&rqi=bOh5wACLzdBD3xJGshKIBUMKz5
GT1MECH-78-001 | c7650c7b-2664-4700-9619-635dad93fdc5 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-13 04:00:00.000 +0400 | Controls Contractor | L3 | DCOS Graphics Issue | DCOS |  | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (1HP_J_1) L3 BMS skid floor layout labelled incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633457&prj=684&rqi=ZXjuGki9KTrRYoh6GEbxK48Kdu
RT1MECH-85-005 | 39a13e27-404f-169f-a6b2-e7cec6822beb | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (1HP_H_2) L2A Heat pump missing thermostat. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633268&prj=684&rqi=uIo1eiS2D6wt1KBvfXKdAQXNj1
RT1ELEC-247-001 | 4f78da66-a480-44cf-bb4e-e3cb27f75a80 | SV18-2 | 684 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-12 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1RPP_K1_1_1 | RPP - Remote Power Panel |  |  | 1RPP_K1_1_1 L2A FST cannabalized a set of screws for one lug kit inside of this RPP. Creating this case to track the replacement of these screws and the lug cover. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633384&prj=684&rqi=fT5Fo92Ryh2qFwaoXhukNLD93r
GT1ELEC-90-001 | e98009e8-50ee-41bc-8c29-099172fb2b39 | SV18-2 | 684 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | 1MSB_H L3 1MSB_H Breaker Q15 control panel has a failed motherboard that requires a replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633267&prj=684&rqi=Q1ojYMJckG9HRdM2ZQGu8FBiId
GT1ELEC-92-001 | e52c5f4b-8f62-4454-b465-1e310604f050 | SV18-2 | 684 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-08-12 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L3 | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | 1MSB_K Tracking Purposes FST has cannabalized the Phase Sequence Relay off of 1MSB_K for installation on 1MSB_F. Please provide an update on the schedule for delivery and replacement in 1MSB_K | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633278&prj=684&rqi=lVGF2eFv8wEO9dy8ssYf101SRF
GT1MECH-27-001 | 4c0f7406-16d3-4e61-869c-dc2e30ce6086 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_10 | CRAH - Computer room air handler |  |  | (1CRAH_G_10) L3 Constant motor overload/EC fan fault alarm | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633072&prj=684&rqi=hhxbvCT2g1xRXlG5OdQrI9uqyS
GT1MECH-24-001 | e51bb125-0232-44db-83d0-a1dc90745ddb | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (1CRAH_G_07) L3 Constant loss of airflow alarm present on the unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633071&prj=684&rqi=PrCT9DejUrSq9d4y8et1ik3zYk
GT1MECH-28-001 | 1e88f07c-12a2-411f-ad7b-0a8f55f819b0 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_11 | CRAH - Computer room air handler |  |  | (1CRAH_G_11) L3 Constant loss of airflow alarm. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633073&prj=684&rqi=g6XmfqYwSpWQwv0sWGsFDXVGUo
GT1MECH-43-001 | 83a52724-aaa1-4032-9fb7-333bedbdb358 | SV18-2 | 684 | AMER | Closed | P1 High CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (1CRAH_K_02) L3 Fan 8 replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633075&prj=684&rqi=8UIvYUvA5v5qvDwJFpbA9YaPny
GT1MECH-44-001 | d03d64c9-ef3e-4daa-8533-34e157f38a16 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_03 | CRAH - Computer room air handler |  |  | (1CRAH_K_03) L3 Unable to put the unit into manual mode | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633076&prj=684&rqi=ehFyAyJUqRD28cyz6UeNlrZ4Aw
GT1MECH-45-001 | b0a85bfb-ca4b-42ea-acd6-ff08063ad14e | SV18-2 | 684 | AMER | Closed | P1 High CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_04 | CRAH - Computer room air handler |  |  | (1CRAH_K_04) L3 Fan 1 replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633078&prj=684&rqi=JcGqZTm5XskBKqoAsxWBlDClSu
BT1MECH-1-001 | bce5b2bf-482d-4e17-a6e6-5b09e6a11a70 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | TRN - Trane | L4 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1ACC_J_09 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_J_09) L4 DC/DC converter for compressor 2 communications failed on R2_06 during 4 hour HLT. Part cannibalized from J_09. Replacement delivered. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633088&prj=684&rqi=l9OFQ5iorgaJyWpBQNMrTcwcZ5
RT1ELEC-190-001 | 21011547-f558-47a4-aa53-74310d545d17 | SV18-2 | 684 | AMER | Open | P3 Low CX | jordan_dubose@fsttechnical.com | 2026-08-11 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1RPP_E1_2_5 | RPP - Remote Power Panel |  |  | (1RPP_E1_2_5) The cover is incorrectly sized by the manufacturer resulting in the exposure of the breakers for the branch circuits 69 and 71. The serial number of the panel is F1251024EQX00647. This issue was entered originally as issue #1048 in SV18-1 before the clarification that the 1st floor 1RPPs are part of Veolia's scope. Anord Mardix Group (AMG) is already aware of this issue and needs to provide estimated date of when the replacement cover can arrive to SV18. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633137&prj=684&rqi=Q5caajvuithN0FQJZ1pV6IbFeb
GT1MECH-46-001 | aceb8f00-489a-4bb2-b8f6-6a575b14bf23 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L3 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_05 | CRAH - Computer room air handler |  |  | (1CRAH_K_05) L3 Unit unable to be put into manual mode. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633080&prj=684&rqi=OdnuwSEwCjVGlyFvcqs7nIGwYs
GT1ELEC-370-001 | 8087e6ec-14d9-459b-913c-75b574129db2 | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | chase.negich@veolia.com | 2026-08-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_R2 | GENL - Generator (LV) |  |  | 1Gen_R2 (L3): E-STOP did not open Gen output breaker. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632951&prj=684&rqi=tA5dKslQfYK1oxxmmntUqQvUrs
GT1MECH-85-001 | 529fc13b-b5ea-42db-8add-fa71353fef24 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-05 04:00:00.000 +0400 | TRN - Trane | L3 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1ACC_R2_05 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_R2_05) L3 Compressor 2 communication module was found to be faulty. Trane had a new one on hand and replaced. Adding as a closed issue. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632327&prj=684&rqi=I233Mw3nKgpCxu4SQgdjnHTQVp
YT1MECH-31-001 | 352f27b4-989a-2e67-fd89-fc4507920bc2 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-08-04 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_06 | CRAH - Computer room air handler |  |  | (1CRAH_G_06) L2B Ground wire disconnected. Re-crimping needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632217&prj=684&rqi=0gsnU7jKvPKHWY1pf0vSjIWQ8z
GT1MECH-84-001 | d1a02846-cc6c-4b05-87ae-e4a887c7e6da | SV18-2 | 684 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-08-04 04:00:00.000 +0400 | TRN - Trane | L3 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1ACC_J_09 | ACC - Chiller â€“ Air Cooled |  |  | (ACC-J-09) L3 During startup, CHWP VFD disconnect failed. Need new part. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632142&prj=684&rqi=29xoUUc2J6TuTe7M3XUZUekVUw
GT1MECH-87-001 | e8db381d-f191-4428-83d3-8ebd89318f95 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-08-04 04:00:00.000 +0400 | TRN - Trane | L3 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1ACC_J_10 | ACC - Chiller â€“ Air Cooled |  |  | (ACC-J-10) L3 CHW leak was found on return side of chiller piping, right before CHW pump. Leak has been narrowed down to the gasket betweeen Victaulic T fitting and black coupling on CHW pipe, gasket to be replaced before running pump. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632144&prj=684&rqi=QA3O0025iDhRCpUtM6519nfd3S
YT1ELEC-95-006 | 8a90c61b-bf57-4502-a7a4-0290ffaf2ec8 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-07-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | 1MSB_K L2B Section 02A had factory installed ferrules from MPS that were too large. The ferrules installed were for gauge 14 wires but the wires are gauge 16, so the wires were pulling out of their pins with little force. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631866&prj=684&rqi=rxeY86brNrlzTYpwwn5of5i6Ri
YT1ELEC-63-001 | 77c84b91-bcbc-45f0-828e-dc04d3cd8881 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_K1_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K1_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631522&prj=684&rqi=PoWsdPKxkIS0ZRbh5pYZRQaht3
YT1ELEC-72-001 | 23dd6c77-ec4a-4759-b692-362995af87ed | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_R2_1_2 | LIBATT - UPS Battery |  |  | 1BATT_R2_1_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631646&prj=684&rqi=zilp9S69rQWZvJ39arKKFtRwub
YT1ELEC-62-001 | a2775cbe-7fa0-4593-8a5c-a30d440cf1e2 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_K1_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K1_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631517&prj=684&rqi=SStiOdFAE5UNeaeVOczSkszIVV
YT1ELEC-55-001 | 09183868-1709-42d7-9390-fc09dd762339 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_J1_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J1_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631510&prj=684&rqi=qgAyfaNSKOSrDVaJCf22pIBzp5
YT1ELEC-60-001 | 89e69c07-ab12-4b8a-8c83-776b2add94f6 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_J2_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J2_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631515&prj=684&rqi=n25cckn1uecnETZK9cZIbZJKQM
YT1ELEC-73-001 | fbf54040-2768-4990-b1c2-218f5d0dbe74 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_R2_1_3 | LIBATT - UPS Battery |  |  | 1BATT_R2_1_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631648&prj=684&rqi=RlSzjich3QYI7TKE66Ukfhkdnd
GI-005 | b080329d-e539-4af5-ba31-1d0302aca42c | SV18-2 | 684 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [7 empty] | Common to all RPPs RPP incoming termination points labeled CBA vice ABC. RPP subfeeds labeled CBA | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631642&prj=684&rqi=FEqAZ0sWOvw9Il8CH5w8PLpeja
YT1ELEC-65-001 | 9eafbc8c-d202-4936-8fc4-b2c6f7a04675 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_K1_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K1_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631636&prj=684&rqi=Pzbe98XWmkmrbZ0PfnsycuK1oM
YT1ELEC-64-001 | 4deed747-370d-475d-ba45-6f53fb0347af | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_K1_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K1_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631632&prj=684&rqi=Coz1ukRBVNxGYFVz8zWhmf6KzH
BT1MECH-8-001 | 36fe3b22-3b27-4f3a-9d46-ef983843a4e0 | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | ethan.hang@veolia.com | 2026-07-30 04:00:00.000 +0400 | TRN - Trane | L4 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1ACC_H_13 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_H_13) L4 For tracking purposes, during a fast restart test while the chiller was at 100% capacity, the CB218 relay intermittently failed. Trane is working on sending a replacement. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631542&prj=684&rqi=gvcHRQAUcfXCPKRpCBSRdUbBNy
YT1ELEC-66-001 | 04b93b7d-3d6a-47b3-87ab-958eeaa28b08 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_K2_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K2_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631637&prj=684&rqi=Awfb1Cal1Ok58ZXH7js0Il6ETx
YT1ELEC-76-001 | 6ed3bcfe-9b98-4a3e-a782-182eac51d6d3 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_R2_2_2 | LIBATT - UPS Battery |  |  | 1BATT_R2_2_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631654&prj=684&rqi=GFBpPd8XchlKvEeL57t01FSFNX
YT1ELEC-347-003 | f3e3f9f8-5de3-454f-8a66-d2d311bd4553 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_G_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G1 L2B Several components have been cannabalized for repair on Phase-1 SKIDs by the Delta team. Equipment that was taken is as follows: 1 M-board 2 P-boards 1 H-board 2 Fans | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631592&prj=684&rqi=VjQBugnynQjLsQ5irG83WX9noU
YT1ELEC-54-001 | 3c69d051-7395-40a0-87a5-466c2831c2f5 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_J1_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J1_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631509&prj=684&rqi=sMYipCAJP7W8LsQKn5U2cwHJqM
YT1ELEC-67-001 | f53bb9f8-b67f-4915-9011-e3c9b88b33fa | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_K2_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K2_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631638&prj=684&rqi=biAW8uyc8xGTfp1aLCm2WERKOo
YT1ELEC-59-001 | 55f3d33b-95f2-44db-a3f9-03ca22b47941 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_J2_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631514&prj=684&rqi=S9XJDdPs98nh12OPSBcGWbm3ob
YT1ELEC-75-001 | 3bec4144-5f52-4b2a-bb14-ef5263807bb9 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_R2_2_1 | LIBATT - UPS Battery |  |  | 1BATT_R2_2_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631650&prj=684&rqi=xhIXG3lPB7RLlMJdnKR63om4XD
YT1ELEC-78-001 | 7e8bc587-5060-4499-81f9-fb28bd6f823f | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_R2_2_4 | LIBATT - UPS Battery |  |  | 1BATT_R2_2_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631656&prj=684&rqi=TyZpx7DYhbs4ZNkyZzU7KzM1qB
YT1ELEC-68-001 | bc7d056e-3cb2-4a12-b6ad-aec5c805149a | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_K2_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631639&prj=684&rqi=MSmKlFK06Zk7YU4FmaejBfxHvU
YT1ELEC-71-001 | d251e573-8cdd-4ceb-a4aa-cbf05579d040 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_R2_1_1 | LIBATT - UPS Battery |  |  | 1BATT_R2_1_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631645&prj=684&rqi=PnZtNYkpuis011gD8TZz4PfQLN
YT1ELEC-58-001 | 11c3d16a-4d1a-4dad-8992-6c642042beb9 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_J2_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J2_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631513&prj=684&rqi=DVj3kXPJMB5bkXBk72h7FtsrjA
GT1MECH-12-001 | d4a6406f-a9ce-4500-a9da-e1aa8f9ae40b | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-30 04:00:00.000 +0400 | TRN - Trane | L3 | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CHWP_J_09 | CHWP - Chilled water pump |  |  | (1CHWP_J_09) L3 During start up, Trane found that the CHWP disconnect had failed. Trane is working on shipping a replacement part. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631547&prj=684&rqi=BHdWfAbXYoij6FZPBQSb4hIlza
YT1ELEC-79-001 | 3ad4fb43-942d-4339-b595-ec2138362b82 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_R2_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_R2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631657&prj=684&rqi=VcLA24JFjl0zBfMrwnXIYYx0TY
YT1ELEC-53-001 | 69ff9f25-4bb4-4ea2-8e29-d785cbd9b07e | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_J1_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J1_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631453&prj=684&rqi=fXaZf1DmcnWpnDReuqdTq9VTSr
YT1ELEC-61-001 | 4c1c8214-ea79-4b6e-8804-1bbd18b06970 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_J3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631516&prj=684&rqi=Rq1nNLtCDMcUn0jvd8ADGGd7cI
YT1ELEC-57-001 | ed290954-674f-409b-b7fd-62cb3e6e442b | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_J2_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J2_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631512&prj=684&rqi=aJQJHEC1r7dozcCf7XAxqIAoQe
YT1ELEC-69-001 | 9c80fb8a-e7ca-49d5-a396-233945f7f96f | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_K2_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K2_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631641&prj=684&rqi=I7MrztsMycAA72id7xHBDdD4cK
YT1ELEC-70-001 | ccf63afe-6ce7-44dd-aba4-9ee26537cd20 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_K3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_K3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631643&prj=684&rqi=oeAHl57gnLmH6qTtQ98QblsrKS
YT1ELEC-56-001 | ae24ef26-2148-44ee-9a36-a121b87219dc | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_J1_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_J1_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631511&prj=684&rqi=PULvz7agc9ufI5D8sPSOXfzjj1
YT1ELEC-77-001 | 09292723-93a0-4675-b495-c126b4496b20 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_R2_2_3 | LIBATT - UPS Battery |  |  | 1BATT_R2_2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631655&prj=684&rqi=fuRjvhtR3g1eW4GTIUSqU1g4kP
YT1ELEC-74-001 | ec5e6a1a-11f9-4565-8205-c672b05adc75 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_R2_1_4 | LIBATT - UPS Battery |  |  | 1BATT_R2_1_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631649&prj=684&rqi=HMMUopLVvktRVDswUlx90uZkoj
YT1ELEC-353-002 | 2a239abf-a54f-467d-bc65-35778fdf98da | SV18-2 | 684 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_J_1 | UPS - Uninterrupted Power Supply |  |  | Exhaust fan control wire from UPS_J_1/2/3 not correctly landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631288&prj=684&rqi=xOyRdJcczrmpo4Ng9Dgfqbk6cF
YT1ELEC-353-001 | 752e331b-fc82-41ee-84a1-fd64091f1dea | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_J_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_J1 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631285&prj=684&rqi=oDIBn5DhPfoULI8if1IC1cM6Fs
YT1ELEC-360-001 | 7cc519e1-87e5-40b8-9f53-6d5647635ff6 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_R2_2 | UPS - Uninterrupted Power Supply |  |  | 1UPS_R2_2 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631297&prj=684&rqi=Cn4QTGzSJnnPu4PGdCT8XOmkGm
YT1ELEC-357-001 | bb3a087f-bac9-4854-aac5-8a07a106f5ba | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_K_2 | UPS - Uninterrupted Power Supply |  |  | 1UPS_K2 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631294&prj=684&rqi=5FdnmgGA4Hhc4tAierL7BSkXl9
YT1ELEC-351-001 | 3b814d62-126e-4b11-81ca-ce9ef5dbb79f | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_H_2 | UPS - Uninterrupted Power Supply |  |  | 1UPS_H2 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631284&prj=684&rqi=pZjmLbo1ApNgccoiECnffLNicG
YT1ELEC-384-001 | 94d41a9e-1a7e-48c9-bb1c-05847ed412bf | SV18-2 | 684 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_J3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_J3 UPS_J_3 MBB breaker Q03 is missing its second set of aux contacts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631312&prj=684&rqi=nSjZiWrcAhw9RlFq3RtM0nDQAG
YT1ELEC-51-001 | 833fa158-f0ef-496c-8d53-bd917c31e89a | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_H2_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H2_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631326&prj=684&rqi=i6FMyikeil5ekZprdOOBTo2Dr0
YT1ELEC-48-001 | 87ca6af0-590d-41df-a73e-6c1ba48e771f | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_H2_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H2_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631320&prj=684&rqi=Mkp0xgmXjcEasTi43S7qCnFQEA
YT1ELEC-151-001 | 9fa98448-5937-4e01-b009-4c7f0215b4d9 | SV18-2 | 684 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1PNL_R2_1_HP | DB - Distribution Boards |  |  | 1PNL_R2_1_HP 1CRAH_R2_13 (SKID CRAH_H_1) landed at 7,9,11 vice 1,3,5 1CRAH_R2_15 (SKID CRAH_H_2) landed at 1,3,5 vice 7,9,11 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631300&prj=684&rqi=RvReHNrAP8FzfSFDIWXngtSBca
YT1ELEC-40-001 | 2cdfce7c-b669-4509-b14a-a1a22be3f98d | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_G2_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G2_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631304&prj=684&rqi=lj2SasQc0nDqJz44vRxVSlC4n3
YT1ELEC-42-001 | 59ff05a2-6841-4ad2-be5d-9e7ceb523ca6 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_G2_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G2_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631306&prj=684&rqi=6tlMwS0P8MPtOHIAoOqdbxQeGw
YT1ELEC-38-001 | d187675e-2e67-4232-8267-6a2424e24486 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_G1_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G1_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631302&prj=684&rqi=ihu26eglBKicWi9jM6O24jH2jk
YT1ELEC-347-001 | 10dffca7-8743-4abe-bd97-fa297fae94b6 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_G_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G1 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631278&prj=684&rqi=9XX1yZWGECiZ2WTChhtfiIoPeK
YT1ELEC-350-002 | 4b556ec4-7bec-464b-bb9c-d62337a6a7e8 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_H_1 | UPS - Uninterrupted Power Supply |  |  | Exhaust fan control wire from UPS_H_1/2/3 not correctly landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631286&prj=684&rqi=j8ppBvihxirQXVbPMSnpXqrLLt
YT1ELEC-347-002 | ca7c2be7-3d1b-4011-9b05-3bf621736f78 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_G_1 | UPS - Uninterrupted Power Supply |  |  | Exhaust fan control wire from UPS_G_1/2/3 not correctly landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631281&prj=684&rqi=CT4gSFDbUlppybhcjfsG1vlvfR
YT1ELEC-359-002 | 8a96628d-0dca-45b4-8560-1276c8d08784 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_R2_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_R2_1 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631296&prj=684&rqi=BGGyFLTkWfYxK81vA2kCWyrMhi
YT1ELEC-350-001 | 91f8607f-72d0-45c3-b1ed-961bc4711b68 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_H_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_H1 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631283&prj=684&rqi=yGhDSaMArh4vADvvo2mzAQuFu0
RT1ELEC-154-001 | 3e8b779a-8229-44c2-a9bd-fbcdb75350be | SV18-2 | 684 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Design Professional | L2A | Design correction needed | Design |  | Electrical â€“ LV | equipment | 1PNL_R2_2_H2 | DB - Distribution Boards |  |  | 1PNL_R2_2_H2 L2B SCCS lists all breakers as having fixed trip setpoints at 50A, however the EATON breakers installed, which are the correct breakers, have variable trip settings that need to be identified and adjusted on the breaker to ensure proper coordination and protection. The SCCS will need to be updated to reflect this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631235&prj=684&rqi=3C6B6PydB6nKxCqUTFzWnC4DsQ
YT1ELEC-50-001 | 9b25a9a8-5522-4b39-bd80-7ea3bd693662 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_H2_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631322&prj=684&rqi=PxQa0XUKrZHOR3sA7JgAfoZswy
YT1ELEC-385-002 | f921dff3-ab2b-4795-bc81-a8caaa9e3889 | SV18-2 | 684 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_K3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_K3 UPS_K_3 MBB breaker Q03 is missing its second set of aux contacts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631313&prj=684&rqi=2zeSDttRClIyIG59QdF1LXOGKb
YT1ELEC-95-005 | 2a27ae01-0c38-417d-adf5-5a6704207072 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2B The key-actuated selector switches on the MSB HMI lock the keys when not in the center position. The selector switches should not lock the keys in any position. Sheet 2 of Hanley Submittal Drawing #HSU-5478FO-ELC-DWG02 specifies this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631209&prj=684&rqi=3MEqP74lGWGRsUwlE2m4DOa1aT
YT1ELEC-382-002 | ae7e8f22-49bb-48a1-80b6-72e3689f5415 | SV18-2 | 684 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_G3 UPS_G_3 MBB breaker Q03 is missing its second set of aux contacts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631310&prj=684&rqi=4esAA9rFa0jdHkI0s6tg9aupUg
GT1ELEC-367-002 | 0dfb74a3-046e-46e9-ad53-153d7ed014a1 | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Comms Issue/ Fault | DCOS |  | Electrical â€“ LV | equipment | 1GEN_H | GENL - Generator (LV) |  |  | 1GEN_H L4 P2P Testing - Identified discrepancy with the GCB breaker status sending inverted status signals to the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631267&prj=684&rqi=tmEPYMmyZKj0vldXfAQjw65YQg
YT1ELEC-386-002 | 2890d6af-26f7-433c-8107-d770fd6cc356 | SV18-2 | 684 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_R2_3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_R2_3 UPS_R2_3 MBB breaker Q03 is missing its second set of aux contacts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631314&prj=684&rqi=gfcrwhd0lIRNCIyZwlMjOF8WDf
YT1ELEC-348-001 | a6cc10ef-c146-4140-9385-e1c42ac78d15 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_G_2 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G2 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631282&prj=684&rqi=gjYx8J7ssJ1iiFNeLVGaKbsZB9
YT1ELEC-37-001 | 4f06187e-6c35-472b-a972-c69634a7b1a7 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_G1_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G1_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631301&prj=684&rqi=0Vd0AHhPN5wWpj2JXzPtHYOnkr
YT1ELEC-41-001 | cdbae2aa-c802-4192-9684-5bbe21f360b0 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_G2_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G2_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631305&prj=684&rqi=9DAwwOMUHgWp4oUwDUdThbEKRE
YT1ELEC-95-004 | a9cb9106-0615-4466-a4df-63af5793054e | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2B MSB HMI has 4 key-actuated selector switches, and only 3 are required. Per Hanley submittal drawing #HSU-5478FO-ELC-DWG02, this switch should be removed and blanked off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631208&prj=684&rqi=3N6VklQUH2YUrZPrVUG7ZvMTXK
YT1ELEC-359-001 | f3e26042-481d-423a-880a-549e2c2ec8b3 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_R2_1 | UPS - Uninterrupted Power Supply |  |  | Exhaust fan control wire from UPS_R_1/2/3 not correctly landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631295&prj=684&rqi=0UxDA4VzjdIjb7fIGYSnkiVLs7
YT1ELEC-39-001 | 221ee1f1-3189-4718-a05b-d74e62aefec3 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_G2_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G2_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631303&prj=684&rqi=ufqQbLwUUnGZVcLDDWBbcsqisW
YT1ELEC-44-001 | f959a798-0755-4d85-bf12-ff837d1dc4bb | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_H1_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H1_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631309&prj=684&rqi=FqZ26VJtRjkrSaaFnTzPFdVzBj
YT1ELEC-356-001 | e9458024-7e71-4d70-9248-10311272919f | SV18-2 | 684 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_K_1 | UPS - Uninterrupted Power Supply |  |  | Exhaust fan control wire from UPS_K_1/2/3 not correctly landed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631290&prj=684&rqi=ARrUtzxP0xyw80jDSXwPy5yATV
YT1ELEC-45-001 | 77ff2dc7-2c25-4498-afcf-84cf275ac87b | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_H1_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H1_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631317&prj=684&rqi=AQyOhuOM6UAS2VZyMG1IWmjMSl
YT1ELEC-46-001 | 275fa88f-01b5-41f3-ae48-1235a1625836 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_H1_3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H1_3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631318&prj=684&rqi=sSdh6XqDoi4QQURZbm10eAGb1h
GT1ELEC-366-001 | cbf5ce2c-d1da-45ea-b76a-1c5ed5177dd0 | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | DCOS Comms Issue/ Fault | DCOS |  | Electrical â€“ LV | equipment | 1GEN_G | GENL - Generator (LV) |  |  | 1GEN_G L4 P2P Testing - Identified discrepancy with the GCB breaker status sending inverted status signals to the BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631260&prj=684&rqi=ksS7hpaMYrhXmTJH55kbTCQrih
YT1ELEC-43-001 | 15335867-a760-4760-a1f3-0646fa343bd5 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_G3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631307&prj=684&rqi=R3VBdHDB3OXLNgp34vr6JqJSOs
YT1ELEC-383-001 | c597ca38-df0a-4cde-b133-f5ea7b62f592 | SV18-2 | 684 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-29 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_H3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_H3 UPS_H_3 MBB breaker Q03 is missing its second set of aux contacts | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631311&prj=684&rqi=WleJPis38771k4xTi7iNPwUrlP
YT1ELEC-49-001 | b252e0b1-88b7-4aa0-a32e-b9f869feb0c5 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_H2_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H2_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631321&prj=684&rqi=zpp3IH3DHJYJcuvNu19Ilnt6NT
YT1ELEC-356-002 | 283e06cc-aa12-44fb-8d37-a06569ff9e3f | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_K_1 | UPS - Uninterrupted Power Supply |  |  | 1UPS_K1 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631289&prj=684&rqi=uELatiCUHFQUilPpZPF7Gn6UnG
YT1ELEC-47-001 | f2db312c-1cfe-4e8e-8b74-954aaa5d7a3c | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_H1_4 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H1_4 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631319&prj=684&rqi=bskrLnie7tJ6eNCnBHaEhIxFN9
YT1ELEC-52-001 | 4b9a389f-dd51-4bb0-a67d-bcd4bfbb07a0 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_H3 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_H3 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631327&prj=684&rqi=f6gNjslZAT4vOi8qoFsYeb7k6P
YT1ELEC-36-001 | 305e44c3-29e2-40a1-8bed-9673baf65cec | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_G1_2 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G1_2 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631299&prj=684&rqi=jAsixlpAnCRn4zIoSo5pojFIrw
YT1ELEC-35-001 | 735f5c6a-1031-48d5-8e1a-61c6be6c40ea | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_G1_1 | LIBATT - UPS Battery |  |  | 1BATT_1UPS_G1_1 L2B LSFT Retrofit Kits need to be installed into all UPS battery cabinets. The battery cables on top of the cabinet have had their connections broken by REG in order to facilitate this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631298&prj=684&rqi=mWJsS4WrYr6QN2bGZltjrsQoaI
YT1ELEC-354-001 | 8b2f18b1-7532-43e0-97b1-b86a7e0dfc96 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_J_2 | UPS - Uninterrupted Power Supply |  |  | 1UPS_J2 L2B All DPMG2 1200KW UPS units have the wrong rectifier hardware installed into the equipment. Correct versions of the hardware must be installed into the UPS before energization. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631287&prj=684&rqi=btiBCKTgy0ZLfc7GMXFxDZg9AD
RT1ELEC-155-002 | a88f2183-98ab-4309-b7d6-62ec3f933a5c | SV18-2 | 684 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Design Professional | L2A | Design correction needed | Design |  | Electrical â€“ LV | equipment | 1PNL_R2_2_H3 | DB - Distribution Boards |  |  | 1PNL_R2_2_H3 L2B SCCS lists all breakers as having fixed trip setpoints at 50A, however the EATON breakers installed, which are the correct breakers, have variable trip settings that need to be identified and adjusted on the breaker to ensure proper coordination and protection. The SCCS will need to be updated to reflect this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631236&prj=684&rqi=X62Mf7SkuVAMYd0vV84kOzQE33
RT1ELEC-153-001 | bb05c60e-c497-4162-9bea-c8f97916c058 | SV18-2 | 684 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-29 04:00:00.000 +0400 | Design Professional | L2A | Design correction needed | Design |  | Electrical â€“ LV | equipment | 1PNL_R2_2_H1 | DB - Distribution Boards |  |  | 1PNL_R2_2_H1 L2B SCCS lists all breakers as having fixed trip setpoints at 50A, however the EATON breakers installed, which are the correct breakers, have variable trip settings that need to be identified and adjusted on the breaker to ensure proper coordination and protection. The SCCS will need to be updated to reflect this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631222&prj=684&rqi=Mg7pAuZ5DHq2bahfieZPLYV9uI
YT1ELEC-144-001 | b4e0e35c-4fdf-4cfe-a3ac-5ab302967fa3 | SV18-2 | 684 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1PNL_GEN_J | DB - Distribution Boards |  |  | 1PNL_GEN_J TRIP/CLOSE switch installed on all phase 2 generator panels. Close feature not operable IAW design. Switch not installed on phase 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631096&prj=684&rqi=rDssoiFJ9Xmqgz06ALlsC9roqr
YT1ELEC-142-001 | 9c7c0eaf-55fa-4e08-9c58-2338d76f8c5b | SV18-2 | 684 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1PNL_GEN_G | DB - Distribution Boards |  |  | 1PNL_GEN_G TRIP/CLOSE switch installed on all phase 2 generator panels. Close feature not operable IAW design. Switch not installed on phase 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631094&prj=684&rqi=MsYB9eRiH94jSmfpGQQLH3NRCC
YT1ELEC-145-001 | 80e3a7a3-2988-4670-9363-e8774cd4224e | SV18-2 | 684 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1PNL_GEN_K | DB - Distribution Boards |  |  | 1PNL_GEN_K TRIP/CLOSE switch installed on all phase 2 generator panels. Close feature not operable IAW design. Switch not installed on phase 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631097&prj=684&rqi=TabpNHEVT4Wl6EPvxVpRwuWlzX
YT1ELEC-147-001 | 5d14ae87-390d-4e8a-be87-6ef014bdc04e | SV18-2 | 684 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1PNL_GEN_R2 | DB - Distribution Boards |  |  | 1PNL_GEN_R2 TRIP/CLOSE switch installed on all phase 2 generator panels. Close feature not operable IAW design. Switch not installed on phase 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631098&prj=684&rqi=NPih8gr2GsRkKp813iNOZLdhS4
YT1ELEC-149-001 | 5c3dea3b-84f2-4925-9c3e-9164a125797a | SV18-2 | 684 | AMER | Open | P3 Low CX | chase.negich@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1PNL_J_HP | DB - Distribution Boards |  |  | (1PNL_J_HP) L2B: Panel schedule does not match the wire tag. Verified that wire tag is correct.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631100&prj=684&rqi=b4nyFcbB7e3kXExGBl5q3lB7Lk
YT1ELEC-143-001 | 93024a49-fc03-4f8d-bd44-9ca14755bad6 | SV18-2 | 684 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-28 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1PNL_GEN_H | DB - Distribution Boards |  |  | 1PNL_GEN_H TRIP/CLOSE switch installed on all phase 2 generator panels. Close feature not operable IAW design. Switch not installed on phase 1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631095&prj=684&rqi=dMOr7nepyYU3FzEWxuPiri8uy7
GI-004 | 6ccf7a4f-a855-4613-97e1-bef4fab28cea | SV18-2 | 684 | AMER | Open | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | Design Professional |  | Design correction needed | Design | [7 empty] | Various issue and in consistantcies found in rev 2 of SCCS: UNPL and PNL breakers listed as fixed. Breakers are adjustable. ABB breakers do not allow for S and Int setpoint to be the same value. S must be smaller than INT | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630773&prj=684&rqi=t4yy8dTkXUkAtLovjOnlFrPvMC
YT1ELEC-95-003 | e944c97f-13e8-48ec-b4b6-2da98db5e5a2 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | 1MSB_K HMI Label plate does not show all switch positions listed in the submittal. Switch label should show all three positions (Auto/Auto, Auto/Man, Man/Man). See attach example. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630757&prj=684&rqi=KuCqO7pAXvVaBnc9KwfeoyIZY0
YT1ELEC-96-004 | 9eceaf6d-2aa8-49e4-8950-5e823e71aa35 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | 1MSB_R2 HMI Label plate does not show all switch positions listed in the submittal. Switch label should show all three positions (Auto/Auto, Auto/Man, Man/Man). See attach example. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630754&prj=684&rqi=Pb7gcybbmwUjaEul6wqKUTPpTt
YT1ELEC-92-002 | 6de159ec-fe77-4bb4-9303-9d915383d35e | SV18-2 | 684 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | 1MSB_G HMI Label plate does not show all switch positions listed in the submittal. Switch label should show all three positions (Auto/Auto, Auto/Man, Man/Man). See attach example. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630761&prj=684&rqi=nIzIORfkYl4RizobHMY9mNAoKm
YT1ELEC-94-002 | b2455bde-9146-4d2f-b9ae-81fcaf7a8855 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | 1MSB_J HMI Label plate does not show all switch positions listed in the submittal. Switch label should show all three positions (Auto/Auto, Auto/Man, Man/Man). See attach example. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630758&prj=684&rqi=D8l09MZH48AwRpEcJboaksMOQf
YT1ELEC-386-001 | 51a21704-c2a6-4299-ace2-b4e2e066c4b8 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_R2_3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_R2_3 L2B K3 Kirk Key (64400) is missing for this UMDSB. Hanley has spare key and will expedite a shipment to site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630751&prj=684&rqi=0E7vuC0kvK4TNFJa1dQGnGRhPB
YT1ELEC-93-004 | 4ef0f118-282b-41b6-896e-7f6547b6c3e5 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | 1MSB_H HMI Label plate does not show all switch positions listed in the submittal. Switch label should show all three positions (Auto/Auto, Auto/Man, Man/Man). See attach example. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630760&prj=684&rqi=bDUeN7l0yhAcOEzM91NUdUDWo1
YT1ELEC-385-001 | fc0e7ece-16aa-4a3b-92dc-2089e79b8d8e | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-24 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_K3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_K3 L2B K3 Kirk Key (64400) is missing for this UMDSB. Hanley has spare key and will expedite a shipment to site. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630750&prj=684&rqi=yaQ0LnO9qwxF6J27Es8mPoQX1P
GT1ELEC-145-001 | c9e253e6-9405-4b53-8e3e-6ab2c3964634 | SV18-2 | 684 | AMER | Open | P2 Medium CX | ian.tsurumoto@veolia.com | 2026-07-23 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1PNL_H_HP | DB - Distribution Boards |  |  | 1PNL_H_HP 1CRAH_H_13 (SKID CRAH_H_1) landed at 2,4,6 vice 1,3,5 1CRAH_H_14 (SKID CRAH_H_2) landed at 1,3,5 vice 2,4,6 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630624&prj=684&rqi=5QgHBP1HAsvYq5q8G4thU0CFne
YT1MECH-66-001 | c6a15c6d-dfeb-98db-b37a-d8ed5dc47429 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_14 | CRAH - Computer room air handler (Skid) |  |  | (CRAH-H-14) L2B Schrader valve core missing from vent point top left of coil | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630391&prj=684&rqi=074UD2o6ivzAiY4AALM8lbCE0f
YT1MECH-40-001 | b5a9b877-169b-b59f-ca1d-3270c614e6cc | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-22 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2B | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_03 | CRAH - Computer room air handler |  |  | (1CRAH_H_03) L2B Source 2 disconnect has been broken off. Replacement needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630461&prj=684&rqi=e18RZi1nzXKaolqf8GuOCnpGVa
YT1ELEC-88-002 | 8a610fd6-7586-4cd1-97f8-573fd5320507 | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_J | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_J) L2BÂ Panel grounding strap not installed in top hat.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630480&prj=684&rqi=5F3sEy16jhkiLfY3sFvWY4SrpB
YT1ELEC-96-003 | 99ef7d95-770b-41fb-9cd1-c6c773b7bfe7 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-22 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB_R2) L2B Failed comm cable in MSB_R2 that connects to PQM3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630433&prj=684&rqi=hygPiSBt4e3pyqPeum1CMzncP2
YT1ELEC-86-004 | fbc1791d-250c-4528-94aa-725bab2fa2d4 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_G) L2B Ground connection to a panel cover was not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630175&prj=684&rqi=dIhpZbxWk2yQNDFZKmM9psikrL
YT1ELEC-86-006 | 1646ff3e-37a6-47e0-77f0-2f2d5dd39d86 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ian.tsurumoto@veolia.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | MDSB_G panel ground inside top hat found disconnected during final inspection | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630622&prj=684&rqi=jPhZJYju8aIkywYEr9CkgpmynB
YT1ELEC-86-005 | fd1763f3-7870-2c6d-361f-5b613d09881a | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ian.tsurumoto@veolia.com | 2026-07-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Cleaning | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | washer found the on incoming bus on MDSB_G | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630621&prj=684&rqi=xZDNfSoNNsEsFrNpwp64PkKtRw
YT1ELEC-86-002 | bd5cce69-33e6-4991-8e21-2a3cefa2c826 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_G (L2B) The lug kits for breaker Q03 that feed 1TX_G_R1 are the wrong size and need to be replaced. This work has been completed by Hanley and verified by Veolia. Adding this issue item as a closed case. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629416&prj=684&rqi=9AVqLuG1ZPet66DqTmIXi0E7x3
YT1MECH-88-003 | dcaa64b8-65f4-4888-ae58-c0ec84bd3863 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-15 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (HP-K-1) L2B Overhead junction box has an unfinished splice that should be a continuous run per Equinix electrical design. Please run a new line from PNL-R2-2-H-1 with no splice. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629434&prj=684&rqi=freTmsiYbvqiqKXdUg5RCAABbF
YT1ELEC-88-001 | b9f4f98d-aa84-4aa5-b5fd-3ff11f9ec0b1 | SV18-2 | 684 | AMER | Open | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_J | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_J L2B Breaker 1UPS_J_3-RIB (Q07) does not have wires pulled or installed on aux contacts for UPS RIB breaker status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629470&prj=684&rqi=LYwMOmdd7YmpzkLznLlzswr1AF
YT1ELEC-96-002 | c125521c-0c0f-4fd3-b272-e824a18cbb27 | SV18-2 | 684 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design |  | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | 1MSB_R2 Level 2B MSB drawings do not have 240VAC control power called out on drawings or physical terminals in Section 02A in MSB for 1BATT_R2_3. (Note: Typical of all MSBs.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629465&prj=684&rqi=W5JgBXExV1nZGhIGkpuoQmnWjs
YT1ELEC-93-003 | e0ffd23f-8b6b-43e3-bb41-87a4f007262f | SV18-2 | 684 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design |  | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | 1MSB_H Level 2B MSB drawings do not have 240VAC control power called out on drawings or physical terminals in Section 02A in MSB for 1BATT_H_3. (Note: Typical of all MSBs.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629462&prj=684&rqi=cZHrG5skLkNl7QTYVTEddWAg76
YT1ELEC-87-002 | dbed8994-007c-43e8-8feb-bf984e017185 | SV18-2 | 684 | AMER | Open | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_H | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_H L2B Breaker 1UPS_H_3-RIB (Q07) does not have wires pulled or installed on aux contacts for UPS RIB breaker status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629469&prj=684&rqi=wpqW8zd2EIRQ5us0fciul8usKl
YT1ELEC-96-001 | 70a6225f-cfa0-4c14-9b5c-41ef7a2acb74 | SV18-2 | 684 | AMER | Work Completed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design |  | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | 1MSB_R2 Level 2B Please see the images below. Need to confirm control wiring (PLC Jumpers) for 1MSB_R2 - Q12 (MBB), Q13 (LBB1), Q14 (IOB1), Q15 (LBB2), Q16 (IOB2). Currently no wiring installation is present in section 10A of MSB. Serial Number: HSUDKEX-6027DV-001 Drawing No: HSU-6027DV-ELC-DWG01 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629458&prj=684&rqi=065adP4uXutU02hYZJHNumx7Al
YT1ELEC-89-001 | 25d20af5-9061-4692-8991-8b916ddd49d7 | SV18-2 | 684 | AMER | Open | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_K | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_K L2B Breaker 1UPS_J_3-RIB (Q07) does not have wires pulled or installed on aux contacts for UPS RIB breaker status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629471&prj=684&rqi=NF8YbtyaOIFRwCCx9aHLEzmkgl
YT1MECH-86-003 | 765b3a72-ddd6-43f2-a48b-ee6ae337222d | SV18-2 | 684 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-15 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (HP-J-1) L2B Overhead junction box has an unfinished splice that should be a continuous run per Equinix electrical design. Please run a new line from PNL-R2-2-H-2 with no splice. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629433&prj=684&rqi=nQNvZB3YaOVLTVBchqwoH7ZT6a
YT1ELEC-90-002 | 5c8833bc-2d59-45d7-a3ea-0111bdcba4de | SV18-2 | 684 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design |  | Electrical â€“ LV | equipment | 1MDSB_R2_1 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_R2_1 Level 2B Aux contacts for breaker status on 1UPS_R2_3-RIB (Q07) are not installed. Aux contacts are installed on XQ10 which is a SPARE. Submittals will need to be updated to reflect aux contacts. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629467&prj=684&rqi=YiKHZh2Oq03KkxkSYRj9De39JD
YT1ELEC-94-001 | d2f4abda-092a-4c48-a694-9f8deb2a5b2c | SV18-2 | 684 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design |  | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | 1MSB_J Level 2B MSB drawings do not have 240VAC control power called out on drawings or physical terminals in Section 02A in MSB for 1BATT_J_3. (Note: Typical of all MSBs.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629463&prj=684&rqi=NxlGXgE6jg2P8xJS3Z5PFm7vkH
YT1ELEC-92-001 | 99f3f718-d870-489d-b1c1-5d057e5d66ce | SV18-2 | 684 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design |  | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | 1MSB_G Level 2B MSB drawings do not have 240VAC control power called out on drawings or physical terminals in Section 02A in MSB for 1BATT_G_3. (Note: Typical of all MSBs.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629459&prj=684&rqi=sySmnYRXRF7Z8OMhR9zFTag3lu
YT1ELEC-95-002 | 7b17fe72-c091-4d7d-8ec5-604038da6cfb | SV18-2 | 684 | AMER | Closed | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Design not as specified | Design |  | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | 1MSB_K Level 2B MSB drawings do not have 240VAC control power called out on drawings or physical terminals in Section 02A in MSB for 1BATT_K_3. (Note: Typical of all MSBs.) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629464&prj=684&rqi=pwQxCzkBTeyCJ9ExvD9fedyf3c
YT1ELEC-86-003 | 98abb82b-44e5-4758-aaa1-37adf38393bc | SV18-2 | 684 | AMER | Open | P3 Low CX | jared.meier@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_G L2B Breaker 1UPS_G_3-RIB (Q07) does not have wires pulled or installed on aux contacts for UPS RIB breaker status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629468&prj=684&rqi=7UqgLHtV2cB1saeb5qkS04eXFs
YT1MECH-72-001 | 70f63151-d2b5-4ed0-802c-53145b532983 | SV18-2 | 684 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_14 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_K_14) L2B The line side of both Source A and Source B breakers are missing phase separators. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629236&prj=684&rqi=x7k1pBxX8DIxfJbkPiLdHHkBr4
YT1ELEC-9-002 | b5d32492-02cf-4778-9bef-23867be46254 | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-14 04:00:00.000 +0400 | SCH - Schneider MV | L2B | Installation not complete | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_R2 | RMU - Ring Main Unit |  |  | (1RMU_R2) L2B Missing nut insert for section 2 dead front panel.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629231&prj=684&rqi=sj86yd2bhNeKl60NkZA5calTIe
YT1ELEC-90-001 | 26d5367b-97c1-48df-9634-21e2d0dcbd33 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_R2_1 | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_R2_1 (L2B) Grounding bushing on top of 1MDSB_R2_1 is loose and needs to be tightened. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629235&prj=684&rqi=j3hMWkZYGAMLbkEwfuK8ASYHiP
YT1MECH-73-001 | 71cfa402-4f79-40d9-9e5d-7c263bbd714b | SV18-2 | 684 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_15 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_K_15) L2B The line side of both Source A and Source B breakers are missing phase separators. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629237&prj=684&rqi=4zZd70JgPwEsZlTxZKUqkV9Sgf
YT1ELEC-87-001 | 2d183fee-1f2f-409d-8abf-0acc25a2b7d3 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_H | MDSB - Mech Distribution Switchboard |  |  | 1MDSB_H (L2B) Cable entry bushings into MDSB_H are not seated properly and need to be adjusted to sit correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629234&prj=684&rqi=dFKLZJp1DnDbyt7XoIbw0boA2T
YT1MECH-81-004 | 8ada3f58-5fd6-4fa8-a97b-20bf2390b933 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_R2_1 | EF - Exhaust Fan |  |  | 1EF_R2_1 L2B Control wires are pulled from UPS_1 and UPS_2, but no control wires are pulled from UPS_3 to Exhaust Fan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629068&prj=684&rqi=HbZdbWt08jN9jwJmgGrLHgniWt
YT1ELEC-358-001 | d78b39d4-54bd-4db9-a38e-dbbdcd70c80a | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_K3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_K3 (L2B) Green plug adapter for the control power/comm cables inside of the cabinet does not exist and needs to be installed to allow for Rosendin to terminate connections on 1UPS_K3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629090&prj=684&rqi=vckBlLVKgbENRxoQ4ajXh4htay
YT1ELEC-349-001 | 067f2b12-b29f-48ce-a7e0-1aa2a02005c5 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_G3 (L2B) Green plug adapter for the control power/comm cables inside of the cabinet does not exist and needs to be installed to allow for Rosendin to terminate connections on 1UPS_G3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629087&prj=684&rqi=oKfN5ldTDIRfK3gWngiyEnbuNC
GT1ELEC-367-001 | 426d79af-6972-4af2-83cb-7fe30626e7ab | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L3 | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_H | GENL - Generator (LV) |  |  | 1GEN_H (L3) KW and PF indications on the GCB and HMI are negative for some values. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629028&prj=684&rqi=sdXS1x0x3fOyVqL7mJIUV1jeVU
YT1ELEC-93-002 | 871e2a04-9b46-40e4-89c7-3642156ebc80 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | 1MSB_H (L2B) The breaker rack in device for Q03 (LB Breaker) in 1MSB_H broke during routine testing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629086&prj=684&rqi=rONc55NIetkqTdJR1B3bRquYGI
YT1ELEC-352-001 | a14087c6-161c-419b-a5bc-8b8c756d219d | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_H3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_H3 (L2B) Green plug adapter for the control power/comm cables inside of the cabinet does not exist and needs to be installed to allow for Rosendin to terminate connections on 1UPS_H3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629088&prj=684&rqi=bgA2WfxZR72VzUHpDsJnlc3be1
YT1MECH-86-002 | 2e117595-2587-41ef-99be-359b6bcce015 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | 1HP_J_1 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629049&prj=684&rqi=VWfsJKsoTRmh5GstBtsjDUyxF9
YT1MECH-89-002 | 0077ca1f-774e-4885-8b74-27e2d8f355c6 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (HP-K-2) L2B Overhead junction box splices 480V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629045&prj=684&rqi=aYIZZ4vHXd8TkNsN5ywaVyu7ST
YT1MECH-84-003 | 6cbead77-2c46-4902-a084-1386d23a1b45 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (HP-H-1) L2B Overhead junction box splices 480V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629042&prj=684&rqi=S3rejqV54e9D37JVcGyOhv8dpZ
YT1MECH-89-003 | 3ba2b028-4bde-41e4-83ce-81f6e923a879 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | 1HP_K_2 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629055&prj=684&rqi=HwEXNPChJvDSsVzywSL9vlzYtf
YT1MECH-79-004 | 8f7e7091-9dcf-4022-a8f1-0a52aa192838 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_J_1 | EF - Exhaust Fan |  |  | 1EF_J_1 L2B Control wires are pulled from UPS_1 and UPS_2, but no control wires are pulled from UPS_3 to Exhaust Fan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629065&prj=684&rqi=awUHkvAAFuvJquOClIE2EO0ptC
YT1MECH-84-004 | 5ca0546c-05c4-4f3d-a108-ca29e3e1d7d9 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | 1HP_H_1 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629046&prj=684&rqi=QeCxvgh1Auf2zy59pr3T9Tbkce
YT1MECH-91-002 | 1f59763b-5a8b-4f0a-ae0b-76b7d7323b6e | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | 1HP_R2_2 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629057&prj=684&rqi=1dXaNSyKaIyE0tn8gEkTsFNngI
YT1MECH-78-003 | eeef3d1e-9b73-4679-9fd8-2e87ed49a6d3 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_H_1 | EF - Exhaust Fan |  |  | 1EF_H_1 L2B Control wires are pulled from UPS_1 and UPS_2, but no control wires are pulled from UPS_3 to Exhaust Fan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629064&prj=684&rqi=8iqNjbNVwZvfPk4DOVFKGarNtq
YT1MECH-82-003 | 7f90c48f-3e46-470e-b7e1-bce6a33088a6 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (HP-G-1) L2B Overhead junction box splices 480V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629044&prj=684&rqi=P0ONqERQQVRPZBqN8ooHYT9tnk
YT1MECH-82-002 | 0583b327-b05c-427d-9fa1-67d73de2a372 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | HP_G_1 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629033&prj=684&rqi=DoTaNzXADUBSe3m4dRLk2kjKMO
YT1ELEC-361-001 | 1d55f79e-34d7-4281-92b5-485fa728b3b2 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_R2_3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_R2_3 (L2B) Green plug adapter for the control power/comm cables inside of the cabinet does not exist and needs to be installed to allow for Rosendin to terminate connections on 1UPS_R2_3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629091&prj=684&rqi=leB9Yt4oe92CBS6WqOduvPeZld
YT1MECH-80-003 | fe3aeb58-68a5-4ada-9d97-429a45b137ef | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1EF_K_1 | EF - Exhaust Fan |  |  | (EF-K-1) L2B Overhead junction box splices 120V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629060&prj=684&rqi=BeOCe19GxevPOXuKoCB5NSSrks
YT1MECH-85-002 | db4cea5d-3ed8-4c17-9704-bb8970661027 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | 1HP_H_2 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629047&prj=684&rqi=iDenc6EbPnWPd4AUojZT8Gjo4G
YT1MECH-80-004 | b5da4903-8cd7-4785-a83b-ab21546dcba2 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_K_1 | EF - Exhaust Fan |  |  | 1EF_K_1 L2B Control wires are pulled from UPS_1 and UPS_2, but no control wires are pulled from UPS_3 to Exhaust Fan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629067&prj=684&rqi=H6ff8OFswUJliZXnYr4Blxi1fk
YT1MECH-90-003 | 048759ad-adef-4c4b-8a90-30d2acb0b02a | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | 1HP_R2_1 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629056&prj=684&rqi=ATaBQJxfY2lJazZ0QOfqQ781qV
YT1MECH-83-003 | 37b79e2c-f82f-45f8-a258-fa0832cb6961 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | HP_G_12 L2B No torque marks in WSHP 20 in lb required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629043&prj=684&rqi=K0cH3mIqOMPClIKnPLT4Z6NBKb
YT1MECH-87-002 | da376326-d7e4-48cd-8d56-737eedb4763b | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | 1HP_J_2 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629051&prj=684&rqi=ooqwyRBIsVvocejcKnfUdwkFhe
YT1MECH-77-004 | d380bd88-6a4f-4c4b-8b74-235a239f7ec5 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_G_1 | EF - Exhaust Fan |  |  | 1EF_G_1 L2B Control wires are pulled from UPS_1 and UPS_2, but no control wires are pulled from UPS_3 to Exhaust Fan. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629062&prj=684&rqi=dVwR84BSnnnxR4uoAgsO4Jh3IB
YT1MECH-77-003 | dfd509ca-e1b8-4523-8f06-f1aa38e95297 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1EF_G_1 | EF - Exhaust Fan |  |  | (EF-G-1) L2B Overhead junction box splices 120V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629048&prj=684&rqi=0e0VBg8pyRDcCcluHgqtyML9o8
YT1MECH-79-003 | 9d76e585-aa73-47a6-b6ad-02d7f6d3b496 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1EF_J_1 | EF - Exhaust Fan |  |  | (EF-J-1) L2B Overhead junction box splices 120V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629058&prj=684&rqi=5WolrFVfSf3WfRnMwYBnXiAl6t
YT1MECH-88-002 | b9514fb5-bdac-4a26-b08a-7f04cabb65f2 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ganesh.singh@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Torque required | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | 1HP_K_1 L2B No torque marks in WSHP 20 in LB required per label on switch terminal box | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629054&prj=684&rqi=SZuTcFLEWLx2BlxqS6rtFsdHyq
YT1ELEC-355-001 | f47a47d0-7020-4dc7-a3ba-d59b2b9dccb7 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-13 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_J3 | UPS - Uninterrupted Power Supply |  |  | 1UPS_J3 (L2B) Green plug adapter for the control power/comm cables inside of the cabinet does not exist and needs to be installed to allow for Rosendin to terminate connections on 1UPS_J3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629089&prj=684&rqi=xynFD6U3I3ukcUvlU3BZ9xfgfS
YT1MECH-81-003 | 6b1615c3-09fa-4c80-be97-d6efff91d10a | SV18-2 | 684 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-07-13 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1EF_R2_1 | EF - Exhaust Fan |  |  | (EF-R2-1) L2B Overhead junction box splices 120V with wire nuts. This is not allowed per Equinix standard; must be a single run. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629061&prj=684&rqi=9ulNAILfdRIWyh5sjsB8DoR9Jc
YT1MECH-81-001 | 9c733353-9d41-4e80-9d0f-a06fe08e200c | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_R2_1 | EF - Exhaust Fan |  |  | (Electrical Skid R2) L2B UPS to Fan interconnection needs to be terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628750&prj=684&rqi=gX0PCEU3Fu1eMyKkop57vL4wvN
YT1MECH-81-002 | 005495a6-82f5-4b22-a684-cf16a05be426 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Controls Contractor | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_R2_1 | EF - Exhaust Fan |  |  | (Electrical Skid R2) L2B Leak detection communication cable needs to be connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628755&prj=684&rqi=V9J6sWaZ7T6ai7bLtAubm8nvUh
YT1ELEC-382-001 | cab3e11a-becb-4a2e-bbff-af0ccab947cf | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-10 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_G (L2B) Phase C lug for Breaker Q04 is stripped and needs to be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628737&prj=684&rqi=fX0kAUDTA2atOmIlehIydDUqhu
YT1MECH-78-001 | 2b90b30e-1787-4632-8e3b-a395fb587200 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_H_1 | EF - Exhaust Fan |  |  | (Electrical Skid H) L2B UPS to Fan interconnection needs to be terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628745&prj=684&rqi=QM1qKuYtFmCOzyYyPtPd8mtHB6
YT1MECH-79-001 | 939f7e81-b308-47fe-8fbb-17b9d9b26650 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_J_1 | EF - Exhaust Fan |  |  | (Electrical Skid J) L2B UPS to Fan interconnection needs to be terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628746&prj=684&rqi=jH77jBtIzVkCHARzOJjKFSFgSG
YT1MECH-78-002 | 1f7781c3-cb54-4e01-870d-07bd8c2b570f | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Controls Contractor | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_H_1 | EF - Exhaust Fan |  |  | (Electrical Skid H) L2B Leak detection communication cable needs to be connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628752&prj=684&rqi=IBezUn8UbYL1Rr6X1E93DgxpiX
YT1MECH-79-002 | 756950bd-d585-448f-b5b2-0688a98a0fb7 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Controls Contractor | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_J_1 | EF - Exhaust Fan |  |  | (Electrical Skid J) L2B Leak detection communication cable needs to be connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628753&prj=684&rqi=lWqem6vfbu1dkdUj87wSCk00BI
YT1MECH-77-001 | a8be4900-e9aa-455b-b696-8fe0ba2828c8 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_G_1 | EF - Exhaust Fan |  |  | (Electrical Skid G) L2B UPS Fan interconnection needs to be terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628744&prj=684&rqi=GmZPwlU8azMR1IUA3QthOTPtP9
YT1MECH-77-002 | cd08792a-68c7-49a1-8633-223c879faff8 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Controls Contractor | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_G_1 | EF - Exhaust Fan |  |  | (Electrical Skid G) L2B Leak detection communication cable needs to be connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628751&prj=684&rqi=gcdYkhmQlpBDtEb1TggOFHz7wD
YT1MECH-80-002 | 719f8b4e-da90-4c09-8bd8-b10e38b9a50d | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Controls Contractor | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_K_1 | EF - Exhaust Fan |  |  | (Electrical Skid K) L2B Leak detection communication cable needs to be connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628754&prj=684&rqi=nPWD3euqwSudf351Pqsjf5tE2n
YT1MECH-80-001 | 0b216c6a-6362-4dad-b85f-9f533b1254f7 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-10 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“Air | equipment | 1EF_K_1 | EF - Exhaust Fan |  |  | (Electrical Skid K) L2B UPS to Fan interconnection needs to be terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628749&prj=684&rqi=3kOfCuV9Cyuun6G0SfGsx7tonn
YT1MECH-83-002 | ae4b6d9b-43c8-0635-38e8-dbe3351f6f4a | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (1HP_G_2) L2B Flex conduit connections are lose. Please connect and tighten. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628623&prj=684&rqi=sviDJPNdCzl8mQQSYuika3iHiI
YT1MECH-90-002 | 474822e2-a481-aec3-ee86-18e3a087d756 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-09 04:00:00.000 +0400 | Electrical Contractor | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L2B Flex conduit connections are lose. Please connect and tighten. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628621&prj=684&rqi=agnoRjcCi97ugrpjZWcypr5LeC
YT1MECH-84-002 | a51a9622-7868-1d4d-ec6f-28b677a7f776 | SV18-2 | 684 | AMER | Open | P2 Medium CX | ethan.hang@veolia.com | 2026-07-09 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Incomplete Connections | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (1HP_H_1) L2B Flex conduit connections are lose. Please connect and tighten. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628622&prj=684&rqi=mtALYSO8AGFTYQAnq92BGiis95
YT1MECH-87-001 | 731abdce-051b-487e-8add-99f9519a7713 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | (1HP_J_2) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628448&prj=684&rqi=2l3wKiV2Wns8fGhQxJvoZLL8MG
YT1MECH-85-001 | 35d845f9-444c-4492-8dbe-622d2723fab9 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (1HP_H_2) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628446&prj=684&rqi=CSy34WBOtfHlY4xyGsdcPWboCz
YT1MECH-82-001 | d85343d4-df31-4081-9686-10f92202ddef | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (1HP_G_1) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628443&prj=684&rqi=9kk0uNi2TbX6UiSXMVTH7iHR6E
YT1MECH-84-001 | 1881a8d2-8afb-4c4f-a741-688b979543fc | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (1HP_H_1) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628445&prj=684&rqi=myPUebojFD4I2iMY0iAmdEX5ty
YT1MECH-91-001 | 001f1960-5688-4d16-b924-b8c7857138d8 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (1HP_R2_2) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628452&prj=684&rqi=uyPiJZj1VU8hb8cCuRvFEyfzvE
YT1MECH-88-001 | 8c835f2a-64a8-49bb-8e64-d076c6bd5790 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (1HP_K_1) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628449&prj=684&rqi=2aTKP4OEXvDNTV4xu4FHFG60v0
YT1MECH-89-001 | 77dec20c-0437-407b-a152-f39ec51ed619 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (1HP_K_2) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628450&prj=684&rqi=yzqMIlehHA4GqXsQ621PU1Wzg8
YT1MECH-86-001 | 9d9a1bf8-3d43-4f21-b3c8-f9c0dcf8042b | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (1HP_J_1) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628447&prj=684&rqi=wwgzQ2J8oxRo08vMco8W8hlY67
YT1MECH-90-001 | c2c76f9e-3fe7-4c03-8196-338b47cc0ca5 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628451&prj=684&rqi=8SbkUlFxWaHrbjJ36G27KnA9Qu
YT1MECH-83-001 | 2a6edb7b-1d0d-4acd-bbe4-ffac6fe136ed | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-07-08 04:00:00.000 +0400 | Electrical Contractor | L2B | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (1HP_G_2) L2B Torque marks required on the line side of the relay in the heat pump | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628444&prj=684&rqi=P5VpNqzBPKeaw9qxemg3ukk4rD
RT1ELEC-386-002 | 689ec0fb-8a50-4155-9db7-d08f0b560951 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_K3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_K3 (L2A) Breaker Q03 is not padlockable because it does not have the locking mechanism installed on the breaker. Per the submittal, drawing # HSU-5736GL-ELC-DWG01 sheet 2, the breaker should be equipped with a locking mechanism that prevents operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628215&prj=684&rqi=LpETJVSpFMZrk7eCdDuRUiXheh
RT1ELEC-387-002 | 49d0540d-7892-422c-87fd-1fcc3b945925 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_R2_3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_R2_3 (L2A) Breaker Q03 is not padlockable because it does not have the locking mechanism installed on the breaker. Per the submittal, drawing # HSU-5736GT-ELC-DWG01 sheet 2, the breaker should be equipped with a locking mechanism that prevents operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628217&prj=684&rqi=rMpvCvt9MCF56ZRB9iULbuOa4H
RT1ELEC-385-001 | ad1dc164-07a0-416e-9a72-3042d120f4cf | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_J3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_J3 (L2A) Breaker Q03 is not padlockable because it does not have the locking mechanism installed on the breaker. Per the submittal, drawing # HSU-5736GL-ELC-DWG01 sheet 2, the breaker should be equipped with a locking mechanism that prevents operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628213&prj=684&rqi=2yWHdqRnTTr1QthhCq6gMWuvrR
GI-003 | 4ce144ba-6ab0-4f2d-8d5b-96eb1e58e8e3 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | dustin.haugh@veolia.com | 2026-07-07 04:00:00.000 +0400 | Electrical Contractor |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1PDU_F1_2 | PDU - Power Distribution Unit |  |  | All PDUâ€™s in data hall are missing one front left floor mounting bolt. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628247&prj=684&rqi=0JLrRrlwTFHopJPzY0vcCyWiD2
YT1ELEC-9-001 | 3318ad17-813e-4a2e-86c5-7ab3711913c6 | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-07 04:00:00.000 +0400 | Controls Contractor | L2B | DCOS Design Issue | DCOS |  | Electrical â€“ MV | equipment | 1RMU_R2 | RMU - Ring Main Unit |  |  | (1RMU_R2) L2B 3rd section of RMU does not communicate with BMS.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628259&prj=684&rqi=3bEXEGYJCyLIRCYvdxDUM4vMiL
RT1ELEC-383-002 | 06bf33c5-a0f3-42f8-b5d1-ea3f70ebbaaa | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_G3 (L2A) Breaker Q03 is not padlockable because it does not have the locking mechanism installed on the breaker. Per the submittal, drawing # HSU-5736GL-ELC-DWG01 sheet 2, the breaker should be equipped with a locking mechanism that prevents operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628206&prj=684&rqi=LZRTL01aAVy0oOL4WVhNR62IfG
RT1ELEC-384-002 | f7a82650-5107-451d-b91b-447e93294507 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-07 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_H3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | 1UMDSB_H3 (L2A) Breaker Q03 is not padlockable because it does not have the locking mechanism installed on the breaker. Per the submittal, drawing # HSU-5736GL-ELC-DWG01 sheet 2, the breaker should be equipped with a locking mechanism that prevents operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628210&prj=684&rqi=tZtHd51erxvPqpqmwU7K5mh57U
RT1ELEC-53-002 | e4768c3b-0798-4af9-8f45-141c50a8042b | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_H3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_H3) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627721&prj=684&rqi=sJu0FJ2rTu59tA6CUy64K5882m
YT1MECH-9-003 | 5e056612-b95c-487f-ab99-da0ae63dbdc1 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-07-02 04:00:00.000 +0400 | TRN - Trane | L2B | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1ACC_G_16 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_G_16) L2B For tracking purposes, the UPS was cannibalized and needs to be replaced. Per Ryan Vincent, for SV18-1b, the UPS failed at 2-2.5 hours at 100%. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627744&prj=684&rqi=qFrOm2Fzhz4bd97KFtwhr7Os9U
RT1ELEC-63-001 | bae4ee2f-bc47-40f7-a23e-f15799048e38 | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_K1_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_K1_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627725&prj=684&rqi=JpRUHJxohbOkQKqFN5vLrsm3hW
RT1ELEC-62-002 | edbff585-816e-4099-88d7-f26f472898e7 | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_J3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_J3) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627724&prj=684&rqi=MQurN4zB9u1u0rWTtyhtrcxRyk
RT1ELEC-67-001 | 72a7b0b6-c473-4eee-9f92-60dfc4f730b5 | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_K2_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_K2_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627726&prj=684&rqi=hRtUcUdKX40HAptIBav4UQZgGn
RT1ELEC-49-001 | 754bd169-3c70-4363-acf0-a1cdc2283202 | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_H2_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_H2_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627720&prj=684&rqi=XoRg2MjG4CkCxBFkUtIurjwap4
RT1ELEC-54-001 | 21c87047-0e49-4f39-a17a-a51119d89bb2 | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_J1_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_J1_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627722&prj=684&rqi=JGLgAJAfWfaKg1rMn28kjJUmXf
RT1ELEC-58-001 | 53bfe70b-faea-4566-a419-e3dd854ad762 | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_J2_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_J2_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627723&prj=684&rqi=1ctCSq7czN0DKL28DaTA3ym8yg
RT1ELEC-76-001 | 5f34ffd2-6008-42ee-b6b7-7cde07d41c38 | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_R2_2_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_R2_2_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627729&prj=684&rqi=ciPA7wwFqSpa6ytO0cv0ciNvJT
YT1ELEC-86-001 | c81a0524-29ef-4cf2-bc83-30cbc234ea4c | SV18-2 | 684 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Design Professional | L2B | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_G) L2A: In the SCCS, there is an issue across ALL MDSB where breaker 1TX_X_R1 is missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627717&prj=684&rqi=9sq2rOSfew2mcPwdJtYnAYc78g
RT1ELEC-45-001 | 513491a8-269f-46b6-bc68-88eea233d8d1 | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_H1_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_H1_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627719&prj=684&rqi=MgW0jfs5ulnOb3HrAfRjCCZE9N
RT1ELEC-80-002 | b828689e-482d-4764-962d-76519a2259f7 | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_R2_3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_R2_3) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627730&prj=684&rqi=3NEatKWWGv1UWBjjVEGbtlEgAc
RT1ELEC-71-002 | a3af02fd-75e5-4878-817e-80c1b7777d4e | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_K3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_K3) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627727&prj=684&rqi=CuGyLgumFknn40BJstUdl453xV
RT1ELEC-8-001 | ddef1555-e5f8-4df4-9438-fbf1462ac1fa | SV18-2 | 684 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-07-02 04:00:00.000 +0400 | SCH - Schneider MV | L2A | Installation Damage | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_K | RMU - Ring Main Unit |  |  | (1RMU_K) L2B Breaker operator has been bent during breaker exercising for P2P checks. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627745&prj=684&rqi=pXZdxMDVtk5h5i3mzgJhS4aH5p
RT1ELEC-72-001 | 349a57c1-31da-496c-bce9-6dab264babb3 | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-07-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_R2_1_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_R2_1_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627728&prj=684&rqi=J8Hovc2JDMM228sNWINpzO6lmm
RT1ELEC-383-001 | c3a89c67-de6d-4578-94b1-f0db7403f76f | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-30 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_G3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | (1UMDSB_G3) L2A REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1UPNL_G3_H1 (Q09) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627475&prj=684&rqi=jb7deGS0eJqkOWt1iIoZMlFKo0
RT1ELEC-44-002 | 83b86c1d-01aa-4446-b74c-e46d2d453467 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_G3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_G3) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627435&prj=684&rqi=J52AFWJupYR7UPF1ioBVRuP7Eu
RT1ELEC-40-001 | 827eae98-24f3-4f83-8ce8-767c2dc43a7c | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-30 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_G2_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_G2_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627415&prj=684&rqi=U5IOJsLc6Up4kKoVoWzLdeaeCw
RT1ELEC-384-001 | 609e9cca-e45d-4eb1-8492-20113a8e45e9 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-30 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_H3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | (1UMDSB_H3) L2A REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1UPNL_H3_H1 (Q09) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627476&prj=684&rqi=beLFLFanvmXOhS6LoWfLkFy7kC
RT1ELEC-155-001 | 2c877679-97f3-41ec-b21e-2e2b0b15d00b | SV18-2 | 684 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-30 04:00:00.000 +0400 | Owner | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1PNL_R2_2_H3 | DB - Distribution Boards |  |  | (SKID R2 HP in F) L2A RFI 539: WSHP #2 Power Supply at PH F (Panel R2-2 Dependency) determined that the HP in SKID F has a power supply that is fed from 1PNL_R2_2_H3. The SKID F HP will be installed and ran on temporary power until the end of the SV18-2 project once SKID R2 has completed all Cx activities. Once ready to restore normal power to 1PNL_R2_2_H3, the temp power system and any associated conduit will need to be removed from SKID F. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627450&prj=684&rqi=TYqPDa5JXtA3uyRRqzmYlh06lm
RT1MECH-86-008 | d6e22e41-d5c3-4f86-b945-16db19208ffc | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (Electrical Skid J) L2A At the SW doors, the speaker strobe & pull station devices cannot be installed as the back boxes are too close to the adjacent conduit and security JB respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627242&prj=684&rqi=YAI4iup1bgCaAQ5ECMl1r7p0lc
RT1MECH-88-008 | 113c0b91-1c30-4212-8588-199d3063b9e8 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-29 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (Electrical Skid K) L2A At the SW doors, the speaker strobe & pull station devices cannot be installed as the back boxes are too close to the adjacent conduit and security JB respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627243&prj=684&rqi=2AUsptYxxjqLzb8SBquyFy5lZ2
RT1ELEC-97-005 | 61080f76-8a03-4acd-b3b3-50a7984b06c1 | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (MSB R2) L2A: Gen main breaker has issues with control module. Not sending power to HMI and ERMS.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627150&prj=684&rqi=FVnENsPfhO0BVHTpaIt29PZmKx
RT1ELEC-97-006 | 208c3e49-95e1-4bc6-9c00-6d790d9c9ecf | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-26 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB R2) L2A: Missing lock tumbler for section 01C.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627151&prj=684&rqi=gMz8m2yTLp63NR2QPhgbWwNKym
RT1ELEC-360-002 | c0dcfd70-3a2f-47bd-9c79-6843db3a7741 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_R2_1 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_1) L2A: Battery cable missing grommet.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627152&prj=684&rqi=S0Xw1vhgqLlIQy1aZvXAPEeTGv
RT1ELEC-361-002 | e7b6a674-8999-42e1-bcca-fbee282c46de | SV18-2 | 684 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-06-26 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_R2_2 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_2) L2A: Multiple battery cables missing grommets.Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627153&prj=684&rqi=HpcTRhFY9AYWXRC3E3NXKTO66t
YT1ELEC-95-001 | 509ca3fa-3611-4953-ade4-1655ea92052f | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-25 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2B During P2P checks, it was identified that the CAT6 cable connecting between 1MSB_K Section 02A and the DMark Panel in SKID K does not work. We verified this by connecting an external CAT6 cable between the two connections and the system worked correctly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626997&prj=684&rqi=Euw5kfXRtgKgsiVBr0YZrWx4UW
YT1ELEC-369-001 | 78349b3b-519b-460c-8277-b06d6736947e | SV18-2 | 684 | AMER | Ready for Verification | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_G | GENL - Generator (LV) |  |  | (1GEN_G) L2B GEN_G door enclosure to the HMI panel has a bent frame from the temporary rigging that was installed to gain access to the equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626250&prj=684&rqi=csyCxExoUm6XpppSG9qyv4rFRU
YT1ELEC-373-001 | 32d9ce58-e027-4e37-a63b-a1b0c22922a3 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-06-19 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2B | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_R2 | GENL - Generator (LV) |  |  | (1GEN_R2) L2B Piping feeding to the pressure transducer on the SCR is routed incorrectly and not connected to the transducer. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626259&prj=684&rqi=7j0dyAdRjebyHkjeJAvz5yWNuO
RT1MECH-74-002 | d97c7e3e-38a5-937f-e648-7b4800afe652 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-06-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_R2_13 | CRAH - Computer room air handler (Skid) |  |  | (CRAH-R2-13) L2A Fan power interconnections not connected correctly. Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625870&prj=684&rqi=MKPHFLWwjltJFz2iucd99IUOxi
RT1MECH-62-001 | 8b528af7-290c-47c5-86d0-979a079c55fd | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_13 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_G_13) L2A Several missing screws on fan access panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625862&prj=684&rqi=TthscdL1kRxCDIHYp4ZudNsc4t
RT1MECH-63-001 | 2948a871-42d3-4fca-a2d3-2ddccdfd3a40 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_14 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_G_14) L2A Missing screws on fan access panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625863&prj=684&rqi=gA5fq7sYGJ5VcnpPeZmD0MNQsZ
RT1ELEC-36-001 | 283ea201-c7cf-4a2b-adbc-3ccf61501540 | SV18-2 | 684 | AMER | Closed | P3 Low CX | chase.negich@veolia.com | 2026-06-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_G1_1 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_G1_1) L2A Battery cabinet has Emergency Power Off push buttons, but Equinix requires them to be removed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625852&prj=684&rqi=TuqtuvtlUN9c4mAvN6sWgxL0oI
YT1ELEC-93-001 | 4425bf54-dd6d-48af-b03b-98c9dcdc4b6f | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-18 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2B | Component/ Equipment Failure | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | (1MSB_H) L2B Breaker Q15 (1ACC_H_14) failed to trip during NETA secondary injection testing of the equipment. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625855&prj=684&rqi=mfbwUOObkmPqSWzdWra0Xvd3oz
RT1ELEC-360-001 | b9fc54e6-23b1-40b9-a8b3-0d8f15fcc35d | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ian.tsurumoto@veolia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_R2_1 | UPS - Uninterrupted Power Supply |  |  | Verify Internal Electrical wiring is completed UPS_R2_1 and UPS_R2_2 Parallel UPS communication cable missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625689&prj=684&rqi=UHhVE9jlXmxiHbHBWtTl9CcZW6
RT1MECH-67-001 | b525ab1f-3311-adb0-657b-e0679545f040 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_15 | CRAH - Computer room air handler (Skid) |  |  | (CRAH-H-15) L2A Fan power wiring in left fan section need to be zip tied down. Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625692&prj=684&rqi=cXpzj9IL2Dbnwsxh6NKGgJagke
RT1MECH-68-001 | 8df3968c-9e9c-d773-6ef9-19ddbc2ff953 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Torque required | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_J_13 | CRAH - Computer room air handler (Skid) |  |  | (CRAH-J-13) L2A Torque marks missing from fan section. Bolt pictured is hand-loose. Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625693&prj=684&rqi=9bD2HjzBiVhlzppZTNjUVs2Tob
RT1ELEC-361-001 | 47df5a4d-157a-4584-b33f-aadddd402f17 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ian.tsurumoto@veolia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_R2_2 | UPS - Uninterrupted Power Supply |  |  | Verify Internal Electrical wiring is completed UPS_R2_1 and UPS_R2_2 Parallel UPS communication cable missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625690&prj=684&rqi=MTI3UYSqptdMtmLtsni72Nxjbk
RT1MECH-73-001 | cc5ea61f-7e49-5ea6-c0dd-11f764a976a4 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-16 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_15 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_K_15) L2A Top left Screw missing on supply air grate | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625546&prj=684&rqi=CK20cqIqDRSXWAa8rCOVH5um6C
RT1ELEC-370-002 | 4a3903d7-eee6-46b9-a045-d7f568d7435a | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-16 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_G | GENL - Generator (LV) |  |  | (1GEN_G) L2A Broken bolt on grounding bar in the back of the GCB enclosure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625483&prj=684&rqi=HDuPrxCwRGmHkCnDw3H7bnRHTO
RT1MECH-42-002 | bf07dab5-ce85-17d7-34d4-b6a13b96efd3 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-16 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_05 | CRAH - Computer room air handler |  |  | (1CRAH_H_05) Filter bracket 5 back top and 6 back bottom are missing screws. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625547&prj=684&rqi=3PbyIKwvEyde0GOKh3BJFkHxFr
GI-002 | 9d4bc105-b7a3-49eb-aa42-661ea8f98761 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-16 04:00:00.000 +0400 | HAN - Hanley Energy Elec |  | Installation not correct | Commissioning | [7 empty] | (1_LBSB) Inspection During inspection of various equipment, it was identified that the Kirk Key cylinder on the Temp Gen breaker for the LBSB is incorrect. The LBSB Temp Gen breaker has a K1 kirk key barrel that has the serial number of '64161'. This does not match the currently installed/ordered GCB K1 kirk key barrels which have a serial number of '64393'. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625533&prj=684&rqi=gxsnz7gEHcdl70IBrxlV63LNuJ
RT1MECH-89-003 | f465a25e-0c40-4e01-937a-d9a90b730ade | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (HP-K-2) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625374&prj=684&rqi=2JBuYB250gpbttoBj7PnOZZ98Z
RT1MECH-84-008 | d271531e-3dc5-47d3-ba5f-9adcc9a0141c | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (HP-H-1) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625369&prj=684&rqi=cf4aReN1xv8fOSPPVktXmKV3yy
RT1MECH-87-004 | 6d830902-7c7e-4f5c-b81c-cdb8c1147472 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | (HP-J-2) Merv 4 filters are currently installed. Must be Merv 8 to match skids G, H, R2. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625376&prj=684&rqi=wGgeCkRYyMD8IcX6txsFBstjBw
RT1MECH-87-003 | 97cc246c-3e66-4de3-b0d8-5e03f4235cbe | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | (HP-J-2) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625372&prj=684&rqi=zp1cEUaQ8eri1wOE1ze2JKbQBj
RT1MECH-90-008 | 359fcd9e-3b64-41e5-8eff-ee9beeaea710 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (HP-R2-1) L2A Unit needs to have flex ducting installed between main fan compartment and ducting. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625380&prj=684&rqi=aOJooRMdBzJT67N748wf5seDVd
RT1MECH-88-007 | f4ec7711-151b-4b8c-ba31-4aa1502cf902 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (HP-K-1) Merv 4 filters are currently installed. Must be Merv 8 to match skids G, H, R2. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625377&prj=684&rqi=ZybVsPxRJHs2ogSXVbaoeE5PfH
GI-001 | 8eb546ae-e040-4ed2-89dd-8952b566dafe | SV18-2 | 684 | AMER | Closed | P2 Medium CX | chase.negich@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_G | GENL - Generator (LV) |  |  | (1GEN_G) L2A Broken bolt on grounding bar in the back of the GCB enclosure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625381&prj=684&rqi=bLJ84RlKEGzKccjcS5RV84I08P
RT1MECH-88-006 | a4332097-ac89-4fc3-80b5-b9de8831c76a | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (HP-K-1) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625373&prj=684&rqi=ckBjHe0OhyBwZvxdGBO4UORVpe
RT1MECH-85-004 | 5641e4ed-d836-4dee-ab85-c1233498ee70 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (HP-H-2) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625370&prj=684&rqi=5Q1J8isXcNRU5iFroi6Vz7atW0
RT1MECH-89-004 | 008ebf62-1707-4331-88e9-3cf2313d736b | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (HP-K-2) Merv 4 filters are currently installed. Must be Merv 8 to match skids G, H, R2. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625379&prj=684&rqi=u5aw6RDh4s03js5KBRfFiM42RR
RT1MECH-86-006 | df47f29b-6ff5-43d1-b5be-d091cc852cdb | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (HP-J-1) L2A Neither Water Source Heat Pumps have a condensate containment curb. See HPs in Skid G and R2 for example. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625371&prj=684&rqi=i9tANdaJkE8zGMdFAigWXGPQOM
RT1MECH-86-007 | 16fe4696-bc17-4129-8b72-045f96e15ce5 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-15 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (HP-J-1) Merv 4 filters are currently installed. Must be Merv 8 to match skids G, H, R2. Issues are raised on the Facility Grid IRL | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625375&prj=684&rqi=zowGNMrb8tYH6W3LJRg1rGU9NX
RT1MECH-90-007 | c050bb2b-7b62-4300-ad60-000a36dcdcc3 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-06-14 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L2A Not enough flex conduit slack to install smoke detectors onto the airflow plenum. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625246&prj=684&rqi=fc3fOqfudPEGLrCKlw3aZR9Eam
RT1MECH-91-011 | 17184413-502b-4388-9199-eeab0336aff1 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-06-14 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (1HP_R2_2) L2A Not enough flex conduit slack to install smoke detectors onto the airflow plenum | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625247&prj=684&rqi=mx9hK8wuciRCAYRR1qcepOKh4U
RT1MECH-46-003 | 5fde2a34-617c-6f7c-f812-69deaf9cde95 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_09 | CRAH - Computer room air handler |  |  | (CRAH-H-9) L2A Filter brackets 1-8 are loose (welds are broken) Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625014&prj=684&rqi=ztPX2luSqjQ6INHKOD7lECmvZZ
RT1MECH-49-001 | a620769d-cc14-6f3e-ea44-b21fc60dd7a0 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_12 | CRAH - Computer room air handler |  |  | (CRAH-H-12) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625017&prj=684&rqi=LMyWLs1KI73tsLnITrHV2D0YqD
RT1MECH-28-001 | cbffb054-10d4-07ea-ea22-26e8906e9505 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_03 | CRAH - Computer room air handler |  |  | (CRAH-G-3) L2A Filter bracket 8 top bolts loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625020&prj=684&rqi=1R9JXPwnZmZguI3NVgraVAq5G1
RT1MECH-31-002 | f923b9f9-9c46-d1aa-2b84-ab05170c0363 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_06 | CRAH - Computer room air handler |  |  | (CRAH-G-6) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625023&prj=684&rqi=5C5DbVuvYrB9D3njDFszNkFiS1
RT1MECH-44-001 | f97a43d8-9390-f145-1bc8-6796af47b1cd | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_07 | CRAH - Computer room air handler |  |  | (CRAH-H-7) L2A Filter bracket 7 Top bolt loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625011&prj=684&rqi=klAYzTQ8yDxs5KovlOla61CieU
RT1MECH-36-001 | ac63afdc-53b2-8cc1-215b-01fe4af9d0a4 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_11 | CRAH - Computer room air handler |  |  | (CRAH-G-11) L2A Filter brackets: #4 both back both top and bottom bolts missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625028&prj=684&rqi=olYh7Ie7JLFdWGXiBbKFbiXYM6
RT1MECH-47-001 | 6fdd922f-6d48-4879-b303-5fd60d0201b5 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_10 | CRAH - Computer room air handler |  |  | (CRAH-H-10) L2A Bracket 2 top back bolt loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625015&prj=684&rqi=hP7uEWJgmb2frIpY0Rp6y3Dbn1
RT1MECH-39-001 | 3a80149f-f704-feff-53fe-9b681270d95f | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_02 | CRAH - Computer room air handler |  |  | (CRAH-H-2) L2A 2 bolts missing on filter bracket 2 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624969&prj=684&rqi=cQgNtCRuju43uJ5s7kb0A2fu14
RT1MECH-32-001 | 2f69c278-b52d-9b5b-5c39-6f05716f350f | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (CRAH-G-7) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625024&prj=684&rqi=LpUvDyJhUUqhEuxdfFGRg1J9Xm
RT1MECH-32-002 | 9a17d224-9450-284d-557d-a6dd6f142578 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_07 | CRAH - Computer room air handler |  |  | (CRAH-G-7) L2A Filter spacer lodged in fan | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625025&prj=684&rqi=O8uJieDCpu7tNAQkkosa71CV5b
RT1MECH-45-003 | 0b685bad-4bb9-18b7-e794-e66a95fa1b84 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_08 | CRAH - Computer room air handler |  |  | (CRAH-H-8) L2A Filter brackets 1-8 are loose (welds are broken) Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625012&prj=684&rqi=nMvIpI0bYJ7lTN0UjhqHT11HTS
RT1MECH-45-004 | 6b3b0b0d-e0bd-69aa-cbec-1c0896d9e434 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_08 | CRAH - Computer room air handler |  |  | (CRAH-H-8) L2A Debris on coil | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625013&prj=684&rqi=OoMWAI6Y6Avh9LMIr7zvEe4s92
RT1MECH-43-001 | dd6ca28e-5539-f9ff-2406-14489f5f7589 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_06 | CRAH - Computer room air handler |  |  | (CRAH-H-6) L2A Filter bracket 8 front bottom bolt loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625009&prj=684&rqi=bcn98l1miuCnHvLGwJUSt4rb8y
RT1MECH-30-001 | f1623df6-ba88-fe9a-ea7e-5e0da6960c83 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_05 | CRAH - Computer room air handler |  |  | (CRAH-G-5) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625022&prj=684&rqi=RwQuiDJ4xXtEUAjLVi68Z7CrS8
RT1MECH-35-002 | f15cee8f-3ccc-b789-15aa-549652197828 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_10 | CRAH - Computer room air handler |  |  | (CRAH-G-10) L2A Filter brackets: #4 top front, #5 top back bolts missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625027&prj=684&rqi=2bMOd1quw3L51ERvexDVbN6DhJ
RT1MECH-26-003 | 91d5c368-6145-0757-5dce-342e970909f3 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_01 | CRAH - Computer room air handler |  |  | (CRAH-G-1) L2A #4 Top back bolt loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625018&prj=684&rqi=mpk20mgrxhVYFSqt5yyeuMCSad
RT1MECH-37-001 | b70c614f-0fd4-786b-e897-7bcd2c90299b | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_12 | CRAH - Computer room air handler |  |  | (CRAH-G-12) L2A Filter brackets: #4 top back bolt missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625029&prj=684&rqi=oPXqZYFGZZYCVRWglWl1AvN1dr
RT1MECH-27-001 | 9b6830e9-565a-5ae8-84c7-81a9818648ec | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_02 | CRAH - Computer room air handler |  |  | (CRAH-G-2) L2A Mystery screw found in top right filter section | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625019&prj=684&rqi=50aNu0u0eRhSMS0eHF1MqNIN7E
RT1MECH-29-001 | e2d59f3b-e5aa-f89a-0a55-39a790fdfa28 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_04 | CRAH - Computer room air handler |  |  | (CRAH-G-4) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625021&prj=684&rqi=hFXE5VAT8dPaPGSxWl4HGjHm8O
RT1MECH-41-001 | 8c741946-59f6-f908-b6ea-0d1223913776 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_04 | CRAH - Computer room air handler |  |  | (CRAH-H-4) L2A Filter bracket 5 bolt is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625008&prj=684&rqi=VHOtRelPGq90iK09GhoeD0oqW4
RT1MECH-33-001 | 6b32fb6e-ae49-e0f6-cdf7-181b58a07274 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_08 | CRAH - Computer room air handler |  |  | (CRAH-G-8) L2A Filter brackets: #4 Top back bolt missing #5 missing integral bolt and completely fallen down | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625026&prj=684&rqi=3Dk7KFNTxM1pLivLbffyCHqsNZ
RT1MECH-48-001 | 7bd7a92d-c04e-f972-c47b-c8da28408260 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-06-11 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_11 | CRAH - Computer room air handler |  |  | (CRAH-H-11) L2A Filter brackets 1-8 are loose (welds are broken) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625016&prj=684&rqi=lCbye6xwq0NcFZZM07xTMDmlGY
RT1MECH-90-006 | ec8a4fc3-a937-4b3c-a054-437759bca846 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A Termination end of leak detection rope is missing it's end of line "Leak Tape" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624186&prj=684&rqi=zwH2Qmz2g0j2VACvj6nRHOOxRg
RT1MECH-82-009 | 2af9025d-f01c-400a-abcb-275cc0d55843 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A Termination end of leak detection rope is missing it's end of line "Leak Tape" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624179&prj=684&rqi=aPrqu9t1PsYM0MeIYq5oBMK4KO
RT1MECH-86-005 | 5abd7a5d-9ca8-43f1-9bb9-995f7568fd08 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (Electrical Skid J) L2A Termination end of leak detection rope is missing it's end of line "Leak Tape" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624183&prj=684&rqi=K2ed3wppahgJmHea5FXdttcvhy
RT1MECH-88-005 | d8e1b7e4-b95c-48b3-9489-bb4a17ce11af | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (Electrical Skid K) L2A Termination end of leak detection rope is missing it's end of line "Leak Tape" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624184&prj=684&rqi=33yy59Gj8o1hM4FryUySQ4n7Xf
RT1MECH-84-007 | 66e14f62-c598-41d1-9329-cbee508c6383 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-06-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (Electrical Skid H) L2A Termination end of leak detection rope is missing it's end of line "Leak Tape | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=624182&prj=684&rqi=jmsLE1KQqSSRnJCxxyzxINx9aH
RT1MECH-85-003 | 05288b39-6cca-6741-fac6-06f31208816e | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (1HP_H_02) L2A Unit missing condensate containment curb. Present in G. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623996&prj=684&rqi=EKjavgf1VKjOQoM8KLm71uzDKG
RT1ELEC-91-002 | dc225b99-e855-4e0c-a554-575e8681bbab | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_R2_1 | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_R2_1) L2A The plastic cover plates beneath the HMI on all six 250A frame breakers (Q01 - Q06) are bent or cracked. This is likely due to the screw on the plastic cover being excessively tightened down. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623716&prj=684&rqi=E4MMr9IvrZa5KfS02zHxOXTGKx
RT1ELEC-362-002 | 18d1c0fb-6113-4a05-a861-e5c56c74df35 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_R2_3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_3) L2A The communication interface should have an additional Relay I/O card installed in the SMART slot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623732&prj=684&rqi=KQr1wLRaWJkuDO6KnZe4Wlc22Y
RT1ELEC-353-002 | 2f9ae9f7-f9b5-465e-bd36-37ae5cefe502 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_H3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_H3) L2A The communication interface should have an additional Relay I/O card installed in the SMART slot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623730&prj=684&rqi=7Pg1F3JiMJbTPsN2ClSVNr4RCK
RT1ELEC-91-003 | f593d136-458c-4873-838b-2aa2434cdc40 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_R2_1 | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_R2_1) L2A The Q10 'SPARE' breaker is not the correct kind of breaker per the submittal. Currently installed is an XT5H 400AF / 400A Plug/Sensor breaker. Per Drawing # HSU-5736GR-ELC_DWG01 of the Hanley submittal, the breaker should be a XT5H 600AF / 600A Plug/Sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623717&prj=684&rqi=Krvr7SpE18eWJFvtdueC2hNFFL
RT1ELEC-350-002 | 5d3d4efa-e515-412e-90f4-bd3c1cb3b543 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_G3) L2A The communication interface should have an additional Relay I/O card installed in the SMART slot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623728&prj=684&rqi=k8JrLSC5W8xRJMXdgIYInWLmZF
RT1ELEC-356-003 | a63cb190-34c7-4fdb-9110-3f360b0d6ddd | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_J3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_J3) L2A The communication interface should have an additional Relay I/O card installed in the SMART slot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623729&prj=684&rqi=KJLG4Vx5vzxEh4cpdqEDCoT8Jd
RT1ELEC-359-002 | ab02cb5a-0fbd-41f7-b555-f529e78e118d | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_K3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_K3) L2A The communication interface should have an additional Relay I/O card installed in the SMART slot. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623731&prj=684&rqi=wwZYFetu6sRmUNHH22tAsLLsZH
RT1ELEC-93-007 | b3f12f2e-3d08-44b7-903c-8d8aacc3681d | SV18-2 | 684 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-06-02 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A 1MSB_G Sections 05A, 06A, 11A, 12A, 13A all have extra hardware installed on the main busway with no cables connected to them. This extra hardware needs to be removed from the busway. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623706&prj=684&rqi=gg90983ZQDx7oi1E9MkkW4JYAs
RT1MECH-38-002 | d3654875-941b-b991-8cea-bd6c2dfe9dd6 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-01 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Cleaning | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_01 | CRAH - Computer room air handler |  |  | (1CRAH_H_01) L2A Fin section needs to be cleaned out. Miscellaneous debris present. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623575&prj=684&rqi=gakRhWpwy1f9RZceKnhgLKJ2l8
RT1ELEC-356-002 | e4df5c49-009d-436d-a588-05a54fcb0652 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_J3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_J3) L2A The cables fed from MDSB_J into UPS_J3 are not long enough to make proper connections inside of the UPS unit. There is a small amount of slack available on the cables inside of the MDSB but unsure if this is enough to make the connection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623566&prj=684&rqi=V7zD9KYfexYZ0nRV3sw4pLfABY
RT1MECH-40-001 | b35002fb-7f89-6442-4845-717b99683d80 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-01 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_03 | CRAH - Computer room air handler |  |  | (1CRAH_H_03) L2A Loose nut/bolts from filter bracket. Fallen onto the fan enclosure. Need to clean out | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623573&prj=684&rqi=XKWSxJLoiRCh5QhfOSmHFgaehz
RT1ELEC-93-005 | 9ad242ed-58f1-4741-8d22-5cabaf2399d6 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-01 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A While performing light tug test on cables inside of 1MSB_G Cabinet 02A, cable J400 disconnected from 'Port 13' on the P/PSU1 unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623568&prj=684&rqi=TAlUAsRj248DHllrkhm57fXLDa
RT1ELEC-93-006 | a5cfd43a-e9d8-4dad-becf-8724fd3b13bc | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-06-01 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A Protective plastic cover in section 06A of 1MSB_G is not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623570&prj=684&rqi=ZcfCF7hJzfUsngd7eqc68sgm7I
RT1MECH-38-001 | 364a45a1-dc29-c2e8-39c1-a33500d2cea4 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-06-01 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_01 | CRAH - Computer room air handler |  |  | (1CRAH _H_01) L2A Upper filter bracket is lose. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623574&prj=684&rqi=MJhnxKi0YSgtcjOVBAuu5tFnxS
RT1MECH-89-001 | 4ef0d253-bcaa-4c84-ba44-74ba11f5a819 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (WSHP-K-2) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622841&prj=684&rqi=C2gbtfdzkj5iAF0pPtAQuHkTgm
RT1MECH-84-002 | ccccaf5e-564d-4c55-9124-ab1512a845ac | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (Electrical Skid H) L2A At the 2 # doors on the north side, the pull box back boxes are too close to the adjacent switch for the pull station to be installed/door opened. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622846&prj=684&rqi=JTHBq35FYQ7G1sy62OlBacx8UT
RT1MECH-84-005 | d14ada26-82e6-48d1-b578-ad28c9daa30a | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (Electrical Skid H) L2A Where insulated CHW lines are supported by unistrut, shields are missing in a couple of locations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622869&prj=684&rqi=IUvoptGUZRgCt4tLTjiwux1T6b
RT1MECH-84-004 | 0f8a6e7f-f2e9-4073-a83b-32e667b11b56 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (WSHP-H-1) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622858&prj=684&rqi=b8mG7flZWAwRvhgiqvVlpBZGGZ
RT1MECH-84-006 | 349dd55d-1870-4a64-abe7-4abe5e627c35 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (Electrical Skid H) L2A At the south end of the PH, the drain valve on the CHW supply line, extends laterally over the UPS. Piping should be modified so it drops down vertically so as to eliminate the possibility of water dripping on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622873&prj=684&rqi=668ncAs1sPIn4cKj8pLcDyzpwS
RT1MECH-84-001 | 6a6adb41-bd0e-41b2-be52-7797264f39d2 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (WSHP-H-1) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622836&prj=684&rqi=QLY94Xnv0V0L6cwE36BXkTZVCq
RT1MECH-84-003 | 9842abec-0060-44a9-a0ca-0d19ad7d201e | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_1 | HP - Heat Pump |  |  | (Electrical Skid H) L2A At the SW doors, the speaker strobe & pull station devices cannot be installed as the back boxes are too close to the adjacent conduit and security JB respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622853&prj=684&rqi=nDAiHSTD8ofAnpqvA27J9k2pw5
RT1MECH-85-002 | f63eca85-d6ae-4ce2-b9b6-0e492800d48a | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (WSHP-H-2) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622859&prj=684&rqi=xI8olA5vxxc0RdQGOYN9dM43on
RT1MECH-85-001 | 43589546-b3f0-40cf-9785-691ebe8aa689 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_H_2 | HP - Heat Pump |  |  | (WSHP-H-2) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622837&prj=684&rqi=U7OpLjcwXzhlRwh2uZQzOYq9wN
RT1MECH-89-002 | dd6e724c-2d62-4988-a64d-9585d6b06865 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_2 | HP - Heat Pump |  |  | (WSHP-K-2) L2A Power wiring to the smoke detectors units is terminated incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622863&prj=684&rqi=bC67jMdd6YcixNhaQ3iyxytWt2
RT1MECH-86-004 | 318d942c-4d12-4a60-8a7d-82b87caa9a61 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (Electrical Skid J) L2A At the south end of the PH, the drain valve on the CHW supply line, extends laterally over the UPS. Piping should be modified so it drops down vertically so as to eliminate the possibility of water dripping on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622874&prj=684&rqi=POZYM0iCMYVkuZquRhnBI9rfLb
RT1MECH-86-003 | f65a525e-0ec0-4405-bbe7-e308a7417d4f | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (Electrical Skid J) L2A Where insulated CHW lines are supported by unistrut, shields are missing in a couple of locations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622870&prj=684&rqi=DeFol8AIrWGoi8iXp2cGNH0vgP
RT1MECH-86-002 | a0a4c849-5eb4-43e3-ac86-24c10c292af8 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (WSHP-J-1) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622860&prj=684&rqi=x9ytGYIku64j5AtFoimpvGMhTo
RT1MECH-86-001 | 4819db89-7049-43aa-a991-10cfbe4ca8bf | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_J_1 | HP - Heat Pump |  |  | (WSHP-J-1) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622838&prj=684&rqi=ysk86iUWoiYCij9a9KMDJgUQMv
RT1MECH-82-005 | e37d6538-9aec-4a60-af35-0cd24a73c972 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (WSHP-G-1) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622855&prj=684&rqi=Lr0sxqddtB3R2XGuMlLd3OYtk7
RT1MECH-82-004 | e82f07ac-d5e7-46f4-bc07-fa6396735126 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A Speaker strobe boxes at each of the 4 # doors, require an extension box. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622851&prj=684&rqi=Dcx3Un2iXdiRkzIOGbYlVADNpx
RT1MECH-82-006 | c1c4a209-dbae-4f0c-b443-629f5cf352b3 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (WSHP-G-1) L2A No CAT 6 cables pulled to WSHP (R-4800 & R-4900 on MPS submitall dwg MPS.522). Associated conduit required as well, see Skid H for example of complete install. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622865&prj=684&rqi=6Nb8cCge4ajIz1mDw1AY8XYOxt
RT1MECH-82-008 | a1b01610-941e-463a-9284-bc4a62ec3c67 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A At the south end of the PH, the drain valve on the CHW supply line, extends laterally over the UPS. Piping should be modified so it drops down vertically so as to eliminate the possibility of water dripping on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622872&prj=684&rqi=i55TfzUtA3TfbxumObV35AViaj
RT1MECH-82-007 | a1285672-11f6-4c64-be4a-7a00a5677519 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A Where insulated CHW lines are supported by unistrut, shields are missing in a couple of locations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622868&prj=684&rqi=5uLYsWd1e7RqELWaFVRi8SfKES
RT1MECH-88-001 | 3bff0e10-9bb1-42c5-85cd-a1113881291f | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (WSHP-K-1) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622840&prj=684&rqi=tUmP61nUXOR7n76QtdGy0AhY4r
RT1MECH-87-001 | abbf7c97-24e7-4f80-8051-3fc2d60be921 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | (WSHP-J-2) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622839&prj=684&rqi=tcCkL7muE2anWt6XArnc8wwnLD
RT1MECH-88-004 | 66d7c63e-c5c1-4893-ba9e-47eafed1aafd | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (Electrical Skid K) L2A At the south end of the PH, the drain valve on the CHW supply line, extends laterally over the UPS. Piping should be modified so it drops down vertically so as to eliminate the possibility of water dripping on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622875&prj=684&rqi=RfjuyBxtmsF2saQDyO0BxPPpZg
RT1MECH-87-002 | 995c49db-1f81-45bd-b61b-b747a11e49ae | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_J_2 | HP - Heat Pump |  |  | (WSHP-J-2) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622861&prj=684&rqi=VfLrRzb193sdK96X3gdjKF8G26
RT1MECH-88-002 | 699f96de-9a65-460d-a56b-5d1678eff93d | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (WSHP-K-1) L2A Power wiring to the smoke detectors units is terminated incorrectly. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622862&prj=684&rqi=10XOhDBtXL3hLHJ2qOflJFOu28
RT1MECH-88-003 | 3dd70cc4-b07e-4d1c-8feb-601485db475b | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_K_1 | HP - Heat Pump |  |  | (Electrical Skid K) L2A Where insulated CHW lines are supported by unistrut, shields are missing in a couple of locations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622871&prj=684&rqi=iqC6J9h632Dr1vtyHXNLwFfh9O
RT1MECH-83-001 | 8e032f3d-1785-4f01-89eb-ddba3ffa477d | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (WSHP-G-2) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622835&prj=684&rqi=cPApl4J26bKnihaGL0TuuFpbLr
RT1MECH-83-003 | ac51eb8a-da1d-4701-9de3-a53bb4ea7796 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (WSHP-G-2) L2A No CAT 6 cables pulled to WSHP (R-4800 & R-4900 on MPS submitall dwg MPS.522). Associated conduit required as well, see Skid H for example of complete install. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622866&prj=684&rqi=kbdWXrmqMeJY3pDOGBoKjezJo9
RT1MECH-83-002 | 61032b2a-eef8-44fd-a755-14aae81e5489 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_2 | HP - Heat Pump |  |  | (WSHP-G-2) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622856&prj=684&rqi=i9Z9z58YkubSNoJHrOOKJrnVJ8
RT1MECH-91-010 | 09ffa12a-a697-4524-9e47-0eb227531e78 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (WSHP-R2-2) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622844&prj=684&rqi=6jYZeJDqERfZ4fLLitFEj9Mvv8
RT1MECH-90-004 | 6e8eb03c-881a-4c43-9b85-44664b172efc | SV18-2 | 684 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (WSHP-R2-1) L2A Power wiring to the smoke detectors units is not pulled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622864&prj=684&rqi=77r19Aei7G5bZmX5aMbILQH0mf
RT1MECH-90-005 | 4fb4bd1c-3213-493a-b5c1-5276c8cbaaf7 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (WSHP-R2-1) L2A No CAT 6 cables pulled to WSHP (R-4800 & R-4900 on MPS submitall dwg MPS.522). Associated conduit required as well, see Skid H for example of complete install. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622867&prj=684&rqi=US6sJR2Q49jUR3yqv6x7qg1wyq
RT1MECH-90-003 | 22fe8809-2c0e-45a6-96e2-3964ee6017b2 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A At the SW doors, the speaker strobe & pull station devices cannot be installed as the back boxes are too close to the adjacent conduit and security JB respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622848&prj=684&rqi=hv1NgTbQE7NpWMq8V81iSMSvTi
RT1MECH-90-002 | faaa89d5-bee9-4265-98a9-e2ac51a8bd67 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (WSHP-R2-1) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622842&prj=684&rqi=bGWLPdMibyY11LIitYFe44o2kd
RT1ELEC-81-002 | d1cbe7e1-13e8-44e2-9b25-a333f0ae319e | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BTU_G | BTU - Battery Tripping unit |  |  | (1BTU_G) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622746&prj=684&rqi=Y3KIQB7bmV91zOnAaPcG7VzmJx
RT1ELEC-359-001 | f9322267-0157-4106-833e-41d96b4c1a24 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_K3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_K3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622744&prj=684&rqi=wrXE3b9jVbNoDubPG5jJHpnwTE
RT1ELEC-93-002 | ccd8f880-49d1-4975-a469-fe235f2cfd76 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A MSB HMI has 4 key-actuated selector switches, and only 3 are required. Per Hanley submittal drawing #HSU-5478FO-ELC-DWG02, this switch should be removed and blanked off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622657&prj=684&rqi=Nm03g1Wyu5y4SzwkN5AuPtOElN
RT1ELEC-85-001 | 901f274c-eaae-4eec-bcec-1415352931af | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BTU_R2 | BTU - Battery Tripping unit |  |  | (1BTU_R2) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622750&prj=684&rqi=q5LbseoeEiguxscsA0ctjl0jUo
RT1ELEC-374-001 | a06dc732-d093-4b93-a7a3-0050bd378b09 | SV18-2 | 684 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_R2 | GENL - Generator (LV) |  |  | (1GEN_R2) L2A Generator Circuit Breaker in GEN_R2 enclosure is missing the kirk key barrel assembly. The required kirk key for this breaker is: K1 (Serial # 64393) The breaker model is: SACE E6.2V-A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622707&prj=684&rqi=Jl9UNqjPF8XlK9AjyaSM0Pcxgg
RT1MECH-82-003 | 89e639e3-d0ae-486c-a151-d3466beed400 | SV18-2 | 684 | AMER | Closed | P3 Low CX | nick.shawger@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (WSHP-G-1) L2A Comms modules for Modbus communication do not have their ground wires terminated on ALL units, and the associated USB connection to the control board is inconsistently terminated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622706&prj=684&rqi=5VFD1Rz4f0Fa95fUl1S93vUuXF
RT1ELEC-83-001 | f14582be-00b1-4277-9f7d-2dca5a5770cc | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BTU_J | BTU - Battery Tripping unit |  |  | (1BTU_J) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622748&prj=684&rqi=xNxUIjWd0XN0lhJBCmiEvgnNFG
RT1ELEC-53-001 | e481a6ce-b7aa-4592-8c5b-bbd2e0293240 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_H3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_H3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622737&prj=684&rqi=VH8xy4Z322MwzgrvfAYopDTxB5
RT1ELEC-80-001 | a5294ff9-a2f0-4f08-9cb2-8742c8c196a8 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_R2_3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_R2_3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622740&prj=684&rqi=F4ST6rCuPSSWippLS32gBqsEss
RT1MECH-45-002 | f809044b-75a0-ce99-a5a6-28844cdc4861 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-21 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_08 | CRAH - Computer room air handler |  |  | (CRAH-H-8) L2A MCP1 fan overload allows user to go straight from "Trip" to "On" without opening the contact first. Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622734&prj=684&rqi=8BRgTDGCBdAU1qZBmcjfsEYevO
RT1ELEC-350-001 | 83e289a1-f3ad-463f-a9cb-854cb248577b | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_G3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_G3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622741&prj=684&rqi=kmdCWa8afOxb3jlpt7834XXKmu
RT1ELEC-84-001 | e44f4efe-0238-4d30-b103-60cda7cbd6d9 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BTU_K | BTU - Battery Tripping unit |  |  | (1BTU_K) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622749&prj=684&rqi=dWUTu0o60z9tagt45FiS7ts3Nd
RT1ELEC-356-001 | 46791d0b-5655-4a1e-b093-45138804612d | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_J3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_J3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622743&prj=684&rqi=5w53RLa9dP2fpbM0cbBX3inqy6
RT1ELEC-82-001 | 1cfa4028-1724-4993-afac-3bf82d1a5f4e | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BTU_H | BTU - Battery Tripping unit |  |  | (1BTU_H) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622747&prj=684&rqi=wDlrs0Ngyd9TOVpcMPlMa8T3kQ
RT1ELEC-94-003 | 87578cfd-d347-4108-95df-286d4c7baa91 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | (1MSB_H) L2A The key-actuated selector switches on the MSB HMI lock the keys when not in the center position. The selector switches should not lock the keys in any position. Sheet 2 of Hanley Submittal Drawing #HSU-5478FO-ELC-DWG02 specifies this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622677&prj=684&rqi=GDhQD7lxOGb4IixzdG7YjarZ6H
RT1ELEC-97-004 | fb40fcb0-0cb7-4a24-b90a-67d75b98d1ac | SV18-2 | 684 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB_R2) L2A FST identified during FWT that there are missing ground bonding cables connecting the MSB switchboard to the top hats on MSB sections 5A, 6A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622755&prj=684&rqi=WBEqL1RXjhqusJbXLlLmMn92iX
RT1ELEC-44-001 | 1f493264-8b83-49c9-a879-35a817fcbf49 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_G3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_G3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622736&prj=684&rqi=pjInlKYrR59gF1zDGCFA3iQyua
RT1ELEC-94-002 | 45d0f60d-bfc2-48d1-9f87-7fd9188129fc | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | (1MSB_H) L2A MSB HMI has 4 key-actuated selector switches, and only 3 are required. Per Hanley submittal drawing #HSU-5478FO-ELC-DWG02, this switch should be removed and blanked off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622676&prj=684&rqi=zQ4YFyeCGR8zcPyeNIHe9FPnrc
RT1ELEC-362-001 | 0a343b7f-2573-4175-85a7-62e0e5d1a73b | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_R2_3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_R2_3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622745&prj=684&rqi=JscDnAqqQkj30XO6XtFq8ii8tj
RT1ELEC-94-004 | 5d490588-23ef-4a27-9e96-d43ebf110ed8 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | (1MSB_H) L2A FST identified during FWT that there are missing ground bonding cables connecting the MSB switchboard to the top hats on MSB sections 5A, 6A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622752&prj=684&rqi=UoCFxoiTbq9y8siPqRZEeQAtgk
RT1ELEC-95-003 | adf24565-fb76-43da-a950-03268f6383bc | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | (1MSB_J) L2A The key-actuated selector switches on the MSB HMI lock the keys when not in the center position. The selector switches should not lock the keys in any position. Sheet 2 of Hanley Submittal Drawing #HSU-5478FO-ELC-DWG02 specifies this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622679&prj=684&rqi=KFAsOjc8As6uMVKUtkT2marIS6
RT1ELEC-95-004 | f7498aa9-9c8a-499c-9838-62139b6f539f | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | (1MSB_J) L2A FST identified during FWT that there are missing ground bonding cables connecting the MSB switchboard to the top hats on MSB sections 5A, 6A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622753&prj=684&rqi=1yaFJIvoPqwr836WDfTJny3R47
RT1ELEC-95-002 | ed41ca1e-3a17-4c64-a864-d9778f2a7760 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | (1MSB_J) L2A MSB HMI has 4 key-actuated selector switches, and only 3 are required. Per Hanley submittal drawing #HSU-5478FO-ELC-DWG02, this switch should be removed and blanked off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622678&prj=684&rqi=6GGht0prcBgwjEUZJYBSCyYYKE
RT1ELEC-97-003 | 8cfb263b-c706-4363-8e63-5c875ab16710 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB_R2) L2A The key-actuated selector switches on the MSB HMI lock the keys when not in the center position. The selector switches should not lock the keys in any position. Sheet 2 of Hanley Submittal Drawing #HSU-5478FO-ELC-DWG02 specifies this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622703&prj=684&rqi=mwz8jy6Q8AA0jU0dkk4MPJXLbh
RT1MECH-31-001 | f71b7078-827b-e99c-f7b1-330874ecd7c4 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-21 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_06 | CRAH - Computer room air handler |  |  | (1CRAH_G_06) L2A HMI panel is showing visible bend. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622735&prj=684&rqi=SkFQMSCxLdj3kpOBs9uCXcNGl3
RT1ELEC-71-001 | 6018bc35-2844-4a20-9095-ee66a511db60 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_K3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_K3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622739&prj=684&rqi=KYGJb8ssffmcDBDE06dYLJRoOA
RT1ELEC-97-002 | 40148923-e6b2-4dbf-8afb-c8426f1bfa6b | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB_R2) L2A MSB HMI has 4 key-actuated selector switches, and only 3 are required. Per Hanley submittal drawing #HSU-5478FO-ELC-DWG02, this switch should be removed and blanked off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622702&prj=684&rqi=rxwrnFmVGeiB23ql2r9lyznRgS
RT1ELEC-353-001 | 60593bfb-ff30-46e9-8aaa-99cea344f5df | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UPS_H3 | UPS - Uninterrupted Power Supply |  |  | (1UPS_H3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622742&prj=684&rqi=oz7VGKoApsvcDYxyWiRU6jJpeY
RT1MECH-42-001 | 671e720b-bd18-5ebf-8607-fe0d4c0ba396 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-21 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Torque required | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_05 | CRAH - Computer room air handler |  |  | (1CRAH_H_05) L2A Disconnect shaft for main power source 1 stats in the disconnect handle instead of the disconnect itself. See attached picture. Set screw threads appear to be stripped Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622733&prj=684&rqi=3QuUPAYVi2oBI1lJjsPTo4E7oe
RT1ELEC-93-004 | 8d33d969-0753-4db8-894f-05361f1342ff | SV18-2 | 684 | AMER | Closed | P2 Medium CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A FST identified during FWT that there are missing ground bonding cables connecting the MSB switchboard to the top hats on MSB sections 5A, 6A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622751&prj=684&rqi=KQ71ldOyfGuiEY7vwgUEocOgNL
RT1ELEC-93-003 | 9cfe89fe-7e34-429e-9c6d-cd0edb1567ac | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A The key-actuated selector switches on the MSB HMI lock the keys when not in the center position. The selector switches should not lock the keys in any position. Sheet 2 of Hanley Submittal Drawing #HSU-5478FO-ELC-DWG02 specifies this. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622670&prj=684&rqi=IQHtgAGysnxo0LrgW2SVozzmHy
RT1ELEC-96-002 | 6b9301bb-b993-455b-aad6-1b82ac015138 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2A MSB HMI is not installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622701&prj=684&rqi=XfkpBQigMqUySN7APVyfy3SiEl
RT1ELEC-62-001 | e7979ed1-2681-48b6-ab73-f1fd4c4054ba | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_1UPS_J3 | LIBATT - UPS Battery |  |  | (1BATT_1UPS_J3) L2A Missing communication cable from the equipment to the D-Mark panel. The MPS submittal for this equipment does not include this cable, so a change order will be required to complete this work. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622738&prj=684&rqi=b8jP6kuYRmKspxNfaruGYjk7hB
RT1ELEC-96-003 | 525d909b-76dc-4476-87ef-86cca93eaac9 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-21 04:00:00.000 +0400 | Electrical Contractor | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2A FST identified during FWT that there are missing ground bonding cables connecting the MSB switchboard to the top hats on MSB sections 5A, 6A, 11A, 12A, and 13A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622754&prj=684&rqi=LdZyjTn5iW7sbeyjbAjZIgzaII
RT1MECH-56-002 | 7fd2eaca-2ee7-4509-2932-3f854e0d9d86 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_07 | CRAH - Computer room air handler |  |  | (1CRAH_K_07) L2A Filter brace 2 is missing bolts. Bolts not found! | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622575&prj=684&rqi=SxMFsHpvOATlBKi5LCT5AcXLrf
RT1MECH-55-001 | 71925fc3-8637-4105-a512-626cc65d3570 | SV18-2 | 684 | AMER | Closed | P1 High CX | ethan.hang@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_06 | CRAH - Computer room air handler |  |  | (1CRAH_K_06) L2A Control board was donated to a CRAH with an earlier start-up date. New control board has been installed, it needs to be programmed during start up. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622524&prj=684&rqi=ETWTvpsRwjfsqSY90JV05X9sml
RT1MECH-55-003 | 46a63922-5abc-979f-ea90-c6290230c819 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Torque required | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_06 | CRAH - Computer room air handler |  |  | (1CRAH_K_06) L2A Loose bolt on fan 4 Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622573&prj=684&rqi=zT2tij1k76P244WUmcHblQs22X
RT1MECH-46-004 | 960193b0-95d1-4046-84a7-2e21dfdd088f | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_09 | CRAH - Computer room air handler |  |  | (1CRAH_H_09) L2A PICV actuator was donated to another CRAH with earlier start-up. New PICV actuator needed and installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622525&prj=684&rqi=ymzvI0FwGq0c6PHS1WY4sHN0Ol
RT1MECH-55-004 | 2ac56717-9658-8a7f-bcf6-fc7eb6ddd234 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_06 | CRAH - Computer room air handler |  |  | (CRAH-J-6) L2A Filter brace welds 5, 6, 7, 8 all broken Issues are raised on FG | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622574&prj=684&rqi=74yvGr7TeUdmaTl1TvHAkhw03P
RT1MECH-46-002 | ca6e54ae-dac1-4c4f-9aca-90b4617f8b77 | SV18-2 | 684 | AMER | Ready for Verification | P2 Medium CX | ethan.hang@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_09 | CRAH - Computer room air handler |  |  | (1CRAH_H_09) L2A Therma has found that the unit has leaks internally on the Vertiv side. A weld and a few spots around the PICV are leaking. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622526&prj=684&rqi=I4MqhvlM2E2vrWLFi0BnlAj2BU
RT1MECH-56-003 | 2827c48d-71fb-0b48-76f1-141b2ae6ca8c | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-20 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Cleaning | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_07 | CRAH - Computer room air handler |  |  | (1CRAH_K_07) L2A Right fan section needs cleaning | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622576&prj=684&rqi=xud9KjU6L3OaHAQWWUormpjNOa
RT1MECH-57-003 | ad9e899b-07f1-83e7-7933-acb7b7fefca7 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_08 | CRAH - Computer room air handler |  |  | (1CRAH_K_8) L2A Filter bracket 3 bolt fallen off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622352&prj=684&rqi=F1DNvsus9TKa4DTDiDcoxbWH61
RT1MECH-54-001 | 1094a1b8-54d8-4fd8-a20d-7a8be764e6b2 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_05 | CRAH - Computer room air handler |  |  | (1CRAH_K_5) L2A Very minor damage to fan 1 due to fallen filter brackets. Small scratches, adding for tracking purposes to keep an eye on it. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622319&prj=684&rqi=2d2pbwWpSErU4bzbjZ7NmaixwZ
RT1MECH-54-003 | e6d11fbc-148a-4fe4-af89-9add769f2c35 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_05 | CRAH - Computer room air handler |  |  | (CRAH-J-5) L2A Weld 5 broken Inspect all sections for dents, scratches, fit, corrosion, etc. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622321&prj=684&rqi=qW4TFkdYTI7pLASatEVcr91Stp
RT1MECH-51-002 | 4fd01a07-1186-455b-a13b-949082f5bbeb | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (1CRAH_K_2) L2A dP sensor loose in left upper fan section. Inspect Equipment for missing hardware | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622315&prj=684&rqi=3frFYSwa8V3Yoe2Ie7WGgBzEIu
RT1MECH-52-001 | ecb3fdb5-3890-4c1d-b807-e7c79922bd38 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_03 | CRAH - Computer room air handler |  |  | (CRAH-J-3) L2A Filter brace weld #7 is broken | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622316&prj=684&rqi=kIaz7dlckgSHzmvv9Hs1AdApQz
RT1ELEC-372-001 | 1753119e-1d16-4341-aee1-734f08a5963c | SV18-2 | 684 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_J | GENL - Generator (LV) |  |  | (1GEN_J) L2A Generator Circuit Breaker in GEN_J enclosure is missing the kirk key barrel assembly. The required kirk key for this breaker is: K1 (Serial # 64393) The breaker model is: SACE E6.2V-A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622356&prj=684&rqi=7Lwb9ypv2cpteej8iTxAWXoRSE
RT1MECH-50-001 | aa04a928-f815-4ea3-a3af-aa70716e89cb | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_01 | CRAH - Computer room air handler |  |  | (1CRAH_K_1) L2A Filter brace missing 2 bolts. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622312&prj=684&rqi=9fj2AITp942w2vTF3YjWYvLrIX
RT1ELEC-387-001 | 39d1156c-5209-4d08-b316-4544c76aa94a | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_R2_3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | (1UMDSB_R2_3) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1UPNL_R2_3_H1 (Q07) 1UPNL_R2_3_H2 (Q08) 1UPNL_R2_3_H3 (Q09) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622338&prj=684&rqi=16WT1CkiJAPEGZPvdG3hHRKzzq
RT1MECH-53-002 | fc1d8024-bb34-4229-a593-22b3023ef142 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_04 | CRAH - Computer room air handler |  |  | (1CRAH_K_4) L2A Lower right panel door upright is missing a rivet. Inspect Equipment for missing hardware | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622318&prj=684&rqi=VV3NLsPyylzHSVZ0rwWo4LjRnX
RT1ELEC-371-001 | 0973c9e2-41fc-479c-9647-eae74206e004 | SV18-2 | 684 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_H | GENL - Generator (LV) |  |  | (1GEN_H) L2A Generator Circuit Breaker in GEN_H enclosure is missing the kirk key barrel assembly. The required kirk key for this breaker is: K1 (Serial # 64393) The breaker model is: SACE E6.2V-A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622355&prj=684&rqi=a58OxmyyFI14MTtQCEcAxHJPyS
RT1MECH-53-001 | 420d6f4b-3863-48b4-a1ee-34defa62f2ae | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_04 | CRAH - Computer room air handler |  |  | (1CRAH_K_4) L2A Filter brace #8 is missing a bolt | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622317&prj=684&rqi=IJvm5op3qNqSvD88hkWR2adIqM
RT1MECH-54-002 | 0a5d6de1-90ef-458a-a175-49ff2db4165b | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_05 | CRAH - Computer room air handler |  |  | (1CRAH_K_5) L2A Bad fitment of left upper fan door Confirm that CRAH access doors open/close freely and have adequate seals | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622320&prj=684&rqi=MujWVhAmv2rYiRxIOA5Jtj122E
RT1MECH-58-001 | 398f0b60-0672-c857-3981-515f31c3422b | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Cleaning | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_09 | CRAH - Computer room air handler |  |  | (1CRAH_K_9) L2A Bolt missing from filter brace 7. Found as fodder above fan see photos. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622349&prj=684&rqi=dbM24FRvMSWkf0ETfVeijlK1Jh
RT1ELEC-373-001 | f1b0c78b-7ff8-43fd-8fd4-b53b98ba6c3e | SV18-2 | 684 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_K | GENL - Generator (LV) |  |  | (1GEN_K) L2A Generator Circuit Breaker in GEN_K enclosure is missing the kirk key barrel assembly. The required kirk key for this breaker is: K1 (Serial # 64393) The breaker model is: SACE E6.2V-A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622357&prj=684&rqi=CQAiy95SIJWKqQTg2YhaSw2nLF
RT1MECH-58-002 | 8516dbb2-3f4a-52ea-be79-0279ef54d367 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_09 | CRAH - Computer room air handler |  |  | (CRAH-J-9) L2A Broken filter brace welds #1 and 4 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622350&prj=684&rqi=AhVrymSWebONAgWbMBk1tALicW
RT1MECH-57-002 | e6deb11f-a738-21c7-946d-4ec30228f877 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_08 | CRAH - Computer room air handler |  |  | (CRAH-J-8) L2A Filter brace weld 8 broken Inspect all sections for dents, scratches, fit, corrosion, etc. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622351&prj=684&rqi=spSzxlDZ2vIMDptW3hwEduNoeC
RT1MECH-59-001 | 63cf5c1c-7b86-89e5-e60e-172fc6c56d82 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_10 | CRAH - Computer room air handler |  |  | (1CRAH_K_10) L2A Filter brace 3 missing bolt | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622348&prj=684&rqi=PnAvnwWfU8kkdwoUxEx0JkbeQg
RT1MECH-60-001 | 7daf45d8-5568-787a-8f69-4a7946fc5742 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_11 | CRAH - Computer room air handler |  |  | (1CRAH_K_11) L2A Missing bolt on #6 filter bracing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622347&prj=684&rqi=Os4N5of2RMeI6bFffJl5jJb9S5
RT1MECH-61-002 | 79f8e641-d6cf-043a-cfc4-63ca5d4d01b5 | SV18-2 | 684 | AMER | Closed | P3 Low CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_12 | CRAH - Computer room air handler |  |  | (CRAH-J-12) L2A Filter brace weld 4 is broken. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622346&prj=684&rqi=6Nv7MUIX2oRQbblQCJRsNzNJiD
RT1MECH-61-001 | cbe0fee4-2f7f-1ba2-75d0-4c4a4f080c9e | SV18-2 | 684 | AMER | Closed | P2 Medium CX | alec.dughi@veolia.com | 2026-05-19 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Cleaning | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_12 | CRAH - Computer room air handler |  |  | (1CRAH_K_12) L2A Air filter brackets have fallen into fan 8. CANNOT STARTUP UNTIL REMOVED | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622345&prj=684&rqi=TGBqvOz8w9mCrbqDx5VmkjvICK
RT1ELEC-5-001 | c3676790-2124-4f40-94d8-453d240ae162 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | SCH - Schneider MV | L2A | Installation not correct | Commissioning |  | Electrical â€“ MV | equipment | 1RMU_G | RMU - Ring Main Unit |  |  | (1RMU_G) L2A RMU cover plates were inadvertently swapped following L2A testing. The left most switch panel cover is currently installed over the center switch. Please refer to attached images for additional information. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622339&prj=684&rqi=1rCY2gBG9Zuhn9jgvvWajtfWVm
RT1ELEC-386-001 | a4e6799b-51c0-417f-ab3d-2b75c0070f82 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UMDSB_K3 | UMDSB - Mech Dist Switchboard (fed from UPS) |  |  | (1UMDSB_K3) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1UTX_K3_L1 (Q06) 1UPNL_K3_H1 (Q09) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622337&prj=684&rqi=ZS6OwqwGhP7AqdXHSgISap9yf8
RT1ELEC-370-001 | eee4878b-f176-475d-bf8d-4714ed9bbd59 | SV18-2 | 684 | AMER | Open | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-19 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1GEN_G | GENL - Generator (LV) |  |  | (1GEN_G) L2A Generator Circuit Breaker in GEN_G enclosure is missing the kirk key barrel assembly. The required kirk key for this breaker is: K1 (Serial # 64393) The breaker model is: SACE E6.2V-A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622353&prj=684&rqi=oL3S0odtxzsb1TgqqsTTIpeOJS
RT1MECH-56-001 | b23cd749-b788-40b6-0de3-42f711b25f0a | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-13 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_07 | CRAH - Computer room air handler |  |  | (1CRAH_K_07) L2A 3A fuse cover on F5 in the power panel is broken. Replacement needed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621735&prj=684&rqi=toh9OTPLZKhs9Y8uet1aEyqar4
RT1MECH-26-002 | 57ee0288-9d15-4492-9795-5f2303a695d6 | SV18-2 | 684 | AMER | Closed | P1 High CX | ethan.hang@veolia.com | 2026-05-13 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_01 | CRAH - Computer room air handler |  |  | (All Data Hall CRAHs) For Tracking Purposes Interconnection between smoke detector and control panel to be completed by Vertiv. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621740&prj=684&rqi=P4vBNhvjovB5nEfAcduNHjDajc
RT1MECH-3-004 | 4f8afa24-e5fb-4a7f-a67e-a47f64c4a78d | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-13 04:00:00.000 +0400 | Controls Contractor | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1ACC_R2_05 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers (ACC)) For tracking purposes Heat trace failures create a hardwired fault status to the BMS, creating a latching BMS fault for the chiller skid. Approved solution is to have ETech run an additional wire from the heat trace relay to use as an additional hardwire point to use for ignoring this hardwire fault status. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621739&prj=684&rqi=cyJHuPcGoAm9bsC0VhzFTuR1tX
RT1MECH-51-001 | e89da63f-ba22-9782-abf2-2c6528acc428 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-13 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_02 | CRAH - Computer room air handler |  |  | (1CRAH_K_02) L2A Cable coming off of CAT6 is missing a connection header. Correct photo attached. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621723&prj=684&rqi=KZ9oVybzBI2zzDSHlTtbKv4SeX
RT1MECH-3-003 | 58ddf0c5-d22c-470f-b84e-9c2a41a3cc68 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-13 04:00:00.000 +0400 | TRN - Trane | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1ACC_R2_05 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers (ACC)) For Tracking Purposes Please confirm that all freeze protection valves are modulating. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621738&prj=684&rqi=GxHOhcc1pmvlXtCTo1PaYq05E2
RT1ELEC-96-001 | 2b7e7f34-c718-43b5-8fcb-0674cad0429a | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_K | MSB - Main Input Switchboard |  |  | (1MSB_K) L2A MSB breaker labels from the Hanley submittal do not match the electrical one line diagram. Specifically, breaker Q02 does not exist on the electrical one line diagram which causes all other breaker labels to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621157&prj=684&rqi=9IkTUHwK0o4Sykn2HJIXirNMYs
RT1ELEC-88-001 | be11ce03-b137-4b6d-b364-0f5bda9b87d9 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_H | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_H) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_H_HP (Q06) 1UPS_H3 (Q07) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621161&prj=684&rqi=FL1EjLWzI4jzYjPCbQl7sYylJQ
RT1ELEC-94-001 | 71b3ec56-a2fd-4c8c-899e-3fabf14d60a0 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_H | MSB - Main Input Switchboard |  |  | (1MSB_H) L2A MSB breaker labels from the Hanley submittal do not match the electrical one line diagram. Specifically, breaker Q02 does not exist on the electrical one line diagram which causes all other breaker labels to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621154&prj=684&rqi=tOuBk958oPjSO6xBnQDArF1Wae
RT1ELEC-93-001 | fea3823b-06e2-4fbd-af2d-e33d17c2ddd5 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_G | MSB - Main Input Switchboard |  |  | (1MSB_G) L2A MSB breaker labels from the Hanley submittal do not match the electrical one line diagram. Specifically, breaker Q02 does not exist on the electrical one line diagram which causes all other breaker labels to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621152&prj=684&rqi=uVCqgkkWguwn8cZByjyh4ewCiw
RT1ELEC-87-001 | b70cae07-f022-495e-b70f-dbcc5192a1f5 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_G | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_G) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_G_HP (Q06) 1UPS_G3 (Q07) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621159&prj=684&rqi=OoeWjkWGSx0UBHz0X0epJNYRrS
RT1ELEC-89-001 | a68171e1-859d-481f-9343-772949e8369c | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_J | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_J) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_J_HP (Q06) 1UPS_J3 (Q07) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621162&prj=684&rqi=j1gBL5cujimhYrxL28eTqedpnY
RT1ELEC-95-001 | 96aa7502-fd3e-47cb-bb61-af1d5e008fd9 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_J | MSB - Main Input Switchboard |  |  | (1MSB_J) L2A MSB breaker labels from the Hanley submittal do not match the electrical one line diagram. Specifically, breaker Q02 does not exist on the electrical one line diagram which causes all other breaker labels to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621155&prj=684&rqi=aINy3BuOGeQwHRyzqt8X29Ylff
RT1ELEC-90-001 | fa185b07-3a5a-42ee-afd8-48828b00dfdd | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-05-11 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_K | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_K) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_K_HP (Q06) 1UPS_K3 (Q07) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621164&prj=684&rqi=4weX14vBm2k4VGyLZrqsuipXMF
RT1MECH-26-001 | 526f3f39-cc8b-4cfd-8ac5-dd8a42d5cdbb | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | General Design Issue | Design |  | Mechanical â€“ Water | equipment | 1CRAH_G_01 | CRAH - Computer room air handler |  |  | (All Data Hall CRAHs) L2A Discrepancy between 18-1 and 18-2 leak detection set up. At 18-1, leak detection was installed by MC and placed on the unit INTERIOR, to identify leaks in the coil. Photo attached with yellow rope leak detector. At 18-2 It's a point leak detector on a cable which has a plug on the bottom left of the unit EXTERIOR. Please confirm if this was the intended part shipped out and if so, when it will be installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620430&prj=684&rqi=S5NFV5s6dXgipVB4DFesUv9eis
RT1MECH-91-008 | e4ecb814-d078-467d-a294-73fa18fc303d | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A Speaker strobe boxes at each of the 4 # doors, require an extension box. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620459&prj=684&rqi=SWNHnLb8gOsCZrVblqZ0g3LkV5
RT1MECH-91-005 | 277f2a2a-cb68-4b43-8103-5556b085af12 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (1HP_R2_2) L2A Conduit clamps for the disconnect are impeding removal of the filter and will damage the filter on removal and maintenance. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620454&prj=684&rqi=hrJeN5SNbm0z4zFbHL4piGqB8x
RT1MECH-91-006 | 0eb591d4-34e7-45dc-90ad-4a311367ee72 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Design correction needed | Design |  | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (R2, and G HPs) Access to the strainer, balancing valve, isolation valves, is very difficult, due to arrangement of fire alarm and various electrical JBâ€˜s in front of them. Issue is not present on J, H, K skids. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620456&prj=684&rqi=1p9Br0eSt9tRAz2ull75KWHCo9
RT1MECH-91-007 | 9a8d3846-93fc-4038-9188-b54e55572ce8 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (WSHP-R2-2) L2A Power wire at the smoke detectors at the Trane WSHPs has not been pulled. Currently they have only pulled the control wiring that shuts the units down. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620457&prj=684&rqi=5HmgCGeOb2WNSGhbjRSgBKOLNo
RT1MECH-91-009 | c72926b2-4829-4730-bfb5-4579e15f2857 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A At the SW doors, the speaker strobe & pull station devices cannot be installed as the back boxes are too close to the adjacent conduit and security JB respectively. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620460&prj=684&rqi=pBfNwE1WrbLLMJ2i6kkyc0jwfN
RT1MECH-82-002 | 04bb0c3b-2497-441f-813b-b709a1b284ae | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A At the 2 # doors on the north side, the pull box back boxes are too close to the adjacent switch for the pull station to be installed/door opened. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620461&prj=684&rqi=DTyDKjQMUUTMvurNpUaPIzA5oW
RT1MECH-74-001 | 32784c42-88a9-47cb-a735-ae4f03d57130 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-05 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_R2_13 | CRAH - Computer room air handler (Skid) |  |  | (1CRAH_R2_3) L2A Pipework has been damaged/cut and isn't holding pressure - needs to be repaired to allow Therma to progress. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620452&prj=684&rqi=xQqlsLHXqNo66DQHqI5CU8PpK8
RT1MECH-82-001 | 255f0f28-6caf-4ed5-a420-c875deca3792 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_G_1 | HP - Heat Pump |  |  | (Electrical Skid G) L2A Intake hoods need to be installed on the exterior of the skid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620300&prj=684&rqi=qQk10GcJ2iVQIC2Ft56vADxfVw
RT1MECH-46-001 | 38009394-2a0a-4b60-94ae-0f47317ba5f4 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_09 | CRAH - Computer room air handler |  |  | (1CRAH_H_09) L2A Right side coil has no pressure. Needs circuit setter housing gasket and flange weld repair on the return side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620285&prj=684&rqi=deDlP7UTtALaov0qDgBUGoHL2S
RT1MECH-91-004 | 800b4b2f-db92-415c-ab0f-b8f7b381fa19 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A Intake hoods need to be installed on the exterior of the skid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620299&prj=684&rqi=ixiOjJ8aycReT40PyIaB8tSsVW
RT1MECH-91-003 | 594d4434-992b-484c-9d4f-195a167f1f50 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (WSHP-R2-2) L2A No CAT 6 cables pulled to WSHP (R-4800 & R-4900 on MPS submitall dwg MPS.522). Associated conduit required as well, see Skid H for example of complete install. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620296&prj=684&rqi=zXXckjslie8pVFknhXziK2iSv7
RT1MECH-90-001 | 75f8b64d-2314-42e7-959c-bcfb1e8cc19f | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_1 | HP - Heat Pump |  |  | (1HP_R2_1) L2A A number of joints on the ductwork have not been sealed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620297&prj=684&rqi=qjQSspaHAiHtXK7t5PyU01yJDC
RT1MECH-6-001 | e3cfcfaf-0b4d-44d5-995a-c609ff6a40b1 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | TRN - Trane | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1ACC_H_13 | ACC - Chiller â€“ Air Cooled |  |  | (1ACC_H_13) L2A N5 jumper in control panel is missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620292&prj=684&rqi=1cj0RtlrI55kZyg5MVLyTrTyv1
RT1MECH-3-002 | 3ef66a98-d32a-234a-1a8f-1c1b3733f719 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Electrical Contractor | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1ACC_R2_05 | ACC - Chiller â€“ Air Cooled |  |  | (All Chillers (ACC)) Putty inconsistently applied to conduit bushings between the harmonic filter and the ACC power cabinet | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620317&prj=684&rqi=2HZ8buVybNbwcJAqkha303ignB
RT1MECH-57-001 | cce26556-20c5-47e9-a618-2ac2842386a5 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_K_08 | CRAH - Computer room air handler |  |  | (1CRAH_K_08) L2A Left side coil has no pressure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620286&prj=684&rqi=tUIH7Ck6pRzJyDvoAOOIwEgrVy
RT1MECH-91-002 | bf8e62e7-e837-4400-b2a7-f185c335ad36 | SV18-2 | 684 | AMER | Closed | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A Where insulated CHW lines are supported by unistrut, shields are missing in a couple of locations | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620295&prj=684&rqi=PNEB4b2DVIPdZp9Lj3MEftOPtj
RT1MECH-45-001 | 601d0c5f-bdf7-4401-8a65-07fa29c067bd | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_H_08 | CRAH - Computer room air handler |  |  | (1CRAH_H_08) L2A Left side coil holds no pressure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620283&prj=684&rqi=9DMI76CPeahir82QKPnTN3AzuL
RT1MECH-35-001 | 7a87c1b9-3f2e-4bc3-9cfb-5a864fe22581 | SV18-2 | 684 | AMER | Closed | P2 Medium CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Ver - Vertiv HVAC | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CRAH_G_10 | CRAH - Computer room air handler |  |  | (1CRAH_G_10) L2A Left side coil holds no pressure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620298&prj=684&rqi=HACd1Jv0rKBqW7cLjUgHkbVxD9
RT1MECH-91-001 | 30d05a93-6628-4680-a252-02e0a650ece1 | SV18-2 | 684 | AMER | Open | P3 Low CX | ethan.hang@veolia.com | 2026-05-04 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1HP_R2_2 | HP - Heat Pump |  |  | (Electrical Skid R2) L2A At the south end of the PH, the drain valve on the CHW supply line, extends laterally over the UPS. Piping should be modified so it drops down vertically so as to eliminate the possibility of water dripping on the UPS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620294&prj=684&rqi=XA43t720kvDs3dEpK38d8gKzmG
RT1ELEC-81-001 | eb1ea741-5c13-4556-95cc-b01f814c87d7 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-04-24 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1BTU_G | BTU - Battery Tripping unit |  |  | (1BTU_G) L2A '1BTU_G ground plate 4' connection is not made up correctly. Please refer to attached photo. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619367&prj=684&rqi=gtIOFL0q3h809odZyvNxuNdyyO
RT1ELEC-91-001 | b4d71f8f-5d51-46b0-813b-262dcc22a394 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-04-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_R2_1 | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_R2_1) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_GEN_R2 (Q02) 1PNL_R2_HP (Q05) 1UPS_R2_3 (Q07) 1UMDSB_R2_3 (Q08) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618583&prj=684&rqi=TyFWtcxClyCEwv6IXxBzW5TPTP
RT1ELEC-97-001 | aae58a67-b51f-4fe2-940d-4e858c35442d | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-04-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_R2 | MSB - Main Input Switchboard |  |  | (1MSB_R2) L2A MSB breaker labels from the Hanley submittal do not match the electrical one line diagram. Specifically, breaker Q02 does not exist on the electrical one line diagram which causes all other breaker labels to be incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618581&prj=684&rqi=RXx5SP1Ud3b7xgN6i0IPqr2IuK
RT1ELEC-92-001 | 102b6f1b-35cc-4794-9be4-bf85feb02961 | SV18-2 | 684 | AMER | Closed | P3 Low CX | carlos.carrillo1@veolia.com | 2026-04-17 04:00:00.000 +0400 | HAN - Hanley Energy Elec | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ LV | equipment | 1MDSB_R2_2 | MDSB - Mech Distribution Switchboard |  |  | (1MDSB_R2_2) L2A FST/REG identified several connections with incorrect lugs during FWT and initial inspections. The breakers with incorrect lugs are as follows: 1PNL_R2_2_H1 (Q02) 1PNL_R2_2_H2 (Q03) 1PNL_R2_2_H3 (Q04) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618585&prj=684&rqi=DGFccUjrssNf9ohAQFdlQKfyxj
L2L3 Sun-27-002 | 61fbd95d-6153-4253-8d99-0a3e4d1eecaf | SY05-4 | 644 | APAC | Open | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-09-14 04:00:00.000 +0400 | General Contractor |  | Installation not correct | Commissioning |  | Communications | equipment | SY5-FCMS-9A | FCMS Outstation |  |  | TMD-M-SY5-4 (Ethernet cables and junction box loose inside of FCMS Panel) The DCOS junction box and ethernet cables are untidy inside the FCMS 9A Panel. See image attached. Can these be installed neatly inside the panel. Please provide evidence of work completed before moving to Ready for verification. If not ready, please leave a date on when the works can be completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637856&prj=644&rqi=QXG8pka4HLV1xn8AICzblb8Whj
L2L3 Sun-27-001 | 28fe7530-926e-4c17-b017-30cb54eb04c2 | SY05-4 | 644 | APAC | Ready for Verification | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-09-14 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning |  | Communications | equipment | SY5-FCMS-9A | FCMS Outstation |  |  | TMD-M-SY5-4 (Missing gland in FCMS Panel) A hole in the bottom of the FCMS Panel where the temporary power cable is coming through is missing a gland. See image attached. Please upload evidence of gland installed before moving to Ready for Verification | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637855&prj=644&rqi=uG0fsQnaETVlRdvfyz8liwxJcT
L2L3 Sun-33-001 | 93cc6f16-0d98-4c0e-af40-108b70709356 | SY05-4 | 644 | APAC | Open | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-09-08 04:00:00.000 +0400 | General Contractor - BMS |  | Documentation not issued/ Required | Commissioning |  | Communications | equipment | SY5-FCMS-10A | FCMS Outstation |  |  | TMD-M-SY5-4 (Crossmuller to supply completed panel drawings) Crossmuller have developed red line drawings due field device changes terminated in the panel. Crossmuller to convert red line drawings to complete drawings and supply physical copies in the panels SY5-FCMS-10A & 10B. Same issue applies for panels SY5-FCMS-9A & 9B as they have the same changes made. Please provide evidence of completion of works before pushing to ready for verification. Alternatively leave a comment on when works will be completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637137&prj=644&rqi=Yrgzpah2UB3pxZD7lIcrmULan2
GI-131 | 946e87bf-1aa7-483e-86d0-1c8ffa13cb55 | SY05-4 | 644 | APAC | Closed | P3 Low CX | steven.hoang@bureauveritas.com | 2026-09-03 04:00:00.000 +0400 | General Contractor |  | DCOS Design Issue | DCOS | [7 empty] | SH-E-SY5-4 (DCOS Graphic Queries) Graphics for STS does not specify where they are receiving supply from EG CB number. It also does not specify which STS is supplying which UDB. Can the template be modified to show text labelling on graphics or is this an approved and agreed graphic design? This issue is raised for the purpose of understanding, tracking and improvements of graphics. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636625&prj=644&rqi=KJKI8JazjvGXpRn18uT3SHN4oL
GI-125 | 8ed8f3de-1386-41a7-800c-1ebbbc8abaaf | SY05-4 | 644 | APAC | Open | P3 Low CX | steven.hoang@bureauveritas.com | 2026-08-24 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [7 empty] | SH-E-SY5-4 (A9 UDB FAT Missing) FAT Documents Missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634982&prj=644&rqi=vOxp18mhyTMnRCg7cF4UO4Vvkm
GI-124 | 62d9561f-dd45-413e-a284-6284d9ea4112 | SY05-4 | 644 | APAC | Open | P3 Low CX | steven.hoang@bureauveritas.com | 2026-08-24 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [7 empty] | SH-E-SY5-4 (A13 UDB FAT Missing) FAT documents missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634981&prj=644&rqi=EncYr2kJg8qJSqYpbCdjayNLYT
GI-120 | ab4a7e4c-9bab-412f-92c9-5128234b894f | SY05-4 | 644 | APAC | Open | P3 Low DCOS | steven.hoang@bureauveritas.com | 2026-08-17 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | SH-E-SY5-4 (No Analogue values on GSB08) - DCOS Mapping Incorrect for GSB breaker up stream of A9 MVTB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634009&prj=644&rqi=Zs2DBv8uAF3hEm4PIDmFmHBVzj
GI-116 | 12896a9c-dd07-4d5e-8894-ebf3982d28e8 | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-14 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | ##SY5-4-E-AOB (COLO13-DAZZA PDU LABELLING) Issue to be raised as assets are being energised for tracking, this is part of the L2 scripts. Understanding they have been ordered. Labels (on order ##Push Issue) PDU-7A PDU-32A PDU-48B PDU-47B PDU-46B PDU-46A PDU-47A PDU-48A TEMP label shave been placed to coverer the energisation process. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633732&prj=644&rqi=PLF09TXwALwg5xgM9JjacL4i52
GI-115 | 7da58cc0-d34f-46cd-9b9c-064d9a704939 | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-14 04:00:00.000 +0400 | General Contractor |  | Incomplete Connections | Commissioning | [7 empty] | SY5-4-E-AOB COLO13 DAZZA (UDB/PDU Common Issues) Raising for tracking, before EE. PDU-26A - loose CT terminal block HDPM6000 PDU-28A - has a loose cable crimp above the fuse F1 HDPM6000 PDU-29A - paper above the HDPM6000 to be removed & cable crimp on top of power terminals PDU-31A - CT terminal block HDPM6000 disconnected & cable crimp above meter which needs to be removed PDU-32A - isobar cover above the PM and loose CT terminal block HDPM6000 PDU-32A - loose CT terminal block HDPM6000 PDU - 39A - loose CT terminal block HDPM6000 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633731&prj=644&rqi=XPhX8D89nPap5DFXpBJWJWCUyk
GI-118 | efa811b2-946a-46fd-ab90-41a96161564d | SY05-4 | 644 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-14 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [7 empty] | SY5-4-E-AOB -Earth Grid / Bar Field Test (CxL2A, CxL2B) Raising this for tracking as no clear asset for this on FG, open to add an earthing asset if this works. FIC003 â€“ Earth Grid / Earth Bar Field Testing is currently planned to be completed as a single activity at the end of the project (longest distance testing point) rather than progressively for each room/area prior to energisation. From a commissioning perspective, progressive completion and recording of earth grid/earth bar testing for each room as it is handed over and energised would provide improved traceability and verification throughout the staged energisation process. This comment is recorded to ensure the item remains visible and is not overlooked during the course of the project, particularly given the staged nature of energisations and potential personnel changes prior to project handover including the CxA team. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633734&prj=644&rqi=sPjFOcomSzUXv6U3r3axuSxIXg
GI-117 | c575889c-f186-4860-9b59-4b821ec09078 | SY05-4 | 644 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-14 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [7 empty] | SY5-4-E-AOB (PDU-COLO13-DAZZA Cable Routing Across Unprotected Metal Edge) The cable entering the assembly is routed across a metal cut-out without any grommet, edge trim, or mechanical protection. The cable sheath is in direct proximity to the sharp edge at the cable entry point. The installation presents a risk of cable sheath abrasion and insulation damage due to contact with the metal edge. This condition is not considered good installation practice for cable protection and may impact the long-term integrity of the cable If this arrangement is intentional and forms part of the Schneider Electric design, please provide confirmation that the cable routing has been assessed and that the risk of cable wear against the metal edge over the operational life of the equipment is accepted by the design authority. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633733&prj=644&rqi=kYbx7EwJ08UKKyRzjPzpe2cbbx
GI-114 | ae3ae407-b35e-4b6a-945a-8ced00ba6263 | SY05-4 | 644 | APAC | Closed | P3 Low CX | steven.hoang@bureauveritas.com | 2026-08-12 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | SH-E-SY5-4 (A9-STS-01A - 08A & A9-STS-01B - 08B) - Permanent labels indicating Sources 1 & 2 supply not present. Issue raised for tracking purposes | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633386&prj=644&rqi=VLT7v34G1TjKr4n7AvFT2AAKO2
GI-113 | 3bb77edb-b184-4e23-b085-b68ad4449932 | SY05-4 | 644 | APAC | Closed | P3 Low CX | steven.hoang@bureauveritas.com | 2026-08-12 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [7 empty] | SH-E-SY5-4 (R2-OSB-09A & R2-OSB-09B) - R2-OSB-09B STS-05B graphics showing Open close position but does not show trip position - R2-OSB-09A STS-05A graphics showing trip position and unable to be cleared to show open & close positions. - R2-OSB-09A & R2-OSB-09B Missing Comms cable connection from ACB to Comms Outlet. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=633382&prj=644&rqi=IkpBK6CZzoGOR1OeO0XeLtSEaY
GI-112 | 793cf1db-e8b7-434f-a346-437e4dc70940 | SY05-4 | 644 | APAC | Open | P3 Low CX | steven.hoang@bureauveritas.com | 2026-08-06 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [7 empty] | SH-E-SY5-4 (CALIBRATION CERTIFICATES FOR FAT EQUIPMENT) L1 FAT Documents reference 3 types of testing instruments. The uploaded equipment certificates do not match what was used during FAT. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632686&prj=644&rqi=A1VKSNakv08SkQooDwgFSrikSD
GI-111 | 1ed80e89-5c23-4672-8152-09c23af31488 | SY05-4 | 644 | APAC | Closed | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-08-05 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | TMD-M-SY5-4 (Fed from labels needed for A9 & A10 MCPs) Power source fed from labels are needed for the MCPs in A9 & A10. Temporary Labels ahave been applied. Issue raised for tarcking. Please provide evidence of completion of wo | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632395&prj=644&rqi=lMfvsMYiGdzz1y1ejlbsHmbHJ0
GI-105 | 8a0b7cd3-c818-4216-a937-7121871dabbb | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-01 04:00:00.000 +0400 | General Contractor |  | Incomplete Connections | Commissioning | [7 empty] | SY5-4-AOB-E-R2 09A & 09B OSB Busduct Elbow Connections Issue raised to facilitate YT The final elbow connections for the R2 09A & 09B OSB busducts remain outstanding. Once the busduct is connected, the asset will have a direct connection to the R2 lineup redundancy block on live facility, creating the potential for energisation. The OSB's require to be Yellow Tagged prior to the final elbows being installed. This issue has been raised to track the outstanding works and ensure the appropriate controls are in place before connection to the live facility. Issue can be close upon final connection and test result upload. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631975&prj=644&rqi=rz3SrnYSM2piIB0Bv3WmEgKtXI
GI-102 | f6dbe2f3-3bf3-45ed-b0ba-d8d0f3af80ca | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-08-01 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [7 empty] | AOB-E-SY5-5 (Delivery Documentation Outstanding) Delivery documentation is outstanding. Acceptance dockets and supporting delivery photographs have not been provided/uploaded for review. These records are required to verify equipment receipt, delivery condition, and completion of project documentation requirements. A09-BAT-01-18 A09-MSB/OSB-01 A09-EDB-01 M5-02-BAT-01-03 M5-02-UPS-01 A10-BAT-01-18 A10-MVTB-01 A10-BTU-01 A10-TRX-01 A10-EDB-01 SY5-R2-OSB-10A SY5-R2-OSB-10B A10-MSB/OSB-01 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631970&prj=644&rqi=pIOVvAc6b964qoEd2lQJorcgFc
GI-097 | f9400e76-7f49-4751-b07d-88499bd20cbc | SY05-4 | 644 | APAC | Ready for Verification | P3 Low CX | steven.hoang@bureauveritas.com | 2026-07-27 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [7 empty] | AOB-E-SY5-4 (A02 & A09-BTU-01) TAPE Residual on Front Door No Visible Torque Marks on Battery Terminals No Cable Label No Panel Label No Battery Manufacturing Date DC cables not Connected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630991&prj=644&rqi=0sO7iVekzl8yLvGp7SFf0kaPJO
GI-098 | 330f06aa-fd99-4372-8a85-ebcecc02c36e | SY05-4 | 644 | APAC | Closed | P3 Low CX | steven.hoang@bureauveritas.com | 2026-07-27 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | AOB-E-SY5-4 (A09-BTU-01) ##LV FIC001 cable dead test and fed from label AC Cable not connected Raising this for tracking only as EDB is not ready. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630992&prj=644&rqi=9NJYsfp9dSPSNQgTsaQEJkyo7c
GI-091 | f01e3621-6b8c-4bcd-af5c-c4bb0f2db29c | SY05-4 | 644 | APAC | Closed | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-07-05 04:00:00.000 +0400 | General Contractor - BMS |  | DCOS General Issue | DCOS | [7 empty] | TMD-M-SY5-4 (Variation of DCOS terminations to A9 MCPs) Termination blocks had to be added to the MCPs to facilitate Crossmuller terminations. Crossmuller to add this to their ITPs to show these works have been completed in the A9 MCP & FCMS Panel Upload ITP with comments of work variation to MCP or FCMS Panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627969&prj=644&rqi=JgVksph151q39uvwVV661deWRu
GI-078 | d7717b8e-e78a-41e0-9e52-b9918dd3885f | SY05-4 | 644 | APAC | Closed | P3 Low CX | raluca.bastucescu@bureauveritas.com | 2026-07-01 04:00:00.000 +0400 | General Contractor |  | Cleaning | Commissioning | [7 empty] | A2 Switchroom to be cleaned | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627660&prj=644&rqi=CwvqGGreBeYxBPBPF3frLCKQZk
GI-074 | 1b7407e5-57f4-4efa-8c4d-44369d1302cd | SY05-4 | 644 | APAC | Open | P3 Low CX | raluca.bastucescu@bureauveritas.com | 2026-06-30 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [7 empty] | TRACKING PURPOSES ONLY - VERTIV PURPOSLY REMOVED AP22-X1 cable in UPS Prior to L3 Cx Calibration Activities. Vertiv will put it back once calibration activities are done. Will be closed once Vertiv have completed the tasks. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627482&prj=644&rqi=xmEK3jH0PdHLaoUWnX7Je8xivk
GI-067 | dddea6e5-2ff6-4231-a71a-5ed5f9cb86eb | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-06-25 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [7 empty] | No visibility of the Earth bonding as this is in underfloor containment. BVPI cannot validate the underfloor containment bonding, test results of bonding and earthing to be reviewed for site / area / sub area. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627029&prj=644&rqi=cQHVlBiY0HI65bghLRoaB3eqj9
GI-059 | f3d438df-d0c1-4a35-a0c2-27bbda60cf87 | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-06-17 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [7 empty] | AOB-E-SY5-4 (A2-MVTB TEMP POWER APPROVAL) Loop & Good Testing Outstanding. Hi @Satheesh Kumar Natarajan, To allow Cx activities to proceed and keep the program moving are you happy to authorise the temporary supply works on A2-MVTB for testing tomorrow morning? This was the first room where we walked earlier today. o Remaining L2 testing (except Loop), see attached, have been completed & witnessed today by BVMC (awaiting documentation upload to FG) ï‚§ Loop Feeder Testing (##Push issue to be raised to track this 29.06) Team, Moving forward, the first priority and aim is to have tags signed off and in place first, as this is what firstly enables permanent / temp energisation, if this not achievable and as per the MVTB scenario can you please ensure the Cx team are aware and present in the room to ensure the correct chain of approval is being followed to allow an issue to be raised for tracking and to ensure this is pre-approved. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625770&prj=644&rqi=javSI3wAZhUGhQGo1IUoYImA1R
GI-058 | 6eb4cbe1-459a-4745-96bb-8df63d0ffe41 | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-06-16 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | AOB-E-SY5-4 (A09 & A10 TRX NAME / SERIAL / RATING PLATE) Physical rating plate visibility/access may be limited, or details have not been captured during installation/inspection. Transformer nameplate information (TRX ID, serial number, rating plate details) not installed on the newly delivered assets. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625557&prj=644&rqi=gztTgyJ5qXgQKoxCHlTAeznpAf
GI-056 | 1c72cdf1-341c-42fe-914b-1d5958034663 | SY05-4 | 644 | APAC | Closed | P3 Low CX | thomas.mcdonagh@bureauveritas.com | 2026-06-14 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [7 empty] | TMD-M-SY5-4 (Ceiling Tiles not modified for CRAH Units) Modification of ceiling tiles above the new 14 CRAH units (7 in COLO1 & 7 in COLO 2) have yet to be completed. L2 Tagging has been pushed back due to incompletion of construction works. Please provide evidence of completion of works. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625255&prj=644&rqi=Ch0APfNJ5vVrx9K6ytTPJMPhO7
GI-054 | 5dab80e3-c21e-4a12-bb23-406da3728ae6 | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | General Design Issue | Design | [7 empty] | AOB-E-SY5-4 STS Panel Openings â€“ Foreign Object & Live Risk This design has been used around the site in all previous phases, Vertiv to comment and acknowledge the risk The Static Transfer Switch (STS) panel has open penetrations on the top of the enclosure (roof). These openings present a risk of foreign objects (e.g., nuts, bolts, tools, debris) falling directly onto internal live electrical components. Operation in bypass mode, where the system is configured to allow maintenance. In this condition, the top (isolated) section of the panel is de-energised, however the bottom section remains live with no physical separation or internal barriers. This creates a risk where tools, fixings, or debris can fall through the top openings and come into contact with energised components below during maintenance activities. During maintenance temp separation will be required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623850&prj=644&rqi=ruIEQkDkqxpDxAp0cAqbVrYATj
GI-055 | eac9d8de-ef37-4284-89fb-40e260a5999e | SY05-4 | 644 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | **QC**AOB-E-SY5-4 (M5 & M6-02A ROOMS EXTERNAL LABELING) External Room labeling currently shows storeroom, this needs to be labeled prior to energisation of any power within this room., this clearly identifies the room in the event of a fault or safety issue. Supporting photo to be uploaded. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623853&prj=644&rqi=1r0Uez9MkCS4CVRWikOWsUvJLU
GI-052 | 287e0f36-1515-4f10-9cd5-805978055376 | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-05-25 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [7 empty] | AOB-E-SY5-4 (A2 STS L1/L2 Documents) â€¢ Equinix â€“ SY05 Phase 4 â€“ STS â€“ GA Drawing â€¢ Equinix â€“ SY05 Phase 4 â€“ STS â€“ Product Description â€¢ Equinix â€“ SY05 Phase 4 â€“ STS â€“ Cross Cabinet â€“ User Manual Screenshot below showing how to upload | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623066&prj=644&rqi=SyeVT4MtLm1FJGrEERms8JBDRb
GI-053 | 6d296bc7-aca4-4a5c-9a73-c848c90dab0f | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-05-25 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [7 empty] | AOB-E-SY5-4 (A2 STS Calibration Certs) Cal certs required for the below FAT & L2 QA/QC ITP testing. 02A 02B 08A 08B Screenshots below | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623067&prj=644&rqi=hugmDKTCQQ65sus6caYALBXB1C
GI-051 | a389fba7-e940-45d8-8a69-f19d183c35aa | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-05-25 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | AOB-E-SY5-4 (A2-STS IDENTIFICATION LABEL's) - Main Label - Fed From (S1&S2) 02A 02B 08A 08B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623063&prj=644&rqi=Ecs3erlRe8e7tEIc4xv2PVkRjW
GI-050 | 51405cd5-b8f5-4001-8d14-8f10c6926861 | SY05-4 | 644 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-04-29 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | **QC**-AOB-E-SY5-4 COLO13 PDU FED From labeling to be addressed and made site location applicable | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619986&prj=644&rqi=gUDwdJEeXrBwpFruziLOK5DSCt
GI-049 | 3a5684f2-eb4a-496d-9a5f-00573f4a33af | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-04-21 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [7 empty] | AOB-E-SY5-4 (A11 to A12 MVTB VLF CONSTRAINTS) The EC has flagged the risk that the â€œloopâ€ line from A11 to A12 MVTB cannot be re-VLF tested at 80% due to the . Since the cable has been cut and terminated loop in/out of MVTB-A12. Missing the VLF testing provides the risk to verify that the cable will withstand normal operating voltage, will the splice hold up. As of 21.04.2026 BVPI had been informed megger testing can still be performed with the removal of VTs/CTs within A11-MVTB which will prevent the risk of trips. Please provide Comments of next steps to move forward. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618935&prj=644&rqi=ciN0q4dgZ9ww06JVOjsCf7LqZ4
GI-047 | 5a47da74-1987-4289-b05e-a0b7e62f4e6c | SY05-4 | 644 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-04-20 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | **QC**-AOB-E-SY5-4 (A1 & A2 UDB LABELING) Updated Labeling to be printed and applied against the below assets. A1-UDB-02A A1-UDB-02B A2-UDB-02A A2-UDB-02B A2-UDB-08A A2-UDB-08B | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618805&prj=644&rqi=xSAaS7y4vtpTmLKarZGFNZ9brE
GI-046 | b1465ff8-8181-4777-a923-72f63295bc4e | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-04-20 04:00:00.000 +0400 | General Contractor |  | DCOS Graphics Issue | DCOS | [7 empty] | AOB-E-SY5-4 (UPS DCOS POINT ERROR BCB) Screenshots and photos to be provided to close out this issue Testing Battery Breaker Open, graphic shows Output Breaker Open getting Output breaker Open and should be Battery breaker Open check Alarm - need to be checked again when testing load we need Output breaker Open alarm active to compare Modbus register This point is reversed on the Modbus register Testing Output Breaker Open , graphic shows Battery Breaker Open, getting Output breaker Open and should be Battery breaker Open check Alarm - need to be checked again when testing load we need Output breaker Open alarm active to compare Modbus register | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618796&prj=644&rqi=nlwhJ6YbygoMyb06KcH3mDloxZ
GI-038 | 46a5410f-7b10-4fa8-bd2c-d0b14059b7e0 | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-04-07 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [7 empty] | AOB-E-SY5-4 (A12-TRX - Documentation Outstanding) Factory Reports - Hitachi to provide Delivary dockets - Hitachi to provide As-Builts (attach as a bulk item to all TRX assets) - Hitachi to provide A12 Equipment layout - WIP - I need to investigate to confirm the status of these submissions. Documents attached to MVTB FIC002 Control Cabling - Uploaded 7/4 FIC012 HV Comms cabling - Uploaded 7/4 FIC-003-Earth Grid-HV- Uploaded 7/4 FIC016 HV Cable Test Cx Reports - Uploaded 7/4 FIC037 : Attached to documents but not visible on the asset (if these can be attached to the asset please) - I need some assistance with linking the documents FIC016 : Attached to documents but not visible on the asset (if these can be attached to the asset please) - I need some assistance with linking the documents | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617466&prj=644&rqi=QFLuY2CSF0ykzha4wALJZu46i5
GI-030 | bc105253-14fe-4d8b-a8ce-89931e4d37e6 | SY05-4 | 644 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-25 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [7 empty] | **QC**-AOB-E-SY5-4 (SCADA / GSB / HSB / ELEC ROOMS SLD) Single Line Diagrams (SLDs) for SCADA, GSB, HSB, and ELEC rooms are outdated and do not reflect recently installed equipment on the SLD. Updated to cover site wide once IFC drawings are approved, Red lines to be completed in the interim . Current diagrams lack new assets, updated electrical connections, circuit configurations. This impacts maintenance procedures, emergency response accuracy, compliance records, and personnel safety. Updated SLDs are required to align with current installations and ensure accurate reference. All HSB / GSB / SCADA ROOMS AND ELEC Rooms to be updated as required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616448&prj=644&rqi=DYJHzpKl4QHPRVSSPut5tYf4sm
GI-032 | b0a4aacf-475e-48f3-8b54-110fdfe25a8e | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-25 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | ##SY5-HSB & GSB No Asset Identification Labels on new incomer / outgoing GSB and HSB for the new assets installed across the site issue applicable to SY5 site wide | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616469&prj=644&rqi=GCNoi5XRtaRKDZoTnIUZlcBh8U
GI-031 | b4afc8e7-d6e0-4a1f-a9b1-a9876511a3e9 | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-25 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [7 empty] | AOB-E-SY5-4 (A12 -MVTB LOOP CONNECTION) connection & testing outstanding Raising push issue to allow Red & Yellow Tags to be installed This issue will track the full Cx process and testing of the outstanding MVTB works, pending CR date of 20th April | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616468&prj=644&rqi=1CTjcosyX7W3Ez2KTJFq0nDSyz
GI-027 | 091802f7-3ff9-4fa6-8dbf-678c9a003852 | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning | Commissioning | [7 empty] | SY5-4 GEN17 & 18 Load Testing @ 1.0 PF SY5-4 - Cummins Generator Power Factor Requirements Hi YK Aaron has just been asking me last week about the power factor requirements for the GENs at SY5-4, I know the site based load bank which is unity has been agreed upon but I can't find the correspondence, Are you able to share please? We're now hyper aware of ensuring we have a track of all agreed deviations from the playbook Thanks very much Matthew KERRIGAN Program Manager Wed 18-Mar-26 11:44 AM Hi Matt, We have a FoK 4hrs load test in Sydney factory due to new enclosure manufacturer.. it will be 0.8pf load bank test.. As onsite, we only have 1pf load bank and many onsite units have been done with 0.8pf, thus, we will proceed with using onsite 1pf load bank for site testing.. Cheers Y.K Choong Senior Commissioning Manager More secure, more connected, more sustainable. Learn more about Equinix Australia. EQUINIX PROFESSIONAL SERVICES, DATA CENTER ¦ 578 Lorimer Street, Port Melbourne, VIC 3207, Australia E ychoong@ap.equinix.com ¦ M +61418 614 393 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615925&prj=644&rqi=eIHWijxg55m4rvxBDOuNzDzNX1
GI-028 | b0a78ed2-9003-4dcd-ba2a-ede1def46a78 | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [7 empty] | SY5-4 PDU AS-BUILT Drawings CB reflect 32A EQX & Grog the costumer has upgraded the brakers to 63A for customer requirements | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615950&prj=644&rqi=mplZxwtAEA2iIevfQgFQf8XWAR
GI-024 | 7a375705-df05-4ba7-ba90-72aff5574f12 | SY05-4 | 644 | APAC | Closed | P3 Low CX | jade.pries@bureauveritas.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Cleaning | Commissioning | [7 empty] | All CRAH units to be properly cleaned on dust and debris prior to energising units. Dust, insulation and footprints present in unit internal chambers and trays. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615761&prj=644&rqi=kzINGqDC576eKFqN0XLvC2e7VJ
GI-025 | 5b20b16c-3ad7-4ad6-831c-df4990c652e2 | SY05-4 | 644 | APAC | Closed | P3 Low CX | jade.pries@bureauveritas.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Torque required | Commissioning | [7 empty] | Earth terminals to be torqued and marked in all CRAH units. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615766&prj=644&rqi=GQOTjzMUSjEkFVZFzg594UQw1y
GI-026 | d5e540c1-684d-48c3-bc42-56ce3a90a7ca | SY05-4 | 644 | APAC | Closed | P3 Low CX | jade.pries@bureauveritas.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Installation not complete | Commissioning | [7 empty] | Tiles require cutting so that return air path is clear and free of restriction. All CRAHs to be checked. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615770&prj=644&rqi=eMlXyHFysksuZ4qnv6HB0Tjlyn
GI-023 | 83c680e7-3487-4c22-82df-e6b4d8b44658 | SY05-4 | 644 | APAC | Closed | P3 Low CX | jade.pries@bureauveritas.com | 2026-03-16 04:00:00.000 +0400 | General Contractor |  | Installation Damage | Commissioning | [7 empty] | Damage found on CRAH unit locks and scratches found to front covers. CRAH units 29 and 30 - Have damaged locks CRAH unit 34 - Scratch to front panel | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615756&prj=644&rqi=J5Zly3i5isj2Kd1LPI7yg8J4QW
GI-022 | c0d9c574-161f-46e6-bdb6-2ae7da6c5ad6 | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-15 04:00:00.000 +0400 | General Contractor |  | Commissioning | Commissioning | [7 empty] | ## #STW-MOP-020 - MDB to EMDB Cutover (COLO14 M5-EMDB) Raising push issue to track the energisation of M5-EMDB-01 with SUB circuits outstanding which fall under MOP-020 M6 EMDB Central Feeds Terminated & Energised > Board will then be de-energised and made safe to install CRAH circuits in COLO14. Panel chart/schedule for CBs to be updated once all sub-circuits are installed This push issue will allow L2A & L2B Tags for initial energisation to test submains before MOP works. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615686&prj=644&rqi=ysFu6VWV5lMMh25aL49v7eJWWJ
GI-015 | db5b9e25-d42b-4fd3-b4ff-c511e8c0011c | SY05-4 | 644 | APAC | Open | P3 Low DCOS | aaron.obrien@bureauveritas.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | **QC**AOB-E-SY5-4 (A12-PDU LABELING) No Asset Identification Labels on PDU's - Issue applicable to all Colo 14 PDU's. PDUs have no fed from or permanent assets tags leaving it unclear to the user if an urgent isolation is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615151&prj=644&rqi=0gZGSvgEtID2bCViGSzUvWWebA
GI-016 | bdcd85de-8516-4612-9687-8469241dda3a | SY05-4 | 644 | APAC | Open | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-09 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | **QC**-AOB-E-SY5-4 (A12-UDB LABELING) No Asset Identification Labels on PDU's - Issue applicable to all Colo 14 PDU's. PDUs have no fed from or permanent assets tags leaving it unclear to the user if an urgent isolation is required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615153&prj=644&rqi=3kvyCaT3pO90Sz7G36yE1hxEwg
GI-013 | f2675a89-c35c-4988-97ef-ff4a22f6f2f9 | SY05-4 | 644 | APAC | Closed | P3 Low CX | luke.kerin@bureauveritas.com | 2026-03-02 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | GSB-12 Panel 03 & 04 Permanent feeder labels not affixed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483493&prj=644&rqi=GDsEAkbNpib5aZ6H5omtEpd2yl
GI-002 | cf3f936c-c051-43e2-8e1a-7451abdbddf2 | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-01-06 04:00:00.000 +0400 | General Contractor |  | Documentation not issued/ Required | Commissioning | [7 empty] | SLD (Panel Drawings) RED MARK terminal numbering to be updated on all pages to reflect relay terminal numbering on A11 MVTB Schneider team working on this internally | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196409&prj=644&rqi=wTrJfJFYLJma36W5j2XYWMKFX2
GI-001 | 0f8f5b1c-7e4e-4126-91d9-d81b71be2f36 | SY05-4 | 644 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-01-06 04:00:00.000 +0400 | General Contractor |  | Component/Equipment Failure | Commissioning | [7 empty] | A11 MVTB Relay K06 (Contact Sticking) Latching Cubicle 103 Schneider HV have replaced this K06 contactor and re-tested the new relay. Tracking purpose as a component has been changed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196407&prj=644&rqi=NVB458jkxwlHxSD8dD9glsrOU0
GI-043 | 82b15292-7abb-4ebd-acf4-b4e605e8b35a | SY09x-2 | 528 | APAC | Closed | P3 Low CX | aaron.obrien@bureauveritas.com | 2026-03-18 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | Error | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615923&prj=528&rqi=CYpTzyXnx3HXm2frRZMFVespVK
FPT-269-001 | 3d08e1b5-7bc3-4a0b-b677-3ad0a8291d7c | SY09x-2 | 528 | APAC | Closed | P1 High CX | matthew.kerrigan@bureauveritas.com | 2026-02-10 04:00:00.000 +0400 | General Contractor | L4 | Installation Not Correct | Commissioning |  |  | equipment type |  |  |  |  | This issue is being raised due to directed works from Equinix to Hanley not yet being performed. Earlier in the project there was a clarification required from Equinix regarding the control wiring of the PQAs in all MSBs across site. This is related to the alarms through the PM8000s where the power meter is used as a gateway to the DCOS Equinix provided clarification and direction to modify wiring. Due to this and the relative simplicity to resolve an issue was not raised however now BVPI has no choice as they are not completed and will delay project progression to L5 Issue is related to L4 activities. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198822&prj=528&rqi=EeB1HFTUow0svJqQaOy1A95b2s
GI-025 | 35c1078a-8ea4-4ffc-89fd-223fd8c1410a | SY09x-2 | 528 | APAC | Closed | P3 Low DCOS | sulaiman.khan@bureauveritas.com | 2026-01-28 04:00:00.000 +0400 | Equinix Design Engineer |  | Commissioning Issue | Commissioning | [7 empty] | CHWP-M4 - FT04 has no value mapped to it in DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197697&prj=528&rqi=vPmjH7JfjPhT6Ne71CroKJMgMi
GI-239 | 6f0287c3-5cfd-49dc-bfbf-1c99c2006249 | SY09x-2 132kV Substation | 562 | APAC | Open | P2 Medium CX | CiaranConlon@commtechasia.com | 2026-09-01 04:00:00.000 +0400 | General Contractor |  | Component/Equipment Failure | Commissioning | [7 empty] | UPS inside comms panel 2-HMTX-2-CP is alarming and needs to be investigated and possibly replaced by Ausconnex. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636231&prj=562&rqi=6p4UWTOP3eiojEPQfbYE6pXQEO
GI-236 | fa3888ff-3f99-411d-a6e5-782bffa17aae | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL3 - HMTX TMR/AVR - PT100 Device displays ER2 (Sensor interrupt) error message across all transformers | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625574&prj=562&rqi=7Y9QoNWXesaRyyPRFrOxUh7nPq
GI-233 | e304ee82-cc81-4e45-873f-823478ef6e1e | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-06-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL3 - 7UT85 Relays - Slight discrepancy seen in settings installed against IFC Grading Study. Settings to be confirmed. See screenshot for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625568&prj=562&rqi=VY9JJzgmdnKXEdK8toKPnKHXr3
GI-232 | 9850f57e-cd21-4f89-b10c-5411ecc4fe21 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-06-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2B - 132kV Cabling - Plus ES Calibration Certs to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625244&prj=562&rqi=IXSTMsonfspDLKZzSCpFrvNPgk
GI-230 | 8c81b39a-2a03-4bb1-9a4f-17888355f27b | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY10 Switchroom & Controlroom - Filters to be installed within vents at access doorways to Switchrooms and Controlrooms. See photo for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623737&prj=562&rqi=TAsH3EIHbp32jQkRve8w8fflNK
GI-229 | 2a77ea92-ec74-417a-835b-6c5265f79eaf | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY9 Switchroom & Controlroom - Filters to be installed within vents at access doorways to Switchrooms and Controlrooms. See photo for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623736&prj=562&rqi=dRvzuXGAdYWLX1s3y8Homz0LKQ
GI-225 | 9a23d533-3170-42d5-abb9-fad2e514bd13 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL3 - SY9 Switchrooms - FCU Labelling incorrect / cable supplies installed in incorrect orientation. When isolating specific FCU in switchroom the alternate FCU is isolated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622757&prj=562&rqi=LpoBWHuQAh27N2w2OfgR4ga98R
GI-226 | e936d8f7-f10d-48d7-b3b7-ba91d7b1065b | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-22 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL3 - SY10 Switchrooms - FCU Labelling incorrect / cable supplies installed in incorrect orientation. When isolating specific FCU in switchroom the alternate FCU is isolated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622758&prj=562&rqi=XEQLiGvKDJ59NRU0V51jf0q1cR
GI-223 | 7e645e9e-acb7-4e30-a185-fb937527f981 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL3 - 1-HMTX-1-PP & 1-HMTX-2-PP - Transformer Protection Relay No.2 has intermittent comms losses to DCOS. Causing repeated comms alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621542&prj=562&rqi=YUNwhLMr87ehLunQ96g6rLB3U4
GI-222 | 04777476-d1f3-439a-b719-8c34f9eb3e4f | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | Electrical â€“ LV | equipment | 1-MDSB-1 | MDSB - Mech Distribution Switchboard |  |  | CxL2A - 1-MDSB-1 - Exhaust Fan Label shows incorrect On/Off position. Label shows EF On when it is Off. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621532&prj=562&rqi=X5wKUHqALfdP9SB6QIdQAfIwUN
GI-224 | 942e5590-5cc4-48df-8708-6cbf9afdc3a5 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-13 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL3 - 2-HMTX-1-PP & 2-HMTX-2-PP - Transformer Protection Relay No.2 has intermittent comms losses to DCOS. Causing repeated comms alarms. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=621543&prj=562&rqi=xZcX6aQBqrLnzmrtp1gx82O2Ry
GI-220 | 493f655e-9f9b-4227-93c4-f5bcd18a8a65 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY10 - Sealing of the floor tiles at door entry of the control / switchrooms yet to be completed (GHD Issue) See photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620888&prj=562&rqi=J1rJjOBGeTyUgtWKBMCSb4N0i2
GI-215 | f6d0f59d-3329-4044-af9c-83108b24515f | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY9 - Excess lengths of earth connection bolts in control room yet to be cut off (GHD Issue) See photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620883&prj=562&rqi=JazNitSKNgC7x6f86VtbjG5Ms7
GI-218 | 0abc6d3c-6e38-4edb-8d44-017e98c32f3b | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY10 - General cleaning required in transformer bund area. Dirt & Debris to be cleared, Rope in cable ducts o be cut back. Stains on the floors of transformer bunds yet to be removed (GHD Issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620886&prj=562&rqi=SXpYslIlQVFcdoNQOd0v9MP29F
GI-209 | 77139dfb-bce3-4e1d-abfb-6a331b1732ad | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY9 132kV Cable screens - Cabling currently secured to supporting structure using plastic cable ties. Correct means of securing cables to be confirmed and updated if required. Potential requirement for cleats or stainless steel. See photos for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620862&prj=562&rqi=8MNJjEXYdF6TFHgqyWDriU2WRj
GI-208 | 8bccedd4-90d2-48a7-972e-887b246edcfc | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY10 132kV Cabling Link Box - Links removed for purposes of testing to be reconnected, torqued and marked on completion of CxL2B testing. Some dust found in link box. Link box to be cleaned. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620860&prj=562&rqi=doFpe2lCfXjYDdhARcYXK1p60B
GI-213 | b5729aab-c09b-4e89-a05e-86a49a842ace | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY9 - Arc flash labels to be installed as mentioned in SYSS1-1-RPT-EL-691.3S Arc Flash Study Report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620880&prj=562&rqi=are4q2HeW6TzMNJ5CDvp9PdoiJ
GI-206 | c7bd0bb5-8909-44d2-affc-50b4938bc018 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | Electrical â€“ MV | equipment | 2-HMTX-1-K2 | HVCABLE - Aerial Flexible Conductor |  |  | CxL2B - 2-HMTX-1-K2 - Ductor Test results missing for C Phase PG Clamp. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620851&prj=562&rqi=3y2NDKyL5aoubwJBcWXpPqmNW8
GI-219 | 5b031666-7978-41c2-bc87-61655be93a64 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY9 - Sealing of the floor tiles at door entry of the control / switchrooms yet to be completed (GHD Issue) See photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620887&prj=562&rqi=WOPQ0iMerXTdhx7gXfUNcOC12o
GI-212 | e8fb7b58-da68-4a5e-9c1e-b5f3faa50495 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY10 Cable Pits - Cable Pits to be sealed against rainwater accumulation (GHD Issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620879&prj=562&rqi=lkpJ0JFt7ik8wmGGB6d9ZUCctz
GI-217 | 94bdfcfe-c669-4b5b-a9b0-31ff4690b65d | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY9 - General cleaning required in transformer bund area. Dirt & Debris to be cleared, Rope in cable ducts o be cut back. Stains on the floors of transformer bunds yet to be removed (GHD Issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620885&prj=562&rqi=NsDsCROfAI49B185kIUCHk9siW
GI-211 | 9f5b97f2-19b1-4a5c-9202-9d3c08bcc426 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY9 Cable Pits - Cable Pits to be sealed against rainwater accumulation (GHD Issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620878&prj=562&rqi=ePJyzxrBXb9LM6s1C2iIHwfLV9
GI-216 | 00e61067-ef52-4d34-a983-95859f9798db | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY10 - Excess lengths of earth connection bolts in control room yet to be cut off (GHD Issue) See photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620884&prj=562&rqi=VIwPxJ8t6pfWsUg3XBvdUwiKsW
GI-210 | 230a5874-c09f-4faa-9187-14c7d86be949 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY10 132kV Cable screens - Cabling currently secured to supporting structure using plastic cable ties. Correct means of securing cables to be confirmed and updated if required. Potential requirement for cleats or stainless steel. See photos for reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620863&prj=562&rqi=Jsi6Jrbx0wfg0BmsNE19rdqY5A
GI-207 | c1066c60-1928-44b3-a78b-7be5d29885e1 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY9 132kV Cabling Link Box - Links removed for purposes of testing to be reconnected, torqued and marked on completion of CxL2B testing. Some dust found in link box. Link box to be cleaned. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620859&prj=562&rqi=a1DOY5k0NPlgz4xlsuDPFhAUyd
GI-221 | b0289d4f-c7d7-4fac-a353-e267887b2f16 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY9B - Earth connection cable within the SY9B transformer bund to be securely clamped to the bund wall (GHD Issue) See photo for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620889&prj=562&rqi=fkMh2dijnsBszuGuekneGoCZAp
GI-214 | 875f75a1-40d4-4bbe-abaa-78da1b2a3658 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY10 - Arc flash labels to be installed as mentioned in SYSS1-1-RPT-EL-691.3S Arc Flash Study Report | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620881&prj=562&rqi=zNaQ17ak4su8acauYOtpEeL5S8
GI-201 | 37ac7a13-0baf-47eb-ab0d-501a233f3ea3 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A & CxL2B - 2-MLTX-1 - Report to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620465&prj=562&rqi=02BAAlZIhwvMScg0p1loPIiO9j
GI-203 | 6cfe3513-cea5-417f-84b9-3d24b30b6078 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2B - 1-MLTX-1 & 1-MLTX-2 - Tap to be adjusted to tap 5. Power Transformer output voltage set to 10.5kV. Auxiliary transformers tap settings to be updated to allow for lower supply voltage | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620470&prj=562&rqi=HE9kBt5ovfnk9AyBfxKAcsvxna
GI-205 | 173649f0-b213-403a-918e-39fb49c5d491 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 2-MLTX-1 & 2-MLTX-2 - Various terminations require torque marking. Surge arrestor termination to chassis, Bonding within CT wiring enclosure (at earth bar and to chassis) and bonding within LV compartment. See photos for further reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620477&prj=562&rqi=9ayqtllUKj8iF8bpa7KnPH6DOK
GI-204 | c09281af-3ff5-49db-8b66-b56620292264 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-05-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 1-MLTX-1 & 1-MLTX-2 - Various terminations require torque marking. Surge arrestor termination to chassis, Bonding within CT wiring enclosure (at earth bar and to chassis) and bonding within LV compartment. See photos for further reference. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=620475&prj=562&rqi=WgL1flXC2LGZK1vtNuR0yIkTGx
GI-200 | fa51316d-00b1-41bf-b64d-983943cb93b5 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY9 Earthing - Earthing to be torqued and marked at all earth bars and cable connections (Switchrooms and Transformer pit) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618953&prj=562&rqi=J1wwFAfvWuZEfH2QlZUEeljoGH
GI-191 | 76209a92-5d4c-404e-b8b5-e69300892bbd | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | Fire Detection | equipment | 2-FIP-1 | FP - Fire Panel |  |  | CxL2A - 2-FIP-1 - Unable to access panel. Key sheared off inside lock. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618474&prj=562&rqi=m6MFTV62rHIv9vvIAdHgB8qDpb
GI-180 | 58703582-22e9-428f-a443-2eaf582f3fa1 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY10B Permanent Labelling to be updated for all equipment and cabling. Includes Equipment, HV Cabling, Submains, Subcircuits and Earthing. Note: In addition to the above SUSP, SEP to be updated. Phase indication for Disco. HV Cabling, Earth Cabling and Subcircuits missing labels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618463&prj=562&rqi=OFXNCw9YalCIKOdR4S7SDoGEVS
GI-182 | 2d34d680-5a01-4f99-85ff-b4be3f0a8ba6 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - 1-SUSP-1 & 1-SUSP-2 - MIMIC Labelling to be updated. Panel 1 Incomer currently shows incoming cable as a feeder. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618465&prj=562&rqi=BcTBV8NxBQk9ZLR8CtMSkxudlw
GI-186 | b825fcb2-dff3-4fa4-a663-1809408c5336 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | Electrical â€“ LV | equipment | 2-DB-1 | ACDB - AC Distribution Board |  |  | CxL2B - 2-DB-1 - Report missing cable test reports. Report to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618469&prj=562&rqi=Os2z6yWNefPNCstPCdwbsX0ktb
GI-192 | f18cd3f4-b1cb-4d87-8dfb-c2b7f440f12d | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | Fire Detection | equipment | 2-FIP-2 | FP - Fire Panel |  |  | CxL2A - 2-FIP-1 & 2-FIP-2 - Cleaning required within panel. Dust and debris present to be removed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618475&prj=562&rqi=GAJ2sLfmQXmZlVc6Vsb6uS4eux
GI-198 | ca9f2db6-b14e-4faf-a63a-f91fd8463da4 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 2-HMTX-1 & 2-HMTX-2 - Cable end box works to be completed. Silicone sealing between gland plates to be installed. Bonding between gland plates to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618486&prj=562&rqi=CxcGYSidf59eVocGFERChEuUFc
GI-193 | e489ab75-d7de-4cfe-8b40-9874110474eb | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | Fire Detection | equipment | 2-FIP-2 | FP - Fire Panel |  |  | CxL2A - 2-FIP-1 & 2-FIP-2 - Earthing requires torque marks | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618476&prj=562&rqi=p4nrwmNxN7rJYSHyFeax2jBmxk
GI-187 | 4ac65141-f3d9-4022-923f-2b1628539b62 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | Electrical â€“ LV | equipment | 2-BTU-1 | DCDB - DC Distribution Board |  |  | CxL2B - 2-BTU-1 - Report missing cable test reports. Report to be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618470&prj=562&rqi=roh1AnEDiRdQHHqvKUh7TwSgJf
GI-179 | d09391ca-0f67-42e5-a734-01bea78500b7 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY10A Permanent Labelling to be updated for all equipment and cabling. Includes Equipment, HV Cabling, Submains, Subcircuits and Earthing. Note: In addition to the above SUSP, SEP to be updated. Phase indication for Disco. HV Cabling, Earth Cabling and Subcircuits missing labels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618462&prj=562&rqi=k2kYSCfyYWtvVR2RAFez4Jh9Fz
GI-197 | f993e98a-696c-4153-8a62-1d92ba44b717 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 1-HMTX-1 & 1-HMTX-2 - Cable end box works to be completed. Silicone sealing between gland plates to be installed. Bonding between gland plates to be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618485&prj=562&rqi=5WhqlJ8f7OrEBnnAx4MZilvXwV
GI-183 | 90cda7db-2707-4f9a-bd48-bcef51a86bf7 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 2-SUSP-1 & 2-SUSP-2 - MIMIC Labelling to be updated. Panel 1 Incomer currently shows incoming cable as a feeder. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618466&prj=562&rqi=bFOPy2qcMilt2BMA1NSizV0HmQ
GI-196 | 2ee04f5e-777e-400a-904d-5a412548da8b | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | Electrical â€“ LV | equipment | 2-DB-1 | ACDB - AC Distribution Board |  |  | CxL2A - 2-DB-1 - Middle cover to be installed and door bonding terminated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618484&prj=562&rqi=3DUP8IOdMQMNmThRExJgGiWBLB
GI-181 | 5255b21a-8fdb-4411-9263-df18153eb85f | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 2-SUSP-1 & 2-SUSP-2 - Thermostats to be set up | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618464&prj=562&rqi=uV8v4ORUiCTTUDBMF4eqEHcjwg
GI-178 | 76ee487f-1bac-43f1-a806-ee293d299a68 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-08 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL3 - 1-DB-3 & 1-DB-4 - Metering not reading current only voltage. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617474&prj=562&rqi=qAIHzdl5sN7dQFwOPUY5qaoj9h
GI-177 | 0ce295a5-d971-439d-bf61-78d050e9d904 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-04-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL3 - 1-HMTX-1 & 1-HMTX-2 - TMR/AVR Various Equipment Rating settings incorrect. Time Not set correctly. Time Sync non functioning correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=617464&prj=562&rqi=et9cxo0Bx3POkFvh8dkCloaR1n
GI-172 | 9cdd2313-9d18-4c95-9079-82f508ff21d8 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-20 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | Communications | equipment | 2-HMTX-2-NP | HMI - HMI Panel (Network Panel) |  |  | CxL2B - 2-HMTX-2-NP - Missing Network cabling test results in report. Updated report to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616051&prj=562&rqi=8p91nlWBTltsw0nXXJs0NL6Wm4
GI-173 | 18f846f6-3df9-469f-86de-58621ddd3c09 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-20 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY9 Substations - WIFI Router to be affixed to agreed location | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616053&prj=562&rqi=K0m9Kndn4eRqwZ6aWYP7v4Vyx4
GI-175 | 62e9c3c3-a4ee-462e-99ef-4292eee1b29e | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL3 - 1-HMTX-1 & 1-HMTX-2 - TMR/AVR Cx Reports incomplete, missing various info and attachments. To be updated | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616055&prj=562&rqi=Zvp2eDQj7y8P9BRE2WPBlcNI6Z
GI-160 | 2fb58d1d-e031-4f93-ac65-9306681dda1c | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL3 - 1-HMTX-1 & 1-HMTX-2 - TMR/AVR DCOS Points not mapped correctly | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615913&prj=562&rqi=DplLw5ejyL8282sfFPMvoxa9gD
GI-168 | 4ec88695-1f57-46d6-8a8f-b85959d3b147 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 2-HMTX-1 & 2-HMTX-2 - Neutral Earthing to be completed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615921&prj=562&rqi=QwLTBPJozGBJ1qkqie0XjwCl9W
GI-164 | 40fea47d-9adf-40e4-8374-cbf5582549cf | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 2-MLTX-1 & 2-MLTX-2 - Extra External Protection needed for 11kV Cables (UV/Water/Mechanical). Cover to be installed over cables to provide extra protection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615917&prj=562&rqi=MJsEMMF2zFhPLGIadL9jLdkvXc
GI-161 | ffac1916-499c-4bf2-9467-5bb2cdad2070 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 2-DB-3 & 2-DB-4 - Labelling to be updated. Labelling associated with DB still shows previous naming convention. All small wiring labelling internal to DB and GPO / Light Switches associated with DB to be updated. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615914&prj=562&rqi=BJAXfudE5hROYlQGP1e3kbhKmL
GI-159 | 9f2b3cdd-6494-4d5e-a9fd-59a258f0ae4b | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL3 - 1-HMTX-1 & 1-HMTX-2 - TMR/AVR LED Mapping not programmed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615912&prj=562&rqi=WkD3OMBl2Bz9ncH4aff54RauVb
GI-158 | 77c5effc-05cb-4140-bd47-944c4dc012b4 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 2-HMTX-1-NP & 2-HMTX-2-NP - UPS Cabling install incomplete | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615911&prj=562&rqi=UxGa9X5LKx8h3hV4Yb2l2vIxUZ
RT1ELEC-1-001 | 55dfc551-1f6a-4e86-b143-c8317ca45033 | SY09x-2 132kV Substation | 562 | APAC | Closed | P1 High CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ MV | equipment | 1-HMTX-1-SA3 | HVCABLE - Surge Arrestors |  |  | CxL2A - 2-HMTX-1 & 2-HMTX-2 - Earthing for surge arrestors to be installed. No bonding between arrestors and earth nest. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615916&prj=562&rqi=XUJd5ZyW56K5OwYTHQc6r1tWUv
GI-166 | 2f0fe5e8-7417-4abe-aacf-6b58542bf088 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 2-SUMP-1 & 2-SUMP-2 - Enclosure door screws not fixed. Panel door to be secured. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615919&prj=562&rqi=nPlLNUl5tkM7nbG9JM3o00VKDp
GI-167 | a7c16ed2-0394-4ac3-b1ef-733f7cb24cad | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 2-DB-1 & 2-DB-2 - Heat Shrink to be installed on bare copper at Load side of MTS to DB Section of Switchboard. Top and bottom sections. See picture for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615920&prj=562&rqi=3p69ToTWavH2Q2Kl187vNqaeEc
GI-165 | 12254374-77ab-4180-bff6-c6f548c5223c | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - SY10 Earthing - Earthing to be torqued and marked at all earth bars and cable connections (Switchrooms and Transformer pit) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615918&prj=562&rqi=rW5B3OlZBiL8jyyTBNrvf3ZaSx
GI-169 | 7bbf0b0f-f0b4-4444-af89-338b60ac7d25 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2B - 2-HMTX-1 & 2-HMTX-2 - Thermostats to be set up within switchgear. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615922&prj=562&rqi=RMxXmTARksfu9XnMXNPhty3ZT1
GI-171 | dcb42b4c-dc2f-4283-a702-104119180c21 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 2-MLTX-1 & 2-MLTX-2 - Neutral earth cable needs to be clearly identified as earth/neutral | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615929&prj=562&rqi=qKZI3c9XbzQqEsaH7vwqnzvGXM
GI-170 | 320eb3be-76ff-4fda-aeba-efa1ea57a790 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 2-HMTX-1 & 2-HMTX-2 - Dust & Debris present within LCP. Cleaning required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615927&prj=562&rqi=sIGaUfoxDeSgLp81wCCMfwq1UH
GI-162 | 2c3d9bd5-9932-4924-9829-e0c3a83c76d4 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 2-BTU-1 & 2-BTU-2 - Holes in escutcheon on DB to be sealed. 2 x large holes within escutcheon of DB cut out to allow for door to be closed, devices will prevent this presently. Some form of recessed cover to be installed in empty spots to seal up holes. Pole fillers also to be in place where missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615915&prj=562&rqi=Yu1NZ7tz45wAjljsQSCCvpUj64
GI-151 | fa5a473f-d7fd-4fef-b52e-2bd09344017e | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | Electrical â€“ LV | equipment | 2-DB-2 | ACDB - AC Distribution Board |  |  | CxL2A - 2-DB-2 - Comms Cabling not terminated. Potentially not required. If not required, it is to be removed and gland blanked off | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615776&prj=562&rqi=P6DPq2R9YOo9SrI2qnEmiAbkfH
GI-152 | 0abdbcc9-6150-47bd-a43c-f37830a4735e | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | Electrical â€“ LV | equipment | 2-DB-2 | ACDB - AC Distribution Board |  |  | CxL2A - 2-DB-2 - Pole Fillers missing. To be installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615777&prj=562&rqi=IDFsfSbtGsZglFSJfNifFHbaoQ
GI-154 | 89ce7ba1-2120-4b18-86f3-48e69888cde0 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY910B Permanent Labelling to be updated for all equipment and cabling. Includes Equipment, HV Cabling, Submains, Subcircuits and Earthing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615780&prj=562&rqi=mqvmAyqSiQhD9AyaJkBwFpIqiM
GI-150 | abc30ce5-db85-4e51-b065-324968284f25 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | Electrical â€“ LV | equipment | 2-DB-2 | ACDB - AC Distribution Board |  |  | CxL2A - 2-DB-2 - Trunking cover misssing interal to Switchboard (Left side) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615775&prj=562&rqi=nUhDjiyJxR9MzLNUEBdP2Nc1QV
GI-153 | a2930b00-be4b-46cb-982a-b6fd6be86385 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 1-DB-1 & 1-DB-2 - Heat Shrink to be installed on bare copper at Load side of MTS to DB Section of Switchboard. Top and bottom sections. See picture for reference | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615778&prj=562&rqi=LeAgzAMogGQaYseZ0MhFLcRRcg
GI-148 | d60d1035-f121-4a0e-98e3-95f813521ef9 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL3 - 1-SUMP-1 & 1-SUMP-2 - Level alarm indication on Pump controller not operating as expected | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615166&prj=562&rqi=LO12L0WfwHlfKyYhGMOiaekJgy
GI-149 | 22a2d09f-b065-4790-8ad4-89a09779912e | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-03-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 1-SUMP-1 & 1-SUMP-2 - Enclosure door screws not fixed. Panel door to be secured. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615168&prj=562&rqi=NF4aknCymS3y4UAkEESvE1jC2x
GI-147 | 3da96a5a-45a9-4b8e-9125-d98655821c79 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-24 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A & CxL2B - SY9 Overhead Conductor - Test reports to be submitted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199810&prj=562&rqi=jHQiNbISknPRbAaZfeR27mwcpZ
GI-146 | 65ddf25d-0111-4999-9685-ae1d01170ef0 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-11 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2B - 1-MLTX-1 & 1-MLTX-2 - Oil Sample / Oil Tests of transformer not completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198975&prj=562&rqi=UWt2t9XZTqiIvTF4TbNnXh3POl
GI-143 | a3152062-38b4-4a69-8e1b-547c6826dd29 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 1-MLTX-1 & 1-MLTX-2 - Extra External Protection needed for 11kV Cables (UV/Water/Mechanical). Cover to be installed over cables to provide extra protection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198823&prj=562&rqi=sWPfTKtxpTHwAmWH3JcIiPxcpB
GI-144 | 828b93c6-0c04-4fbb-a202-82d7f7653554 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 132kV Power Transformers - LCP Supplied by vendor allows for two power sources from alternate supplies (9A & 9B). Allowance made for this with both AC & DC Supplies. Currently only 1 Source has been provided to the LCP. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198829&prj=562&rqi=CxnUE7yjrdWFnkF5yhJ7m9bXJE
GI-145 | e270cf84-b819-4e44-bddb-9df7b765ae95 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-10 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - SY9 Earthing - Earthing to be torqued and marked at all earth bars and cable connections (Switchrooms and Transformer pit) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198832&prj=562&rqi=UXBTC4aTzkbKgvPevyxamlcBpo
GI-136 | 2fa404b1-3f2a-419c-a3a2-df92f3e5bf8d | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | Fire Services Installer - Calibration Certificates to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198745&prj=562&rqi=RAhki6i7B8xrV3GhlxaDm1Zvwy
GI-135 | 3fd70dfa-4a9d-411a-a53a-41a8338c5a8c | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | Fire Protection System - SOO to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198742&prj=562&rqi=J5uaQ9Le80I0JQFn3zYXFLGMuH
GI-138 | 11ab2e70-290b-4052-876c-7ac4253997eb | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 1-FIP-1 & 1-FIP-2 - Bonding to be torque marked | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198747&prj=562&rqi=6gndTvuy1NoU6YYfddpVmW7qnN
GI-141 | 0ab53c19-b274-4a0e-84af-a89f8ffe5d4e | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 2-HMTX-1 & 2-HMTX-2 - Neutral CT to be installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198751&prj=562&rqi=43medkebtYPro6mmCT9CuYrqWV
GI-142 | 406727bd-a615-4f4c-ae74-bb65a981cff8 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 1-HMTX-1 & 1-HMTX-2 - Dust & Debris present within LCP. Cleaning required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198752&prj=562&rqi=cdgJZQzGmXHKV16E3Yj3sCMAJR
GI-137 | 8f2d0a77-e5d2-428b-bfc3-17e077fc51bc | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 1-FIP-1 & 1-FIP-2 - Dust and Debris present within panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198746&prj=562&rqi=uNJYdLPnFC3WZOURjxJsU2D0BG
GI-139 | 21e95f35-b50d-49d9-959a-b116e49ad84e | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-09 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | Fire Detection | equipment | 1-FIP-1 | FP - Fire Panel |  |  | CxL2A - 1-FIP-1 - Unused gland on top of panel to be removed and blanked off if not required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198748&prj=562&rqi=i32hdnyUASWVikEfQ2zNXpKcgt
GI-134 | 3ad56c39-800e-472c-9f3a-c798083f935b | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY9A Switchroom - Cabling not secured. Phase tape used to secure earthing in cable tray. Cable to be secured with cable ties. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198664&prj=562&rqi=lbg9cceTlNS57N1DzjvWIpAC6F
GI-133 | ba7deb87-4246-4c27-a522-7580a130fd65 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY9A Switchroom - Light not securely fitted. Held up with cable ties on one side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198663&prj=562&rqi=0hQOnhUojaKc52owrPZxOmnumA
RT1ELEC-1-002 | adcbdfc5-b985-430a-a5ee-1399f28142f5 | SY09x-2 132kV Substation | 562 | APAC | Closed | P1 High CX | AmmarKhawaja@commtechasia.com | 2026-02-05 04:00:00.000 +0400 | General Contractor | L2A | Incomplete Connections | Commissioning |  | Electrical â€“ MV | equipment | 1-HMTX-1-SA3 | HVCABLE - Surge Arrestors |  |  | CxL2A - 1-HMTX-1 & 1-HMTX-2 - Earthing for surge arrestors to be installed. No bonding between arrestors and earth nest. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198570&prj=562&rqi=VIybVRDKXWDCw2RNfAcWnJJR7X
GI-129 | d043ba0e-7672-40b9-8c4c-18e443c9e492 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-02-03 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 132kV Disconnectors and Overheads - Some concern present of tension being on Disconnectors and Surge Arrestors/Bushings. Tension seems to be caused by overhead length and rotating disconnector terminal plates. Potential for damage to equipment when operating disconnectors. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198181&prj=562&rqi=dQKmwXcv4kj0eENt5iJNz8vRGR
GI-121 | 5290a115-f9ef-4e47-8926-4e355a3cfe92 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL3 - 110VDC Battery Chargers - Unable to see DCOS status for various points | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197825&prj=562&rqi=3faJTFhKlyySUZfGUA1Li8o4nn
GI-125 | d65ef6e3-60af-4156-a567-256f7c2552e2 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL3 - Sump Pump All - Unable to see change of state for various DCOS Points. Potential wiring issue | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197840&prj=562&rqi=ythUfqHUaiRTsMHtZG5h3ICzAw
GI-123 | 3cff65b4-2917-4697-8c3d-e4fb0ff26ba7 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | Electrical â€“ LV | equipment | 1-MDSB-1 | MDSB - Mech Distribution Switchboard |  |  | CxL3 - 1-EF-1 - Exhaust Fan in fault | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197827&prj=562&rqi=NciH7hkEkpQjQM5SsJCZ1u2Meh
GI-127 | 8e0a0ffd-c551-4d92-bb15-2d802247c152 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - MLTX All - Amalgamating tape to be applied at Aux Tx 11kV Cabling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197844&prj=562&rqi=pDTQiaOgo1KhLRhddbETcmaGN4
GI-122 | c7ce1ea6-9f8c-4195-ade4-64b5a0b57be4 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL3 - FCU All - Unable to see status of all FCU on DCOS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197826&prj=562&rqi=SpZKLnUMU4IrTHxilRTzZqFXZn
GI-126 | fe31a6cb-2b2f-40b7-acf5-4d50b5d846ba | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-29 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - ACDB All - Lack of clearance between Main Neutral cabling and MTS secondary outgoing contacts. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197842&prj=562&rqi=UVCwgAtN7hbqFPsen9M0sNTSyM
GI-120 | 2ae623cd-0abe-4496-9d6a-d3a7d6b4ad96 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-27 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2B - 132kV Power Transformers - Siemens Calibration Certificates to be provided | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=197632&prj=562&rqi=yiOkpolrUyIdxLAhZaXGnVSE4o
GI-117 | 8bc58f65-bb9e-4fa0-be20-f159963f6b2c | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 132kV Transformers - Interface cabling required to be installed between TMR and SUSP for voltage monitoring. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196934&prj=562&rqi=rarF1wt2jlMZY8u2V0qsrVHmM2
GI-119 | f0c59bfa-0e8a-4e48-a6bf-3c0021c87794 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - SY9 Auxiliary Transformers - 11kV Cabling earth screens to be sealed with amalgamating tape | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196939&prj=562&rqi=CI41WbNWE1GQFuOxckVl1BI7rD
GI-115 | e6af4efc-34b4-4c5d-83b5-c5abbd75d345 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | Electrical â€“ MV | equipment | 1-ERTH-1 | ERTH - Earthing |  |  | CxL2A - Earthing - SY9A & SY9B Control Room Door bonding loose | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196908&prj=562&rqi=4ZZbrr874MdqAIg8kcH4elCzip
GI-114 | 89fe1d57-23df-415a-bc50-481f70ec2418 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  | Electrical â€“ MV | equipment | 1-ERTH-1 | ERTH - Earthing |  |  | CxL2A - Earthing - 1-BTU-1 Earthing loose at earth bar | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196907&prj=562&rqi=evI21NsPqFlsbgBU2uIX2rJInE
GI-116 | abffa7ef-47a4-46e4-a453-77328d1c87ed | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-15 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - Earthing - Bonding required on various trays within SYA&B. Oil Water Separator, Linkbox & Auxiliary Transformer MV Cable support structure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196933&prj=562&rqi=UE7DVQoPeteXOZhctGAaCbEZZz
GI-111 | ac082cbb-c89c-4601-9d58-fc0ac9890778 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 1-DB-1 & 1-DB-2 - Neutral cabling resting on live outgoing terminals. Separation to be created between cabling and terminals. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196835&prj=562&rqi=CKHytzwztaJplioxVGAxXDacJs
GI-112 | dd3244ca-7b9e-4c6e-b2b9-922a3474f6a5 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | AmmarKhawaja@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 1-MLTX-1 & 1-MLTX-2 - Neutral earth cable needs to be clearly identified as earth/neutral | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196834&prj=562&rqi=D0cJrj9fA6MkoWe23k2TfvihVT
GI-110 | a7dc257e-957c-4337-a47c-3e9fe47a478c | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL3 - FCU All - No visibility of FCU's on DCOS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196833&prj=562&rqi=PTCnCLb6IdDZjBDSNoFaIPNXkr
GI-108 | 1de1adbd-63d8-482e-97be-11ba014e9943 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - SY9A Permanent Labelling to be updated for all equipment and cabling. Includes Equipment, HV Cabling, Submains, Subcircuits and Earthing Note: In addition to the above SUSP, SEP to be updated. Phase indication for Disco. HV Cabling, Earth Cabling and Subcircuits missing labels. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196832&prj=562&rqi=AXZXiGtxaSqh3yG8UxrNaUSrBi
GI-109 | 4894f9a6-62f1-4598-95dc-964f15d5448a | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | AmmarKhawaja@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - SY9 Auxiliary Transformers - Bonding required for MV Cable support structure. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196830&prj=562&rqi=qQhQSLa0L2x7xWHCY83AxOFelW
GI-107 | a1590499-31e8-474d-b487-2f4c7a5af337 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | AmmarKhawaja@commtechasia.com | 2026-01-14 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - SY9 Auxiliary transformers - Not bolted down/fixed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196829&prj=562&rqi=om5myVuG1CQbM3QvZiVOgbIPoI
GI-106 | 9a3c3272-7fdd-445b-a254-3a9b1b334006 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-08 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 132kV Power Transformers - No presence of earth cabling between LCP Earth Bars and transformer chassis. No continuity seen between various Earth Bars within LCP to Transformer chassis. Potential requirement for adding more bonding. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196541&prj=562&rqi=SgTS7i2HDw35gm0hvWvmg5RmZ3
GI-105 | b0dc3513-c2b8-46a6-b337-6521f6c09623 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-07 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - 1-SUSP-2 - A04 CB Cover damaged. To be replaced. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196405&prj=562&rqi=ZNwcUMLr7lpbTYzyD1s7tMbxPr
GI-104 | 7e9414c1-8a8c-4d1f-a316-fe21fdacc30d | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-06 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning |  |  | equipment type |  |  |  |  | CxL2A - 1-HMTX-1-K1 & 1-HMTX-2-K1 - Supports / cable cleats required to be installed for cabling. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196365&prj=562&rqi=jIeU6AVSwVu6tEUJIxYgKhf4IY
GI-103 | 9c384edb-a649-4c48-9909-a774f1ac72d8 | SY09x-2 132kV Substation | 562 | APAC | Closed | P3 Low CX | JakeWilloughby@commtechasia.com | 2026-01-05 04:00:00.000 +0400 | General Contractor |  | Commissioning Issues | Commissioning | [7 empty] | CxL2A - LPS - Lightning Mast Pending installation. Works to be completed & Test report to be submitted | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=196298&prj=562&rqi=57B173LOufJQbmezWS8OaohDcK
GI-613 | 2f07f4e5-5502-4d16-bbec-39fe84d40560 | TR06-2 | 358 | AMER | Closed | P3 Low CX | Ocean.Kwan@veolia.com | 2026-06-01 04:00:00.000 +0400 | General Contractor |  | Installation | Commissioning | [7 empty] | Main Service gear 1PUSP_1 & 2 sections are missing equipment identifiers/labels, e.g., Interrupter, Protective Relay, Power Quality Meter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623563&prj=358&rqi=QCycjjS6M6Ubr9tx1TcmCReoc7
GI-612 | 1fb6272c-a45f-4afe-bc82-a23da1048c61 | TR06-2 | 358 | AMER | Closed | P3 Low CX | Ocean.Kwan@veolia.com | 2026-06-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Manufacturing | Commissioning | [7 empty] | The posted procedures at the new MSBs is not correct. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623562&prj=358&rqi=Db50S4dBHPASpdwskvOc1ofvBz
GI-614 | 2665602a-3084-46fa-8085-313b5f9eb8ac | TR06-2 | 358 | AMER | Closed | P3 Low CX | Ocean.Kwan@veolia.com | 2026-06-01 04:00:00.000 +0400 | Vendor- Manufacturer |  | Manufacturing | Commissioning | [7 empty] | TR6-2 (Electrical Block A & R SKID): A few MSB_A breakers were mislabeled (incorrect spelling, incorrect label background color, font size), e.g., UPS_RIB_2, 1UPS-A-2-LBB, 1-CH-A-2, 1LBB_A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623564&prj=358&rqi=fCfMbZgAiQ9wEu0lZvnvBxVSkE
GI-116 | f39a549d-b308-0716-4c18-b47a6e69fe60 | TR06-3 | 657 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-09-15 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | FWT | Factory Witness Test |  |  | equipment type |  |  |  |  | AMG NETA Report - Following a preliminary review of the breaker test reports provided for TR6-3, it was noted that the primary injection test of the INS protection for the MSB circuit breakers was not included. AMG to verify with your testing team whether additional reports covering this test are available? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638208&prj=657&rqi=uj59bKNNoXuueWZeLVIX6AdSFK
GI-117 | 0864591c-e769-7a37-83d7-fca3dadba95e | TR06-3 | 657 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-09-15 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | FWT | Factory Witness Test |  |  | equipment type |  |  |  |  | AMG MSBs- While reviewing the FAT documents, it was noticed no torque reports available for the bus. Report is missing this information. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638210&prj=657&rqi=ILTeAUAXO5YJnVHvTJZHKdTr88
GI-115 | 1f86f195-44f3-405f-ea41-521abad75616 | TR06-3 | 657 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-09-15 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | FWT | Factory Witness Test |  |  | equipment type |  |  |  |  | AMG Breaker Test Reports - Upon reviewing the reports, it was identified that certain records include Ground Fault Protection test results for 400A breaker equipment fitted with the MicroLogic 5.3 trip unit. However, the MicroLogic 5.3 unit provides LSI protection only and does not include ground fault protection. AMG is to review and clarify this discrepancy. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638196&prj=657&rqi=gglXYa4vf9DnHMK3foexuUq2Hn
RT1MECH-32-001 | 34b5f1c6-dbbb-44ea-b38d-7dc941407364 | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-09-11 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_A_2 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-A-2: The fitting connecting the pump skid to the chiller evaporator is a different model number comapred to fitting seen on the remaining 6 chillers. Please refer to the attached pictures. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637815&prj=657&rqi=IGmtS2blbraGzGew4S6UrN7RK2
GI-114 | 620a70dd-ef52-4a00-b6da-deb4049efc96 | TR06-3 | 657 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-09-10 04:00:00.000 +0400 | SCH - Schneider Mech |  | Component/ Equipment Failure | Commissioning | [7 empty] | 0.75 in gap in chilled water piping connection between top and bottom mega crah | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=637701&prj=657&rqi=8VYUhBgLhWksZy68zY7ATsy7DZ
RT1MECH-87-009 | 674bcc50-4d64-4a33-89d9-a0387f2cdb80 | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-09-04 04:00:00.000 +0400 | Consultant | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Applicable to all Skid CRAHs - Secondary source fed from R Block: The max input current mentioned on the CRAH name plate is 13A, the upstream breaker for primary source of the CRAHs installed by MPS are 20 A. However referring to drawing # E715, the upstream breakers for second source on the panel schedule mentions 35 A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636925&prj=657&rqi=o6smcE890Jf8RVfnUvD8PbRQxI
GI-113 | b9fcc5da-44b7-4938-8310-538a3deb9b7b | TR06-3 | 657 | AMER | Open | P1 High CX | steve.knezevic@veolia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | Water ingress through conduit penetrations behind MSB and at middle shipping split of skid | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636751&prj=657&rqi=osFiMUR6izGlq0i6mEBUxbuj3T
RT1MECH-116-001 | 8ca8de89-ba07-4e15-a197-a897b4c350d3 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-09-03 04:00:00.000 +0400 | Consultant | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1HP_R_05 | HP - Heat Pump |  |  | Common for all MPS skid Trane WSHPs: On the water source heat pump submittal, the "Max Overload protection (A) is given as 15A. On the panel schedule for WHSP fed from R block, The upstream breakers on the panel schedule are 20 A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636780&prj=657&rqi=khFhsC3QCR0VCUS6TbFmWATeMM
GI-112 | 6a094fe6-eea9-4c5c-82e6-2d9b5d800e4a | TR06-3 | 657 | AMER | Open | P1 High CX | steve.knezevic@veolia.com | 2026-09-03 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D | MSB - Main Input Switchboard |  | no | Water ingress through conduit penetrations behind MSB | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636750&prj=657&rqi=Ihuz6c5TcfMp84VDzYbHoV2R8U
GI-108 | b804d4bd-29df-4e8f-80c8-72ebad87f4a7 | TR06-3 | 657 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UDP_C_1 | UDP - UPS Output Switchboard |  |  | UDP_C_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636558&prj=657&rqi=aAjY5dCGAwrJRJSbhIU8eqo9Wz
GI-105 | d225d82c-dd5f-4676-8cc1-adf54a61a5c0 | TR06-3 | 657 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  | no | UPS_C_1_LBB & UPS_C_2_LBB status contacts were not wired to a terminal block to be monitored by the UPS. Three spare EF contacts exist at each breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636555&prj=657&rqi=wIr9Dx113Cy3bJ999e7AvPUfKi
GI-106 | 268d650b-dbdf-4fc4-98b9-48ef3cfd1417 | TR06-3 | 657 | AMER | Open | P3 Low CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D | MSB - Main Input Switchboard |  | no | UPS_D_1_LBB & UPS_D_2_LBB status contacts were not wired to a terminal block to be monitored by the UPS. Three spare EF contacts exist at each breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636556&prj=657&rqi=901LOH6fYFyv7DVswHioBOHYjC
GI-102 | e63f730b-672a-4ed6-b87f-976f9332f396 | TR06-3 | 657 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UDPR_D_1 | UDP - UPS Output Switchboard |  |  | UDPR_D_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636547&prj=657&rqi=Yz3MR7erFtVtQfz9ApEelQEPda
GI-111 | 31cbf357-6e6a-4dfa-b4a6-961281439f88 | TR06-3 | 657 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UDPR_C_2 | UDP - UPS Output Switchboard |  |  | UDPR_C_2 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636561&prj=657&rqi=9F2RpXTqyu7zskUBHHaTJcnuZZ
GI-110 | 5620dad9-41fc-4fef-b00a-c73ae46e477a | TR06-3 | 657 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UDP_C_2 | UDP - UPS Output Switchboard |  |  | UDP_C_2 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636560&prj=657&rqi=dEz3n2TlZHRVCdPPz1zAmKdZi8
GI-107 | 1b8e983a-37c9-49fc-becb-38aee4527c34 | TR06-3 | 657 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | UPS_E_1_LBB & UPS_E_2_LBB status contacts were not wired to a terminal block to be monitored by the UPS. Three spare EF contacts exist at each breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636557&prj=657&rqi=3nroV1phZXJVc1YmdFWixql20v
GI-103 | 614e3dee-1162-4019-a4e7-b8c59a2aa786 | TR06-3 | 657 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UDP_D_1 | UDP - UPS Output Switchboard |  |  | UDP_D_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636548&prj=657&rqi=TZLUaKJ9LHbIpDv2OluId6dpD6
RT1MECH-112-001 | b2ae1aa7-9cb6-4d67-8bd7-6a2eba1cf40a | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-09-02 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1HP_B_04 | HP - Heat Pump |  |  | Common for all MPS skid Trane WSHPs: On the water source heat pump submittal, the "Max Overload protection (A) is given as 15A. The upstream breakers on the panel schedule are 20 A for the skid WSHPs. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636525&prj=657&rqi=KsAgyhxO8nuDDXLKgqS0jysypY
GI-104 | 54bcaf35-0ba6-4c79-8553-cbc1b6f312a5 | TR06-3 | 657 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UDP_D_2 | UDP - UPS Output Switchboard |  |  | UDP_D_2 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636554&prj=657&rqi=3dWcsIjka9LfyPHlRsy8GfI9IM
GI-109 | 3c85d7f6-df81-4ec0-ae01-09597ad1e2a9 | TR06-3 | 657 | AMER | Open | P3 Low CX | steve.knezevic@veolia.com | 2026-09-02 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1UDPR_C_1 | UDP - UPS Output Switchboard |  |  | UDPR_C_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636559&prj=657&rqi=VcGTZfUeOS5jVGi1PzuLlHepVN
RT1MECH-87-006 | 080b1288-d816-4678-9bc5-6e1b269ae497 | TR06-3 | 657 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | As per review of drawing M405 and on site configuration it was noted that the CRAH labeled 1CRAH_ER_11 is mislabeled as 1CRAH_ER_10. This impacts the following: -BAPI10 - incoming and outcoming EMT labels -wire labels for CB1 and CB2 and main ground. -CRAH Label itself | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636166&prj=657&rqi=KoZ3t3u5XttuwPkBMSRS0ECTl8
RT1MECH-88-002 | 6567f430-0eca-498a-b9fb-5b9f142efdfb | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | Applicable for all MPS Skid Delta CRAHs: The T Sensors in the submittal, if the intend of these is to sense the chilled water return and chilled water supply temperature, then these sensor were found not to be thermowells but to touch the copper pipes. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636083&prj=657&rqi=C1tyYbw8b3Gc181L99BGHimSHQ
RT1MECH-88-004 | eb26bceb-dcea-4591-9311-3cb786079e95 | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | For 1CRAH-ER-13: As per review of drawing M405 and on site configuration it was noted that the CRAH labeled 1CRAH_ER_13 is mislabeled as 1CRAH_ER_12. This impacts the following: -BAPI10 - incoming and outcoming EMT labels -wire labels for CB1 and CB2 and main ground. -CRAH Label itself | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636190&prj=657&rqi=Rmks9aRsNlqSIpwpvbzuwNblwQ
RT1MECH-88-005 | 07d903ab-2f23-450b-ba59-21f34fc8c776 | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | Common for all MPS Skid CRAHs: The safety labels on the CRAH electrical panels need to be in English and French for Skid ESA inspections to pass. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636208&prj=657&rqi=0RZ17MmaV2BeoJjOqzBJ6eU4tI
RT1MECH-88-006 | 652a8c2c-d9ea-41bd-9a43-3115c3564e4c | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | Common for all three CRAH units in Skid E: The panel schedule needs to be revised as per the CRAH asset names inside Skid. It was found that the CRAH names do not match as per drawing M405 (Attached) Also refer to Issue # 152, 155 and 156 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636211&prj=657&rqi=2kBsGcCzDnWzcJv3FwmYdVk1Qu
RT1MECH-88-003 | bf850eb4-75e3-4225-bfd5-e5037fa6bd79 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | Applicable to all MPS Skid CRAHs: Missing cut sheet of the T sensors on the submittal. (Attaching pictures to indicate the sensors we are referring to) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636089&prj=657&rqi=mcup1OKZ6XXIt280eOwDWF5iRv
RT1MECH-88-001 | e8f68af0-02df-4485-99b6-51f079be00f0 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_ER_13 | CRAH - Computer room air handler |  |  | Applicable to all MPS skids Delta CRAHs: The controls wiring drawing provided in the submittal is not readable, cannot be used for verification of the wiring or the controls components. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636079&prj=657&rqi=4uN147nFMHP4H5y94W50bSmqZo
RT1MECH-87-004 | bc3d5af9-3240-4a1a-89f0-dd04c3ae61c2 | TR06-3 | 657 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Terminal block labels deviate from the shop drawing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636162&prj=657&rqi=rr9eTdxvRkPMrmrTvDhhsXEHGx
RT1MECH-87-008 | a073c1ac-76a4-41b1-9082-4b42c6680fdd | TR06-3 | 657 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Cleaning | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Construction dust and FOD found inside high-voltage electrical section and on top of the unit. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636168&prj=657&rqi=495nJSmffiKChGnMkOZ01RN69x
RT1MECH-87-007 | ddc21604-5f96-4f1a-9ff8-7b90fb243ab6 | TR06-3 | 657 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Upon review of submittal OFCI-12 Section 2.1.2.2 Single Line Diagram -it was noted the following fuses have FA Fuses, which deviate from the shop drawing. F3 4Amp fuses found instead of the specified 10Amps F5 10A fuse found instead of a 3Amp fuse. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636167&prj=657&rqi=Gcpejanb7lWuFHCeXboCiCYNjY
RT1MECH-87-003 | 35872bd0-fe03-4a27-811c-b744b7e5c14d | TR06-3 | 657 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | CB1 and CB2 are loosely mounted, there is significant play in the breakers upon inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636161&prj=657&rqi=iVo6HQcHudhREQ8RFjthScaccX
RT1MECH-86-001 | 213285e8-5e42-44df-b93a-1fb02fe2ad3a | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier | L2A | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_ER_12 | CRAH - Computer room air handler |  |  | For 1CRAH_ER_12: As per review of drawing M405 and on site configuration it was noted that the CRAH labeled 1CRAH_ER_12 is mislabeled as 1CRAH_ER_11. This impacts the following: -BAPI10 - incoming and outcoming EMT labels -wire labels for CB1 and CB2 and main ground. -CRAH Label itself | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636193&prj=657&rqi=ITc1lYOYzCtG3XH8QVsYhl6A3W
GI-101 | 5b2a3c54-31fd-4256-ac7d-8c2d6d7fb075 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-08-31 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  |  | system | meWall E |  |  |  | Skid E: Rope Leak Detector: Extra Slack on the rope leak detector is not secured neatly in the skid. (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636206&prj=657&rqi=VGHHv0w1dbPn6hfN1Lx4oGnugR | https://equinix.facilitygrid.co.uk/x/project/657/system/13317
RT1MECH-87-002 | ae29bce2-a691-40d7-b025-40f0bbb66251 | TR06-3 | 657 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Installation not correct | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Ferrule connectors are exposed for terminal 1.1, 1.2, 2.1, 2.2 on component QUINT CAP 4KJ. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636159&prj=657&rqi=qHnxM1sUG3WiCBOSVu7bwCw79d
RT1MECH-87-005 | d0ccbe9a-f873-4f76-bcd4-ba522b04c387 | TR06-3 | 657 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | As per review of the submittal package RMC070, the specification cut sheet individual components are not attached. review Table 2.6 Spare Parts item 12,15,16 -EC Fan -MC-22b -MC-9b -Auxiliar contactor -Step down Transformer | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636163&prj=657&rqi=uWtki2vCBHzs14bsGo2Y75d8zF
RT1MECH-87-001 | 85b4287f-e3ab-4d59-bc10-cbab0f6f905b | TR06-3 | 657 | AMER | Open | P3 Low CX | Frank.du@veolia.com | 2026-08-31 04:00:00.000 +0400 | DEL - Delta Elec | L2A | Installation Damage | Commissioning |  | Mechanical â€“Air | equipment | 1CRAH_ER_11 | CRAH - Computer room air handler |  |  | Damage cooling coil observed upon inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636158&prj=657&rqi=HPEsVKmdKJ3y6Aqc5yJmHAcD5c
RT1MECH-37-008 | faaceaeb-4e28-4722-8d56-85b901c08720 | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-08-21 04:00:00.000 +0400 | General Contractor | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: Housekeeping PAD has one corner broken. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634620&prj=657&rqi=RVrj46z6OJvL6T6SDiOUv62cey
GI-093 | 3e991b52-bca1-40c0-92df-fcac43d0cedc | TR06-3 | 657 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UDP_B_1 | UDP - UPS Output Switchboard |  |  | UDP_B_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634543&prj=657&rqi=mBTZN8fhi3N0z1RHh8R482ornk
GI-097 | 92f30738-2df5-4caa-bd69-70dd7fb5b671 | TR06-3 | 657 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  | no | SPD bus in section 01C missing cover. Hazard to operators is currently present with exposed busbars | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634547&prj=657&rqi=KAbItalaL5e6BxDpfdRosYduVm
GI-100 | 2e5f7461-29c6-4566-bcef-1afbe179ca48 | TR06-3 | 657 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning | [7 empty] | At UPS_B_1 & UPS_B_2 (XVLDC 21-24) the UPS Charge Limit wiring has not been installed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634551&prj=657&rqi=CRQIs50g0rAgcZjx9BK16OoOpu
GI-098 | 5bc7af90-5b8e-43ca-9fd2-bb08947a2abc | TR06-3 | 657 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  | no | UPS_B_1_LBB & UPS_B_2_LBB status contacts were not wired to a terminal block to be monitored by the UPS. Three spare EF contacts exist at each breaker | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634548&prj=657&rqi=DMqitiwQ2231fF2UCXUFrOeW6y
GI-094 | 57ba5f3d-2e94-4dd5-93b1-0ae796b94dd5 | TR06-3 | 657 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UDP_B_2 | UDP - UPS Output Switchboard |  |  | UDP_B_2 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634544&prj=657&rqi=2oyXhunhS4ODF91qDNw2lcDca9
GI-096 | 26d87c92-b0b9-4c34-9c80-80409ab6f02b | TR06-3 | 657 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UDPR_B_2 | UDP - UPS Output Switchboard |  |  | UDPR_B_2 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634546&prj=657&rqi=Z3F2uwgQ9QPDXR0MaJZZqa1RtU
GI-095 | ac4ba16c-256f-49ce-8250-d69619be3568 | TR06-3 | 657 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UDPR_B_1 | UDP - UPS Output Switchboard |  |  | UDPR_B_1 800A breaker lug kits (AL800M23) accept a maximum conductor size of 500MCM. The SLD calls out parallel 600MCM. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634545&prj=657&rqi=aKrAlQE2si5I3ZniEVPHd46Juh
GI-099 | 3ec56cae-30cc-4822-9ed9-137ca9dabbd1 | TR06-3 | 657 | AMER | Open | P2 Medium CX | steve.knezevic@veolia.com | 2026-08-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1BATT_B_1_1 | LIBATT - UPS Battery |  |  | TB3 1-3 from the BIBR to battery cabinets (MCCB Status) has not been completed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=634549&prj=657&rqi=AONDNUKdVHdFWnr43Zu9okqhMt
GI-092 | 4861a98b-acaf-49c2-aca7-35fcb6a40b7f | TR06-3 | 657 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-08-07 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | FWT | Factory Witness Test | [7 empty] | Skid D: 1UDP_B_1 and 1UDP_C_1 on the TR6-3 project. The current configuration does not provide sufficient space in the front lug holes to achieve the required wire bend radius, causing the lug to press against the insulator. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=632770&prj=657&rqi=iJPBAwtt6OY4Y3gdbU8GHzRJU7
GI-091 | a2dfbdd5-96a9-4546-a9cb-17face2c04d4 | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-28 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Common to all chillers: Model # of the Onicon Flow meter does not match the cut sheet on the submittal. The one received on site Model # is FT-3400-200-1C31 Vs the Submittal which mentions F-3500 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631082&prj=657&rqi=x0QR82tiklMF4hgKg2AGAtppm4
GI-090 | 42bdbea2-539b-4122-a24b-23cb86089ea4 | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-28 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Applicable to three Chillers as of now: The Air Vent on the Air Separator was found to be able to rotate by a push. The connection need to be inspected. See on below chillers. (video available on request) 1CH-A-2 1CH-B-2 1CH-B-1 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=631076&prj=657&rqi=RwqAhzaWB4rPNKn2aBoHNY1srS
RT1MECH-38-021 | 212d7a33-b449-456a-95b9-0ad2d2a8d650 | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“ Water | equipment type |  | ACC - Chiller â€“ Air Cooled |  |  | Common for all chillers: CBTB1 - fusible terminal blocks FU-SIA1 through FU-SIA8 do not denote fuse size. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630934&prj=657&rqi=93AcCZ8ID40ZmuFxLQRqa6Hiwo
RT1MECH-38-020 | f89031c1-f05e-4a11-83ba-5f4c2e7dc2f0 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to TR6-3 chiller submittal: For the MG2 module on the chiller condenser, the drawing shows the termination at P1- and P1 + terminals. The actual terminations on site are on P2- and P2 + terminals. These two terminals are not shown on the drawing. The drawings needs to be updated to match the site installation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630932&prj=657&rqi=nZ22CshzeTCCnUXBg4kYMgPGsS
RT1MECH-38-017 | 69e1e572-8bcb-4df3-9654-a8b376b0720b | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to TR6-3 Chiller Submittal: Missing Cutsheets for the following components: 1.) Evaporator Liquid Level Sensor 2.) Smardt Lift VFD Module 3.) Expansion Valve 4.) Freeze Protection Bypass Valve (BRAY) 5.) Temperature transducers 6.) Pressure transducers 7.)Evaporator Barrel cutsheet provided is a general cutsheet does not provide a model number specific to TR6-3 project. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630899&prj=657&rqi=bc6Z9M3LiYhzyFE9lw3saSn58Y
RT1MECH-38-018 | d575d039-ac3b-4272-80bb-e99bc8029365 | TR06-3 | 657 | AMER | Closed | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-E-1: Missing outdoor air sensor. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630926&prj=657&rqi=2tjVoBhZnpXBadiTggLmEsqOoN
RT1MECH-38-014 | e7d5e105-1675-4618-9f47-c6eca855ceee | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-E-1, pump skid electrical panel: As per the drawings FU-5 is 8 A fuses but we found 5A fuses installed downstream of 5L1 and 5L2. (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630889&prj=657&rqi=NsYK7nAhWXN6AxmVJvpJXX7MHf
RT1MECH-38-015 | 2673eca7-f37f-4562-aeb8-93455e5e9504 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | Applicable to TR6-3 Chiller Submittal: On the panel drawing for the pump, the transformer in the panel layout is shown as 460 to 120 V, in the electrical single line drawings it is shown 460 to 24 V and the wiring on site is also as per 460 to 24V. The panel layout drawing needs to be corrected. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630895&prj=657&rqi=cVCIhdhx6NWySvkctU0zVcWaGb
RT1MECH-38-019 | b1213a81-d214-4e2d-92dd-55c14e9e0c72 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation Damage | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CU-E-1: The fins are bent on the condenser on the roof. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630930&prj=657&rqi=raPoRdmpYaqCpcPZRWcz2y0a7s
RT1MECH-38-016 | 610759cf-e764-4077-890d-ec5abf8800d0 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-27 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-E-1: The FU2 fuse holder label needs to be rectified on the submittal. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630898&prj=657&rqi=CldEt2s8Pg38dzRqt2NxaQFH56
RT1MECH-37-007 | db7a5288-4775-45ad-8735-9556ad664575 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-24 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: The conduit connection in the splitter panel entering panel L3 enclosure side is loose and not properly torqued | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630779&prj=657&rqi=MshZEJoTkFOCO2JPMx0rWRvvLn
RT1MECH-38-013 | be4e623b-b2b1-42e9-bba5-ca7228c2b43a | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-24 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | Applicable to 1CH-E-1 and 1CH-D-1: The model number of the two isolation control valves at the bottom side does not match the cutsheet. Refer to the attached pictures. The Model Number mentioned on the cutsheet is PKRBUP-MFT-T and these two valves the model number is PKXUP-3-T | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630756&prj=657&rqi=9xLEJoRv3Njv8p3nTQyikhEbvD
RT1MECH-37-006 | 06695b23-38e0-42be-a660-bc6de6b27031 | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-24 04:00:00.000 +0400 | SMT - SMARDT | L2A | Component/ Equipment Failure | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: ABB breaker SACE Tmax XT4H 250 in L2 enclosure is not resetting, and stuck in the tripped position, preventing door from closing and requires inspection. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630777&prj=657&rqi=rPNbPz1q7TNMECz2XVk4yKumXI
RT1MECH-38-011 | cbc14ab8-5746-497d-a179-d736632d4a37 | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-24 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | Applicable to new chillers 1CH-E-1 and 1CH-D-1: The model number of the freeze protection bypass value does not match the model number of the freeze protection bypass valve installed in the TR6-2 phase. As compared to TR6-2 bypass valve (800 In Lbs.) the torque value is less on the TR6-3 chiller bypass valve (600 In Lbs.) The SMRARDT submittal for TR6-3 phase does not include the cutsheet of the BRAY valve. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630718&prj=657&rqi=eJES0kbHVGKLyc6vLFOESxDrVe
RT1MECH-38-012 | ec4ef419-fbb2-4bcc-87e3-ef191afa70b1 | TR06-3 | 657 | AMER | Closed | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-24 04:00:00.000 +0400 | SMT - SMARDT | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to 1CH-D-1 & 1CH-E-1: Missing the onicon flow meter on the pump skid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630741&prj=657&rqi=AMJXmEhyhnA8d9ZpGBsT0aooNr
RT1MECH-38-009 | 892e5d8e-5acc-4fb5-8ad9-5575b4072421 | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to 1CH-E-1 & 1-CH-D-1: (As of now these two chillers are on site) The model number of the main disconnect of the chiller does not match the model number mentioned on the submittal. On the submittal the selection is highlighted on Model # OT600U03 and the model # noted on the onsite chiller main disconnect is OT800U03. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630586&prj=657&rqi=aPQpuCWtvXQrQTrOVrHmsB7aPo
RT1MECH-38-008 | 87ee626d-dd20-4e25-802c-cdda34a8532a | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to the 1CH-E-1 & 1-CH-D-1: (At this point inspection is done only on the chillers received on site) As per the EOR comments on the Pump Skid submittal the fittings on the pump skid connecting to the building chilled water header is supposed to be Victaulic. The fitting seen on the these two chillers is not Victaulic. (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630579&prj=657&rqi=DppQTRtIAJMcoigl0I21CXRGYj
RT1MECH-37-005 | 5a0219af-3f6b-46c2-ad6f-0177108d7cb7 | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CHWP-D-1: The chilled water pump electrical panel door is jammed and does not open all the way. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630606&prj=657&rqi=Yi83w1MDhp3c1Ezfao9z6Y8kbW
RT1MECH-37-004 | ec7a0041-d593-44f2-8c4b-d9702c551c5f | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: Seals / Ports missing on the below location on the chiller. - Pump skid and Chiller connection. - Evaporator two ports - Air Separator bottom drain port. Concerns of FOD /Rust . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630604&prj=657&rqi=JjBB5uk0X0cRljpSbVXqHL8SnO
RT1MECH-37-003 | 3cea3353-87b7-4b3c-94e1-a65a5ff69cff | TR06-3 | 657 | AMER | Ready for Verification | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | SMT - SMARDT | L2A | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: Power Entry Label is incorrect. Shows 480 V but this is a 120V panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630595&prj=657&rqi=PMCdKtOV227T65otVRE1O66yVH
GI-089 | e2b97334-d3d8-4607-850e-b4d45046e72c | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Applicable to 1CH-E-1 and 1CH-D-1: The location of the flow switch was changed in last phase from its original location (close to the evaporator) to a location on the pump skid. But the new chillers on site still has the flow switch installed close to the evaporator. (Reference picture attached) (Also Refer Issue # 1109 on TR6-2 Facility Grid) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630661&prj=657&rqi=snGXMpgV5WlXrFjnXEQsLSPJjo
RT1MECH-38-010 | caba8952-718a-4533-9442-0bf890aea344 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-23 04:00:00.000 +0400 | General Contractor | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-E-1: Seals / Ports missing on the below location on the chiller. - Pump skid and Chiller connection. - Evaporator two ports - Air Separator bottom drain port. Concerns of FOD /Rust . | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630602&prj=657&rqi=sTodOcXleKW8c0Hj8kDnSP6J8i
GI-087 | f9924d9b-bd81-f410-4496-599a61798d5f | TR06-3 | 657 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-22 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  | no | Insulation boards are missing at Sections 6 and 10, a recurring issue previously observed on Skid C. An email has been sent to AMG requesting immediate action before MPS closes the back panels; we are awaiting their response. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630458&prj=657&rqi=STyeZTfIr4F1wNjpVDlViBV1tQ
GI-088 | 9981909f-f8fe-b87a-f175-db1bc5aa3ec0 | TR06-3 | 657 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-22 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_B | MSB - Main Input Switchboard |  | no | Insulation boards are missing at Sections 6 and 10, a recurring issue previously observed on Skid C. An email has been sent to AMG requesting immediate action before MPS closes the back panels; we are awaiting their response. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630459&prj=657&rqi=CABFyWJh1JFtvo7rVVrHWg5JeK
RT1MECH-38-004 | 896f6de1-a0a5-406d-bd53-ef129f9e152b | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Documentation not issued/ Required | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | Applicable to 1CH-E-1 & 1CH-D-1: Power Entry # 3 drawing on the submittal does not match the panel on site. (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630195&prj=657&rqi=v0uMaWwOaNQPUjeUJrmewFKuaF
RT1MECH-37-002 | 0ea0a324-e09e-4675-9292-1b5d34387d17 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-D-1: The Equipment label does not match the label on the submittal. The submittal mentions two part numbers one on the main header page and one has a detailed name plate. (Refer to the attached picture) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630208&prj=657&rqi=gUeQcYSziFN4vdCEm889rDh7OE
RT1MECH-38-001 | e957374b-230a-42fb-a8e5-42e824f3e86a | TR06-3 | 657 | AMER | Ready for Verification | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH_E_1: The pump skid CHWR piping are not aligned, and needs adjustment so that the pump skid can be connected to the chiller. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630178&prj=657&rqi=HHLup5VI6PdkMjRuAG4Zy6bENF
RT1MECH-37-001 | 3c17a251-744f-41fd-addd-d59587f65d6f | TR06-3 | 657 | AMER | Ready for Verification | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not complete | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_D_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH_D_1: The pump skid CHWR piping are not aligned, and needs adjustment so that the pump skid can be connected to the chiller. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630177&prj=657&rqi=Kd3UN6XiSdyyCScdzXvEvv2cXP
GI-086 | 3a88a152-2307-4e9a-90da-7215e3a6cd88 | TR06-3 | 657 | AMER | Ready for Verification | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | Applicable to all Chillers: Issue is for tracking purpose. Smardt to confirm the chiller proof of flow logic and confirm if its as per Equinix standards. (Also tracked on the on going email chain. screenshot attached) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630332&prj=657&rqi=4006VzOgrk1kakLK8uNIdbBwwO
RT1MECH-38-005 | 92f030fd-d05f-4285-9fce-862a19783f3f | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Installation not correct | Commissioning |  | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to all chillers part of TR6-3 Phase: In order to resolve the ongoing chiller compressor fault on low ambient temperature (Refer to Issue # 1113 from TR6-2 phase) the three discharge isolation valves were to be wired such that they can be controlled individually to open / close from the Kiltech controller. Referring to the new submittal for TR6-3 phase it looks like this correction has not been made. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630198&prj=657&rqi=RS4YImXmkvDefnZWTAuqN3pDtc
RT1MECH-38-007 | f0d9c6b4-932a-497c-920b-96e4bd5158a8 | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - BMS | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to all Chillers : We noticed that the phase monitoring relay is not present in the Compressor panel # 2 as seen on the TR6-2 phase chillers. Upon review of the new submittal for TR6-3 we noted that the phase loss relay is not shown on the single line diagram of the compressor # 2 panel. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630212&prj=657&rqi=0QpA3pQbsHdtN6JOzg9OJ9i4J0
RT1MECH-38-003 | 0ac74904-f361-4413-bb17-c5d73ffa1efe | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | Applicable to 1CH-E-1 & 1CH-D-1: Power Entry # 3 Panel: As per the Submittal Pg # (13 of 48), the circuit diagram shows one LED or light but the panel on site does not have any LED or Light. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630194&prj=657&rqi=jyKYmxdjcASCgCikhJD59eYvRa
RT1MECH-38-006 | 05cd9c38-fc07-4bf0-9f1e-4631942c5d9e | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | SMT - SMARDT | L2A | Labelling | Commissioning |  | Mechanical â€“ Water | equipment | 1CH_E_1 | ACC - Chiller â€“ Air Cooled |  |  | For 1CH-E-1: The Equipment label does not match the label on the submittal. The submittal mentions two part numbers one on the main header page and one has a detailed name plate. The header matches the name plate model number on the chiller (Refer to the attached picture) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630201&prj=657&rqi=m3tiNGu4pMkQpbs2oPGHgfnOUp
RT1MECH-38-002 | bc37da4d-2c8f-4f4d-851a-14b8594a676d | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-21 04:00:00.000 +0400 | General Contractor - BMS | L2A | Missing Components | Commissioning |  | Mechanical â€“ Water | equipment type | ACC - Chiller â€“ Air Cooled | ACC - Chiller â€“ Air Cooled |  |  | Applicable to all chillers part of TR6-3 phase: The Equinix PLC Control panel is missing on the chiller. On the TR6-2 phase chillers this control panel came from SMARDT Factory with the chiller LCP installed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=630181&prj=657&rqi=hHQH1dgBrJcw1Y7VXMr95DIfnw
GI-083 | 5f18f99f-6364-4685-baf6-882616758d25 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | For B Skid: Applicable to the control power section of UDP - B1 and UDP -B2: The section should have a protective plastic cover and caution label since a 460 V input is landed in this section. " | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629750&prj=657&rqi=iDuYWrBAE2h6yL1rO7ETgKcnpX
GI-084 | 6f071697-4c1b-4222-b7be-73583f4fcaff | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1UDPR_E_2 | UDP - UPS Output Switchboard |  |  | "Applicable to 1UDPR-E2: The location of the sub feed breaker 5 does not match the location shown on the submittal. (refer to the attached pictures)" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629758&prj=657&rqi=oPQRGRNLF9EBJ1SY752GuuaNgC
GI-081 | d8576709-b9d2-4caf-ab9c-8a5b3e7a9284 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | "For C Skid: Applicable to the control power section of UDP - C1 and UDP -C2: The section should have a protective plastic cover and caution label since a 460 V input is landed in this section. " | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629748&prj=657&rqi=hxlDUvZr3gHPncz91Ey1bKSHfG
GI-079 | 30e6170d-e020-4549-a8be-2b9aba157617 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1UDP_C_2 | UDP - UPS Output Switchboard |  |  | For 1UDP-C2: The sub feed breaker # 5, micrologic module is missing is the protective plastic cover which is seen on the dials. (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629743&prj=657&rqi=SxI73bZzERSr9VIyU2deDwYSci
GI-085 | 33062b37-7879-4c7b-8860-f9f71bf0120e | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | Applicable to the all the MPS Skid Equipment: Below lamcoids are needed: - MSB labels for the breaker as mentioned in the MSB submittal. - Fed from labels for all equipment - CRAH - WSHP - UPS - UDPR (subfeed breaker # as well) - Battery cabinets - STS (Some pictures attached for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629766&prj=657&rqi=vO5CyYbok6xnoCmF3LquB0pxB4
GI-082 | 18597281-137c-413c-b7b3-a8101362f49d | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  |  | equipment type |  |  |  |  | "For D Skid: Applicable to the control power section of UDP - D1 and UDP -D2: The section should have a protective plastic cover and caution label since a 460 V input is landed in this section. " | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629749&prj=657&rqi=lVjakAQBkHPAcMlH051nuIVBG8
GI-080 | 08008737-6842-41e4-a7b7-ba0955a3b10e | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-16 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  | no | For MPS Skid C - Section 06C: Edge guarding for controls cables is missing on the edges as seen on other skids (Highlighted in the attached picture) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629745&prj=657&rqi=cWTGtwaPIXKcxk8vBDSXpoO9QW
GI-072 | 18e2c0ae-f0bb-4165-aafc-aab3cc848a04 | TR06-3 | 657 | AMER | Ready for Verification | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1BTU_RMU_B | BTU - Battery Tripping unit |  |  | For MPS Skid B: The BTU rough in work is not completed. As per discussion during the Factory visit on 15th July, it was decided that will be done by MPS before shipping the skid. (Reference pictures attached from E skid) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629480&prj=657&rqi=b5KC9wlkfRmNvenEmmq2UBV3X4
GI-078 | 6434f149-e38e-46e9-91a5-d5d08bc72205 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Documentation not issued/ Required | Commissioning |  | Electrical â€“ LV | equipment | 1UDPR_C_2 | UDP - UPS Output Switchboard |  |  | Applicable to 1UDPR-C2: The location of the sub feed breaker 5 does not match the location shown on the submittal. (refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629490&prj=657&rqi=sXe0PVjBmfXeraxb71wATN6z1j
GI-070 | 56420015-584d-49ef-9c06-6be0c00f98d5 | TR06-3 | 657 | AMER | Ready for Verification | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1BTU_RMU_D | BTU - Battery Tripping unit |  |  | For MPS Skid D: The BTU rough in work is not completed. As per discussion during the Factory visit on 15th July, it was decided that will be done by MPS before shipping the skid. (Reference pictures attached from E skid) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629478&prj=657&rqi=TLC8r6K3YPEEzXotkyar628w6C
GI-074 | 1f1bc26e-9c8e-47ab-9856-7b76839a8141 | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [7 empty] | For MPS Skid D: The CSA / UL Label is currently not present on the Skid Label. (Per discussion on site this will be once the Skid is at TR6 site) (Issue is added for tracking purpose) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629482&prj=657&rqi=zI0trVq8doZjgL741cvbUuHCGd
GI-077 | cb312f3c-c583-4628-be57-a33277adff24 | TR06-3 | 657 | AMER | Closed | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UDP_D_1 | UDP - UPS Output Switchboard |  |  | Applicable to 1UDP-D-1: As per the submittal the breaker should be LSI, but the sub feed breakers 1,2,3 and 4 installed in this UDP are with micrologic 6.0A (with ground fault) trip units. (Picture attached for one sub feed breaker for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629488&prj=657&rqi=0j9XIO3mrW2vsT5B6z92FJYtpM
GI-069 | 226bc764-9394-4711-8fde-da43098e97cd | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1BTU_RMU_E | BTU - Battery Tripping unit |  |  | For MPS Skid E: The BTU rough in work inside the MPS Skid is not completed. As per discussion during the Factory visit on 15th July, it was decided that will be done by MPS before shipping the skid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629477&prj=657&rqi=OZzA2WP3VEXGswvXzi9Vp7aaly
GI-071 | dde6b593-a7c1-4cae-bc6c-639ab5b6a4d5 | TR06-3 | 657 | AMER | Ready for Verification | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1BTU_RMU_C | BTU - Battery Tripping unit |  |  | For MPS Skid C: The BTU rough in work is not completed. As per discussion during the Factory visit on 15th July, it was decided that will be done by MPS before shipping the skid. (Reference pictures attached from E skid) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629479&prj=657&rqi=dCnF0tu4bYnzebkoEkvgW1orOz
GI-076 | 5bf60de6-bc47-4b8b-a7d7-eb673c7b321c | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [7 empty] | For MPS Skid B: The CSA / UL Label is currently not present on the Skid Label. (Per discussion on site this will be once the Skid is at TR6 site) (Issue is added for tracking purpose) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629484&prj=657&rqi=c8DQKByay55GeaJjVTmccgiHk6
GI-073 | 2c83c2db-62ef-4418-8a7a-ffffe8ae2934 | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [7 empty] | For MPS Skid E: The CSA / UL Label is currently not present on the Skid Label. (Per discussion on site this will be once the Skid is at TR6 site) (Issue is added for tracking purpose) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629481&prj=657&rqi=yTCSilK7SEni3szJzZIDvtrxIu
GI-075 | d2b9594b-bf0a-48c3-bbec-e995dc05996b | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-15 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [7 empty] | For MPS Skid C: The CSA / UL Label is currently not present on the Skid Label. (Per discussion on site this will be once the Skid is at TR6 site) (Issue is added for tracking purpose) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629483&prj=657&rqi=dfge76syKuqveXNlMfQ7ZQnfpz
GI-061 | cd9e9bc6-3591-7016-476f-5f78c373b42d | TR06-3 | 657 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | Breaker 12B - 1600A LSI breaker is missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629278&prj=657&rqi=mazco6oxbyEQfc7eRCcUB8ctQ6
GI-062 | 16967d42-0a49-40fa-a6a4-52f45b6fdafc | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  | no | For MSB C: Noted during Spilt Inspection at MPS Factory: The Mimic representation is missing on the areas highlighted in the attached pictures. This is where a plate is installed by AMG for the ERMS switch . (Refer to the attached pictures) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629274&prj=657&rqi=QMYD3iPo3t2TaOMIqNKuavjARX
GI-058 | 6b7e1e65-5bd2-4102-a015-e64516a20ee5 | TR06-3 | 657 | AMER | Closed | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_C | MSB - Main Input Switchboard |  | no | For Skid C: Missing Kirk Keys on the MSB C. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629273&prj=657&rqi=GpUtRitJzmpkIrXVJkoBG0wenD
GI-065 | 43de89b6-a089-a72b-e831-ba751fa80e5f | TR06-3 | 657 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1UDPR_E_1 | UDP - UPS Output Switchboard |  |  | UDPR-E-1 &2 : Incorrect LSIG tripping units have been used for 800A LSI breakers in both UDPR-E 1 & 2. Need correction. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629283&prj=657&rqi=naFbQB7ai6BrVKugXeayeqNfFA
GI-057 | acd1e1b3-882e-74d7-0906-de1b60f3f537 | TR06-3 | 657 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | Metallic debris falling into the breaker and busbar compartments. This hazard must be mitigated while drilling and installing the conduit assembly at Section 03A and other Sections. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629272&prj=657&rqi=4rgErNrhqRUhJzrF82qQqb2nhe
GI-059 | a919a8aa-4696-1c65-5795-ed84bb8f17ee | TR06-3 | 657 | AMER | Open | P3 Low CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Labelling | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | -Sections 07 & 10 UPS Instructions SOO need to update with correct equipment ID. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629275&prj=657&rqi=2gKZ8aOSp6GfBPOJURkvtLwgCC
GI-063 | a019689f-2ac7-c321-fdc7-e28a7d1a4481 | TR06-3 | 657 | AMER | Ready for Verification | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | MSB back cover bolts were not tightened. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629280&prj=657&rqi=h0n1QCqs20X3xk2KBYY3gUrwUT
GI-064 | b85aae5c-349d-720f-956a-f7cdc9d6baae | TR06-3 | 657 | AMER | Ready for Verification | P3 Low CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | MSB LV panel: Missing circuit directories | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629282&prj=657&rqi=MUffagIdWAadZV8wUyvQC3l97W
GI-060 | fce3d78d-d3a4-d1ea-438b-3b7a07235be4 | TR06-3 | 657 | AMER | Open | P3 Low CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | Section 08C - Missing mimic lines | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629276&prj=657&rqi=lfGJrqtAYjfKa9WzG3tsVB2HZg
GI-056 | 723ae445-87f0-4198-5c15-5686617eb6e6 | TR06-3 | 657 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | All Skids : K-Kirk devices are missing. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629219&prj=657&rqi=f5c3J5mIXSnzlL7YsKnjc9N2XA
GI-066 | bff383eb-7491-4957-bbf7-e79ddcafa7b5 | TR06-3 | 657 | AMER | Ready for Verification | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning |  | Mechanical â€“Air | equipment | 1EF_E_3 | EF - Exhaust Fan |  |  | For MPS Skid E, applicable to the Exhaust fan control panel; The auto / Run selector switch is not labelled. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629315&prj=657&rqi=lzx022WqFaNoSPDysyG9vVEHCN
GI-068 | 6bf023fb-96b5-4be3-ac25-f70546158db9 | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-07-14 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | For E Skid: Applicable to the control power section of UDP - E1 and UDP -E2: The section should have a protective plastic cover and caution label since a 460 V input is landed in this section. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629327&prj=657&rqi=yRzvBVnRxdmRjaa41oEfbMFRlj
GI-067 | f232c77a-517d-4296-a49f-8778a14e472d | TR06-3 | 657 | AMER | Ready for Verification | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-14 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Labelling | Commissioning | [7 empty] | For MPS Skid E: The CRAH labelling in the skid does not match the labelling provided on the mechanical schedule. On the mechanical skid its 1CRAH-ER-11, 1CRAH-ER-12 and 1CRAH-ER-13. Inside the skid the CRAH labelling is 1CRAH-ER-10, 1CRAH-11 and 1CRAH-12 | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=629325&prj=657&rqi=D9tF82dmv2uoNBxBNyXZ7fleHl
GI-055 | a6afb89c-4029-467b-b7f4-c50808eadd46 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-07-12 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | Applicable to 7 Harmonic Filters: During the receiving inspection, it was noted that the harmonic filters on site do not match the Motor Size (HP/kW) parameter mentioned on the submittal | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=628779&prj=657&rqi=SnhfAHsKmVSOwHzppNmZO1aS0f
GI-053 | 660b8c82-4180-464f-a249-799d8fd74982 | TR06-3 | 657 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | [7 empty] | UDP/UPR (note that only saw the "E" block) - 800A Breaker lugs appear to only be capable for cables up to 500MCM. Per the site design and the breaker schedule attached, the lugs should be able to accomodate up to 600MCM. Anord to confirm and replace lugs as required. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627697&prj=657&rqi=NtBChYBRmUP66T8hmWkWEijqMr
RT1ELEC-404-001 | def170ff-8163-42ed-b636-f552b946b16e | TR06-3 | 657 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group | L2A | Missing Components | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_D | MSB - Main Input Switchboard |  | no | MSB-D - Section 11 is missing the barrier that is installed in the same Section 11 on MSB-D on the critical bus section. Anord to install barrier in MSB-D assuming it is needed and to make consistent. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627691&prj=657&rqi=LTqdTyqSbEiD61RDVEELozAjh2
GI-050 | c8327302-6e3c-4374-a327-eb24debb2355 | TR06-3 | 657 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Design correction needed | Design | [7 empty] | MSB (General) - There is nothing in the submittal that indicates where barriers are to be installed. Is there a drawing that can be provided? In light of the issue above and issues at other sites, we request Anord verify all barriers needed are installed. In particular, we noticed that in Section 6 & Section 11, we don't have barriers on any MSB above the UPS output (IOB). This is the only cable termination section that doesn't have a barrier below. Is this intentional by design? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627693&prj=657&rqi=F3P3ZGjIG6R1FdPvwKmTw9szRN
RT1ELEC-405-001 | 835f74a3-c022-484b-9418-d36f2d312414 | TR06-3 | 657 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group | L2A | Installation Damage | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_E | MSB - Main Input Switchboard |  | no | MSB-E - Main PQM 5000A Phase C CT has a cut on the wire. Wire should be repaired. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627695&prj=657&rqi=Obu0mvvwgCpLqoWeP7tBuclU20
GI-052 | 4d7a90ac-d46e-4f54-8d32-44eaabc9b8e9 | TR06-3 | 657 | AMER | Open | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | [7 empty] | UDP & UPDR were shipped with a random combination of 800A Micrologic 5.0A (without ground fault) and Micrologic 6.0A (with ground fault) trip units. Per Equinix standard, the submittals and the breaker schedule attached, all breakers should be 5.0A (without ground fault). | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627696&prj=657&rqi=jKPJNw2o7my7mHHMDM3Vp8oqDN
GI-054 | 1310d35e-594f-42cd-a281-71c618637638 | TR06-3 | 657 | AMER | Ready for Verification | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation not correct | Commissioning | [7 empty] | TR6-3 submittal: It looks like the HMI terminals were not shown correctly on the MSB side. I updated the names in the yellow cells. Some of the MSB terminals were not shown correctly for breaker, on gen and on static bypass signals. The corrections are in the yellow highlights. The LBB breaker statuses I could not find in the Anord submittal. Did MPS find this or make an assumption? The items highlighted in blue may have to be added by Anord. The maintenance bypass breaker status is not something that MPS wires. These are installed by Anord internal to the gear. Therefore those cells in red should be removed. Assuming these are the standard Vertiv battery cabinets, these should have the 480V control power to the receptacles and SO cords above the battery cabinets. If this has not yet been discussed with Equinix, please discuss to add in MPS scope. This will also need to corrected in the orange cells. Missing some of the battery controls, which I did not add to the spreadsheet. MPS will wire the major/minor alarm (TB1158) from the BIBR to the top hat terminal block in Cabinet 1 [already shown in spreadsheets but missing detail of point to point shown below]. TB1158 #1 (Critical Alarm COM) = Maj Alarm COM TB1158 #2 (Critical Alarm NC) = Maj Alarm NO [Note Samsung and Vertiv NO and NC terminology are inverted] TB1158 #3 (Critical Alarm NO) = Maj Alarm NC [Note Samsung and Vertiv NO and NC terminology are inverted] TB1158 #4 (Maint Alarm COM) = Min Alarm COM TB1158 #5 (Maint Alarm NC) = Min Alarm NO [Note Samsung and Vertiv NO and NC terminology are inverted) TB1158 #6 (Maint Alarm NO) = Min Alarm NC [Note Samsung and Vertiv NO and NC terminology are inverted) MPS will wire the trip (TB4) field wires from the BIBR to the top hat terminal block in Cabinet 1 [not shown in spreadsheets]. TB4-1 - Ground TB4-3 - Input MPS will wire the Vertiv dry contact wire harness from the battery cabinet module to the top hat in Cabinet 1. MPS will wire the MCCB (breaker status) field wires from the BIBR TB3 to cabinet #1 (2 wires) and cabinet #7 (1 wire). Leave the wires coiled up in front of the battery breaker. MPS will leave the MCCB (breaker status) Vertiv wire harness coiled up in front of the battery breaker. Vertiv will make the connections between the MCCB wire harnesses between cabinets and the TB3 field wires. This is at least what we agreed with the DC21 Vertiv team. Will need to confirm with the TR6 Vertiv team. Perhaps Veolia can assist. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627698&prj=657&rqi=h5meE16XnFPCoLQIRCD8yM8b3L
GI-051 | 77ae06e6-68b4-4a9b-86de-cc3e90126c9b | TR06-3 | 657 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-07-01 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Installation not correct | Commissioning | [7 empty] | MSB (General) - Section 6 & Section 11 have the voltage present lights for the IOB breakers tapped on the "Critical Bus" output side of the IOB breaker. The voltage present lights by Equinix design should be tapped on the "UPS Output" (cable side) of the IOB breaker. Anord should move the voltage present taps to the same side of the IOB breaker as the PQM voltage sensing leads. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=627694&prj=657&rqi=0jKZSjhGUPeBsgI7k4VZ3HYuRM
GI-048 | 2c9004ff-2bcb-49de-adf4-0e864898a22e | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-06-24 04:00:00.000 +0400 | SMT - SMARDT |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | Common for all chiller condensers: Discrepancy in the condenser model number Vs model number noted on the condenser nameplate received on site. On the submittal the model number is "CA150.A020RA.010" On the nameplate of Condensers received on site the model number is "CA150.A020RA.F10" | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626708&prj=657&rqi=oOIazUu9nFEPbkzIlaOk3M2nzq
GI-049 | 3704e873-ddf7-41f0-bea7-db4f3ead85e1 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-06-24 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1CH_E_1 PQF | HF - Harmonic Filter |  |  | For 1-CU-E-1: One condenser fan is clipped was found to be not connected to the fan guard. (Fan 1) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626797&prj=657&rqi=Dkr8OWNT5QD5ghPrK2R5rwOLpR
GI-029 | 28b97fd2-e49a-406e-8286-1f96d2896ef0 | TR06-3 | 657 | AMER | Closed | P3 Low CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | for all condenser unit submittal drawing and unit don't match contactor showed 20 in drawing, only 10 in unit. Two fans connected to one contactor, vendor to notify if wiring valid. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625820&prj=657&rqi=qI2LiKhxNSBU71QIub81lG5Mp7
GI-031 | 304ee7d7-d7ca-497b-8d17-d7d11b51e3cf | TR06-3 | 657 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not correct | Commissioning | [7 empty] | unit 4430, 4433: exposed copper wire in disconnect | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625825&prj=657&rqi=6gVaDu1r8kanm5V1U5euwqkCZm
GI-025 | 782c9949-41da-405f-9b33-a117119db5f6 | TR06-3 | 657 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not correct | Commissioning |  |  | equipment type |  |  |  |  | Condenser skid unit: For all 7 units skid Refrigerant line holder too low, do not support refrigerant piping weight.(Pictures attached) After inspecting this for existing chiller condensers it was noted that this issue is also applicable to 1CU-A-1, 1CU-903B-1, 1CU-904-1, 1CU-R-1 and 1CU-R-2. (Pictures Attached) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625799&prj=657&rqi=wWsZHxBZcR3HST7RAm85Kqff4D
GI-030 | 8e22d98e-5824-4d64-b1e9-579be919042b | TR06-3 | 657 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Component/ Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | condenser unit 4032, no tag: com wire out | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625821&prj=657&rqi=DTfYKmSHTqPfh0FBFJUW2BB5ue
GI-027 | 57533936-9f79-4d50-bc33-5d9251d127bf | TR06-3 | 657 | AMER | Open | P3 Low CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Component/ Equipment Failure | Commissioning |  |  | equipment type |  |  |  |  | Missing plug for fill in port in condenser | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625808&prj=657&rqi=k7t0QVto2oz6yKxL5PSQnjgTWy
GI-026 | e4ac628c-ba09-4ce8-b36c-c7913485d39b | TR06-3 | 657 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | condenser units: 2 units missing product tag/serial number | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625806&prj=657&rqi=0RzJRmHduiSpb22vtOEQ7eoRBK
GI-028 | f13f84d3-278c-4721-baff-ea6233ea4b5b | TR06-3 | 657 | AMER | Open | P3 Low CX | jerome.deschenes@veolia.com | 2026-06-17 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning |  |  | equipment type |  |  |  |  | condenser unit 4432, 4030, no tag missing book and spair gasket | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625817&prj=657&rqi=N0mFhSKXBiKUf6DbrN0c1NiMfV
GI-024 | 2f807254-3d79-4b87-899b-00e3a326aee4 | TR06-3 | 657 | AMER | Closed | P2 Medium CX | vijay.singh@veolia.com | 2026-06-11 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | FWT | Factory Witness Test | [7 empty] | MSB-E: CTs 4 and 6 may be wired or labelled incorrectly. Phase A has wiring for CT6 and phase C has wiring for CT4. This is reversed from the submittals orientation: | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=625010&prj=657&rqi=4EyKnqnra1znsl8u8kmmDtWqSR
GI-021 | 215ee44c-153c-4ef8-93c0-5369e452442b | TR06-3 | 657 | AMER | Open | P3 Low CX | qubert.quintal@veolia.com | 2026-06-04 04:00:00.000 +0400 | AMG - Anord Mardix Group |  | Labelling | Commissioning | [7 empty] | The posted SOO procedures at the new MSBs is not correct. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623968&prj=657&rqi=NfRLk5ap5vQ4NhsMTRnSFItHET
GI-023 | f02dcce6-b884-44ec-8689-f5e3ffd09893 | TR06-3 | 657 | AMER | Closed | P3 Low CX | qubert.quintal@veolia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | Main Service entrance switchgear 1PUSP_1 & 2 sections are missing equipment identifiers/labels, e.g., Interrupter, Protective Relay, Power Quality Meter. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623971&prj=657&rqi=Qfa25IvrP9YqOXKjTdwlnzYGZm
GI-022 | 144f49bb-6e3c-45f1-bc20-d77412ed0050 | TR06-3 | 657 | AMER | Closed | P3 Low CX | qubert.quintal@veolia.com | 2026-06-04 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning | [7 empty] | Electrical Block A & R SKID: A few MSB_A breakers were mislabeled (incorrect spelling, incorrect label background color, font size), e.g., UPS_RIB_2, 1UPS-A-2-LBB, 1-CH-A-2, 1LBB_A. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623969&prj=657&rqi=7fjuMI5ZUJBv1WjiN2OPpfzQv3
GI-020 | f5a5002b-5e7b-44be-b35b-ce88ca6faa8e | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-06-03 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | Applicable to all the Chillers for TR6-3: It came up part of the GOE inspection that the chillers should include the lamacoid which also matches the name on the BMS along with the lamacoid as per schedule. The chiller panel are missing the labels mentioned on the BMS faceplate associated to the chiller. (refer to the attached picture)(We have used the TR6-2 chillers to demonstrate an example) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623796&prj=657&rqi=rhCIBCPBMsSkZx4oHs0UyM7Em0
GI-019 | a7366b15-a850-4818-a202-4495f99b642b | TR06-3 | 657 | AMER | Open | P3 Low CX | jerome.deschenes@veolia.com | 2026-05-25 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning | [7 empty] | chillers submittal need to be provided with new updated drawing 57-0161, as new chillers differ in design from the existing one on Equinix Tr6 from project 2. Valves need to have individual tag and number. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623127&prj=657&rqi=IPjmRFpsm8BUG1KiT9ONknRyY8
GI-018 | 3c1160ab-6c1c-4dab-aa4e-036ecfbdb910 | TR06-3 | 657 | AMER | Closed | P2 Medium CX | jerome.deschenes@veolia.com | 2026-05-25 04:00:00.000 +0400 | SMT - SMARDT |  | Installation not complete | Commissioning | [7 empty] | Chillers not completed for factory visit Piping cleaned up and joints Missing parts and tie ins for controls and compressors completed. Valves missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623052&prj=657&rqi=WBvdqkqLPPD5MH0nyu01HO7mrJ
GI-017 | 63835109-27ce-4c6f-aa52-b91017ba7d0a | TR06-3 | 657 | AMER | Closed | P3 Low CX | jerome.deschenes@veolia.com | 2026-05-22 04:00:00.000 +0400 | SMT - SMARDT |  | Documentation not issued/ Required | Commissioning | [7 empty] | Torque report is required for all high voltage, with calibrated tools, date, value. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622831&prj=657&rqi=PigT7YbbJDlYHqv5KFefAHoJLM
RT1ELEC-128-001 | 12b7352d-1c1f-a6da-71f4-0d3d7dc39bba | TR06-3 | 657 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-04-23 04:00:00.000 +0400 | AMG - Anord Mardix Group | L2A | Installation not complete | Commissioning |  | Electrical â€“ LV | equipment | 1MSB_Z | MSB - Main Input Switchboard |  | no | Factory assembly is in progress. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619266&prj=657&rqi=aeLWJzfgdMEW9SnduYvUoisHDG
GI-016 | f8e99aca-e76d-4e85-b348-e277263fcb9a | TR06-3 | 657 | AMER | Open | P2 Medium CX | derrick.dsouza@veolia.com | 2026-04-23 04:00:00.000 +0400 | Consultant |  | General Design Issue | Design |  |  | equipment type |  |  |  |  | For MPS Skid CRAHs in TR6-2 Phase, issue was raised for missing strainers. Based on the discussion with Equinix Design / GOE team this was going to be captured in future designs. Creating issue to track this item or capture feedback on the requirement of strainer on skid crahs. (Refer to attached email chain in the document section of this issue) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619260&prj=657&rqi=czf72drrKfT6otFL86cqQeonpw
GI-015 | 996b2af8-dba3-4466-add1-8d9fb8d7a6bc | TR06-3 | 657 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-03-02 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design | [7 empty] | Upon failure of the preferred source, the STS will transfer to the alternate source fed by System R. In the event of multiple UPS failures, the first primary block UPS load will transfer to System R via the STS. However, there is a risk of overloading System R if control signals are not sent to the other primary block STSs to engage a transfer inhibit function. This function is necessary to prevent those STSs from also transferring to the redundant block. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483425&prj=657&rqi=t20MDs2CRt66CZfgzz2I73Jnrg
GI-012 | 7b66eeab-4c03-4cf0-831e-338ba41f5d93 | TR06-3 | 657 | AMER | Closed | P3 Low CX | Ocean.Kwan@veolia.com | 2026-02-24 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design | [7 empty] | Electrical Single Line for Block B, C, D & E - E605 to E608 Logic detail of K-Key interlock betewwn equipment's to be provided. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199962&prj=657&rqi=MMy7Sy3prrVHjNdEQXf8K8RZBX
GI-013 | 05ac73c3-4654-4b0e-8ac7-6abfd4952377 | TR06-3 | 657 | AMER | Closed | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-24 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design |  |  | equipment type |  |  |  |  | The Room # mentioned in the mechanical schedule (dwg # M702) for "B Block Mech UPS & Batt.Room 1613" does not match with room # mentioned for this room on the dwg # M131.F and dwg# A120.F, which is Room 1612.Â Same for D Block, in the mechanical schedule for "D Block Mech UPS & Batt.Room 1613", where as in rest of the drawings its 1614. (Refer to the attached pictures)Â | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204067&prj=657&rqi=8CzuwcEFYQDix6wMPNnky42SW9
CCD-L0-3-001 | 9534cc45-3b91-4491-9e80-331323bc1980 | TR06-3 | 657 | AMER | Closed | P2 Medium CX | Ocean.Kwan@veolia.com | 2026-02-24 04:00:00.000 +0400 | Consultant | DELIVERABLES | Design correction needed | Design | [7 empty] | Electrical drawing E602 MV Single Line diagram has missed RMU shunt trip signal line to RMU protection relay from downstream transformers: - 1RMU_Z -1RMU_901/2 -1RMU_903R -1RMU_903A | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199957&prj=657&rqi=lIlfAA9pxBwxtkCubB7Zoxlh5a
GI-011 | fbc9f3e0-1c41-4f68-bfcc-74d9065d8726 | TR06-3 | 657 | AMER | Closed | P3 Low CX | Ocean.Kwan@veolia.com | 2026-02-24 04:00:00.000 +0400 | Consultant |  | General Design Issue | Design | [7 empty] | Electrical drawing E601 - The key interlock details for K32 and K31 to prevent parallel of two MV sources is not provided. The number of keys be avaliable and captured in the corresponding cylinder to be specified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199960&prj=657&rqi=hi2l4nwmaWKde6pJAEJlAnl8lM
GI-009 | 47c21637-be98-4bc0-a142-789be533a801 | TR06-3 | 657 | AMER | Closed | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-22 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design |  | Mechanical â€“Air | equipment | 1HP_R_03 | HP - Heat Pump |  |  | 1HP_R_01: The asset name has already used by the WSHP in Block R Electrical Skid. (Attaching screenshot from Mechanical Schedule dwg # M701) (Attaching screenshot from TR6-2 phase BMS screen for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199722&prj=657&rqi=dUX1qZ2NJL24KytPyaNLlHoh7j
GI-007 | ecf9239b-c2b8-476a-b5c3-34fa457e4bca | TR06-3 | 657 | AMER | Ready for Verification | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-22 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Design correction needed | Design |  |  | equipment type |  |  |  |  | Referring to the Mechanical Schedule Dwg # M702 (Issue G1) (Issued on 5th Feb 2026) For the Electrical Skid CRAH's, the chilled water entering temperature specified is 70 deg F, whereas the Chiller Plant leaving water temperature for the building is 65 deg F. (Screenshot attached) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199719&prj=657&rqi=6bJdb5kDmcWbonhxEZWaSVeXks
GI-008 | 93f5b017-aa48-4776-85e5-7c7aedfb086d | TR06-3 | 657 | AMER | Closed | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-22 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design |  | Mechanical â€“Air | equipment | 1HP_B_03 | HP - Heat Pump |  |  | 1HP_A_01: The asset name has already used by the WSHP in Block R Electrical Skid. (Attaching screenshot from Mechanical Schedule dwg # M701) (Attaching screenshot from TR6-2 phase BMS screen for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199720&prj=657&rqi=BFmX58WPyc94Nf6WECcq73wMol
GI-010 | befb98b3-e430-4f33-bad0-ee8c12f21c2e | TR06-3 | 657 | AMER | Closed | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-22 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design |  | Mechanical â€“Air | equipment | 1HP_R_05 | HP - Heat Pump |  |  | 1HP_R_02: The asset name has already used by the WSHP in Block A Electrical Skid. (Attaching screenshot from Mechanical Schedule dwg # M701) (Attaching screenshot from TR6-2 phase BMS screen for reference) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199723&prj=657&rqi=xddFV8FLNEuMS8gD233pyQZ0Oa
GI-006 | 06c1e16b-2b73-4f11-810d-f88255586055 | TR06-3 | 657 | AMER | Open | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-22 04:00:00.000 +0400 | SCH - Schneider Mech |  | Design correction needed | Design |  |  | equipment type |  |  |  |  | Referring to the Mechanical Schedule Dwg # M702 (Issue G1) (Issued on 5th Feb 2026) The DH 906 and DH 907, the leaving air temperature is shown 76 deg F. Comparing with the TR6-2, phase DH908 CRAH's, the leaving air temperature in schedule was 71 deg F. (Screenshot attached) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199718&prj=657&rqi=p8aNYWZj55nRlpcjueWi6h6Bqr
GI-005 | 46df4eea-628a-4c82-b0f9-97780e829810 | TR06-3 | 657 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-02-21 04:00:00.000 +0400 | Consultant |  | Design not as specified | Design |  | Electrical â€“ LV | equipment | 1CH_B_1 PQF | HF - Harmonic Filter |  |  | ACCH have recuring issues regarding cold start-up when OAT not available to enable free-cooling. This generate fails to start alarm each time, requiring a service call and unavailability of a redundant chiller during fail period. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199715&prj=657&rqi=7AruXwGP1MijgfzSQwaZVqCOIU
GI-004 | c14a35c8-8542-4005-a83e-f5d5a1cd2a57 | TR06-3 | 657 | AMER | Closed | P3 Low CX | derrick.dsouza@veolia.com | 2026-02-20 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design |  | Mechanical â€“ Water | equipment | 1TST_A_2 | TST - Thermal Storage Tank |  |  | For 1-CH-A-2, the associated thermal storage tank asset name is "1TST A-2". In the TR6-2, phase the asset name "1TST A-2" has been used by the Thermal storage tank associated with chiller 1-CH-903B-1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199703&prj=657&rqi=TZ6xzMkWBySZ1tYRx0OkRx66wL
CCD-L0-2-001 | 08099d58-68e7-4719-b722-872f0971f647 | TR06-3 | 657 | AMER | Open | P3 Low CX | jerome.deschenes@veolia.com | 2026-02-18 04:00:00.000 +0400 | General Contractor - BMS | DELIVERABLES | Design correction needed | Design | [7 empty] | SOO is missing from specification package. A building standard operating sequence will provide clarity of how the system is designed to operate at day1, avoiding cost and changes during cx | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199471&prj=657&rqi=7bQh1jPfrhnNLku3YT7IRnyuqV
GI-003 | a8711a36-45ae-4570-8029-3010a16f6f89 | TR06-3 | 657 | AMER | Open | P2 Medium CX | jerome.deschenes@veolia.com | 2026-02-18 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design | [7 empty] | Chilled water filtration missing from system | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199463&prj=657&rqi=m7s6dfcVw3lodFTAUvt4nX20Gh
GI-002 | bc083535-a994-4bbc-8273-bed1b3361b5c | TR06-3 | 657 | AMER | Closed | P2 Medium CX | jerome.deschenes@veolia.com | 2026-02-17 04:00:00.000 +0400 | Consultant |  | Design correction needed | Design |  |  | equipment type |  |  |  |  | Outside air temperature for chillers are set at 102.4 F (39.1 C) Last year highest temperature was 36 C, on ground. Chiller capacity shall be selected at a 20 yrs extreme outside temperature, to allow for optimum capacity of remote condenser at peak summer month. Also , chiller remote condensers are now juxtaposed one to one in TR6-3 projects, creating a increased air temperature at condenser intake, plus roof air temperature. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199382&prj=657&rqi=IxeP2e4MfSan53UE1p6VWmQjhD
GI-006 | e538396d-fc04-4c7e-86d4-f5ccd95cd2c5 | TY11-P3 | 649 | APAC | Closed | P3 Low CX | gerrydevera@commtechasia.com | 2026-06-18 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | UPS No. 6 IST On the BMS screen â€œPDU-U46-A1,B1,â€ the assignment for the common spare circuit breaker display for PDU-U46-B1-5C1 was incorrect. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=626026&prj=649&rqi=aQ84sNeAHTX6QgWnuA2faLbo7x
GI-005 | 99cc9d9c-9e3c-4806-a233-3a5c90672fb6 | TY11-P3 | 649 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-04-22 04:00:00.000 +0400 | Commissioning Authority |  | Component/Equipment Failure | Commissioning | [7 empty] | During an in-house PDU switching test, the thyristor fuse (200A) blew. The cause was identified as the transformer's inrush current. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=619208&prj=649&rqi=iQBnKM7kKC7Mu8jHqKF0PwWvNR
GI-004 | f032ee25-ca30-437d-aae1-9740656b9b9f | TY11-P3 | 649 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-04-15 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | SAT-Elec-Lv2-The breaker labels are not attached to PDU distribution panels for Units 7 and 8. The breakers for PDU No. 1 to 6 also require verification. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618313&prj=649&rqi=mmqnNNb3j8NLHqTGutku2VBQbw
GI-003 | 3910742a-94ed-4c65-8ec9-a2137db3ff90 | TY11-P3 | 649 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-04-14 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | SAT-Elec-Lv2-Load names (FED FROM) are not affixed to PDU power distribution panels Units 1 to 8. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618183&prj=649&rqi=NIo9QIYdTyIyAV4gOCe7Q6zLkl
GI-002 | 23a18f66-5d0c-4e56-9944-8a602d74614b | TY11-P3 | 649 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-02-17 04:00:00.000 +0400 | Commissioning Authority |  | Installation not complete | Commissioning | [7 empty] | CxLv3-ELEC-UPS No.6-BMS communication test pending due to incomplete wiring from the relay terminal panel to BMS. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199437&prj=649&rqi=9MVznkvSmS8r0a5iIsZeOBqxTI
GI-001 | 53f34dd6-460f-48bc-869f-06c67685c706 | TY11-P3 | 649 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-02-16 04:00:00.000 +0400 | Commissioning Authority |  | Installation Damage | Commissioning | [7 empty] | SAT-ELEC-Lv2-UPS No.6-The side part of output breaker 52P603 was found damaged. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199327&prj=649&rqi=5fB97HzceFo03bMYc9e1MFXwWw
GI-018 | c91126f2-a890-4a79-bfff-8f9351b93a8d | TY15-1 | 352 | APAC | Closed | P3 Low CX | JezkielDomingo@sygna-apac.com | 2026-04-06 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | SAT: Mechanical L3 During the operation check of the CHW motor valve, condensation occurred on the CHW pipe near 2-1-SWIT-12-4 including the bypass pipeline. The room temperature at the time of the test was 26Â°C, the humidity was 71%, and the CHW supply temperature was 20Â°C. contact Takasago for the cause and solution. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=88453&prj=352&rqi=xMJa9DqRAODqDzve19TmfMk5Lg
GI-081 | 58332069-7789-4592-8ce1-ebcc381c026c | TY15-2 | 548 | APAC | Closed | P3 Low CX | MasafumiOkuno@commtechasia.com | 2026-08-25 04:00:00.000 +0400 | Commissioning Authority |  | improper settings | DCOS | [7 empty] | B-IST No.5 The relationship between the UHV-B power output of 0 kW and the TRB secondary-side power of 107 kW; the reason for measuring power at the TR secondary side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635036&prj=548&rqi=suJOs3hDdhbqr1u8b6wXQiYmaq
GI-079 | a04fda02-9453-4503-bd93-eb0beb445aea | TY15-2 | 548 | APAC | Open | P3 Low CX | MasafumiOkuno@commtechasia.com | 2026-08-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | B-IST No.2 (Generator Failure/Restoration Test) Because the procedures for restoring the generator and DPF system are complex, detailed instructions and sequences should be included in the user manual. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635023&prj=548&rqi=kH7id5WF29DsJcY5UcZaC3Kb4m
GI-080 | 807f9da7-fee8-4425-a7fd-dd7956f45a31 | TY15-2 | 548 | APAC | Closed | P3 Low CX | MasafumiOkuno@commtechasia.com | 2026-08-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | B-IST No.1 (Power outage test) After the switch to GEN power, the four exhaust fans in generator rooms No. 6 and No. 7 (1-1-EF-12 18a, 1-1-EF-12 18b, 1-1-EF-12 19a, 1-1-EF-12 19b) were supposed to shut down, but they continued to operate. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635030&prj=548&rqi=X6P2mMto4JhCORFfbqxoCfmtQq
GI-078 | dacf1b15-6b6b-4268-a9dc-08c477de3278 | TY15-2 | 548 | APAC | Closed | P3 Low CX | MasafumiOkuno@commtechasia.com | 2026-08-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | B-IST No.1 After switching to GEN power, a communication error was reported for the following FCU. On-site, it was confirmed that the equipment continued to operate, and the alarm on the BMS automatically reset approximately 5 minutes later. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635015&prj=548&rqi=zcczxC7X2490JNkjEM2LmGQsGT
GI-082 | 4fd34f53-bdf5-4904-809d-a22e7d7c347b | TY15-2 | 548 | APAC | Open | P3 Low CX | MasafumiOkuno@commtechasia.com | 2026-08-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | B-IST No.1 Regarding the timer setting for the black smoke removal system: although it is currently set to 20 seconds (with a maximum of 24 seconds), black smoke was observed being emitted for several minutes. Discussions are required to reconfigure the timer setting. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635037&prj=548&rqi=zXCiK1HyCVRw6leTN0TK8Mr5si
GI-074 | 067c8871-14eb-47dc-baf5-4f7804bdbac8 | TY15-2 | 548 | APAC | Closed | P3 Low CX | SabinBasnet@commtechasia.com | 2026-05-27 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | During MIST operation check on chiller (8-1-CH-12-1), it was confirmed that the solenoid valve on drain pipe on Mist panel-1 was broken which caused the flow of water into the drain as soon as the Mist system was started. Although the MIST Control check is done on all the mist systems from BMS side, the MIST system operation confirmation is yet to be checked on (8-1-CH-12-3) as the main breaker for MIST system had to be replaced and yet not replaced. so confirmation on valves and operation of (8-1-CH-12-3) mist is yet to be confirmed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623175&prj=548&rqi=T0n67qQRhgLslX27z1LGXnwjc5
GI-073 | 03fbc960-74b0-4df9-9447-f4693c0dddbe | TY15-2 | 548 | APAC | Closed | P3 Low CX | SabinBasnet@commtechasia.com | 2026-05-26 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | During MIST operation check on chiller (8-1-CH-12-4) even when the run command was issued on auto mode from BMS side the Mist pump on controller-1 didnot start up causing up a congestionor breakge alarm on BMS side and the MIST-2 started instead. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623092&prj=548&rqi=RG7ylQbRiqmQWUmvLwYrXzWSdM
GI-072 | f197983b-5295-4b35-8200-052237772414 | TY15-2 | 548 | APAC | Closed | P2 Medium CX | SabinBasnet@commtechasia.com | 2026-05-25 04:00:00.000 +0400 | Commissioning Authority |  | Component Failure | Commissioning |  |  | equipment type |  |  |  |  | SAT : - Mechanical - (Mist System on Chiller) [NTTF/Carrel - 8-1-CH-1, 8-1-CH-2, 8-1-CH-3 &8-1-CH-4) - Cx3] During Mist operation check on chillers(8-1-CH-1, 8-1-CH-2, 8-1-CH-3 &8-1-CH-4) alarm signal was being received on BMS side for an instant only whenever mist operation was started. Due to which the mist pump was stopping soon afterwards. therefore the mist control operation couldnot be confirmed on time. (refer to issue GI-066) | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623022&prj=548&rqi=6rWXlwzl4ODXxUJs4Sjg0CQZVh
GI-071 | b20674c2-a0be-4485-9b43-2843ba3fd750 | TY15-2 | 548 | APAC | Closed | P3 Low CX | SabinBasnet@commtechasia.com | 2026-05-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | During Mist operation check on chillers, the nozzle head on the sprinklers pipe of mist system of 8-1-CH-12-12 got blown away while the mist system was on operation. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=623017&prj=548&rqi=A5QKke5iTlPs2sVrDbOB6cpuxc
GI-068 | 20ebcbe7-52a2-41ae-9d1f-4077695842cb | TY15-2 | 548 | APAC | Closed | P3 Low DCOS | SabinBasnet@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | During UPS No.5 IST Test6, during the STS automatic switching test, on the BMS side both the primary and redundant side sources were shown as supplying the output for 7-1-STS-12-U5-2-1. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622605&prj=548&rqi=DYOcHEo9gDK9toD18WP3rNCLT4
GI-069 | f95b5dd4-5acc-4719-92e8-62a1b6441f5a | TY15-2 | 548 | APAC | Closed | P3 Low CX | SabinBasnet@commtechasia.com | 2026-05-21 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | During UPS No.5 IST (Test9: Fire system test) while deactivating the central fire system control the BMS side control was also disabled mistakely so the fire alarm did not show up on BMS | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=622607&prj=548&rqi=YuTACAOlCxumCaVaXqeMzAarfn
GI-066 | bae94af7-36d7-499a-a95a-a2d6c39c5f6f | TY15-2 | 548 | APAC | Closed | P3 Low CX | christiandupalco@commtechasia.com | 2026-03-17 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | SAT-Chiller system-regarding the mist system (æ•£æ°´) , NTT-F plans to interchange the Solenoid Valves and Low Switches location on all chillers due to recurring alarms. However, parts must be ordered from Italy (unavailable in Japan), causing procurement delays. They admit this may push completion beyond the end-March deadline, despite their efforts. Requested action: They must submit a report detailing their exact plan and schedule immediately. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=615793&prj=548&rqi=VJa9RcFTLFl3cpe7MgHHXiwxsV
GI-064 | b6280f97-5cce-451b-908a-66948be50eaa | TY15-2 | 548 | APAC | Closed | P3 Low DCOS | SabinBasnet@commtechasia.com | 2026-03-04 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | During STS load test, Analog values did not match during communication between the STS and BMS. During testing, when switching communication mapping between the old and new addresses, the old address was considered even when the new address was correct. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614686&prj=548&rqi=iPjpbW5mhFDYs6Il4Oes4wkWBH
GI-063 | a11a66f0-6123-41a6-967e-da019d8af320 | TY15-2 | 548 | APAC | Closed | P3 Low DCOS | SabinBasnet@commtechasia.com | 2026-03-02 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | During the alarm verification on STS, the General Alarm on the BMS screen for the STS ((5-1-STS-12-U5-2-2) was not showing up even though the alarm was produced on the equipment side. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=483414&prj=548&rqi=PDfcjX5WZgrGu8jblEMhKxb6yK
GI-062 | 82814f93-c0bf-4be9-b5fe-68a4d057f3a3 | TY15-2 | 548 | APAC | Closed | P3 Low DCOS | SabinBasnet@commtechasia.com | 2026-02-25 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | BMS Graphics Errors: 1.On the Generator (No. 3, 4) BMS screen, the [Synchronizing] setting for DEG No. 4 was not set. The point during synchronization verification was selected incorrectly, so the [Synchronization] indicator did not light up. 2. On the Generator (No. 5, 6) Gen No. 5 screen, [Manual] was displayed even though the mode was automatic. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=204136&prj=548&rqi=fxfuzpKhx73o80783Vr8rztA43
GI-060 | c7b4a108-4e5d-494e-b70f-da9c13d6cb4b | TY15-2 | 548 | APAC | Closed | P3 Low CX | SabinBasnet@commtechasia.com | 2026-02-02 04:00:00.000 +0400 | Commissioning Authority |  | Commissioning Issue | Commissioning | [7 empty] | On the display panel of generator circuit breaker board (1-1GSB-GCBP-4) & (1-1GSB-GCBP-5) of DEG no. 4 &5, the output voltage and current to theã€€DEG control panel (1-1-GSB-CP-4&5) through transformer was displayed as zero although the output on the control panel display was okay. The same problem might be there on other DEG system as well so it is necessary to check the previously commissioned DEG No. 1, 2&3. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=198089&prj=548&rqi=apavTzxTZoiZiSXzQeTEjoPETD
GI-127 | 245613ec-4598-485f-b7e6-d709ac8e5820 | ZH04-6 | 555 | N-EMEA | Open | P3 Low CX | gmcdonough@global-cxm.com | 2026-09-18 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  | Mechanical â€“ Water | system | CHW System |  |  |  | DP sensors in faut not working correctly when moved on the ground floor, which halted works for CRAH integration. Aware works are being carried out on them this week. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=638649&prj=555&rqi=EWKMR8KMTavbzSWTtQSe7Bsamq | https://equinix.facilitygrid.co.uk/x/project/555/system/11930
GI-125 | 6738bf82-f35a-4dbc-b08e-476571fb81c7 | ZH04-6 | 555 | N-EMEA | Open | P3 Low CX | agryszko@global-cxm.com | 2026-09-04 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | Permament label with ID name missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636842&prj=555&rqi=XCXg1yso2DDBkTjjhg4NyGvxNg
GI-124 | 3f53a728-e424-4d0b-81f6-214c5c063783 | ZH04-6 | 555 | N-EMEA | Open | P3 Low CX | agryszko@global-cxm.com | 2026-09-04 04:00:00.000 +0400 | General Contractor |  | Labelling | Commissioning |  |  | equipment type |  |  |  |  | Permament label with ID name missing | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636841&prj=555&rqi=EiTs55TjEFpQHvJqAbwdoZ8U2U
FPT-98-002 | d0d7b63b-91e7-4169-9f9d-36b9bf697247 | ZH04-6 | 555 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Multi-Discipline | system | Migration A |  |  |  | fuse blown on A2 during switch to put IT load on batteries | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636761&prj=555&rqi=akkUnyxoUQH68UDV5RDiR8GI0g | https://equinix.facilitygrid.co.uk/x/project/555/system/14760
FPT-98-001 | ee30f8d1-b547-4c9d-8588-8af8f92e0136 | ZH04-6 | 555 | N-EMEA | Closed | P3 Low CX | gmcdonough@global-cxm.com | 2026-09-03 04:00:00.000 +0400 | General Contractor | L4 | Commissioning Issue | Commissioning |  | Multi-Discipline | system | Migration A |  |  |  | potential issue during switching A5. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636759&prj=555&rqi=ai9SpgdECI0Q1mCiZPFayakOsl | https://equinix.facilitygrid.co.uk/x/project/555/system/14760
GI-122 | 595c10bf-0b8c-4675-8614-56e531c8a24e | ZH04-6 | 555 | N-EMEA | Open | P3 Low CX | gmcdonough@global-cxm.com | 2026-09-03 04:00:00.000 +0400 | General Contractor |  | Commissioning Issue | Commissioning |  |  | equipment type |  |  |  |  | All test conducted on CRAH-03-13 and only the fan failure test failed. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636680&prj=555&rqi=w74aU8bkJ0GyOtcCFzK5T3muMH
GI-123 | 6ed13b7f-c489-45f2-91c2-9746bb3f9d14 | ZH04-6 | 555 | N-EMEA | Open | P3 Low CX | gmcdonough@global-cxm.com | 2026-09-03 04:00:00.000 +0400 | General Contractor |  | DCOS Comms Issue/Fault | DCOS |  |  | equipment type |  |  |  |  | During the power failure test, when the alternative power supply was open the alarm info on Vertiv control side stats fire alarm in steady alternative power supply open. Seems like an addressing issue, potentially related to the software upgrade? | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=636683&prj=555&rqi=w6EkdbDSWzGzsTlIaIab6WsysQ
GI-121 | 488dc7af-d852-43a5-bc36-aaf7f24a92ea | ZH04-6 | 555 | N-EMEA | Open | P1 High CX | agryszko@global-cxm.com | 2026-08-27 04:00:00.000 +0400 | Equinix Project Manager |  | Component/Equipment Failure | Commissioning | [7 empty] | During RMU testing GEN tripped on overcurrent without any load on it, during investigation, burned spots on Step-up transformer were identified. Equipment on that connection is being investigated by Siemens/Schneider/Avesco, The asset will be updated as soon the root cause of the issue is identified. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635579&prj=555&rqi=1UzapIclhlcOlkmdYqgzPYzUT7
GI-120 | cb59b977-1230-470e-adca-82d7bb147663 | ZH04-6 | 555 | N-EMEA | Open | P2 Medium CX | gmcdonough@global-cxm.com | 2026-08-25 04:00:00.000 +0400 | General Contractor |  | Incomplete Connections | Commissioning |  |  | equipment type |  |  |  |  | Shielding cable on the CRAH DB not completely sleeved from cable to earth bar. This is an issue on EVERY ground floor CRAH, not on one or 2 but on all. Hardly any ferrules attached to the sleeving either to the earth bar, again need to be rectified before powered on. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=635034&prj=555&rqi=LkmVPcDQheHD4b10r5wm3tI6DS
GI-108 | e49ad94e-bcfb-439a-8ea7-2ba69a8c0ebf | ZH04-6 | 555 | N-EMEA | Closed | P2 Medium CX | agryszko@global-cxm.com | 2026-04-21 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Installation Not Correct | Commissioning |  |  | equipment type |  |  |  |  | Trip Lockout not working properly for intertrip. Breaker opens properly, but operator is able to close it immediately, without clearing the lockout. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=618823&prj=555&rqi=igRMcR4sv2ImmS2ad7ExaRsvrs
GI-104 | d3c261b8-95e8-4ae7-86e2-7d9d9f467cc4 | ZH04-6 | 555 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-03-04 04:00:00.000 +0400 | General Contractor |  | Installation Not Correct | Commissioning | [7 empty] | Cable connections into the 3rd floor CRAH's Glands are lose as the cable is smaller than the gland size | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=614684&prj=555&rqi=ab7VARDNtUuVv8y9p7Eez8BDkS
GI-106 | 0554d30a-778b-4c62-8820-06a995e2c8dc | ZH04-6 | 555 | N-EMEA | Open | P2 Medium DCOS | Matt.Harker@eu.equinix.com | 2026-02-24 04:00:00.000 +0400 | Equinix Project Manager |  | Commissioning Issue | Commissioning | [7 empty] | Major incident occurred when Siemens attempted to upload additional pieces of Equipment to the live system: Extract of RCA issued by Siemens below: In calendar week 8, the PLC CPU (S7-400) had to be set to "Stop" mode for loading new components as part of project ZH4.6 (project ZH4.6 relevant). After the software download and the restart of the CPU, a MODBUS RTU communication string to several CRAHs could not be put back into operation (existing BMS relevant). This communication strand belongs to the investment part "legacy system" and comes from earlier projects. Siemens started the investigation in coordination with Mr. Milovan Kovacevic (email of 19.02.2026, 15:31). The aim was on the one hand to restart the aforementioned MODBUS RTU string and on the other hand to identify the cause of the fault (existing BMS relevant). In the course of the recommissioning of this mentioned string and the troubleshooting, a firmware update was prepared for the affected legacy part of the BMS. This update was planned for 02/24/2026 and related exclusively to the legacy part of the BMS. The installation of the FW update was carried out exclusively on the PLC level via Profibus (ZH4.6 no longer has Profibus but exclusively Profinet). Further details can be found in the document "Technical Root Cause Analysis Modbus RTU.pdf". Resolution to be added once finalised. | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=616273&prj=555&rqi=gqZwU1uMU8MXNGExg1ljdzI7tT
GI-100 | 14811bde-43bb-4f2c-98e9-838b0f825f01 | ZH04-6 | 555 | N-EMEA | Closed | P3 Low CX | sdreik@global-cxm.com | 2026-02-20 04:00:00.000 +0400 | Manufacturer, Vendor, Supplier |  | Design not as Specified | Design |  | Fuel | system | Fuel System |  |  |  | In the Fuel system SOO, the day tanks have 5 different Fuel level sensor and values. However, on site only 3 sensors are in the tanks. Clarification needed | https://equinix.facilitygrid.co.uk/inquire?action=eiss&PID=199659&prj=555&rqi=D6aixkc0NCgsKAhbGmdQBcWw3c | https://equinix.facilitygrid.co.uk/x/project/555/system/13439